## Active Projects
State of Nevada
Active Project List
State Public Works Division
Facility Condition Analysis
March 11, 2021
This is a living document. As projects are verified as completed, they could be removed from the report. As projects are recommended, they could be added to the report. This report is effective as of the date listed above.
Project Number | Project Title | FCA Building Number | Project Description | Building Name | Site Number | Department | Division | Agency | City | Year Built | Square Feet | Survey Date | Priority Class Description | Priority Class Description2 | Priority Class Code | Construction Cost
9939SIT2 | REMOVE MOBILES FROM SITE | 9939 | There are four mobile homes located on site that are being used as office space. These manufactured homes are not designed or intended for non-residential use. It would be cost prohibitive to bring the units into compliance with commercial coach requirements, to allow them to meet code and be used as offices. This project provides costs for disconnecting utilities, removal of the skirting, overhangs and steps, and removing the trailers from the site. Some of these costs could be recovered by selling the units to a mobile home dealer. | NEVADA ARMY NATIONAL GUARD CC SITE | 9939 | Admin | PubWorks | B&G | Carson City |  | 0 | 2002-06-17 | Immediate to Two Years | Currently Critical | 1 | 11542.4638
2313EXT91 | EXTERIOR FINISHES | 2313 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. | QUONSET #14 (VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1960 | 500 | 2003-01-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
2313LGT1 | LONG-TERM NEEDS | 2313 | Projects in this category address possible long term needs of the facility. This does not represent a cost for all future maintenance but is a budgetary number for future Capital Improvement projects related to maintenance. The cyclical treatment of the building exterior and interior is very important to help maintain the finish, weather proofing, integrity and appearance of the building. This treatment does not include the roofing material itself but it should include everything that has to do with water proofing the building envelope including painting or staining, sealing, repair, and caulking where applicable; for example, around all windows, flashing, fixtures, sills, etc. This also includes interior applied finishes such as paint, grout, caulking, etc. Special attention should be paid to areas that are exposed to moisture. This project also accounts for possible system replacements. | QUONSET #14 (VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1960 | 500 | 2003-01-10 | Four to Ten Years | Long-Term Needs | 3 | 1000
9955LGT1 | LONG-TERM NEEDS | 9955 | Projects in this category address possible long term needs of the site. This does not represent a cost for all future maintenance but is a budgetary number for future Capital Improvement projects related to maintenance. This project accounts for possible system repair or replacement, and cyclical maintenance, including the parking lots, sidewalks, fences, and other site systems. | NORTHERN NEVADA CHILDREN'S HOME SITE | 9955 | Admin | PubWorks | B&G | Carson City | 0 |  | 2003-01-10 | Four to Ten Years | Long-Term Needs | 3 | 100000
9955SIT1 | INSTALL EXTERIOR SITE LIGHTING | 9955 | This project recommends installing general security lighting fixtures around the parking areas and paved portions of the site. Cost includes light fixtures, wiring, trenching and installation, based on a 20 foot pole. Work should be performed prior to or concurrent with parking lot replacement. | NORTHERN NEVADA CHILDREN'S HOME SITE | 9955 | Admin | PubWorks | B&G | Carson City | 0 |  | 2003-01-10 | Immediate to Two Years | Currently Critical | 1 | 30000
9955SIT7 | SITE DRAINAGE ISSUES | 9955 | A number of the buildings have moisture damage due to improper drainage. The offices have problems with irrigation runoff, rain and snow melt collecting in the courtyards or draining into the crawl spaces under the buildings. The courtyard concrete patios are cracked and buckling, which adds to these problems. This project recommends gutters be installed, courtyard patios demolished and re-poured, and the grade re-worked to promote drainage away from the buildings. Additional work will be required to transport the drainage to a storm drain or other system to minimize localized flooding. | NORTHERN NEVADA CHILDREN'S HOME SITE | 9955 | Admin | PubWorks | B&G | Carson City | 0 |  | 2003-01-10 | Immediate to Two Years | Currently Critical | 1 | 150000
9955SIT5 | REMOVE PLANTERS | 9955 | Several buildings at the site have planters that are elevated a few feet up onto the exterior wall. This practice promotes water infiltration through the side of the building and has been known to cause mold growth along the exterior walls of buildings. There is evidence of recurring water damage on the interior wall finishes in several locations. This project recommends that the planters be removed as soon as possible. | NORTHERN NEVADA CHILDREN'S HOME SITE | 9955 | Admin | PubWorks | B&G | Carson City | 0 |  | 2003-01-10 | Immediate to Two Years | Currently Critical | 1 | 5000
9955PLM2 | BACKFLOW ASSEMBLY, VAULT, AND POWER | 9955 | State Health law now mandates backflow prevention on domestic water lines and fire sprinkler or standpipe lines. This project makes allowance for installation of a 6" reduced pressure backflow prevention assembly, required fittings, an above ground vault, and allowance for 200 feet of 1" conduit to provide power for the required heat source inside the vault. This installation will serve the site. | NORTHERN NEVADA CHILDREN'S HOME SITE | 9955 | Admin | PubWorks | B&G | Carson City | 0 |  | 2003-01-10 | Immediate to Two Years | Currently Critical | 1 | 26000
9955SIT6 | REPLACE SANITARY SEWER | 9955 | The sanitary sewer lines are original to the site and showing evidence of partial collapse and failure. The vitreous clay piping has cracked, hubs have separated, and tree roots have infiltrated in a number of locations, contributing to problems. This project recommends the entire system be replaced. Additional monies are included to replace the building laterals. Costs were developed from a similar project at the Stewart Facility, and is based on an 8" main and 4" or 6" laterals. | NORTHERN NEVADA CHILDREN'S HOME SITE | 9955 | Admin | PubWorks | B&G | Carson City | 0 |  | 2003-01-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 550000
9955ADA1 | ADA PARKING RE-STRIPING | 9955 | The accessible parking area striping is fading, and is becoming difficult to identify. The area does not have the proper signage identifying the parking space as accessible. CABO/ANSI A117.1 - 1992 Section 4.6.2 states, "...accessible parking spaces shall be identified by a sign showing the international symbol of accessibility..." The lot will be re-striped and accessible routes of travel identified. This project covers up to 4 spaces. Signage is included. ADA parking is required at the front parking lot, serving the Boys and Girls Club, Volunteers of America and Hispanic Services, and the rear parking lot, serving Child and Family Services offices. These costs were developed from the RS Means ADA Compliance Pricing Guide. | NORTHERN NEVADA CHILDREN'S HOME SITE | 9955 | Admin | PubWorks | B&G | Carson City | 0 |  | 2003-01-10 | Immediate to Two Years | Currently Critical | 1 | 4000
9955SIT3 | SIDEWALK REPLACEMENT | 9955 | The existing sidewalks serving buildings on this site have deteriorated and are failing. In some areas cracks wider than four inches have been identified, and there is substantial settling in a number of locations. This project addresses removal and replacement of existing sidewalks as needed. The sidewalks should include flared curb cuts for site accessibility. | NORTHERN NEVADA CHILDREN'S HOME SITE | 9955 | Admin | PubWorks | B&G | Carson City | 0 |  | 2003-01-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 140000
9955PLM1 | INSTALL WATER SHUT-OFF VALVES TO EACH BUILDING | 9955 | The site has a central water shut-off. In the event that plumbing work needs to be done that requires the water to be turned off, most of the buildings on the site are without water. The Uniform Plumbing Code (UPC) states in Section 605.2, "...water piping supplying more than one building on any one premises shall be equipped with a separate full way valve to each building, so arranged that the water supply can be turned on or off to any individual or separate building..." It is recommended that a shut-off valve be installed on the remainder of the buildings that have water service to them. | NORTHERN NEVADA CHILDREN'S HOME SITE | 9955 | Admin | PubWorks | B&G | Carson City | 0 |  | 2003-01-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
9955SIT4 | TRIM OR REMOVE TREES ADJOINING BUILDINGS | 9955 | Several of the buildings have trees which are growing up against the structures. The trees move in windy conditions, rubbing the roofs, which can cause premature failure of system and voiding roof warranties. The root systems are causing shifting and heaving of foundations and sidewalks, creating unsafe conditions. There are also several large trees that are in need of trimming. This lack of maintenance could become a safety issue. There were numerous branches on the ground at the time of survey and damage to a fence had occurred due to a falling tree. This project recommends that these issues be addressed, before additional damage is done. Carson City is responsible for site landscaping and maintenance, and there may be some cost sharing or savings working with city staff to address this issue. | NORTHERN NEVADA CHILDREN'S HOME SITE | 9955 | Admin | PubWorks | B&G | Carson City | 0 |  | 2003-01-10 | Immediate to Two Years | Currently Critical | 1 | 25000
9955SIT2 | REPLACE ASPHALT PAVING | 9955 | The asphalt at the site is failing, with significant alligatoring and cracks observed. The macadam has deteriorated to the point that it is no longer viable. This project covers the removal and replacement of existing blacktop for parking and site access, and additional parking at the main parking areas. | NORTHERN NEVADA CHILDREN'S HOME SITE | 9955 | Admin | PubWorks | B&G | Carson City | 0 |  | 2003-01-10 | Immediate to Two Years | Currently Critical | 1 | 300000
0298LGT1 | LONG-TERM NEEDS | 0298 | Projects in this category address possible long term needs of the facility. This does not represent a cost for all future maintenance but is a budgetary number for future Capital Improvement projects related to maintenance. The cyclical treatment of the building exterior and interior is very important to help maintain the finish, weather proofing, integrity and appearance of the building. This treatment does not include the roofing material itself but it should include everything that has to do with water proofing the building envelope including painting or staining, sealing, repair, and caulking where applicable; for example, around all windows, flashing, fixtures, sills, etc. This includes interior applied finishes such as paint, grout, caulking, etc. Special attention should be paid to areas that are exposed to moisture. This project also accounts for scheduled replacement of flooring, water heaters, HVAC, and the like. | ICE HOUSE #7 (VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1950 | 1700 | 2003-01-10 | Four to Ten Years | Long-Term Needs | 3 | 17000
0301EXT2 | REPLACE ROOF | 0301 | The existing roof on this building was in poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 15 years. The roof warranty expires at the end of the same time frame. It is recommended that this building be re-roofed consistent with the roofing program and the end of the warranty period. | VOA FOSTER CARE HOUSING #6(VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1960 | 2760 | 2003-01-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14000
0301LGT1 | LONG-TERM NEEDS | 0301 | Projects in this category address possible long term needs of the facility. This does not represent a cost for all future maintenance but is a budgetary number for future Capital Improvement projects related to maintenance. The cyclical treatment of the building exterior and interior is very important to help maintain the finish, weather proofing, integrity and appearance of the building. This treatment does not include the roofing material itself but it should include everything that has to do with water proofing the building envelope including painting or staining, sealing, repair, and caulking where applicable; for example, around all windows, flashing, fixtures, sills, etc. This includes interior applied finishes such as paint, grout, caulking, etc. Special attention should be paid to areas that are exposed to moisture. This project also accounts for scheduled replacement of flooring, water heaters, HVAC, and the like. | VOA FOSTER CARE HOUSING #6(VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1960 | 2760 | 2003-01-10 | Four to Ten Years | Long-Term Needs | 3 | 28000
0301EXT1 | EXTERIOR ENERGY RETROFIT | 0301 | The building is constructed of concrete masonry units (CMU) with no insulation. The windows are original to the building, and of single pane construction. Buildings of this type are not energy efficient. This project recommends adding an exterior insulating finish system (EIFS) over the CMU, augmenting the windows with a removable storm-type window system, and replacing the exterior doors. This work will make the building more energy efficient. If the EIFS system is not installed, the building will require exterior finishes, caulking around windows and doors, and similar improvements. This work should be performed following surface preparation and repair or replacement of fascias and overhangs. Costs would run approximately $5.00 per square foot. | VOA FOSTER CARE HOUSING #6(VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1960 | 2760 | 2003-01-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 56000
0300EXT1 | EXTERIOR ENERGY RETROFIT | 0300 | The building is constructed of concrete masonry units (CMU) with no insulation. The windows are original to the building, and of single pane construction. Buildings of this type are not energy efficient. This project recommends adding an exterior insulating finish system (EIFS) over the CMU, augmenting the windows with an exterior mounted, removable storm-type window system, and replacing the exterior doors. This work will make the building more energy efficient. If the EIFS system is not installed, the building will require exterior finishes, caulking around windows and doors, and similar improvements. This work should be performed following surface preparation and repair or replacement of fascias and overhangs. Costs would run approximately $5.00 per square foot. | RUBY STATION #2 (VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1960 | 2760 | 2003-01-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 56000
0300LGT1 | LONG-TERM NEEDS | 0300 | Projects in this category address possible long term needs of the facility. This does not represent a cost for all future maintenance but is a budgetary number for future Capital Improvement projects related to maintenance. The cyclical treatment of the building exterior and interior is very important to help maintain the finish, weather proofing, integrity and appearance of the building. This treatment does not include the roofing material itself but it should include everything that has to do with water proofing the building envelope including painting or staining, sealing, repair, and caulking where applicable; for example, around all windows, flashing, fixtures, sills, etc. This includes interior applied finishes such as paint, grout, caulking, etc. Special attention should be paid to areas that are exposed to moisture. This project also accounts for scheduled replacement of flooring, water heaters, HVAC, and the like. | RUBY STATION #2 (VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1960 | 2760 | 2003-01-10 | Four to Ten Years | Long-Term Needs | 3 | 28000
0300ELE1 | MINOR ELECTRICAL UPGRADE | 0300 | This building was constructed as a residence and lacks the electrical capacity needed in a modern office. This project will provide for additional outlets and electrical capacity, as well as some expansion capability. Additional funds are included to replace and augment exterior lighting on and around the building. | RUBY STATION #2 (VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1960 | 2760 | 2003-01-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 13000
0299ELE1 | MINOR ELECTRICAL UPGRADE | 0299 | This building was constructed as a residence and lacks the electrical capacity needed in a modern office. This project will provide for additional outlets and electrical capacity, as well as some expansion capability. Additional funds are included to replace and augment exterior lighting on and around the building. | FRIDAY STATION #11 (VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1960 | 2760 | 2003-01-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 13000
0301ELE1 | MINOR ELECTRICAL UPGRADE | 0301 | This building was constructed as a residence and lacks the electrical capacity needed in a modern office. This project will provide for additional outlets and electrical capacity, as well as some expansion capability. Additional funds are included to replace and augment exterior lighting on and around the building. | VOA FOSTER CARE HOUSING #6(VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1960 | 2760 | 2003-01-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 13000
0299EXT1 | EXTERIOR ENERGY RETROFIT | 0299 | The building is constructed of concrete masonry units (CMU) with no insulation. The windows are original to the building, and of single pane construction. Buildings of this type are not energy efficient. This project recommends adding an exterior insulating finish system (EIFS) over the CMU, augmenting the windows with an exterior mounted, removable storm-type window system, and replacing the exterior doors. This work will make the building more energy efficient. If the EIFS system is not installed, the building will require exterior finishes, caulking around windows and doors, and similar improvements. This work should be performed following surface preparation and repair or replacement of fascias and overhangs. Costs would run approximately $5.00 per square foot. | FRIDAY STATION #11 (VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1960 | 2760 | 2003-01-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 56000
0302EXT1 | EXTERIOR ENERGY RETROFIT | 0302 | The building is constructed of concrete masonry units (CMU) with no insulation. The windows are original to the building, and of single pane construction. Buildings of this type are not energy efficient. This project recommends adding an exterior insulating finish system (EIFS) over the CMU, augmenting the windows with a removable storm-type window system, and replacing the exterior doors. This work will make the building more energy efficient. If the EIFS system is not installed, the building will require exterior finishes, caulking around windows and doors, and similar improvements. This work should be performed following surface preparation and repair or replacement of fascias and overhangs. Costs would run approximately $5.00 per square foot. | SAND SPRINGS STATION #5 (VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1960 | 2760 | 2003-01-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 56000
0297SFT1 | INSTALL EMERGENCY EGRESS LIGHTING | 0297 | There are older emergency egress lighting in this building. These units have a finite lifespan, and this project recommends the installation of new egress lights along the main exit routes when reoccupying the building.. | REHAB BUILDING #3 (VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1975 | 2400 | 2003-01-10 | Immediate to Two Years | Currently Critical | 1 | 4000
0297EXT1 | EXTERIOR FINISHES | 0297 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. | REHAB BUILDING #3 (VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1975 | 2400 | 2003-01-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8500
0297EXT2 | REPLACE ROOF | 0297 | The existing roof on this building was in poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 15 years. This roof appears to be at least that old. It is recommended that this building be re-roofed consistent with the roofing program and the end of the warranty period. | REHAB BUILDING #3 (VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1975 | 2400 | 2003-01-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
0299LGT1 | LONG-TERM NEEDS | 0299 | Projects in this category address possible long term needs of the facility. This does not represent a cost for all future maintenance but is a budgetary number for future Capital Improvement projects related to maintenance. The cyclical treatment of the building exterior and interior is very important to help maintain the finish, weather proofing, integrity and appearance of the building. This treatment does not include the roofing material itself but it should include everything that has to do with water proofing the building envelope including painting or staining, sealing, repair, and caulking where applicable; for example, around all windows, flashing, fixtures, sills, etc. This includes interior applied finishes such as paint, grout, caulking, etc. Special attention should be paid to areas that are exposed to moisture. This project also accounts for scheduled replacement of flooring, water heaters, HVAC, and the like. | FRIDAY STATION #11 (VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1960 | 2760 | 2003-01-10 | Four to Ten Years | Long-Term Needs | 3 | 28000
0303LGT1 | LONG-TERM NEEDS | 0303 | Projects in this category address possible long term needs of the facility. This does not represent a cost for all future maintenance but is a budgetary number for future Capital Improvement projects related to maintenance. The cyclical treatment of the building exterior and interior is very important to help maintain the finish, weather proofing, integrity and appearance of the building. This treatment does not include the roofing material itself but it should include everything that has to do with water proofing the building envelope including painting or staining, sealing, repair, and caulking where applicable; for example, around all windows, flashing, fixtures, sills, etc. This includes interior applied finishes such as paint, grout, caulking, etc. Special attention should be paid to areas that are exposed to moisture. This project also accounts for scheduled replacement of flooring, water heaters, HVAC, and the like. | B&G CLUB/HISP SERVICES #10 (VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1960 | 2269 | 2003-01-10 | Four to Ten Years | Long-Term Needs | 3 | 23000
0307EXT1 | EXTERIOR FINISHES | 0307 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. This project will not be needed if the asbestos containing siding is abated and replaced. | GARAGE #13 (VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1960 | 2000 | 2003-01-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7000
0307LGT1 | LONG-TERM NEEDS | 0307 | Projects in this category address possible long term needs of the facility. This does not represent a cost for all future maintenance but is a budgetary number for future Capital Improvement projects related to maintenance. The cyclical treatment of the building exterior and interior is very important to help maintain the finish, weather proofing, integrity and appearance of the building. This treatment does not include the roofing material itself but it should include everything that has to do with water proofing the building envelope including painting or staining, sealing, repair, and caulking where applicable; for example, around all windows, flashing, fixtures, sills, etc. This also includes interior applied finishes such as paint, grout, caulking, etc. Special attention should be paid to areas that are exposed to moisture. This project also accounts for possible system replacements. | GARAGE #13 (VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1960 | 2000 | 2003-01-10 | Four to Ten Years | Long-Term Needs | 3 | 10000
0305LGT1 | LONG-TERM NEEDS | 0305 | Projects in this category address possible long term needs of the facility. This does not represent a cost for all future maintenance but is a budgetary number for future Capital Improvement projects related to maintenance. The cyclical treatment of the building exterior and interior is very important to help maintain the finish, weather proofing, integrity and appearance of the building. This treatment does not include the roofing material itself but it should include everything that has to do with water proofing the building envelope including painting or staining, sealing, repair, and caulking where applicable; for example, around all windows, flashing, fixtures, sills, etc. This includes interior applied finishes such as paint, grout, caulking, etc. Special attention should be paid to areas that are exposed to moisture. This project also accounts for scheduled replacement of flooring, water heaters, HVAC, and the like. | BUCKLAND STATION #4 (VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1965 | 2425 | 2003-01-10 | Four to Ten Years | Long-Term Needs | 3 | 24000
0305EXT1 | EXTERIOR ENERGY RETROFIT | 0305 | The building is constructed of concrete masonry units (CMU) with no insulation. The windows are original to the building, and of single pane construction. Buildings of this type are not energy efficient. This project recommends adding an exterior insulating finish system (EIFS) over the CMU, augmenting the windows with a removable storm-type window system, and replacing the exterior doors. This work will make the building more energy efficient. If the EIFS system is not installed, the building will require exterior finishes, caulking around windows and doors, and similar improvements. This work should be performed following surface preparation and repair or replacement of fascias and overhangs. Costs would run approximately $5.00 per square foot. | BUCKLAND STATION #4 (VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1965 | 2425 | 2003-01-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 49000
0305ELE1 | MINOR ELECTRICAL UPGRADE | 0305 | This building was constructed as a residence and lacks the electrical capacity needed in a modern office. This project will provide for additional outlets and electrical capacity, as well as some expansion capability. Additional funds are included to replace and augment exterior lighting on and around the building. | BUCKLAND STATION #4 (VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1965 | 2425 | 2003-01-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
0304ELE1 | MINOR ELECTRICAL UPGRADE | 0304 | This building was constructed as a residence and lacks the electrical capacity needed in a modern office. This project will provide for additional outlets and electrical capacity, as well as some expansion capability. Additional funds are included to replace and augment exterior lighting on and around the building. | MTN. SPRINGS STATION #1 (VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1963 | 2425 | 2003-01-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
0302ELE1 | MINOR ELECTRICAL UPGRADE | 0302 | This building was constructed as a residence and lacks the electrical capacity needed in a modern office. This project will provide for additional outlets and electrical capacity, as well as some expansion capability. Additional funds are included to replace and augment exterior lighting on and around the building. | SAND SPRINGS STATION #5 (VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1960 | 2760 | 2003-01-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 13000
0304EXT1 | EXTERIOR ENERGY RETROFIT | 0304 | The building is constructed of concrete masonry units (CMU) with no insulation. The windows are original to the building, and of single pane construction. Buildings of this type are not energy efficient. This project recommends adding an exterior insulating finish system (EIFS) over the CMU, augmenting the windows with a removable storm-type window system, and replacing the exterior doors. This work will make the building more energy efficient. If the EIFS system is not installed, the building will require exterior finishes, caulking around windows and doors, and similar improvements. This work should be performed following surface preparation and repair or replacement of fascias and overhangs. Costs would run approximately $5.00 per square foot. | MTN. SPRINGS STATION #1 (VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1963 | 2425 | 2003-01-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 49000
0295PLM1 | REPLACE WATER HEATERS | 0295 | The average life span of a water heater is eight to ten years. With the passage of time and constant use, these units are showing signs of wear. It is recommended that new on-demand appliances be installed for efficient use of energy. | BOYS & GIRLS CLUB GYM #12 (VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1898 | 2925 | 2003-01-10 | Immediate to Two Years | Currently Critical | 1 | 2000
0303ELE1 | MINOR ELECTRICAL UPGRADE | 0303 | This building was constructed as a residence and lacks the electrical capacity needed in a modern office. This project will provide for additional outlets and electrical capacity, as well as some expansion capability. Additional funds are included to replace and augment exterior lighting on and around the building. | B&G CLUB/HISP SERVICES #10 (VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1960 | 2269 | 2003-01-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
0303EXT2 | REPLACE ROOF | 0303 | The roof on this building was in poor condition at the time of the survey. Recent storms damaged the roof, there are missing shingles, and active leaks are reported by the occupants. The statewide roofing program has set the useful life of an average roof at 15 years. The roof warranty expires at the end of the same time frame. It is recommended that this building be re-roofed in the next year to be consistent with the roofing program and the end of the warranty period. Additional monies are included to replace some fascia and missing attic vent screens. | B&G CLUB/HISP SERVICES #10 (VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1960 | 2269 | 2003-01-10 | Immediate to Two Years | Currently Critical | 1 | 15000
0303EXT1 | EXTERIOR FINISHES | 0303 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. | B&G CLUB/HISP SERVICES #10 (VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1960 | 2269 | 2003-01-10 | Immediate to Two Years | Currently Critical | 1 | 8000
0302LGT1 | LONG-TERM NEEDS | 0302 | Projects in this category address possible long term needs of the facility. This does not represent a cost for all future maintenance but is a budgetary number for future Capital Improvement projects related to maintenance. The cyclical treatment of the building exterior and interior is very important to help maintain the finish, weather proofing, integrity and appearance of the building. This treatment does not include the roofing material itself but it should include everything that has to do with water proofing the building envelope including painting or staining, sealing, repair, and caulking where applicable; for example, around all windows, flashing, fixtures, sills, etc. This includes interior applied finishes such as paint, grout, caulking, etc. Special attention should be paid to areas that are exposed to moisture. This project also accounts for scheduled replacement of flooring, water heaters, HVAC, and the like. | SAND SPRINGS STATION #5 (VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1960 | 2760 | 2003-01-10 | Four to Ten Years | Long-Term Needs | 3 | 28000
0295EXT2 | REROOF BUILDING | 0295 | The roof is showing signs of wear and deterioration, and is reaching the end of its useful life. This report recommends that the roof be replaced. | BOYS & GIRLS CLUB GYM #12 (VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1898 | 2925 | 2003-01-10 | Immediate to Two Years | Currently Critical | 1 | 29000
0302EXT2 | REPLACE ROOF | 0302 | The existing roof on this building was in poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 15 years. The roof warranty expires at the end of the same time frame. It is recommended that this building be re-roofed consistent with the roofing program and the end of the warranty period. | SAND SPRINGS STATION #5 (VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1960 | 2760 | 2003-01-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14000
0304LGT1 | LONG-TERM NEEDS | 0304 | Projects in this category address possible long term needs of the facility. This does not represent a cost for all future maintenance but is a budgetary number for future Capital Improvement projects related to maintenance. The cyclical treatment of the building exterior and interior is very important to help maintain the finish, weather proofing, integrity and appearance of the building. This treatment does not include the roofing material itself but it should include everything that has to do with water proofing the building envelope including painting or staining, sealing, repair, and caulking where applicable; for example, around all windows, flashing, fixtures, sills, etc. This includes interior applied finishes such as paint, grout, caulking, etc. Special attention should be paid to areas that are exposed to moisture. This project also accounts for scheduled replacement of flooring, water heaters, HVAC, and the like. | MTN. SPRINGS STATION #1 (VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1963 | 2425 | 2003-01-10 | Four to Ten Years | Long-Term Needs | 3 | 24000
0295EXT1 | EXTERIOR FINISHES | 0295 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. | BOYS & GIRLS CLUB GYM #12 (VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1898 | 2925 | 2003-01-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
0295ENR1 | LIGHTING UPGRADE | 0295 | The building lighting fixtures are older T-12 fluorescent types and not energy efficient. This project will upgrade lighting fixtures to T-8 lamps with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. Sensors will be installed in restrooms and other low occupancy areas for additional savings. | BOYS & GIRLS CLUB GYM #12 (VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1898 | 2925 | 2003-01-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7000
0294EXT1 | EXTERIOR FINISHES | 0294 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. This project will not be needed if the asbestos containing siding is abated and replaced. | BOYS & GIRLS CLUB #9 (VACANT) | 9955 | Admin | PubWorks | B&G | Carson City |  | 4578 | 2003-01-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16000
0294HVA1 | REPLACE HVAC SYSTEM | 0294 | The building has an older HVAC system, which appears to be original to the building. The boiler is not operational, and has been disconnected, and this project recommends replacing the system. Most of the building rely on windows cooling units, which is not recommended under current energy guidelines. New hot water heaters and ducting will be needed. | BOYS & GIRLS CLUB #9 (VACANT) | 9955 | Admin | PubWorks | B&G | Carson City |  | 4578 | 2003-01-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 137000
0294ENR1 | LIGHTING UPGRADE | 0294 | The building lighting fixtures are older T-12 fluorescent types and not energy efficient. This project will upgrade lighting fixtures to T-8 lamps with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. Sensors will be installed in restrooms and other low occupancy areas for additional savings. | BOYS & GIRLS CLUB #9 (VACANT) | 9955 | Admin | PubWorks | B&G | Carson City |  | 4578 | 2003-01-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
0294LGT1 | LONG-TERM NEEDS | 0294 | Projects in this category address possible long term needs of the facility. This does not represent a cost for all future maintenance but is a budgetary number for future Capital Improvement projects related to maintenance. The cyclical treatment of the building exterior and interior is very important to help maintain the finish, weather proofing, integrity and appearance of the building. This treatment does not include the roofing material itself but it should include everything that has to do with water proofing the building envelope including painting or staining, sealing, repair, and caulking where applicable; for example, around all windows, flashing, fixtures, sills, etc. This also includes interior applied finishes such as paint, grout, caulking, etc. Special attention should be paid to areas that are exposed to moisture. This project also accounts for possible system replacements. | BOYS & GIRLS CLUB #9 (VACANT) | 9955 | Admin | PubWorks | B&G | Carson City |  | 4578 | 2003-01-10 | Four to Ten Years | Long-Term Needs | 3 | 23000
0294ELE1 | ELECTRICAL UPGRADE | 0294 | This building was constructed before the high demand for new types of electrical devices were needed. As time progressed, the building's electrical demand has changed. It is utilized to its current maximum potential. The electrical panels and receptacles are at their limit. It is recommended the entire system be upgraded to meet the evolving needs of the building. | BOYS & GIRLS CLUB #9 (VACANT) | 9955 | Admin | PubWorks | B&G | Carson City |  | 4578 | 2003-01-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 115000
0297LGT1 | LONG-TERM NEEDS | 0297 | Projects in this category address possible long term needs of the facility. This does not represent a cost for all future maintenance but is a budgetary number for future Capital Improvement projects related to maintenance. The cyclical treatment of the building exterior and interior is very important to help maintain the finish, weather proofing, integrity and appearance of the building. This treatment does not include the roofing material itself but it should include everything that has to do with water proofing the building envelope including painting or staining, sealing, repair, and caulking where applicable; for example, around all windows, flashing, fixtures, sills, etc. This includes interior applied finishes such as paint, grout, caulking, etc. Special attention should be paid to areas that are exposed to moisture. This project also accounts for scheduled replacement of flooring, water heaters, HVAC, and the like. | REHAB BUILDING #3 (VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1975 | 2400 | 2003-01-10 | Four to Ten Years | Long-Term Needs | 3 | 25000
0295LGT1 | LONG-TERM NEEDS | 0295 | Projects in this category address possible long term needs of the facility. This does not represent a cost for all future maintenance but is a budgetary number for future Capital Improvement projects related to maintenance. The cyclical treatment of the building exterior and interior is very important to help maintain the finish, weather proofing, integrity and appearance of the building. This treatment does not include the roofing material itself but it should include everything that has to do with water proofing the building envelope including painting or staining, sealing, repair, and caulking where applicable; for example, around all windows, flashing, fixtures, sills, etc. This also includes interior applied finishes such as paint, grout, caulking, etc. Special attention should be paid to areas that are exposed to moisture. This project also accounts for possible system replacements. | BOYS & GIRLS CLUB GYM #12 (VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1898 | 2925 | 2003-01-10 | Four to Ten Years | Long-Term Needs | 3 | 15000
2483EXT3 | TREATMENT OF EXTERIOR FINISHES | 2483 | At the time of the survey, the exterior block was beginning to deteriorate due to frost damage. It is important to maintain the finish, weather resistance and appearance of the building. This project includes items to protect the exterior building envelope other than the roof, including painting, staining, or other applied finishes, and sealant and gaskets in and around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. | RENO MOTOR POOL | 9846 | Admin | PubWorks | B&G | Reno | 1990 | 2155 | 2004-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8750
2483HVA1 | SYSTEM TUNE-UP | 2483 | The HVAC system shows evidence of considerable dirt in the ductwork and it is reported that the thermostat is out of calibration. This project would generally clean-up the system, tighten the spaces around the furnace filters, and recalibrate or replace the thermostat. | RENO MOTOR POOL | 9846 | Admin | PubWorks | B&G | Reno | 1990 | 2155 | 2004-10-19 | Four to Ten Years | Long-Term Needs | 3 | 2500
2483INT1 | REPLACE VINYL FLOORING | 2483 | The flooring finishes in this building are reaching the end of their useful life. It is recommended that the flooring and cove base in the building be replaced. This project includes minor repair of sub floor or surface preparation prior to installing new floor materials. | RENO MOTOR POOL | 9846 | Admin | PubWorks | B&G | Reno | 1990 | 2155 | 2004-10-19 | Four to Ten Years | Long-Term Needs | 3 | 1575
2483PLM1 | INSTALL BACKFLOW PREVENTER COVER | 2483 | The landscape irrigation system backflow preventer has recently been replaced due to freezing. This project would install an above ground vault, and allowance for 200 feet of 1" conduit to provide power for freeze protection. | RENO MOTOR POOL | 9846 | Admin | PubWorks | B&G | Reno | 1990 | 2155 | 2004-10-19 | Immediate to Two Years | Currently Critical | 1 | 7500
2483SEC1 | INSTALL FIRE ALARM CONTROL | 2483 | The building currently has only an exterior bell for fire notification. Due to the remote location, there is concern that in the event of a fire, no one will hear the bell . This project would install a fire alarm panel with dial-up notification to the local responder. | RENO MOTOR POOL | 9846 | Admin | PubWorks | B&G | Reno | 1990 | 2155 | 2004-10-19 | Immediate to Two Years | Currently Critical | 1 | 8500
2483EXT2 | INSTALL ROOF ACCESS | 2483 | At the time of the survey, there was no built-in roof access. This project would install a roof access hatch and ladder at the same time the roof is replaced. | RENO MOTOR POOL | 9846 | Admin | PubWorks | B&G | Reno | 1990 | 2155 | 2004-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
2483EXT1 | REPLACE ROOF | 2483 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 15 years. The roof warranty expires at the end of the same time frame. It is recommended that this building be re-roofed within the next two to four years to be consistent with the roofing program and the end of the warranty period. | RENO MOTOR POOL | 9846 | Admin | PubWorks | B&G | Reno | 1990 | 2155 | 2004-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 28810
1901EXT1 | EXTERIOR FINISHES | 1901 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. | SEWAGE BUILDING (VACANT) | 9979 | Admin | PubWorks | B&G | Carson City | 1960 | 96 | 2005-02-14 | Four to Ten Years | Long-Term Needs | 3 | 500
2451ENV2 | CONCRETE WIER REHABILITATION | 2451 | The existing concrete weir structure is in need of cleaning and rehabilitation. This project would provide for resurfacing the concrete wier channels with a water resistant epoxy coating, replacing about 20 lineal feet of water intake piping, new filters and cleaning. | STEWART IRRIGATION DIVERSION BLDG | 9820 | Admin | PubWorks | B&G | Carson City | 1890 | 200 | 2005-03-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
2451SIT1 | SITE FENCING | 2451 | The Building / Weir site is located in Clear Creek Canyon. The site currently is wide open to the public and is a safety hazard. This project would provide for an 6 foot tall industrial chain link fence with a locked gate to prevent the public from entering the site and building. Signage is included. | STEWART IRRIGATION DIVERSION BLDG | 9820 | Admin | PubWorks | B&G | Carson City | 1890 | 200 | 2005-03-11 | Immediate to Two Years | Currently Critical | 1 | 6000
1900EXT2 | EXTERIOR FINISHES | 1900 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. This project or a portion there of was previously recommended in the FCA report dated 03/14/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/05/2008. | GARAGE | 9818 | Admin | PubWorks | B&G | Las Vegas | 1974 | 500 | 2008-02-05 | Four to Ten Years | Long-Term Needs | 3 | 70870
2062INT2 | INTERIOR FINISHES | 2062 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA report dated 03/17/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/05/2008. | B&G HVAC GARAGE | 9977 | Admin | PubWorks | Admin | Las Vegas | 1976 | 810 | 2008-02-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4190
2062ADA1 | ADA UPGRADE | 2062 | The only restroom in this building is not compliant with the Americans with Disabilities Act (ADA) regulations and a retrofit is necessary. Given the current configuration of the bathroom, the work will include the installation of a new water closet, a urinal, sink, grab bars, faucets, mirrors, dispensers, hardware and to provide for a unisex restroom. It is also necessary to create an accessible parking area for this building to comply. The parking lot near the building is compliant and proper striping is the only thing necessary to achieve this. A marked crossing across the vehicle way will also be required. The building is lacking ADA signage. Americans with Disabilities Act (ADA) regulations pertaining to building access, route of travel and restrooms has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances, route of travel inside the building and restrooms. IBC - 2006, ICC/ANSI A117.1 - 2003 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2003 were referenced for this project. This project or a portion there of was previously recommended in the FCA report dated 03/17/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/05/2008. | B&G HVAC GARAGE | 9977 | Admin | PubWorks | Admin | Las Vegas | 1976 | 810 | 2008-02-05 | Immediate to Two Years | Currently Critical | 1 | 25000
2062SFT2 | FIRE ALARM SYSTEM INSTALLATION | 2062 | This building is lacking a fire alarm and detection system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2006 Section 7 and the 2006 International Fire Code. This project or a portion there of was previously recommended in the FCA report dated 03/17/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/05/2008. | B&G HVAC GARAGE | 9977 | Admin | PubWorks | Admin | Las Vegas | 1976 | 810 | 2008-02-05 | Immediate to Two Years | Currently Critical | 1 | 5866
2062SFT1 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 2062 | The existing exit signs in this building are older types and should be replaced with new self-illuminated or LED style signs with battery-backed internal systems. Emergency exit lighting should be installed and/or replaced to provide illumination along the egress route. This project or a portion there of was previously recommended in the FCA report dated 03/17/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/05/2008. | B&G HVAC GARAGE | 9977 | Admin | PubWorks | Admin | Las Vegas | 1976 | 810 | 2008-02-05 | Immediate to Two Years | Currently Critical | 1 | 1000
2062EXT2 | REPLACE OVERHEAD COILING DOOR | 2062 | The existing overhead coiling door appears to be original to the building. It has been damaged and is showing signs of wear and deterioration. The trim around the perimeter of the door is also damaged. This building is being used as a classroom and the door is not used very frequently. It has been stated that larger pieces of equipment are used occasionally in the classroom and the size of the door is necessary. It is recommended that it be replaced with a new insulated overhead coiling door and also the trim be replaced. This project or a portion there of was previously recommended in the FCA report dated 03/17/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/05/2008. | B&G HVAC GARAGE | 9977 | Admin | PubWorks | Admin | Las Vegas | 1976 | 810 | 2008-02-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
2062ELE1 | LIGHTING UPGRADE | 2062 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts to current standards, resulting in increased efficiency and reduced costs associated with illumination. Occupancy sensors will be installed in restrooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 03/17/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/05/2008. | B&G HVAC GARAGE | 9977 | Admin | PubWorks | Admin | Las Vegas | 1976 | 810 | 2008-02-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2514
2062EXT3 | EXTERIOR FINISHES | 2062 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. An elastomeric paint is recommended for the stucco. This project or a portion there of was previously recommended in the FCA report dated 03/17/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/05/2008. | B&G HVAC GARAGE | 9977 | Admin | PubWorks | Admin | Las Vegas | 1976 | 810 | 2008-02-05 | Four to Ten Years | Long-Term Needs | 3 | 8380
2062EXT4 | REPLACE EXTERIOR DOOR | 2062 | The existing exterior commercial grade metal door assemblies appear to be original to the building. They are showing signs of wear and deterioration from constant use and abuse. Due security concerns and the condition of the doors, this project recommends the installation of new metal doors, frames and hardware and includes the disposal of the existing door assemblies. This project or a portion there of was previously recommended in the FCA report dated 03/17/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/05/2008. | B&G HVAC GARAGE | 9977 | Admin | PubWorks | Admin | Las Vegas | 1976 | 810 | 2008-02-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
9977SIT1 | SLURRY SEAL ASPHALT PAVING | 9977 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site wide including loading zones, access roads and parking areas. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 381,000 square feet of asphalt area was used to generate this estimate which includes the parking areas around and between the DMV and the Bradley buildings as well as the access roads. | EAST SAHARA SITE | 9977 | Admin | PubWorks | B&G | Las Vegas |  | 0 | 2008-02-05 | Four to Ten Years | Long-Term Needs | 3 | 228600
9977ADA1 | ADA PARKING UPGRADE | 9977 | The existing three ADA curb ramps that lead from the parking lot to the sidewalk in front of the Bradley Building are too steep, they all exceed 1:12. The maximum slope allowed for these ramps is 1:12. The maximum slope allowed for the flared sides of these ramps is 1:10. Refer to IBC/ANSI A117.1 - 2003 Chapter 4. It is recommended these curb ramps be replaced. Saw cutting, removal and disposal of concrete is included in this estimate. IBC - 2006, ICC/ANSI A117.1 - 2003 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2003 were referenced for this project. This project or a portion there of was previously recommended in the FCA report dated 03/17/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2008. | EAST SAHARA SITE | 9977 | Admin | PubWorks | B&G | Las Vegas |  | 0 | 2008-02-05 | Immediate to Two Years | Currently Critical | 1 | 25000
0418ENR2 | INSULATE LABORATORY | 0418 | The Metrology laboratory on the North side of the building was built in an existing garage that does not have proper insulation. The heating and cooling is not efficient in the room, the sensitive measuring and testing equipment is affected by the inconsistent temperatures and the staff working in the lab do not have a comfortable work environment. This project would provide for the furring of the interior side of the CMU, board insulation, 5/8" Type X gypsum board, paint and ceiling insulation to bring the room up to the appropriate "R" value to match the rest of the building. | LV B&G - PUBLIC WORKS OFFICE | 9818 | Admin | PubWorks | B&G | Las Vegas | 1974 | 7087 | 2008-02-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 65000
0418SEC1 | SECURITY SYSTEM | 0418 | The facility currently does not have a security system installed. Access on or off of the property is uncontrolled and there have been security problems including the homeless inhabiting areas of the property. This project recommends card-access control, security fencing, security cameras and additional site lighting be installed to remedy this problem. | LV B&G - PUBLIC WORKS OFFICE | 9818 | Admin | PubWorks | B&G | Las Vegas | 1974 | 7087 | 2008-02-05 | Four to Ten Years | Long-Term Needs | 3 | 200000
0418SFT4 | INSTALL SEISMIC GAS SHUT-OFF VALVE | 0418 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the energy management system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel brace. | LV B&G - PUBLIC WORKS OFFICE | 9818 | Admin | PubWorks | B&G | Las Vegas | 1974 | 7087 | 2008-02-05 | Immediate to Two Years | Currently Critical | 1 | 3500
0418PLM2 | PLUMBING / WASTE LINE ASSESSMENT | 0418 | The plumbing / waste lines are original to the building and major failures are beginning to surface including broken waste lines and corroded flanges. This project recommends that a licensed plumbing contractor perform a camera scope to assess the condition of the piping especially the waste lines. Future projects would be based on this report. | LV B&G - PUBLIC WORKS OFFICE | 9818 | Admin | PubWorks | B&G | Las Vegas | 1974 | 7087 | 2008-02-05 | Immediate to Two Years | Currently Critical | 1 | 5000
0418INT7 | RESURFACE CONCRETE FLOOR | 0418 | The painted concrete floor in the East wing laboratory is worn and cracked and should be resurfaced. This project provides for cleaning and repairing the existing floor, applying a bonding agent, pouring a new polymer surface and applying an appropriate finish product. | LV B&G - PUBLIC WORKS OFFICE | 9818 | Admin | PubWorks | B&G | Las Vegas | 1974 | 7087 | 2008-02-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0418SIT3 | CARPORT STRUCTURE | 0418 | There are approximately 10 state vehicles parked in the rear parking lot at any given time. Many of these vehicles carry sensitive measuring and testing equipment which can deteriorate quickly due to exposure to the elements. This project would provide a steel carport capable of protecting 10 vehicles to be built on the North side of the site. | LV B&G - PUBLIC WORKS OFFICE | 9818 | Admin | PubWorks | B&G | Las Vegas | 1974 | 7087 | 2008-02-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 200000
0418SIT6 | LANDSCAPE SPRINKLER REPLACEMENT | 0418 | The landscape sprinkler system is old and consists of at least three different types of piping. The existing copper, PVC and galvanized iron piping has been spliced together over the years and is a constant maintenance problem. This project would provide for the replacement of the entire sprinkler system including piping, sprinkler heads, check valves and a new backflow preventer. The estimate includes disposal of the existing materials. An allowance for 300 feet of 2" schedule 40 PVC pipe, excavation and backfill is included with this estimate. | LV B&G - PUBLIC WORKS OFFICE | 9818 | Admin | PubWorks | B&G | Las Vegas | 1974 | 7087 | 2008-02-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0418EXT4 | REPLACE STOREFRONT ENTRANCE SYSTEMS | 0418 | There are two separate storefront glazing systems that are showing signs of failure due to broken seals and general wear and tear. The storefront systems are an exterior application and are exposed to weather extremes. This project would provide removal and disposal of the (2) 15' wide storefronts and purchase and installation of two new systems including hardware. | LV B&G - PUBLIC WORKS OFFICE | 9818 | Admin | PubWorks | B&G | Las Vegas | 1974 | 7087 | 2008-02-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
0418INT4 | CARPET REPLACEMENT | 0418 | The carpet in the Supervisor/ Metrology's office is showing signs of extreme wear. It is recommended that the carpet be replaced with heavy duty commercial grade carpet in the next two to three years. This project or a portion there of was previously recommended in the FCA report dated 03/14/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/05/2008. | LV B&G - PUBLIC WORKS OFFICE | 9818 | Admin | PubWorks | B&G | Las Vegas | 1974 | 7087 | 2008-02-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0418ADA3 | ADA PARKING UPGRADE | 0418 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The main entrance to the building has ADA parking stalls which do not entirely meet the requirements of the code. This project provides funding to bring the existing ADA parking area up to code including a compliant path of travel from the spaces to the building entrance, updated signage and any other necessary upgrades. IBC - 2006, ICC/ANSI A117.1 - 2003 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2003 were referenced for this project. This project or a portion there of was previously recommended in the FCA report dated 03/14/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/05/2008. | LV B&G - PUBLIC WORKS OFFICE | 9818 | Admin | PubWorks | B&G | Las Vegas | 1974 | 7087 | 2008-02-05 | Immediate to Two Years | Currently Critical | 1 | 35000
0418SIT5 | SLURRY SEAL ASPHALT PAVING | 0418 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site wide including loading zones, access roads and parking areas. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 20,000 square feet of asphalt area was used to generate this estimate. | LV B&G - PUBLIC WORKS OFFICE | 9818 | Admin | PubWorks | B&G | Las Vegas | 1974 | 7087 | 2008-02-05 | Four to Ten Years | Long-Term Needs | 3 | 18000
0418INT3 | INTERIOR FINISHES | 0418 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA report dated 03/14/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/05/2008. | LV B&G - PUBLIC WORKS OFFICE | 9818 | Admin | PubWorks | B&G | Las Vegas | 1974 | 7087 | 2008-02-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35435
0418ENR1 | INSTALL ENERGY MANAGEMENT SYSTEM | 0418 | This project recommends the installation of an Energy Management System (EMS) for the building. This system will monitor and control the heating, ventilation, air conditioning and lighting equipment through a central computer system. Electronic sensors will be installed on each piece of equipment which will feed information into the computer system. The maintenance staff can then control and monitor the equipment remotely which will significantly lower energy costs. Along with electricity, gas and water meters, this system will provide detailed reports on energy consumption allowing the maintenance staff to analyze and customize the energy used by the facility. | LV B&G - PUBLIC WORKS OFFICE | 9818 | Admin | PubWorks | B&G | Las Vegas | 1974 | 7087 | 2008-02-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 60000
0418EXT3 | WINDOW REPLACEMENT | 0418 | The windows in the original building are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. Several of the windows also have a metal wall panel below them that should be removed and replaced with a framed and insulated wall to match the adjacent walls. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 20 units and does not include the windows in the storefront entrance systems which are addressed in a separate project. | LV B&G - PUBLIC WORKS OFFICE | 9818 | Admin | PubWorks | B&G | Las Vegas | 1974 | 7087 | 2008-02-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 40000
0418ELE1 | LIGHTING UPGRADE | 0418 | The existing lighting fixtures in the original building are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. Any electrical wiring upgrades are not included in this estimate. The estimate is based on quotes recently acquired by the staff for this project. This project or a portion there of was previously recommended in the FCA report dated 03/14/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/05/2008. | LV B&G - PUBLIC WORKS OFFICE | 9818 | Admin | PubWorks | B&G | Las Vegas | 1974 | 7087 | 2008-02-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0418SIT4 | REMOVE PALM TREES | 0418 | There are numerous palm trees along the perimeter of the paved parking along the north side of the site. They are damaging the concrete curbing and are in need of removal. This project would provide for the removal of the palm trees and repair of the damaged curbing. | LV B&G - PUBLIC WORKS OFFICE | 9818 | Admin | PubWorks | B&G | Las Vegas | 1974 | 7087 | 2008-02-05 | Immediate to Two Years | Currently Critical | 1 | 10000
0418EXT5 | OVERHEAD DOOR REPLACEMENT | 0418 | There is a 16'x14' overhead coiling door which is damaged and does not function properly. It is original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead coiling door and replacement with a motorized door. | LV B&G - PUBLIC WORKS OFFICE | 9818 | Admin | PubWorks | B&G | Las Vegas | 1974 | 7087 | 2008-02-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
0418PLM1 | WATER HEATER REPLACEMENT | 0418 | The average life span of a water heater is eight to ten years. The existing 40 gallon gas water heater in the building has reached the end of its expected life and is not energy efficient. This project would provide for the removal and disposal of the old water heater and installation of a new 40 gallon gas water heater. | LV B&G - PUBLIC WORKS OFFICE | 9818 | Admin | PubWorks | B&G | Las Vegas | 1974 | 7087 | 2008-02-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0418HVA1 | REPLACE ROOFTOP HVAC UNITS | 0418 | The heating and cooling to this building is provided by several rooftop packaged units of which 3 appear to be original equipment. They are in poor condition and have reached the end of their expected life. This project would provide for the installation of 3 new rooftop packaged HVAC units including connections to existing utilities. Removal and disposal of the old units is included in this estimate. This project is recommended to be undertaken at the same time as the energy management system installation. | LV B&G - PUBLIC WORKS OFFICE | 9818 | Admin | PubWorks | B&G | Las Vegas | 1974 | 7087 | 2008-02-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 54000
0418PLM3 | 4" BACKFLOW ASSEMBLY, VAULT, AND POWER | 0418 | State Health Law (NAC 445A.67185) and the International Plumbing Code (IPC Section 608) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution can be discharged or drawn into the public water system as a result of back siphonage or backpressure. There is no backflow prevention on domestic water lines and fire sprinkler or standpipe lines. This project would provide funding for installation of a 4" reduced pressure backflow prevention assembly, required fittings, a vault below grade, and allowance for 200 feet of 1" conduit to provide power for the required heat source inside the vault. This estimate includes two assemblies, one for the domestic water and one for the fire line. | LV B&G - PUBLIC WORKS OFFICE | 9818 | Admin | PubWorks | B&G | Las Vegas | 1974 | 7087 | 2008-02-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
0418INT6 | RESTROOM REMODEL | 0418 | There are several restrooms in this building. This project would provide for a complete remodel and rehabilitation of one Men and one Women restroom in the original building including fixtures, casework, floor and wall finishes and hardware. This project is recommended to be completed after the PLUMBING / WASTE LINE ASSESSMENT project has determined the state of the plumbing system. This estimate does not include any funds for under slab plumbing and / or waste line replacement. | LV B&G - PUBLIC WORKS OFFICE | 9818 | Admin | PubWorks | B&G | Las Vegas | 1974 | 7087 | 2008-02-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 60000
0418EXT2 | EXTERIOR FINISHES | 0418 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. This project or a portion there of was previously recommended in the FCA report dated 03/14/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/05/2008. | LV B&G - PUBLIC WORKS OFFICE | 9818 | Admin | PubWorks | B&G | Las Vegas | 1974 | 7087 | 2008-02-05 | Four to Ten Years | Long-Term Needs | 3 | 70870
0418ELE2 | ELECTRICAL UPGRADE | 0418 | This building was constructed before the high demand for electrical services were needed for computers and other electrical devices. As time has progressed, the building's electrical demand and system has changed. It is utilized to its current maximum potential. The electrical panels and receptacles are at their limit. It is recommended the entire system be upgraded to meet the evolving needs of the building including three-phase power. This project or a portion there of was previously recommended in the FCA report dated 03/14/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/05/2008. | LV B&G - PUBLIC WORKS OFFICE | 9818 | Admin | PubWorks | B&G | Las Vegas | 1974 | 7087 | 2008-02-05 | Immediate to Two Years | Currently Critical | 1 | 141740
2159SEC1 | BUILDING DEMOLITION | 2159 | This building is dilapidated, damaged and is no longer being used. This project would provide for the removal of the structure. This site is on the National Registrar of Historic Places and any request to remove this structure will have to be approved by them prior to proceeding with any demolition. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #055 STORAGE (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart |  | 400 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 5000
0266SFT8 | FIRE ALARM INSTALLATION | 0266 | This building is equipped with an automatic fire detection and alarm system that is the original system and should be scheduled for replacement. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. When completed, the new system will provide smoke detection, horns and strobes throughout the facility in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | BRADLEY BUILDING (VACANT) | 9977 | Admin | PubWorks | B&G | Las Vegas | 1975 | 28275 | 2013-06-05 | Immediate to Two Years | Currently Critical | 1 | 113100
0266EXT4 | EXTERIOR FINISHES | 0266 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the metal paneling and stucco and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 02/05/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 6/5/2013. | BRADLEY BUILDING (VACANT) | 9977 | Admin | PubWorks | B&G | Las Vegas | 1975 | 28275 | 2013-06-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 141375
0266INT2 | INTERIOR FINISHES | 0266 | The interior finishes are in poor condition. It is recommended that the interior walls and ceilings be painted at least once in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA reports dated 02/10/2005 and 02/05/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2013. | BRADLEY BUILDING (VACANT) | 9977 | Admin | PubWorks | B&G | Las Vegas | 1975 | 28275 | 2013-06-05 | Immediate to Two Years | Currently Critical | 1 | 141375
0266SIT3 | ROOF DRAIN DOWNSPOUT MODIFICATIONS | 0266 | The roof drain downspouts currently terminate within inches of the building with no continuous drainage away from the foundation. This is causing the water to pool next to the foundation and damage the foundation and the sloped concrete and stone walls at the base of the building. Water also flows across the concrete sidewalks causing damage to the concrete and creating a potential slipping hazard. This project would provide for the extension of the roof drains from the downspouts to approximately 5'-0" away from the perimeter of the building to prevent pooling and damage to the building. This project or a portion thereof was previously recommended in the FCA report dated 02/05/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 6/5/2013. | BRADLEY BUILDING (VACANT) | 9977 | Admin | PubWorks | B&G | Las Vegas | 1975 | 28275 | 2013-06-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0266SFT3 | EMPLOYEE BREAK ROOM CONVERSION | 0266 | There is a portion of the existing garage located along the north side of the building which has been converted to an employee break room. The ceiling in this space is less than the required 7'-6" minimum ceiling height for habitable spaces. In addition, the corridor serving the space appears to not meet the requirements for egress. The only way into or out of the space is through a narrow corridor. This project recommends abandoning the use of this space as an employee break room and converting it into a storage room. Signage indicating the use of the space for storage is suggested. This project or a portion thereof was previously recommended in the FCA report dated 02/05/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 6/5/2013. | BRADLEY BUILDING (VACANT) | 9977 | Admin | PubWorks | B&G | Las Vegas | 1975 | 28275 | 2013-06-05 | Immediate to Two Years | Currently Critical | 1 | 1000
0266HVA2 | ELEVATOR MACHINE ROOM VENTILATION | 0266 | The elevator Machine Room has solid state elevator equipment located inside. The IBC 2012, Chapter 30, Section 3006.2 requires ventilation of the elevator Machine Room. This project will provide for a ventilation system for this room. It is recommended that this work be done at the same time as the HVAC upgrades. This project or a portion there of was previously recommended in the FCA reports dated 02/10/2005 and 02/05/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2013. | BRADLEY BUILDING (VACANT) | 9977 | Admin | PubWorks | B&G | Las Vegas | 1975 | 28275 | 2013-06-05 | Immediate to Two Years | Currently Critical | 1 | 25000
0266ELE1 | INSTALL GFCI OUTLETS | 0266 | Each restroom has a standard Decora style outlet near the sink. These outlets must be changed to GFCI type outlets per the NEC. This project would provide for the purchase and installation of GFCI duplex outlets. This project or a portion there of was previously recommended in the FCA reports dated 02/10/2005 and 02/05/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2013. | BRADLEY BUILDING (VACANT) | 9977 | Admin | PubWorks | B&G | Las Vegas | 1975 | 28275 | 2013-06-05 | Immediate to Two Years | Currently Critical | 1 | 1500
0266HVA1 | HVAC REPLACEMENT | 0266 | The building is equipped with a central heating and air conditioning system controlled by a direct digital control system. Staff reported during the 2013 survey that the DDC system is no longer operating. The maintenance staff and building occupants report that the air conditioning and heating in the building does not maintain a consistent temperature and is inadequate in some areas. The addition of computers and other electronic equipment, which gives off heat, was thought to contribute to problems with the cooling system. The EvapCo cooling tower is rusting through on the upper portion and is starting to leak. It was also noted that the heat in the building is inadequate. The third floor is heated, the 1st floor does not have a heating coil to provide heat in the cold season and the 2nd floor has been retrofitted with a heating coil but it is inadequate and problematic from a maintenance perspective. This project recommends a building-wide system upgrade which includes the boiler, chiller, cooling tower, air handlers, VFD's, DDC system and duct system in the next 1-2 years. This project or a portion thereof was previously recommended in the FCA reports dated 02/10/2005 and 02/05/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 6/5/2013. | BRADLEY BUILDING (VACANT) | 9977 | Admin | PubWorks | B&G | Las Vegas | 1975 | 28275 | 2013-06-05 | Immediate to Two Years | Currently Critical | 1 | 1200000
0266PLM2 | DOUBLE CHECK VALVE INSTALLATION | 0266 | State Health Law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of back siphonage or backpressure. This project allows for the installation of a double check valve on the fire riser to comply with these requirements. This project or a portion there of was previously recommended in the FCA report dated 02/10/2005 and 02/05/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/05/2013. | BRADLEY BUILDING (VACANT) | 9977 | Admin | PubWorks | B&G | Las Vegas | 1975 | 28275 | 2013-06-05 | Immediate to Two Years | Currently Critical | 1 | 15000
0266PLM3 | DOMESTIC WATER LINE INSTALLATION | 0266 | The domestic water currently comes into the building through the same pipe as the fire suppression system water. Once inside the building, this 6" pipe turns vertically for the fire riser, but there is a tee to a 2 1/2" pipe for the domestic water just below the riser. There should be a dedicated line for the domestic water from the main city line and there is no backflow prevention or double check valves on any portion of the water pipes. This project would provide for installing a new 2 1/2" domestic water line from the city main water line in the street to the building including a backflow prevention device between the main and the building. A hot tap, traffic control and asphalt concrete road patching is included. | BRADLEY BUILDING (VACANT) | 9977 | Admin | PubWorks | B&G | Las Vegas | 1975 | 28275 | 2013-06-05 | Immediate to Two Years | Currently Critical | 1 | 90000
0266ADA5 | ELEVATOR EQUIPMENT UPGRADE | 0266 | The elevators were built and installed in 1975 and require periodic repairs. However, they are currently due for a complete refurbishment of all mechanical parts to maintain the elevator in a safe working order including the hydraulic motors. They are also not ADA compliant and will require new signage, call buttons, two-way communication and any other necessary equipment to comply with the ADA. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | BRADLEY BUILDING (VACANT) | 9977 | Admin | PubWorks | B&G | Las Vegas | 1975 | 28275 | 2013-06-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0266SFT5 | FIRE CAULK PENETRATIONS | 0266 | Numerous locations throughout the building have piping, conduits and other penetrations through fire rated assemblies. This project would provide fire caulking and/or Intumescent and listed sealants to return the assemblies to full rating. This project or a portion thereof was previously recommended in the FCA reports dated 02/10/2005 and 02/05/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 6/5/2013. | BRADLEY BUILDING (VACANT) | 9977 | Admin | PubWorks | B&G | Las Vegas | 1975 | 28275 | 2013-06-05 | Immediate to Two Years | Currently Critical | 1 | 5000
0266SFT6 | FIRE SUPPRESSION PIPE REPLACEMENT | 0266 | It is estimated that after installing the double check valve on the fire riser that the water pressure in the fire suppression piping will be reduced by 10%. This reduction in pressure will not supply enough water to the 3rd floor. The Las Vegas Valley Water District is installing a backflow prevention device on the line, the pressure will be reduced by an additional 10%. To compensate for the reduced pressure, it is recommended to replace the 3rd floor piping with larger diameter pipes. This project would provide for re-piping the fire suppression system lines on the 3rd floor to maintain an adequate supply of water for the system. | BRADLEY BUILDING (VACANT) | 9977 | Admin | PubWorks | B&G | Las Vegas | 1975 | 28275 | 2013-06-05 | Immediate to Two Years | Currently Critical | 1 | 12000
0266INT4 | JANITOR CLOSET FRP | 0266 | There are three Janitor's closets that are in need of wall protection. This project would provide for the installation of a fiberglass reinforced panel (FRP) to be installed on the walls adjacent to the mop sink. | BRADLEY BUILDING (VACANT) | 9977 | Admin | PubWorks | B&G | Las Vegas | 1975 | 28275 | 2013-06-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2250
0266SFT7 | RELOCATE SPRINKLER HEADS | 0266 | Numerous areas in the facility have inadequate sprinkler coverage due to partition wall construction and relocation, which has cut-off many sprinkler heads. This project would re-design the system and correct the coverage deficiencies. This project or a portion there of was previously recommended in the FCA reports dated 02/10/2005 and 02/05/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2013. | BRADLEY BUILDING (VACANT) | 9977 | Admin | PubWorks | B&G | Las Vegas | 1975 | 28275 | 2013-06-05 | Immediate to Two Years | Currently Critical | 1 | 25000
0266ADA6 | BUILDING / SITE ADA IMPROVEMENTS | 0266 | The existing ADA accessible parking curb cuts are not completely ADA compliant. The restrooms are not 100% ADA compliant and the building is lacking ADA compliant signage. This project would provide for removing and replacing the non-compliant ADA curb cuts, minor restroom modifications including new and / or relocated fixtures, and a sign package for the entire facility. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | BRADLEY BUILDING (VACANT) | 9977 | Admin | PubWorks | B&G | Las Vegas | 1975 | 28275 | 2013-06-05 | Immediate to Two Years | Currently Critical | 1 | 30000
0266ADA3 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0266 | This building contains drinking fountains on each floor. The drinking fountains on the 1st and 2nd floors have been upgraded to meet current requirements, but the 3rd floor is still without a compliant drinking fountain. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains on the 3rd floor to meet the ADA requirements. This project or a portion thereof was previously recommended in the FCA reports dated 02/10/2005 and 02/05/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 6/5/2013. | BRADLEY BUILDING (VACANT) | 9977 | Admin | PubWorks | B&G | Las Vegas | 1975 | 28275 | 2013-06-05 | Immediate to Two Years | Currently Critical | 1 | 2000
0266ELE3 | ELECTRICAL UPGRADE | 0266 | This building was constructed before the high demand for electrical services were needed for computers and other electrical devices. As time has progressed, the buildings electrical demand and system has changed. It is utilized to its current maximum potential. The electrical panels are at their limit and the breakers trip often. The receptacles are in the floor. There are not enough receptacles and the floor mounted system is old and problematic. It is recommended the entire system be upgraded to meet the evolving needs of the building including switchgear, interior transformers, panel boxes, breakers, wiring and receptacles. This project or a portion thereof was previously recommended in the FCA report dated 02/05/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2013. | BRADLEY BUILDING (VACANT) | 9977 | Admin | PubWorks | B&G | Las Vegas | 1975 | 28275 | 2013-06-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 565500
0266INT3 | FLOORING REPLACEMENT | 0266 | The VCT (vinyl composite tile) and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the next 2-3 years. | BRADLEY BUILDING (VACANT) | 9977 | Admin | PubWorks | B&G | Las Vegas | 1975 | 28275 | 2013-06-05 | Immediate to Two Years | Currently Critical | 1 | 168000
0266EXT1 | EXTERIOR METAL WALL PANEL REPLACEMENT | 0266 | The exterior is a dark anodized enamel aluminum wall panel system and is faded due to weather. The dark color increases summertime heat gain, which puts a strain on the HVAC system. There is also discoloration on the south side of the building below the state seal. This project recommends replacing it with a lighter metal wall panel system for increased energy efficiency. Includes removal and disposal of the old system. This project or a portion there of was previously recommended in the FCA reports dated 02/10/2005 and 02/05/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2013. | BRADLEY BUILDING (VACANT) | 9977 | Admin | PubWorks | B&G | Las Vegas | 1975 | 28275 | 2013-06-05 | Four to Ten Years | Long-Term Needs | 3 | 660000
0266EXT2 | EXTERIOR INSULATION & FINISH SYSTEM REPAIRS | 0266 | The EIFS (Exterior Insulation and Finish System) near the South building exit and at the column areas is showing signs of damage, cracking and appears to be failing. This project will provide for repair and painting of the damaged areas. This project or a portion there of was previously recommended in the FCA reports dated 02/10/2005 and 02/05/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2013. | BRADLEY BUILDING (VACANT) | 9977 | Admin | PubWorks | B&G | Las Vegas | 1975 | 28275 | 2013-06-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
0266EXT3 | ROOF REPLACEMENT | 0266 | The rolled asphalt roof on this building was in poor condition at the time of the survey. Efforts have been made to repair leaks many times, but the water proofing ability of the roofing is at the end of its useful life. It is recommended that this building be re-roofed in the next 1-2 years with a new single ply roofing membrane and new underlayments. This estimate includes removal and disposal of the old roofing. This project or a portion thereof was previously recommended in the FCA reports dated 02/10/2005 and 02/05/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2013. | BRADLEY BUILDING (VACANT) | 9977 | Admin | PubWorks | B&G | Las Vegas | 1975 | 28275 | 2013-06-05 | Immediate to Two Years | Currently Critical | 1 | 200000
0266ADA4 | BREAK ROOM REMODEL | 0266 | The kitchenettes and associated cabinets in the employee break rooms are original to the building. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and countertops are delaminating and failing. This project recommends the replacement of the existing kitchen countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards For Accessible Design should be incorporated into the design such as providing an accessible sink. The estimate is for remodeling 3 break rooms, one on each floor. | BRADLEY BUILDING (VACANT) | 9977 | Admin | PubWorks | B&G | Las Vegas | 1975 | 28275 | 2013-06-05 | Immediate to Two Years | Currently Critical | 1 | 30000
2562EXT2 | ROOF REPLACEMENT | 2562 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2004. It is recommended that this building be re-roofed in the next 8-10 years to be consistent with the roofing program and the end of the warranty period. | MICROWAVE BUILDING | 9990 | Admin | PubWorks | B&G | Carson City | 2004 | 480 | 2014-05-01 | Four to Ten Years | Long-Term Needs | 3 | 5760
2562EXT1 | EXTERIOR FINISHES | 2562 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the stone walls caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | MICROWAVE BUILDING | 9990 | Admin | PubWorks | B&G | Carson City | 2004 | 480 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2400
2484INT2 | INTERIOR FINISHES | 2484 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 5-6 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | LAKEVIEW HOUSE | 9899 | Admin | PubWorks | B&G | Carson City | 1873 | 2300 | 2015-02-25 | Four to Ten Years | Long-Term Needs | 3 | 11500
2484SFT4 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 2484 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. | LAKEVIEW HOUSE | 9899 | Admin | PubWorks | B&G | Carson City | 1873 | 2300 | 2015-02-25 | Immediate to Two Years | Currently Critical | 1 | 4000
2498EXT2 | EXTERIOR FINISHES | 2498 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 02/18/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/25/2015. | WATER MASTER HOUSE SHED | 9899 | Admin | PubWorks | B&G | Carson City | 1992 | 120 | 2015-02-25 | Four to Ten Years | Long-Term Needs | 3 | 600
2498SIT1 | CONCRETE REPLACEMENT | 2498 | The concrete slab-on-grade in the shed is deteriorating. Spalling and cracking have occurred. Exposure to the weather is a contributing factor. This project addresses removal and replacement of the existing concrete slab. 120 SF of 4" thick concrete was used for this estimate. This project or a portion thereof was previously recommended in the FCA report dated 02/18/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/25/2015. | WATER MASTER HOUSE SHED | 9899 | Admin | PubWorks | B&G | Carson City | 1992 | 120 | 2015-02-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2400
2484SFT1 | SMOKE ALARM INSTALLATION | 2484 | Section 907.2.11 of the 2012 IBC and 2012 IFC explains the requirements for smoke alarms in dwelling units including installing and maintaining smoke alarms in each sleeping room and on the ceiling or wall outside of each separate sleeping area in the immediate vicinity of bedrooms. State Fire Marshal NAC 477.915 (3) requires that smoke detectors be connected to the wiring of the building with a battery backup. This project would provide funding for the purchase and installation of smoke alarms in accordance with these codes. This project or a portion thereof was previously recommended in the FCA report dated 02/18/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/25/2015. | LAKEVIEW HOUSE | 9899 | Admin | PubWorks | B&G | Carson City | 1873 | 2300 | 2015-02-25 | Immediate to Two Years | Currently Critical | 1 | 2000
2484EXT4 | EXTERIOR FINISHES | 2484 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | LAKEVIEW HOUSE | 9899 | Admin | PubWorks | B&G | Carson City | 1873 | 2300 | 2015-02-25 | Four to Ten Years | Long-Term Needs | 3 | 11500
2488ENR1 | LIGHTING REPLACEMENT | 2488 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in the restroom, office and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | MARLETTE LAKE OFFICE/STORAGE BUILDING | 9899 | Admin | PubWorks | B&G | Carson City | 1986 | 2400 | 2015-02-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3600
2484SFT2 | EXTERIOR STAIR HANDRAIL INSTALLATION | 2484 | The exterior stairs and wrap around porch are lacking handrails and guardrails as required in section R311.7.8 of the 2012 International Residential Code. This project would provide for wood framed handrails and guardrails to be installed in accordance with the code. This project is contingent upon the approval of the State Historic Preservation Office. This project or a portion thereof was previously recommended in the FCA report dated 02/18/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/25/2015. | LAKEVIEW HOUSE | 9899 | Admin | PubWorks | B&G | Carson City | 1873 | 2300 | 2015-02-25 | Immediate to Two Years | Currently Critical | 1 | 5000
2488EXT1 | ROOF REPLACEMENT | 2488 | The standing seam metal roof on this building was in poor condition at the time of the survey and had active leaks. It is recommended that this building be re-roofed in the next 2-3 years with a new single-ply roofing system which will be installed directly over the existing metal roof. This will allow the roof to qualify for the statewide roofing program warranty and preventative maintenance agreement. This project or a portion thereof was previously recommended in the FCA report dated 02/18/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/25/2015. | MARLETTE LAKE OFFICE/STORAGE BUILDING | 9899 | Admin | PubWorks | B&G | Carson City | 1986 | 2400 | 2015-02-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 28800
2488ADA2 | UNISEX ADA RESTROOM | 2488 | The building does not have an ADA accessible restroom. The existing restroom does not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. Relocation of the water heater is also part of this project. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | MARLETTE LAKE OFFICE/STORAGE BUILDING | 9899 | Admin | PubWorks | B&G | Carson City | 1986 | 2400 | 2015-02-25 | Immediate to Two Years | Currently Critical | 1 | 12400
2488EXT3 | EXTERIOR FINISHES | 2488 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 3-4 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | MARLETTE LAKE OFFICE/STORAGE BUILDING | 9899 | Admin | PubWorks | B&G | Carson City | 1986 | 2400 | 2015-02-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2400
2488PLM1 | WATER HEATER REPLACEMENT | 2488 | There is a 40 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 5-6 years. It is recommended that a new gas-fired water heater be installed for more efficient use of energy. This estimate includes: 100 feet of gas pipe, fittings, couplers, and labor for installation. Removal and disposal of the existing equipment is included in this estimate. | MARLETTE LAKE OFFICE/STORAGE BUILDING | 9899 | Admin | PubWorks | B&G | Carson City | 1986 | 2400 | 2015-02-25 | Four to Ten Years | Long-Term Needs | 3 | 3500
2488INT2 | INTERIOR WALL UPGRADE | 2488 | The interior walls have open framing with exposed batt insulation between the steel framing. It is recommended to install gypsum board to the interior walls along with taping, texturing and painting. There are public presentations held in this building and the exposed insulation is ripped and falling out in some places. This upgrade will improve the insulating properties of the building and provide a more finished look for the staff and visitors. | MARLETTE LAKE OFFICE/STORAGE BUILDING | 9899 | Admin | PubWorks | B&G | Carson City | 1986 | 2400 | 2015-02-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24000
2488SFT5 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 2488 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 02/18/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/25/2015. | MARLETTE LAKE OFFICE/STORAGE BUILDING | 9899 | Admin | PubWorks | B&G | Carson City | 1986 | 2400 | 2015-02-25 | Immediate to Two Years | Currently Critical | 1 | 4000
2488SEC1 | SECURITY SYSTEM INSTALLATION | 2488 | The existing office storage building currently does not have a security system installed. Because the small office area contains the computer-controlled water distribution system for Virginia City, a security system is recommended. This project recommends motion detection, door switches, access control and related items be installed and interfaced with the fire alarm. This project or a portion thereof was previously recommended in the FCA report dated 02/18/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/25/2015. | MARLETTE LAKE OFFICE/STORAGE BUILDING | 9899 | Admin | PubWorks | B&G | Carson City | 1986 | 2400 | 2015-02-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
2488SFT2 | SAFETY CABINETS | 2488 | The storage building contains gasoline, aerosol cans and other hazardous products on open shelves and on the floor. This does not meet OSHA standards for hazardous materials containment. This project would provide two hazardous storage containers in the building and install placards on the building exterior in accordance with OSHA 1910.106 (d). This project or a portion thereof was previously recommended in the FCA report dated 02/18/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/25/2015. | MARLETTE LAKE OFFICE/STORAGE BUILDING | 9899 | Admin | PubWorks | B&G | Carson City | 1986 | 2400 | 2015-02-25 | Immediate to Two Years | Currently Critical | 1 | 10000
2488INT1 | INTERIOR FINISHES | 2488 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings of the office and restroom at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 02/18/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/25/2015. | MARLETTE LAKE OFFICE/STORAGE BUILDING | 9899 | Admin | PubWorks | B&G | Carson City | 1986 | 2400 | 2015-02-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
2488HVA1 | HVAC EQUIPMENT REPLACEMENT | 2488 | The existing HVAC system consists of a wall mounted air conditioner and a wall mounted heater for the office along with an older ceiling mounted heater for the warehouse area. The electric heaters are inefficient and should be replaced with natural gas fired heaters. This project would provide for replacing the existing equipment with exterior ground mounted packaged units that provide natural gas fired heating as well as air conditioning. This project or a portion thereof was previously recommended in the FCA report dated 02/18/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/25/2015. | MARLETTE LAKE OFFICE/STORAGE BUILDING | 9899 | Admin | PubWorks | B&G | Carson City | 1986 | 2400 | 2015-02-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 36000
2488ENR2 | EXIT SIGN AND EGRESS LIGHTING INSTALLATION | 2488 | The building does not have any emergency lighting and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 02/18/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/25/2015. | MARLETTE LAKE OFFICE/STORAGE BUILDING | 9899 | Admin | PubWorks | B&G | Carson City | 1986 | 2400 | 2015-02-25 | Immediate to Two Years | Currently Critical | 1 | 6000
2488SFT3 | NONABSORBENT FINISHES | 2488 | 2012 IBC Section 1210 requires the installation of smooth, hard, nonabsorbent surfaces in the following restroom areas: on floors in toilet, bathing and shower rooms that extend upward onto the walls at least 4 inches, within 2 feet of the sides of urinals and water closets to a height of not less than 4 feet above the floor and in shower compartments to a height not less than 70 inches above the drain inlet. Accessories such as grab bars, towel bars, paper dispensers and soap dishes, provided on or within walls, shall be installed and sealed to protect structural elements from moisture. This project recommends the installation of Fiberglass Reinforced Panel (FRP) or an equal material to comply with this code section. This project or a portion thereof was previously recommended in the FCA report dated 02/18/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/25/2015. | MARLETTE LAKE OFFICE/STORAGE BUILDING | 9899 | Admin | PubWorks | B&G | Carson City | 1986 | 2400 | 2015-02-25 | Immediate to Two Years | Currently Critical | 1 | 3000
9899SEC1 | EXTERIOR SOLAR SITE LIGHTING INSTALLATION | 9899 | There is no site lighting for the property which is a security and safety concern. This project would provide for the installation of 10 solar powered LED exterior light fixtures, 20 foot tall poles and 30" diameter raised concrete bases. This installation will eliminate the need for trenching and electrical connections. | MARLETTE LAKE WATER SYSTEM OFFICE SITE | 9899 | Admin | PubWorks | B&G | Carson City | 0 |  | 2015-02-25 | Four to Ten Years | Long-Term Needs | 3 | 65000
9899SIT4 | CRACK FILL & SEAL ASPHALT PAVING | 9899 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the paving site wide including access roads and parking areas. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 15,000 square feet of asphalt area was used to generate this estimate. | MARLETTE LAKE WATER SYSTEM OFFICE SITE | 9899 | Admin | PubWorks | B&G | Carson City | 0 |  | 2015-02-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
9899SIT2 | FENCE REPLACEMENT | 9899 | The Marlette Lake site has several types of fencing surrounding the perimeter, all of which are in poor condition. Some sections are completely missing or have been blown down by the wind. This project recommends the installation of a 6 foot high 6 gauge wire perimeter chain link fence around the entire site with two 14 foot wide gates with hardware. The cost estimate also includes demolition and disposal of the existing fence. An agency approval of fencing design and/or material may be required and is not reflected in this project. This project or a portion thereof was previously recommended in the FCA report dated 02/18/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/25/2015. | MARLETTE LAKE WATER SYSTEM OFFICE SITE | 9899 | Admin | PubWorks | B&G | Carson City | 0 |  | 2015-02-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 56000
9899SIT5 | ASPHALT PAVING INSTALLATION | 9899 | The site has several areas with inadequate drainage due to erosion and clogged drains. A majority of the site is not paved allowing runoff to erode the dirt. Installing asphalt and drainage swales would allow for control of the runoff and prevention of flooding. This project would provide asphalt cement paving for the dirt areas of the site. The estimate includes grading, 6" base, compaction and installation of 4" thick asphalt cement paving. | MARLETTE LAKE WATER SYSTEM OFFICE SITE | 9899 | Admin | PubWorks | B&G | Carson City | 0 |  | 2015-02-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 217800
2790PLM1 | WATER HEATER REPLACEMENT | 2790 | There is a 100 gallon natural gas-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 3-4 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | CAMPOS OFFICE & PARKING COMPLEX | 9794 | Admin | PubWorks | B&G | Las Vegas | 2009 | 188061 | 2015-03-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
2790SIT1 | CARPORT STRUCTURE INSTALLATION | 2790 | There is a need for a carport structure on the top floor of the parking garage. The employee vehicles are exposed to the sun and the carport could provide solar power to the building. This project would provide for the purchase and installation of a 60' x 250' steel carport structure on the top floor of the parking garage with a photovoltaic system including solar panels, deep cycle solar batteries and all associated electrical boxes and hardware to connect it to the electrical system. | CAMPOS OFFICE & PARKING COMPLEX | 9794 | Admin | PubWorks | B&G | Las Vegas | 2009 | 188061 | 2015-03-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500000
2790EXT1 | EXTERIOR FINISHES | 2790 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the joints, windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CAMPOS OFFICE & PARKING COMPLEX | 9794 | Admin | PubWorks | B&G | Las Vegas | 2009 | 188061 | 2015-03-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 376122
2790PLM2 | WATER TREATMENT SYSTEM REPLACEMENT | 2790 | The existing water softening/ treatment systems in the building are currently not operational or are ineffective. Failure of the equipment causes wear and tear on the domestic water supply lines, plumbing fixtures and HVAC equipment. A significant amount of scaling was observed on the cooling towers indicating a problem with the water treatment system. This project would provide for the replacement of the existing water softeners/ treatment systems with new equipment. This project would also provide for a chemical treatment program including an updated chemicals control system, service and employee training provided by a qualified water treatment vendor. The annual maintenance fee charged by the water treatment vendor would be determined after an investigation of the water system is complete. These annual costs are not included in this project cost. For budgeting purposes, a $12,000 fee is suggested. | CAMPOS OFFICE & PARKING COMPLEX | 9794 | Admin | PubWorks | B&G | Las Vegas | 2009 | 188061 | 2015-03-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
2790INT1 | INTERIOR FINISHES | 2790 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | CAMPOS OFFICE & PARKING COMPLEX | 9794 | Admin | PubWorks | B&G | Las Vegas | 2009 | 188061 | 2015-03-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 424070
9790ADA1 | ADA UPGRADES | 9790 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. A compliant path of travel from the accessible parking spaces and from the public right of way to the entrance are necessary to comply with ADA accessibility requirements. The current path from the parking spaces is not in compliance due to a curb ramp that is too small and the downspout protruding into the path. There is also no path from the public right of way. This project would provide for complaint concrete walkways and curb ramps. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | FLEET SERVICES - LAS VEGAS SITE | 9790 | Admin | PubWorks | B&G | Las Vegas | 2007 |  | 2015-03-18 | Immediate to Two Years | Currently Critical | 1 | 25000
9790ENR1 | EXTERIOR SOLAR SITE LIGHTING UPGRADE | 9790 | There is one existing light pole at the site. With increased traffic and development in the area, insufficient site lighting is a security and safety concern. This project would provide for the installation of 8 solar powered LED exterior light fixtures, 20 foot tall poles and 30" diameter raised concrete bases. This installation will eliminate the need for trenching and electrical connections. The existing pole may be acceptable to re-use. If so, the estimate can be reduced accordingly. | FLEET SERVICES - LAS VEGAS SITE | 9790 | Admin | PubWorks | B&G | Las Vegas | 2007 |  | 2015-03-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6500
9794SIT1 | EXTERIOR SOLAR SITE LIGHTING INSTALLATION | 9794 | There are approximately 10 existing light poles around the site with metal halide fixtures. The older fixtures are not energy efficient and are due for an upgrade to a higher efficiency unit with a longer life cycle. This project would provide for the installation of 10 solar powered LED exterior light fixtures on the existing poles. | CAMPOS OFFICE & PARKING COMPLEX SITE | 9794 | Admin | PubWorks | B&G | Las Vegas | 2009 |  | 2015-03-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
3155INT2 | CARPET REPLACEMENT | 3155 | The carpet in the Conference Room is showing signs of extreme wear and should be scheduled for replacement. It is recommended that the carpet be replaced with heavy duty commercial grade carpet in the next 2-3 years. | FLEET SERVICES OFFICE - LAS VEGAS | 9790 | Admin | PubWorks | B&G | Las Vegas | 2007 | 4085 | 2015-03-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1050
3155EXT2 | EXTERIOR FINISH REPAIRS | 3155 | The exterior of the building is covered by an Exterior Insulation Finishing System (EIFS). There are at least 3 large cracks in the EIFS that should be repaired in order to maintain a waterproof envelope around the building. This project would provide funding to repair the cracks and bring the finish back to its original condition. | FLEET SERVICES OFFICE - LAS VEGAS | 9790 | Admin | PubWorks | B&G | Las Vegas | 2007 | 4085 | 2015-03-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
3155ENR1 | EXTERIOR LIGHTING UPGRADE | 3155 | There are 12 wall pack lighting fixtures mounted on the exterior of the building. These light fixtures are old, failing and not energy efficient. This project would provide for the replacement of the 12 exterior lighting fixtures with new LED light fixtures, using existing wiring. | FLEET SERVICES OFFICE - LAS VEGAS | 9790 | Admin | PubWorks | B&G | Las Vegas | 2007 | 4085 | 2015-03-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3600
3155EXT1 | EXTERIOR FINISHES | 3155 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | FLEET SERVICES OFFICE - LAS VEGAS | 9790 | Admin | PubWorks | B&G | Las Vegas | 2007 | 4085 | 2015-03-18 | Four to Ten Years | Long-Term Needs | 3 | 20425
3155INT1 | INTERIOR FINISHES | 3155 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | FLEET SERVICES OFFICE - LAS VEGAS | 9790 | Admin | PubWorks | B&G | Las Vegas | 2007 | 4085 | 2015-03-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20425
3155HVA1 | HEATING UPGRADE | 3155 | The electric heater in the garage is broken and the wash bay does not currently have any heating equipment. The garage is uncomfortably cold in the winter and the wash bay cannot be used in cold temperatures. It is recommended to install heating equipment in these areas to ensure a comfortable work environment and an operational wash bay. This project would provide for the purchase and installation of three electric heaters including all required connections to existing utilities. | FLEET SERVICES OFFICE - LAS VEGAS | 9790 | Admin | PubWorks | B&G | Las Vegas | 2007 | 4085 | 2015-03-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
9790SIT1 | CRACK FILL & SEAL ASPHALT PAVING | 9790 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the paving site wide including access roads and parking areas. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 35,000 square feet of asphalt area was used to generate this estimate. | FLEET SERVICES - LAS VEGAS SITE | 9790 | Admin | PubWorks | B&G | Las Vegas | 2007 |  | 2015-03-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 21000
9855ENR3 | EXTERIOR LIGHTING REPLACEMENT | 9855 | The 23 perimeter light poles around the site have a total of 28 light fixtures. These fixtures are metal halide and not energy efficient. This project would provide for the replacement of the exterior lighting fixtures with new LED light fixtures, using existing wiring. | DATA CENTER SITE | 9855 | Admin | PubWorks | B&G | Carson City | 0 |  | 2016-06-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 42000
9855SIT3 | SITE DRAINAGE UPGRADES | 9855 | The grade does not slope away from the building effectively. This is causing water to pool against the foundation. In the winter months, water freezes against the foundation and over time this will cause damage to the foundation. It is recommended per the International Building Code 1804.3 site grading shall be sloped away from the building at a slope of 5-percent for a minimum distance of 10 feet measured perpendicular to the face of the wall. This project would remove the concrete planter wall, excavate the excess soil, install new landscaping, and create positive flow away from the buildings. Additional French drains shall be installed around 450 feet of the building. It is recommended that the this project be completed within 2-3 years. | DATA CENTER SITE | 9855 | Admin | PubWorks | B&G | Carson City | 0 |  | 2016-06-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 60000
9855ADA3 | ADA SIGNAGE & STRIPING | 9855 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The ADA parking area and passenger loading area are missing proper signage and striping to comply with ADA requirements. There is a missing "No Parking" sign at the ADA parking area and the striping has faded. This project would provide for striping, purchase and installation of the sign, and any other necessary upgrades to the parking area. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | DATA CENTER SITE | 9855 | Admin | PubWorks | B&G | Carson City | 0 |  | 2016-06-01 | Immediate to Two Years | Currently Critical | 1 | 3500
9855SIT1 | LOADING DOCK MODIFICATIONS | 9855 | The concrete apron leading up to the loading dock is dysfunctional in its current configuration. The slope from the sidewalk to the gate is too steep causing vehicles to scrape bumpers and hitches on it. When trucks pull up to the dock, they are too high and there is no dock leveler. There is not enough space for most trucks to turn and back up in the street adjacent to the loading area. These issues have caused many delivery companies to refuse to use the ramp requiring the staff to unload in the street. It is recommended to procure engineering services to re-design the approach to the loading dock to ensure a functional system. This project would provide for the removal and disposal of the concrete from the sidewalk to the loading dock, re-grading and installing a total of 1,000 square feet of new concrete, removing and re-installing the automatic gate, and installing a new dock leveler. | DATA CENTER SITE | 9855 | Admin | PubWorks | B&G | Carson City | 0 |  | 2016-06-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 100000
9855SIT2 | CRACK FILL & SEAL ASPHALT PAVING | 9855 | It is important to maintain the asphalt paving on the site. This project would provide for minor crack filling and striping of the parking lot. This project should be scheduled within 2-3 years to maintain the integrity of the paving and prevent premature failure. | DATA CENTER SITE | 9855 | Admin | PubWorks | B&G | Carson City | 0 |  | 2016-06-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19285
9855ADA1 | ADA RAMP MODIFICATIONS | 9855 | In order to comply with current Americans with Disabilities Act (ADA) requirements, modifications will be necessary for the ADA ramp and stairs on the south side of the building. The standards for a ramp require a 36" clear space. Currently, the handrails encroach on this clearance and reduce the clear space to less than 32". The concrete on the stairs and the ramp is deteriorating. Spalling and cracking have occurred. Exposure to the elements is a contributing factor. This project recommends modifying the steel handrails to comply with ADA guidelines, repairing the concrete on the ramp, and replacing the concrete stairs. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | DATA CENTER SITE | 9855 | Admin | PubWorks | B&G | Carson City | 0 |  | 2016-06-01 | Immediate to Two Years | Currently Critical | 1 | 25000
0393INT6 | INTERIOR FINISHES | 0393 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and adequately prepared to receive the coating. An epoxy-based paint should be utilized in wet areas for durability. | DATA CENTER | 9855 | Admin | PubWorks | B&G | Carson City | 1970 | 22928 | 2016-06-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 229280
0393ENR1 | EXTERIOR LIGHTING REPLACEMENT | 0393 | The building has perimeter lighting on the exterior of the building. The light fixtures are metal halide and not energy efficient. This project would provide for the replacement of the 8 exterior wall pack light fixtures with new LED light fixtures, using existing wiring. | DATA CENTER | 9855 | Admin | PubWorks | B&G | Carson City | 1970 | 22928 | 2016-06-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4800
0393HVA1 | AIR CONDITIONING REPLACEMENT | 0393 | The current backup air conditioning unit serving the computer room is 40 years old. The air conditioning unit is beyond its useful life expectancy. If the backup air conditioning unit did not turn on or if it stops working, the server room would become too hot, and this could lead to a catastrophic failure of all the statewide servers (due to overheating). It is recommended to install a new backup air conditioning system. This project would provide for the purchase and installation of a new air conditioning unit, to include all required modifications and connections to the utilities. | DATA CENTER | 9855 | Admin | PubWorks | B&G | Carson City | 1970 | 22928 | 2016-06-01 | Immediate to Two Years | Currently Critical | 1 | 125000
0393EXT3 | ROOF REPLACEMENT | 0393 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty for this building is 15 years. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2006. It is recommended that this building be re-roofed in the next 8-10 years to be consistent with the roofing program and the end of the warranty period. | DATA CENTER | 9855 | Admin | PubWorks | B&G | Carson City | 1970 | 22928 | 2016-06-01 | Four to Ten Years | Long-Term Needs | 3 | 275136
0393PLM1 | WATER HEATER REPLACEMENT | 0393 | There is a 75 gallon gas-fired water heater in the building. The average life span of a water heater is eight to ten years. The water heater was installed in 2006. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 1-2 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | DATA CENTER | 9855 | Admin | PubWorks | B&G | Carson City | 1970 | 22928 | 2016-06-01 | Immediate to Two Years | Currently Critical | 1 | 2500
0393SFT5 | PANIC HARDWARE IN ELECTRICAL ROOMS | 0393 | The electrical room with the Uninterruptible Power Supply system contains equipment that meets or exceeds 1,200 amps. It is recommended per the 2012 International Building Code (IBC) 1008.1.10 that panic and fire exit hardware be installed. This equipment was not required at the time of the 2007 remodel but is suggested in this report as an increased safety measure. It is recommended that this project be completed within 1-2 years. The estimate is based on three doors that require panic hardware. | DATA CENTER | 9855 | Admin | PubWorks | B&G | Carson City | 1970 | 22928 | 2016-06-01 | Immediate to Two Years | Currently Critical | 1 | 9000
0393HVA2 | HVAC SYSTEM REPLACEMENT | 0393 | The HVAC system (chillers, cooling tower, boilers, heat exchanger and associated equipment) was installed in 2006. This project would provide for installation of a new HVAC system and cleaning of the existing duct work and grilles in the next 8-10 years. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | DATA CENTER | 9855 | Admin | PubWorks | B&G | Carson City | 1970 | 22928 | 2016-06-01 | Four to Ten Years | Long-Term Needs | 3 | 573200
0393EXT5 | ROOF REPLACEMENT | 0393 | The roof above the mechanical room was in poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed over 20 years ago. It is recommended that this building be re-roofed in the next 1-2 years. | DATA CENTER | 9855 | Admin | PubWorks | B&G | Carson City | 1970 | 22928 | 2016-06-01 | Immediate to Two Years | Currently Critical | 1 | 9000
0393INT7 | CARPET REPLACEMENT | 0393 | The carpet in the building is showing signs of extreme wear and should be scheduled for replacement. It is recommended that the carpet be replaced with heavy duty commercial grade carpet in the next 2-3 years. | DATA CENTER | 9855 | Admin | PubWorks | B&G | Carson City | 1970 | 22928 | 2016-06-01 | Immediate to Two Years | Currently Critical | 1 | 73500
0393SFT4 | SAFETY CABINETS | 0393 | The building contains many different paints, stains, and other hazardous products located on open shelves and on the floor. This does not meet OSHA standards or International Fire Code for hazardous materials containment. This project would provide for a self-closing hazardous storage container in the building and installation of placards on the building exterior in accordance with OSHA 1910.106 (d) and International Fire Code chapter 57 section 5704.3.2.1.3. | DATA CENTER | 9855 | Admin | PubWorks | B&G | Carson City | 1970 | 22928 | 2016-06-01 | Immediate to Two Years | Currently Critical | 1 | 5000
0393ADA3 | BREAK ROOM REMODEL | 0393 | One of the break rooms in the building dates back to the original construction in 1970. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and countertops are delaminating and failing. This project recommends the replacement of the existing countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards for Accessible Design should be incorporated into the design such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. | DATA CENTER | 9855 | Admin | PubWorks | B&G | Carson City | 1970 | 22928 | 2016-06-01 | Immediate to Two Years | Currently Critical | 1 | 15000
0393INT5 | FLOOR TILE REPLACEMENT | 0393 | The 2"x2" floor tiles in the restrooms are reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12"x12" tiles within the next 2-3 years. | DATA CENTER | 9855 | Admin | PubWorks | B&G | Carson City | 1970 | 22928 | 2016-06-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 27000
0393EXT4 | CEILING REPAIRS | 0393 | There are voids in the lath and plaster ceiling in the mechanical room that need to be repaired. This project recommends patch and repair of all holes in the ceiling. | DATA CENTER | 9855 | Admin | PubWorks | B&G | Carson City | 1970 | 22928 | 2016-06-01 | Immediate to Two Years | Currently Critical | 1 | 2000
0393ADA2 | ADA EMPLOYEE LOUNGE UPGRADES | 0393 | In order to comply with current Americans with Disabilities Act (ADA) requirements, modification will be necessary for the employee lounge in the addition and the kitchenette in the conference room. It is recommended to upgrade some of the features of the rooms for compliance with accessibility standards for employees. This project would provide funding for construction of an accessible sink and faucet, an accessible space at one of the dining tables, and an accessible path of travel throughout the room. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as a reference for this project. | DATA CENTER | 9855 | Admin | PubWorks | B&G | Carson City | 1970 | 22928 | 2016-06-01 | Immediate to Two Years | Currently Critical | 1 | 4000
0393EXT2 | EXTERIOR FINISHES | 0393 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete wall panels, brick and masonry, and caulking of the windows, flashing, fixtures, and all other penetrations. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | DATA CENTER | 9855 | Admin | PubWorks | B&G | Carson City | 1970 | 22928 | 2016-06-01 | Four to Ten Years | Long-Term Needs | 3 | 229280
2503ENV1 | PEST CONTROL | 2503 | There are numerous rodent droppings throughout this building. Due to the potential risk of disease, this project would provide for the treatment and cleanup of the rodent droppings by a licensed pest control business. | MARLETTE LAKE STORAGE SHED | 9895 | Admin | PubWorks | B&G | Carson City | 0 | 48 | 2016-08-17 | Immediate to Two Years | Currently Critical | 1 | 5000
2503INT1 | INTERIOR FINISHES | 2503 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | MARLETTE LAKE STORAGE SHED | 9895 | Admin | PubWorks | B&G | Carson City | 0 | 48 | 2016-08-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 480
2503EXT2 | EXTERIOR FINISHES | 2503 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MARLETTE LAKE STORAGE SHED | 9895 | Admin | PubWorks | B&G | Carson City | 0 | 48 | 2016-08-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 480
2504EXT1 | EXTERIOR FINISHES | 2504 | It is important to maintain the finish, weather resistance and appearance of the tank. This project recommends work to protect the exterior of the tank to include; preparation for painting, caulk and paint. It is recommended for this project to be implemented in the next 2-3 years. Additional recommendations are to conduct inspections and testing on a cyclical basis based per NAC 445. | MARLETTE 1.5 MIL GALLON STORAGE TANK | 9895 | Admin | PubWorks | B&G | Carson City | 0 | 2600 | 2016-08-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 26000
2504INT2 | CONCRETE FOUNDATION | 2504 | The storage tank floor is made of concrete and was in poor condition at the time of the survey. This project would provide for the removal of the spalling and cracking concrete floor and the installation of a 4" thick concrete floor inside the walls of the water tank. | MARLETTE 1.5 MIL GALLON STORAGE TANK | 9895 | Admin | PubWorks | B&G | Carson City | 0 | 2600 | 2016-08-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 260000
2489ENR1 | LIGHTING UPGRADE | 2489 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | MARLETTE LAKE CHLORINE BUILDING | 9895 | Admin | PubWorks | B&G | Carson City | 1989 | 512 | 2016-08-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4096
2504INT1 | INTERIOR FINISHES | 2504 | It is important to maintain water quality, quantity and the interior finish of the water tank. This project would include inspection and cleaning of the interior walls and would also include: welding, sandblasting, repair work and to add protective coatings, if needed. It is important to follow ANSI, NSF and AWWA approved ways to disinfect and repair water tanks. The standard recommendation is to conduct a comprehensive inspection inside the water tank every 5 years, except for newly constructed tanks. Newly constructed water tanks should be inspected within 10 years of service and every 5 years thereafter. | MARLETTE 1.5 MIL GALLON STORAGE TANK | 9895 | Admin | PubWorks | B&G | Carson City | 0 | 2600 | 2016-08-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
2487EXT1 | EXTERIOR FINISHES | 2487 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking, sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MARLETTE LAKE WATER TREATMENT BUILDING | 9895 | Admin | PubWorks | B&G | Carson City | 1984 | 3500 | 2016-08-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7000
2485INT1 | INTERIOR FINISHES INTERIOR FINISHES | 2485 | It is important to maintain water quality, quantity and the interior finish of the water tank. This project would include hiring certified divers or draining the tank to inspect and clean the interior walls, and to weld, sandblast and perform repairs and add protective coatings, if needed. It is important to follow all ANSI, NSF and AWWA approved ways to disinfect and repair water tanks. The standard recommendation is to conduct a comprehensive inspection inside the water tank every 5 years, except for newly constructed tanks. Newly constructed water tanks should be inspected within 10 years of service and every 5 years thereafter. | MARLETTE LAKE 3 MIL GALLON STORAGE TANK | 9895 | Admin | PubWorks | B&G | Carson City | 1979 |  | 2016-08-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
2485EXT2 | GUARDRAIL | 2485 | The NFPA 22 standard designates the requirements for water tanks used for private fire protection. This tank is used to store water for fire protection and is an AWWA D100 tank that is required to have 360° guardrails. This project would provide for the purchase and installation of new guardrails to be located at the top of the water tank. | MARLETTE LAKE 3 MIL GALLON STORAGE TANK | 9895 | Admin | PubWorks | B&G | Carson City | 1979 |  | 2016-08-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
2486EXT2 | GUARDRAIL | 2486 | The NFPA 22 standard designates the requirements for water tanks used for private fire protection. This tank is used to store water for fire protection and is an AWWA D100 tank that is required to have 360° guardrails. This project would provide for the purchase and installation of new guardrails to be located at the top of the water tank. | MARLETTE LAKE 1 MIL GALLON STORAGE TANK | 9895 | Admin | PubWorks | B&G | Carson City | 1984 |  | 2016-08-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
2489EXT2 | ROOF REPLACEMENT | 2489 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayment. This estimate includes removal and disposal of the old roofing. | MARLETTE LAKE CHLORINE BUILDING | 9895 | Admin | PubWorks | B&G | Carson City | 1989 | 512 | 2016-08-17 | Four to Ten Years | Long-Term Needs | 3 | 6144
2489EXT3 | EXTERIOR FINISHES | 2489 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 5-6 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MARLETTE LAKE CHLORINE BUILDING | 9895 | Admin | PubWorks | B&G | Carson City | 1989 | 512 | 2016-08-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5120
2489INT1 | INTERIOR FINISHES | 2489 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | MARLETTE LAKE CHLORINE BUILDING | 9895 | Admin | PubWorks | B&G | Carson City | 1989 | 512 | 2016-08-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 512
2489ENV1 | PEST CONTROL | 2489 | There are numerous rodent droppings throughout this building. Due to the potential risk of disease, this project would provide for treatment and cleanup of the rodent droppings by a licensed pest control business. | MARLETTE LAKE CHLORINE BUILDING | 9895 | Admin | PubWorks | B&G | Carson City | 1989 | 512 | 2016-08-17 | Immediate to Two Years | Currently Critical | 1 | 5000
2486EXT1 | EXTERIOR FINISHES | 2486 | It is important to maintain the finish, weather resistance and appearance of the tank. This project recommends work to protect the exterior of the tank to include; preparation for painting, caulk and paint. It is recommended for this project to be implemented in the next 2-3 years. Additional recommendation is to conduct inspections and testing on a cyclical basis based per NAC 445. | MARLETTE LAKE 1 MIL GALLON STORAGE TANK | 9895 | Admin | PubWorks | B&G | Carson City | 1984 |  | 2016-08-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
2486INT1 | INTERIOR FINISHES | 2486 | It is important to maintain water quality, quantity and the interior finish of the water tank. This project would include hiring certified divers or draining the tank to inspect and clean the interior walls, and to weld, sandblast and perform repairs and add protective coatings, if needed. It is important to follow all ANSI, NSF and AWWA approved ways to disinfect and repair water tanks. The standard recommendation is to conduct a comprehensive inspection inside the water tank every 5 years, except for newly constructed tanks. Newly constructed water tanks should be inspected within 10 years of service and every 5 years thereafter. | MARLETTE LAKE 1 MIL GALLON STORAGE TANK | 9895 | Admin | PubWorks | B&G | Carson City | 1984 |  | 2016-08-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
2485EXT1 | EXTERIOR FINISHES | 2485 | It is important to maintain the finish, weather resistance and appearance of the tank. This project recommends work to protect the exterior of the tank to include; preparation for painting, caulk and paint. It is recommended for this project to be implemented in the next 2-3 years. Additional recommendation is to conduct inspections and testing on a cyclical basis based per NAC 445. | MARLETTE LAKE 3 MIL GALLON STORAGE TANK | 9895 | Admin | PubWorks | B&G | Carson City | 1979 |  | 2016-08-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 52000
2487ENV1 | PEST CONTROL | 2487 | There are numerous rodent droppings throughout this building. Due to the potential risk of disease, this project would provide for treatment and cleanup of the rodent droppings by a licensed pest control business. | MARLETTE LAKE WATER TREATMENT BUILDING | 9895 | Admin | PubWorks | B&G | Carson City | 1984 | 3500 | 2016-08-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
9895SIT2 | FENCING | 9895 | The Marlette Lake/ Ash Canyon Site is currently fenced off to the general public for safety. There are some areas of the fence that are damaged and should be repaired. This project would provide for repairs to the existing 6 foot tall industrial chain link fence. This project or a portion thereof was previously recommended in the FCA report dated 03/03/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/17/2016. | MARLETTE LAKE/ ASH CANYON SITE | 9895 | Admin | PubWorks | B&G | Carson City | 0 |  | 2016-08-17 | Four to Ten Years | Long-Term Needs | 3 | 8750
9895SIT4 | IRRIGATION SYSTEM | 9895 | The existing irrigation system’s sprinkler heads spray and wet the buildings. Much of the control wiring to the irrigation valves and some of sprinkler pipes are broken. The underground control values are worn and leaking. This project would provide funding for the repair and replacement of the necessary irrigation systems, water conservation and to move the irrigation to prevent the water from spraying on the building. This project or a portion thereof was previously recommended in the FCA report dated 03/03/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/17/2016. | MARLETTE LAKE/ ASH CANYON SITE | 9895 | Admin | PubWorks | B&G | Carson City | 0 |  | 2016-08-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 85000
3763SFT1 | EXTERIOR LANDING INSTALLATION | 3763 | There is an out-swinging exterior door from the building that swings out over a step and does not have a landing that complies with IBC 2012. IBC Section 1008 which requires a landing to be not more than 1/2" below the threshold. This project would provide for the installation of a compliant landing for the door. | DIVERSION DAM METER BLDG | 9788 | Admin | PubWorks | B&G | Carson City | 2007 | 72 | 2016-09-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
3031INT1 | INTERIOR FINISHES | 3031 | It is recommended to repair and seal the interior concrete block walls at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. | GENERATOR BUILDING | 9788 | Admin | PubWorks | B&G | Carson City | 2009 | 952 | 2016-09-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9520
3762EXT2 | GUARDRAIL | 3762 | The NFPA 22 standard designates the requirements for water tanks used for private fire protection. This tank is used to store water for fire protection and is an AWWA D100 tank that is required to have 360° guardrails. This project would provide for the purchase and installation of new guardrails to be located at the top of the water tank. | LAKEVIEW WATER TANK | 9788 | Admin | PubWorks | B&G | Carson City | 1987 | 205 | 2016-09-13 | Immediate to Two Years | Currently Critical | 1 | 12000
3762EXT1 | EXTERIOR FINISHES | 3762 | It is important to maintain the finish, weather resistance and appearance of the tank. This project recommends work to protect the exterior of the tank to include; preparation for painting, caulk and paint. It is recommended for this project to be implemented in the next 4-5 years. An additional recommendation is to conduct inspections and testing on a cyclical basis based per NAC 445. | LAKEVIEW WATER TANK | 9788 | Admin | PubWorks | B&G | Carson City | 1987 | 205 | 2016-09-13 | Four to Ten Years | Long-Term Needs | 3 | 2050
3031EXT1 | EXTERIOR FINISHES | 3031 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | GENERATOR BUILDING | 9788 | Admin | PubWorks | B&G | Carson City | 2009 | 952 | 2016-09-13 | Four to Ten Years | Long-Term Needs | 3 | 9520
3031SFT1 | BATTERY STORAGE | 3031 | Section 608 of the 2012 IFC explains the requirements for stationary storage of battery systems. Batteries shall have safety caps, spill control and neutralization, mechanical ventilation and/or cabinet ventilation, supervision over the mechanical ventilation, building or cabinet signage, seismically braced and a smoke alarm. This project will provide funding for the requirements of Section 608 of the 2012 IFC proper way to store, charge and/or use batteries indoors. | GENERATOR BUILDING | 9788 | Admin | PubWorks | B&G | Carson City | 2009 | 952 | 2016-09-13 | Immediate to Two Years | Currently Critical | 1 | 25000
3031HVA1 | HEATER REPLACEMENT | 3031 | The building currently has open combustion air for the generator. The combustion air is located on the side wall and on the ceiling. When the heater runs in the building the heat rises and escapes through the combustion air on the ceiling. This makes the building very unpleasant to work in when the weather is cold. This project would remove the existing heater and provide for the installation of two suspended radiant heaters. The estimate includes two radiant heaters, seismic supports and connections to all the utilities. | GENERATOR BUILDING | 9788 | Admin | PubWorks | B&G | Carson City | 2009 | 952 | 2016-09-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
3761EXT2 | EXTERIOR FINISHES | 3761 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit and T1-11 walls, and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | LAKEVIEW METER BUILDING | 9788 | Admin | PubWorks | B&G | Carson City | 1987 | 200 | 2016-09-13 | Four to Ten Years | Long-Term Needs | 3 | 2000
3031SIT2 | GENERATOR MAINTENANCE | 3031 | Preventative maintenance for generators plays a critical role in maximizing reliability, minimizing repairs, reducing long term costs and prolonging the life expectancy of generators. This project would provide for a licensed contractor to perform the preventive maintenance on the generator that is required from the manufacturer specifications. | GENERATOR BUILDING | 9788 | Admin | PubWorks | B&G | Carson City | 2009 | 952 | 2016-09-13 | Immediate to Two Years | Currently Critical | 1 | 10000
9788SIT1 | FENCING INSTALLATION | 9788 | The Marlette Lake Water System Site has several buildings, abandoned water ways, and many areas where the general public use the area for hiking, biking, and other outdoor activities. This site requires a higher level of security for the safety of the general public and also to protect the drinking water supply. This project would provide for permanent chain link fencing to surround the high security buildings to protect the drinking water supply. Additional chain link fencing is needed for the general public’s safety to protect them from areas where safety is a concern. This project would provide 1000 LF of chain link fencing throughout the site at $35 per LF. | MARLETTE LAKE WATER SYSTEM SITE | 9788 | Admin | PubWorks | B&G | Carson City | 0 |  | 2016-09-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35000
9788SFT1 | WALKING SURFACES/ GUARDRAILS | 9788 | The Marlette Lake Water System Site has several dams, uneven walking surfaces and wet locations that don’t have the proper slip resistant platform walking surfaces required by OSHA 1910.22(a)(2), Where wet processes are used, drainage shall be maintained and false floors, platforms, mats, or other dry standing places should be provided where practicable. There are several locations where it is required for employees to access dams, buildings and other locations where there is possible risk of falling into pits, dams and ditches. Per OSHA 1910.22(c), covers and/or guardrails shall be provided to protect personnel from the hazards of open pits, tanks, vats, ditches, etc. This project will provide funding for OSHA required nonslip platforms and railings to be installed across dams, ditches, and uneven surfacing throughout the site where necessary. | MARLETTE LAKE WATER SYSTEM SITE | 9788 | Admin | PubWorks | B&G | Carson City | 0 |  | 2016-09-13 | Immediate to Two Years | Currently Critical | 1 | 25000
3760EXT1 | EXTERIOR FINISHES | 3760 | It is important to maintain the finish, weather resistance and appearance of the structure. This project recommends work to protect the exterior building envelope including repairs to the exterior fencing, privacy slats, fence posts and hardware. This project would provide funding to protect the exterior of the building excluding the roof. It is recommended that this project be implemented in the next 4-5 years and it is also recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | LAKEVIEW PROPANE STORAGE BLDG | 9788 | Admin | PubWorks | B&G | Carson City | 1987 | 40 | 2016-09-13 | Four to Ten Years | Long-Term Needs | 3 | 80
3763EXT1 | EXTERIOR FINISHES | 3763 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | DIVERSION DAM METER BLDG | 9788 | Admin | PubWorks | B&G | Carson City | 2007 | 72 | 2016-09-13 | Four to Ten Years | Long-Term Needs | 3 | 720
3761EXT3 | ROOF REPLACEMENT | 3761 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 1-2 years with a new 50 year asphalt composition shingle roof and new underlayment. This estimate includes removal and disposal of the old roof. | LAKEVIEW METER BUILDING | 9788 | Admin | PubWorks | B&G | Carson City | 1987 | 200 | 2016-09-13 | Immediate to Two Years | Currently Critical | 1 | 2400
3765EXT1 | EXTERIOR FINISHES | 3765 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOBART METER BUILDING | 9788 | Admin | PubWorks | B&G | Carson City | 2007 | 48 | 2016-09-13 | Four to Ten Years | Long-Term Needs | 3 | 480
3762INT1 | INTERIOR FINISHES | 3762 | It is important to maintain water quality, quantity and the interior finish of the water tank. This project would include hiring certified divers or draining the tank to inspect and clean the interior walls, and to weld, sandblast and perform repairs and add protective coatings, if needed. It is important to follow all ANSI, NSF and AWWA approved ways to disinfect and repair water tanks. The standard recommendation is to conduct a comprehensive inspection inside the water tank every 5 years, except for newly constructed tanks. Newly constructed water tanks should be inspected within 10 years of service and every 5 years thereafter. | LAKEVIEW WATER TANK | 9788 | Admin | PubWorks | B&G | Carson City | 1987 | 205 | 2016-09-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
3031SIT1 | SITE DRAINAGE UPGRADES | 3031 | The grade does not slope away effectively from the building. Water has pooled against the foundation. In the winter months, as the water freezes against the foundation, over time, this can cause damage to the foundation. It is recommended per IBC 1804.3, Site Grading the ground immediately adjacent to the foundation shall be sloped away from the building at a slope of not less than one vertical in 20 units horizontal (5-percent slope) for a minimum distance of 10 feet (3048 mm) measured perpendicular to the face of the wall. This project would create a 5% slope away from the building. Additional drainage swales shall be installed, as needed. It is recommended that the grading be completed within 2-3 years. | GENERATOR BUILDING | 9788 | Admin | PubWorks | B&G | Carson City | 2009 | 952 | 2016-09-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
3031ENV1 | SPILL CONTAINMENT | 3031 | The building does not have a method for containing spills or leakage from drums. This project would add secondary containment pallets for all containers in the building and install placards on the building’s exterior. | GENERATOR BUILDING | 9788 | Admin | PubWorks | B&G | Carson City | 2009 | 952 | 2016-09-13 | Immediate to Two Years | Currently Critical | 1 | 6500
3031SFT2 | EXIT SIGN AND EGRESS LIGHTING | 3031 | The building does not have emergency lighting and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC 2012 Chapter 10 was referenced for this project. | GENERATOR BUILDING | 9788 | Admin | PubWorks | B&G | Carson City | 2009 | 952 | 2016-09-13 | Immediate to Two Years | Currently Critical | 1 | 4760
3761SFT1 | EXTERIOR LANDING INSTALLATION | 3761 | There is an out-swinging exterior door from the building which swings out over a step and does not have a landing that complies with IBC 2012. IBC Section 1008 requires a landing to be not more than 1/2" below the threshold. This project would provide for the installation of a compliant landing for the door. | LAKEVIEW METER BUILDING | 9788 | Admin | PubWorks | B&G | Carson City | 1987 | 200 | 2016-09-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
1680INT6 | INTERIOR FINISHES | 1680 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | GRANT SAWYER STATE OFFICE | 9835 | Admin | PubWorks | B&G | Las Vegas | 1995 | 224000 | 2017-12-14 | Four to Ten Years | Long-Term Needs | 3 | 1120000
1680SFT4 | BOILER ROOM EMERGENCY SHUTOFF INSTALLATION | 1680 | The existing boiler room has no emergency shut off switch as required by code for boilers with a fuel input of greater than 2,500,000 btu/h. Each of these boilers has a maximum input of 3,500,000 btu/h. This project would install a mushroom switch just outside the boiler room door to shut down all power to both boilers in an emergency. It is also recommended to replace the labels on all of the shut off switches in the building including those for the chillers and exhaust fans. The 2006 Uniform Mechanical Code Table 10-3 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 12/08/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/27/2011. | GRANT SAWYER STATE OFFICE | 9835 | Admin | PubWorks | B&G | Las Vegas | 1995 | 224000 | 2017-12-14 | Immediate to Two Years | Currently Critical | 1 | 2500
1680SEC1 | SECURITY SYSTEM UPGRADE | 1680 | The site and building security system is outdated and there is at least one area where the system is vulnerable. Since the Gaming Control Board, Governor's Office and other highly secure offices are located here, it is recommended to upgrade the system in the next 2-3 years. This project addresses replacement of the cameras, door sensors and alarms including new digital recording equipment with sufficient storage capacity. | GRANT SAWYER STATE OFFICE | 9835 | Admin | PubWorks | B&G | Las Vegas | 1995 | 224000 | 2017-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 560000
1680SFT8 | INTERIOR DOOR REPAIRS | 1680 | Numerous locks, closers, weather strips, smoke seals, and magnetic door holders need repair and adjustment. The magnetic door holders and automatic closers are all failing. This compromises the fire protection system in the building and should be addressed immediately. This project provides funding to repair, replace, or adjust door hardware throughout the facility. This project or a portion thereof was previously recommended in the FCA report dated 12/08/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/27/2011. | GRANT SAWYER STATE OFFICE | 9835 | Admin | PubWorks | B&G | Las Vegas | 1995 | 224000 | 2017-12-14 | Immediate to Two Years | Currently Critical | 1 | 40000
1680HVA4 | HVAC UPGRADE | 1680 | The HVAC system in the building is approaching the end of its expected life and should be scheduled for replacement. The cooling towers have already been replaced. The boilers, chillers, air handlers, control system, water treatment equipment and piping are all original to the building. Most equipment has an expected life of about 20-25 years. Also, the piping for the HVAC water lines is steel that is crimped at the connections. This type of piping is prone to leaking and should be replaced. The existing system is not energy efficient and has reached the end of its expected and useful life. This project would provide for installation of new HVAC equipment throughout the building and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC equipment and all required connections to utilities. | GRANT SAWYER STATE OFFICE | 9835 | Admin | PubWorks | B&G | Las Vegas | 1995 | 224000 | 2017-12-14 | Four to Ten Years | Long-Term Needs | 3 | 6720000
1680SFT7 | REPAIR PARKING LOT LIGHT BASES | 1680 | Several light poles in the parking lot have deteriorated concrete bases. This project would replace the cap concrete and seal it against weather deterioration. This project or a portion thereof was previously recommended in the FCA report dated 12/08/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/27/2011. | GRANT SAWYER STATE OFFICE | 9835 | Admin | PubWorks | B&G | Las Vegas | 1995 | 224000 | 2017-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
1680EXT9 | ROOF REPLACEMENT | 1680 | The roof on this building was in poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. Exterior wall tiles have fallen on the roof membrane resulting in a large number of patches in the membrane. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1995. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 12/08/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/27/2011. | GRANT SAWYER STATE OFFICE | 9835 | Admin | PubWorks | B&G | Las Vegas | 1995 | 224000 | 2017-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 600000
1680PLM2 | WATER HEATER REPLACEMENT | 1680 | Three of the four 100 gallon gas-fired water heaters in the boiler room have been replaced recently. The average life span of a water heater is eight to ten years. With the passage of time and constant use, the older unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed. The other three water heaters in the room have been replaced recently, but do not have seismic straps installed. This project includes seismic straps for all four water heaters. Removal and disposal of the existing equipment is included in this estimate. | GRANT SAWYER STATE OFFICE | 9835 | Admin | PubWorks | B&G | Las Vegas | 1995 | 224000 | 2017-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
1680SFT3 | INSTALL SAFETY CAGE ON FIRE PROTECTION RISER | 1680 | The fire riser on the loading dock provides fire suppression to the Gaming Control Board computer room. The riser is exposed to delivery trucks and other vehicles using the loading dock which could damage the equipment. This poses a serious risk to the sensitive and highly secure information with regards to the Gaming Control Board. This project would install bollards and a chain link fence cage around the riser to protect it from impact damage and tampering. This project or a portion thereof was previously recommended in the FCA report dated 12/08/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/27/2011. | GRANT SAWYER STATE OFFICE | 9835 | Admin | PubWorks | B&G | Las Vegas | 1995 | 224000 | 2017-12-14 | Immediate to Two Years | Currently Critical | 1 | 5000
1680ELE1 | VIDEO FEED INSTALLATION | 1680 | When the Governor holds press conferences here, the press personnel does not have a live video feed to hook up to in the parking lot. They must go to the Governors Office in order to connect their media trucks which creates a crowded room with excess wiring and equipment strewn about. Staff recommended utilizing the existing connection near the loading dock and installing a wireless transmitter there which can be accessed throughout the site. This project would provide for installing a transmitter to send a wireless signal from the Governor's Office to the entire site in order to simplify the coordination of the press conferences. | GRANT SAWYER STATE OFFICE | 9835 | Admin | PubWorks | B&G | Las Vegas | 1995 | 224000 | 2017-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
1680EXT6 | ROOF HATCH REPLACEMENT | 1680 | The roof hatch is original to the building and has reached the end of its useful life. The compression spring operators on this large and heavy hatch do not function properly, the latches and handles are worn and the seals and flashing have deteriorated. A faulty roof hatch is a safety hazard to anyone accessing the roof. This project would provide for removal and disposal of the existing roof hatch and purchase and installation of a new roof hatch. | GRANT SAWYER STATE OFFICE | 9835 | Admin | PubWorks | B&G | Las Vegas | 1995 | 224000 | 2017-12-14 | Immediate to Two Years | Currently Critical | 1 | 3500
1680HVA7 | PROVIDE SEPARATE MAIL ROOM HVAC | 1680 | Mail rooms have become a security issue in recent years and Homeland Security recommends separating mail room HVAC systems from the remainder of the building systems. This project would provide a separate system for the mail room with an emergency shut off switch. This project or a portion thereof was previously recommended in the FCA report dated 12/08/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/27/2011. | GRANT SAWYER STATE OFFICE | 9835 | Admin | PubWorks | B&G | Las Vegas | 1995 | 224000 | 2017-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35000
1680SFT5 | SIGNAGE UPGRADES | 1680 | The interior of the building is lacking evacuation diagrams and directional signage in most areas. Evacuation plans are required by the National Fire Protection Association for buildings with an occupancy greater than 500. Employees and visitors are often confused by the existing directional signage and labeling of the six story structure. Restrooms, stairs and elevators are difficult to find with the existing lack of signage. This project would provide additional evacuation diagrams throughout the building and a comprehensive upgrade to the directional signage for visitors and employees. This project or a portion thereof was previously recommended in the FCA report dated 12/08/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/27/2011. | GRANT SAWYER STATE OFFICE | 9835 | Admin | PubWorks | B&G | Las Vegas | 1995 | 224000 | 2017-12-14 | Immediate to Two Years | Currently Critical | 1 | 15000
1680INT3 | RELOCATE DATA/ COM EQUIPEMENT | 1680 | The equipment in the Data/ Com Room on the first floor is subject to damage by leaking water pipes above it and should be relocated. Equipment in Room 1038 includes computer servers, spare computer parts, telephone equipment, data lines and other related items. Above this equipment, near the ceiling are several different types of pipes containing water including fire suppression system pipes, sewer pipes and water supply pipes for the HVAC equipment. All of these water pipes are susceptible to leaking from normal aging or a natural event such as an earthquake. It is recommended to relocate the sensitive data and communications equipment to a different room which does not have water pipes in it. The estimate includes reconnecting all equipment in the new location. | GRANT SAWYER STATE OFFICE | 9835 | Admin | PubWorks | B&G | Las Vegas | 1995 | 224000 | 2017-12-14 | Immediate to Two Years | Currently Critical | 1 | 15000
1680EXT2 | EXTERIOR FINISHES | 1680 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing the entire building, repairing the tile and grout as needed, priming and painting the stucco and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building finishes are addressed in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | GRANT SAWYER STATE OFFICE | 9835 | Admin | PubWorks | B&G | Las Vegas | 1995 | 224000 | 2017-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 224000
1680HVA2 | KITCHEN MAKE-UP AIR UNIT INSTALLATION | 1680 | The exhaust hoods in the kitchen currently take air from the building and the building is balanced for this exhaust. Changes in building operation require the HVAC system to operate 24 hours a day yet the kitchen closes down over night. This creates an unbalanced air delivery system. This project would install a dedicated make-up air system for the kitchen to compensate for the hoods and rebalance the buildings HVAC system. The estimate is based on a 40,000 CFM make-up air unit. This project or a portion thereof was previously recommended in the FCA report dated 12/08/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/27/2011. | GRANT SAWYER STATE OFFICE | 9835 | Admin | PubWorks | B&G | Las Vegas | 1995 | 224000 | 2017-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 29900
1680SFT1 | LOADING DOCK LIFT INSTALLATION | 1680 | The existing loading dock does not accommodate smaller delivery trucks requiring personnel to lift equipment onto the loading dock. The loading dock is also missing a ramp which would provide for some of the smaller deliveries to be wheeled up. Gaming Commission deliveries must be brought into the building through the building's rear personnel door which poses a security risk. This project would install a powered 6' x 8' loading dock lift and a concrete ramp for smaller deliveries in place of the damaged stairs. This project or a portion thereof was previously recommended in the FCA report dated 12/08/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/27/2011. | GRANT SAWYER STATE OFFICE | 9835 | Admin | PubWorks | B&G | Las Vegas | 1995 | 224000 | 2017-12-14 | Immediate to Two Years | Currently Critical | 1 | 22500
1680EXT7 | EXTERIOR DOOR REPLACEMENT | 1680 | The exterior metal door at the loading dock is damaged from age and general wear and tear and has reached the end of its expected life. Carts and hand trucks have caused most of the damage during normal deliveries to the building. This project would provide for the replacement of the door assembly with a new metal door, frame and hardware. Removal and disposal of the existing door is included in this estimate. | GRANT SAWYER STATE OFFICE | 9835 | Admin | PubWorks | B&G | Las Vegas | 1995 | 224000 | 2017-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3500
3099PLM1 | SUMP PUMP REPLACEMENT | 3099 | The existing sump pump in the Fire Pump Room is undersized and should be scheduled for replacement. The State's property insurance company has recommended a larger pump. This project provides for replacing the existing 1/3 horsepower pump with a 1/2 horsepower pump. Removal and disposal of the existing equipment is included in the estimate. | GRANT SAWYER GARAGE/PUMP HOUSE | 9835 | Admin | PubWorks | B&G | Las Vegas | 1995 | 2462 | 2017-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1250
9835ENR1 | EXTERIOR SOLAR SITE LIGHTING UPGRADE | 9835 | There are approximately seventeen existing light poles around the site. The existing light fixtures are the older high pressure sodium type. These are costly to replace and are not energy efficient. It is recommended to upgrade the fixtures to higher efficiency units with a longer life cycle. This project would provide for the installation of 17 solar powered LED exterior light fixtures. | GRANT SAWYER OFFICE SITE | 9835 | Admin | PubWorks | B&G | Las Vegas | 0 |  | 2017-12-14 | Four to Ten Years | Long-Term Needs | 3 | 110500
3099EXT1 | EXTERIOR FINISHES | 3099 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | GRANT SAWYER GARAGE/PUMP HOUSE | 9835 | Admin | PubWorks | B&G | Las Vegas | 1995 | 2462 | 2017-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12310
9835ADA1 | ADA SIGNAGE UPGRADES | 9835 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The concrete parking area and passenger loading area are missing proper signage in accordance with ADA requirements. This project would provide for purchasing and installing a "NO PARKING" sign at one of the loading zones next to the accessible parking space and replacing a "WHEEL CHAIR" sign with a current directional sign on the east elevation of the building. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | GRANT SAWYER OFFICE SITE | 9835 | Admin | PubWorks | B&G | Las Vegas | 0 |  | 2017-12-14 | Immediate to Two Years | Currently Critical | 1 | 1000
9835SIT1 | SEAL ASPHALT PAVING | 9835 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the paving site wide including access roads, parking areas and the maintenance yard. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 400,000 square feet of asphalt area was used to generate this estimate. | GRANT SAWYER OFFICE SITE | 9835 | Admin | PubWorks | B&G | Las Vegas | 0 |  | 2017-12-14 | Four to Ten Years | Long-Term Needs | 3 | 200000
2395INT2 | INTERIOR FINISHES | 2395 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings in the office portion of the building be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | LAS VEGAS PURCHASING WAREHOUSE | 9914 | Admin | PubWorks | B&G | Las Vegas | 1960 | 13000 | 2018-05-24 | Four to Ten Years | Long-Term Needs | 3 | 7500
2395SFT4 | FIRE ALARM SYSTEM INSTALLATION | 2395 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2006 Section 7 and the 2006 International Fire Code. | LAS VEGAS PURCHASING WAREHOUSE | 9914 | Admin | PubWorks | B&G | Las Vegas | 1960 | 13000 | 2018-05-24 | Immediate to Two Years | Currently Critical | 1 | 45500
2396EXT1 | DEMOLISH STRUCTURE | 2396 | The wood framed structure is structurally failing and is in danger of falling down. At least one post has sheared off and is resting on the asphalt, numerous wood members are splitting and numerous connections between structural members have detached. The roof sheathing is also failing and is dangerous due to wood pieces becoming detached by the wind. The structure is dilapidated and deteriorating and has reached the end of its useful life. This project would provide funding for the demolition of the structure. | PURCHASING WAREHOUSE CARPORT | 9914 | Admin | PubWorks | B&G | Las Vegas | 1960 | 2000 | 2018-05-24 | Immediate to Two Years | Currently Critical | 1 | 20000
2395EXT2 | EXTERIOR FINISHES | 2395 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting or sealing the concrete masonry unit walls and caulking of the windows, flashing, fixtures, and all other penetrations. It is recommended that the building be painted, sealed, and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | LAS VEGAS PURCHASING WAREHOUSE | 9914 | Admin | PubWorks | B&G | Las Vegas | 1960 | 13000 | 2018-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 65000
2395EXT5 | ROOF REPLACEMENT | 2395 | The roof on this building was in poor condition at the time of the survey. The current roofing system which was installed in 2007 is an elastomeric silicone coating and rigid insulation over the original standing seam metal roof panels. The elastomeric coating is splitting and cracking in many areas due to expansion and contraction of the metal roof framing. It is recommended that this building be re-roofed in the next 1-2 years to maintain the integrity of the structure. | LAS VEGAS PURCHASING WAREHOUSE | 9914 | Admin | PubWorks | B&G | Las Vegas | 1960 | 13000 | 2018-05-24 | Immediate to Two Years | Currently Critical | 1 | 156000
2395INT3 | COLUMN REPAIRS | 2395 | The existing gypsum board wrapped columns are severely damaged from water infiltration and impacts from forklifts and / or vehicles. This project would provide for column repairs which could include a spray on foam fire proofing system or a gypsum board column wrap. | LAS VEGAS PURCHASING WAREHOUSE | 9914 | Admin | PubWorks | B&G | Las Vegas | 1960 | 13000 | 2018-05-24 | Immediate to Two Years | Currently Critical | 1 | 18000
2395EXT6 | WINDOW REPLACEMENT | 2395 | There are four old single pane windows which are in need of replacement. This project would provide for four new insulated window units to be installed. Removal and disposal of the old units is included in this estimate. | LAS VEGAS PURCHASING WAREHOUSE | 9914 | Admin | PubWorks | B&G | Las Vegas | 1960 | 13000 | 2018-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
2395EXT3 | EXTERIOR DOOR REPLACEMENT | 2395 | The exterior metal man door is damaged from age and general wear and tear and has reached the end of its expected life. This project would provide for the replacement of the single man door assembly with a new metal door, frame, and hardware. Removal and disposal of the existing door is included in this estimate. | LAS VEGAS PURCHASING WAREHOUSE | 9914 | Admin | PubWorks | B&G | Las Vegas | 1960 | 13000 | 2018-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
2395ENR2 | HVAC EQUIPMENT REPLACEMENT | 2395 | One of the two HVAC roof top units above the office area has reached the end of its expected and useful life. This project would provide for installation of one new HVAC packaged unit and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC unit and all required connections to utilities. | LAS VEGAS PURCHASING WAREHOUSE | 9914 | Admin | PubWorks | B&G | Las Vegas | 1960 | 13000 | 2018-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7000
2395SFT3 | FIRE SUPPRESSION SYSTEM INSTALLATION | 2395 | The building is more than 12,000 square feet. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 or R-2 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. | LAS VEGAS PURCHASING WAREHOUSE | 9914 | Admin | PubWorks | B&G | Las Vegas | 1960 | 13000 | 2018-05-24 | Immediate to Two Years | Currently Critical | 1 | 123500
2395SFT1 | INTERIOR STAIR HANDRAIL REPLACEMENT | 2395 | The interior stair handrail is older and does not meet code for safety or accessibility. The gripping surfaces are incorrect, the handrail is missing from one side of the stair and it does not have proper returns. This project recommends the installation of handrails on both sides of the stairs, with proper returns and supports. Removal and disposal of the existing railing is included. NRS 338.180, 2006 IBC Chapter 10, Section 1012, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 10/14/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/10/2012. | LAS VEGAS PURCHASING WAREHOUSE | 9914 | Admin | PubWorks | B&G | Las Vegas | 1960 | 13000 | 2018-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
2395ENR1 | LIGHTING UPGRADE | 2395 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, the conference room, and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | LAS VEGAS PURCHASING WAREHOUSE | 9914 | Admin | PubWorks | B&G | Las Vegas | 1960 | 13000 | 2018-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 32500
2395EXT4 | LOADING DOCK UPGRADE | 2395 | The loading dock is damaged and due for major repairs. The concrete is cracked and failing to the point of exposing the reinforcing steel and jeopardizing the integrity of the structure. The ramp from the parking lot also has significant deterioration and requires complete replacement. This project would provide for repairs to the loading dock including removing and replacing damaged concrete and bumpers, replacement of the ramp, and installing a mechanical dock leveler. | LAS VEGAS PURCHASING WAREHOUSE | 9914 | Admin | PubWorks | B&G | Las Vegas | 1960 | 13000 | 2018-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 125000
2395STR1 | STRUCTURAL / SEISMIC RETROFIT | 2395 | The concrete masonry and steel framed structure was built in 1960 and is due for structural repairs. There are major cracks in the concrete masonry unit walls which have gotten worse year by year. Water which infiltrates the cracks freezes in the winter and causes the cracks to widen. Cracking at the southwest corner of the building is significant and may indicate a settling issue below the foundation. The water infiltration also damages the interior of the building and is a health department violation due to the storage of dry goods in the building. It is recommended to repair the structure immediately by patching and sealing any existing cracks. Further evaluation of the structure should be done to determine whether more permanent repairs are needed such as pumping under the foundation or rebuilding the walls. | LAS VEGAS PURCHASING WAREHOUSE | 9914 | Admin | PubWorks | B&G | Las Vegas | 1960 | 13000 | 2018-05-24 | Immediate to Two Years | Currently Critical | 1 | 390000
2395ADA2 | ADA RESTROOM REMODEL | 2395 | The Men's and Women's restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom. The items may include a new sink, toilet, hardware, mirror, fixture, flooring and paint. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | LAS VEGAS PURCHASING WAREHOUSE | 9914 | Admin | PubWorks | B&G | Las Vegas | 1960 | 13000 | 2018-05-24 | Immediate to Two Years | Currently Critical | 1 | 15000
9914SEC1 | FENCE REPLACEMENT | 9914 | The majority of the fencing on the west and north sides has reached the end of its expected life and should be scheduled for replacement. This project recommends the installation of a 6 foot high 6 gauge wire perimeter chain link fence with barbed or razor wire on the south, west and north sides of the property. The fence on the east side was recently replaced and is in good condition. The cost estimate also includes demolition and disposal of the existing fence. | LAS VEGAS PURCHASING WAREHOUSE SITE | 9914 | Admin | PubWorks | B&G | Las Vegas | 1960 |  | 2018-05-24 | Immediate to Two Years | Currently Critical | 1 | 30000
9914ADA1 | ADA ACCESSIBLE PARKING AND PATH OF TRAVEL | 9914 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the office door are necessary to comply with ADA accessibility requirements. This project would provide for a concrete van accessible ADA parking and loading space and concrete walkway to the existing sidewalk. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2006 IBC, ICC/ANSI A117.1 - 2003 and the most current version of the Americans With Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. 750 square feet of concrete was used for this estimate. It is recommended that this project coincide with the ASPHALT PAVING REPLACEMENT project. | LAS VEGAS PURCHASING WAREHOUSE SITE | 9914 | Admin | PubWorks | B&G | Las Vegas | 1960 |  | 2018-05-24 | Immediate to Two Years | Currently Critical | 1 | 10000
9914SEC2 | EXTERIOR SOLAR SITE LIGHTING INSTALLATION | 9914 | There is no site lighting for the site which is a security and safety concern. This project would provide for the installation of 5 solar powered LED exterior light fixtures, 20 foot tall poles and 30" diameter raised concrete bases. This installation will eliminate the need for trenching and electrical connections. | LAS VEGAS PURCHASING WAREHOUSE SITE | 9914 | Admin | PubWorks | B&G | Las Vegas | 1960 |  | 2018-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 32500
9914SIT1 | ASPHALT PAVING REPLACEMENT | 9914 | The asphalt paving around the building is failing, with significant alligatoring, settling and cracks observed. This project covers the removal and replacement of the existing asphalt site wide for parking, site access and deliveries. Striping for safety, parking and loading zones is included in this estimate. 25,000 square feet was used to generate this estimate. This project should be implemented concurrently with the ADA ACCESSIBLE PARKING AND PATH OF TRAVEL project. This project or a portion thereof was previously recommended in the FCA report dated 10/14/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/10/2012. | LAS VEGAS PURCHASING WAREHOUSE SITE | 9914 | Admin | PubWorks | B&G | Las Vegas | 1960 |  | 2018-05-24 | Immediate to Two Years | Currently Critical | 1 | 250000
2450EXT2 | CONSTRUCT WIND BREAK | 2450 | The west entrance to the building has automatic sliding doors in an aluminum storefront system. The doors have been damaged and have had operational problems due to strong winds ever since the building was constructed. This project would provide for the installation of a windbreak structure near the west entrance to prevent the wind from damaging the doors. A CIP was requested by the agency for FY 2009 in the amount of $132,000, but it was not known at the time of the survey whether this project would be approved. | RICHARD H. BRYAN BUILDING | 9867 | Admin | PubWorks | B&G | Carson City | 2005 | 120490 | 2018-07-31 | Immediate to Two Years | Currently Critical | 1 | 132000
2450EXT1 | EXTERIOR FINISHES | 2450 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and it is also recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | RICHARD H. BRYAN BUILDING | 9867 | Admin | PubWorks | B&G | Carson City | 2005 | 120490 | 2018-07-31 | Four to Ten Years | Long-Term Needs | 3 | 602765
2450INT1 | INTERIOR FINISHES | 2450 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next four to five years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | RICHARD H. BRYAN BUILDING | 9867 | Admin | PubWorks | B&G | Carson City | 2005 | 120490 | 2018-07-31 | Four to Ten Years | Long-Term Needs | 3 | 602765
2450HVA1 | HVAC ALTERATIONS | 2450 | The server rooms throughout the building are often overheated which can lead to premature failure of the systems. The rooms are not on a separate HVAC system from the common office areas nearby. This project would provide for alterations to the HVAC system to isolate the server rooms from the common office areas. | RICHARD H. BRYAN BUILDING | 9867 | Admin | PubWorks | B&G | Carson City | 2005 | 120490 | 2018-07-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
9867SIT1 | SLURRY SEAL ASPHALT PAVING - MAIN LOT | 9867 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the main parking lot. Striping is included in this estimate. It is recommended that this project be implemented in the next 2 to 3 years and should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 125,000 square feet of asphalt area was used to generate this estimate. | RICHARD H. BRYAN SITE | 9867 | Admin | PubWorks | B&G | Carson City | 2005 |  | 2018-07-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 93750
9867SIT2 | SLURRY SEAL ASPHALT PAVING - EAST LOT | 9867 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the East parking lot. Striping is included in this estimate. It is recommended that this project be implemented in the next 4 to 5 years and should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 25,000 square feet of asphalt area was used to generate this estimate. | RICHARD H. BRYAN SITE | 9867 | Admin | PubWorks | B&G | Carson City | 2005 |  | 2018-07-31 | Four to Ten Years | Long-Term Needs | 3 | 18750
9863SIT2 | REMOVE AND REPLACE CONCRETE PAVING | 9863 | The existing concrete paving on the eastside adjacent to the loading dock and the west side of the building from the sidewalk to the entry stairs has deteriorated and is beginning to fail in some areas. There is cracking and settling which will continue to deteriorate and present potential tripping hazards. This project addresses removal and replacement of existing concrete as required. 3,600 square feet was used to generate this estimate. | PAUL LAXALT STATE BUILDING SITE | 9863 | Admin | PubWorks | B&G | Carson City | 1891 |  | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 36000
9863SIT3 | ROOF DRAIN DOWNSPOUT MODIFICATIONS | 9863 | The roof drain downspouts currently terminate within inches of the building and some do not have continuous drainage away from the building. This is causing the water to pool next to the building and causing damage to the building and surrounding concrete. This project would provide for the extension of the roof drains from the downspouts to approximately 5'-0" away from the perimeter of the building to prevent pooling and damage to the building. | PAUL LAXALT STATE BUILDING SITE | 9863 | Admin | PubWorks | B&G | Carson City | 1891 |  | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
9863SFT3 | INSTALL SEISMIC GAS SHUTOFF VALVE AND BOLLARDS | 9863 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. In addition, the project would install bollards and horizontal barriers to protect the gas meter and valves from damage. Note that the meter is located in the approach to the loading dock and is currently unprotected from collision. This project or a portion thereof was previously recommended in the FCA report dated 10/05/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/28/2009. | PAUL LAXALT STATE BUILDING SITE | 9863 | Admin | PubWorks | B&G | Carson City | 1891 |  | 2018-08-09 | Immediate to Two Years | Currently Critical | 1 | 7500
9863ADA1 | LAXALT PLAZA STAIR AND ADA MODIFICATIONS | 9863 | The Laxalt Plaza is constructed with paver stones. There are terraces with steps and a ramp along with seating areas for the public. This area also has the designated ADA accessible route from the parking stall to a platform lift. The platform lift does not have an ADA compliant landing at the lower level and the upper level platform lift door does not have the required forward approach clearance. The ADA ramp also does not have a compliant landing and a portion of the slope exceeds 8.3%. There are also some cross slopes that exceed 2%. There are some stair risers that exceed the 3/8" maximum uniformity requirement and some handrails are missing or non compliant on the stairs and ramp. The public table at the upper terrace is also not ADA compliant. This project would provide for the required modifications mentioned above including removal and reinstallation of the pavers as required, regrading, handrails and table modifications. This project will need to be approved by the Nevada State Historical Preservation Office. | PAUL LAXALT STATE BUILDING SITE | 9863 | Admin | PubWorks | B&G | Carson City | 1891 |  | 2018-08-09 | Immediate to Two Years | Currently Critical | 1 | 36000
9863SFT2 | GUARD INSTALLATION | 9863 | The east side approach to the loading dock area of the site has an elevation change from the concrete driveway to the natural grade below that exceeds 30 inches. This project recommends the installation of a guard to form a protective barrier along the open side in accordance with the 2006 IBC Chapter 10, Section 1013. Approval of this project will be required by the Nevada State Historical Preservation Office. 140 lineal feet was used to generate this estimate. | PAUL LAXALT STATE BUILDING SITE | 9863 | Admin | PubWorks | B&G | Carson City | 1891 |  | 2018-08-09 | Immediate to Two Years | Currently Critical | 1 | 7000
9863SFT1 | EXTERIOR STAIR HANDRAIL REPLACEMENT | 9863 | There are several sets of stair handrails around the exterior of the building that are older and do not meet code for safety. The gripping surfaces are incorrect, they are not continuous from the top to bottom landings and/ or they are installed on only one side of the stair. There is also a damaged rail near the north basement stairs that should be repaired. This project recommends the installation of handrails as needed in accordance with IBC Section 1012. This project will require the Nevada State Historic Preservation Office approval and excludes the plaza area on the north side of the property. | PAUL LAXALT STATE BUILDING SITE | 9863 | Admin | PubWorks | B&G | Carson City | 1891 |  | 2018-08-09 | Immediate to Two Years | Currently Critical | 1 | 2500
0394EXT9 | ROOF REPAIRS | 0394 | The standing seam metal roof on this building has active leaks on the north and south sides of the building. The roof has been inspected and the cause of the problem has to do with the integral gutter system. The gutters have lost their waterproof coating due to exposure and should be replaced throughout the entire roof system. It is recommended that the gutters be repaired immediately. Additional costs are included in the estimate due to the steep pitch of the roof and the historical nature of the building. | PAUL LAXALT STATE BUILDING | 9863 | Admin | PubWorks | B&G | Carson City | 1891 | 26110 | 2018-08-09 | Immediate to Two Years | Currently Critical | 1 | 60000
0394HVA2 | BOILER REPAIRS | 0394 | At the time of the survey, one of the hot water boilers was not operating. The side panel had been removed and it was unclear why the boiler was not online. It is important to have both boilers in working condition to ensure that the building has constant service. This project would provide for labor and parts to repair the boiler. | PAUL LAXALT STATE BUILDING | 9863 | Admin | PubWorks | B&G | Carson City | 1891 | 26110 | 2018-08-09 | Immediate to Two Years | Currently Critical | 1 | 2500
0394SFT3 | INTERIOR STAIR HANDRAIL REPLACEMENT | 0394 | There are several sets of interior stair handrails throughout the building that are older and do not meet code for safety. The gripping surfaces are incorrect, they are not continuous from the top to bottom landings and/ or they are installed on only one side of the stair. This project recommends the installation of handrails on both sides of the stairs, with proper returns and supports in accordance with the 2006 IBC Chapter 10, Section 1012. Approval of this project may be required by the Nevada State Historical Preservation Office. | PAUL LAXALT STATE BUILDING | 9863 | Admin | PubWorks | B&G | Carson City | 1891 | 26110 | 2018-08-09 | Immediate to Two Years | Currently Critical | 1 | 5000
0394EXT2 | REPLACE NORTH BASEMENT DOOR | 0394 | The exterior basement door on the North side is original to the building and is deteriorated with age. This door can no longer be considered secure and must be replaced to prevent unauthorized entry. This project would provide for the purchase and installation of a new hollow metal door, frame and hardware. Removal and disposal of the existing door and painting of the new door is included in this estimate. Approval of this project may be required by the Nevada State Historical Preservation Office. This project or a portion thereof was previously recommended in the FCA report dated 10/05/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/28/2009. | PAUL LAXALT STATE BUILDING | 9863 | Admin | PubWorks | B&G | Carson City | 1891 | 26110 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0394ADA3 | ADA CANE DETECTION BARRIER INSTALLATION | 0394 | The stairwell on the south side of the building has an overhead hazard at the cane detection area under the stairs. This project recommends the installation of a permanent barrier under the stairs. IBC - 2006 Section 1012 and ADAAG 4.4.2 were referenced for this project. | PAUL LAXALT STATE BUILDING | 9863 | Admin | PubWorks | B&G | Carson City | 1891 | 26110 | 2018-08-09 | Immediate to Two Years | Currently Critical | 1 | 1000
0394SFT2 | SAFETY CABINETS | 0394 | The storage room in the basement contains many different paints, stains and other hazardous products on open shelves and window sills. This does not meet OSHA standards for hazardous materials storage. This project would provide two hazardous material storage cabinets for the building and install placards on the building exterior in accordance with OSHA 1910.106 (d). | PAUL LAXALT STATE BUILDING | 9863 | Admin | PubWorks | B&G | Carson City | 1891 | 26110 | 2018-08-09 | Immediate to Two Years | Currently Critical | 1 | 10000
0394INT2 | INTERIOR FINISHES | 0394 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next four to five years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | PAUL LAXALT STATE BUILDING | 9863 | Admin | PubWorks | B&G | Carson City | 1891 | 26110 | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 130550
0394EXT8 | EXTERIOR FINISHES | 0394 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are sealing and tuck pointing the masonry and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | PAUL LAXALT STATE BUILDING | 9863 | Admin | PubWorks | B&G | Carson City | 1891 | 26110 | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 261100
0394HVA1 | PROVIDE CLEARANCE AROUND BOILER VENT | 0394 | The existing boiler vent is a stainless steel assembly with a clearance label stating clearances to combustibles. The penetration through the gypsum wall must have a "thimble" installed to provide clearance between the vent and the gypsum board. Note that gypsum board is classed as a "limited combustible" in the fire code. This project or a portion thereof was previously recommended in the FCA report dated 10/05/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/28/2009. | PAUL LAXALT STATE BUILDING | 9863 | Admin | PubWorks | B&G | Carson City | 1891 | 26110 | 2018-08-09 | Immediate to Two Years | Currently Critical | 1 | 5000
0394PLM2 | WATER HEATER REPLACEMENT | 0394 | There is a 40 gallon gas-fired water heater in the basement. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 5-6 years. It is recommended that a new gas-fired water heater be installed. | PAUL LAXALT STATE BUILDING | 9863 | Admin | PubWorks | B&G | Carson City | 1891 | 26110 | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 1500
0394INT4 | VCT FLOORING REPLACEMENT | 0394 | The VCT (vinyl composite tile) flooring in the 1st floor Men's and Women's restrooms is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. | PAUL LAXALT STATE BUILDING | 9863 | Admin | PubWorks | B&G | Carson City | 1891 | 26110 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2700
0394EXT10 | WINDOW REPLACEMENT | 0394 | The windows are original, single pane construction in a wooden frame. These older windows are drafty, not energy efficient and the wooden frames have deteriorated significantly. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 112 units including wooden frames which will require approval from the State Historical Preservation Office. Removal and disposal of the existing windows is included in this estimate. | PAUL LAXALT STATE BUILDING | 9863 | Admin | PubWorks | B&G | Carson City | 1891 | 26110 | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 224000
0394INT1 | REPLACE CARPET | 0394 | The carpet in the building, especially on the second and third floors, is beginning to show significant signs of wear. It is recommended that the carpet be replaced with heavy duty commercial grade carpet in the next two to three years. This project or a portion thereof was previously recommended in the FCA report dated 10/05/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/28/2009. | PAUL LAXALT STATE BUILDING | 9863 | Admin | PubWorks | B&G | Carson City | 1891 | 26110 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 77000
2456INT1 | INTERIOR FINISHES | 2456 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | EQUIPMENT SHED | 9978 | Admin | PubWorks | B&G | Carson City | 2003 | 120 | 2018-09-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 600
2455EXT1 | EXTERIOR FINISHES | 2455 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | STORAGE BUILDING | 9978 | Admin | PubWorks | B&G | Carson City | 2003 | 720 | 2018-09-11 | Four to Ten Years | Long-Term Needs | 3 | 7200
2456EXT1 | EXTERIOR FINISHES | 2456 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | EQUIPMENT SHED | 9978 | Admin | PubWorks | B&G | Carson City | 2003 | 120 | 2018-09-11 | Four to Ten Years | Long-Term Needs | 3 | 1200
9978SIT2 | LANDSCAPE WALL REPAIR | 9978 | The painted concrete masonry unit landscape walls around the site show varying degrees of wear including cracking and flaking. The top layer of paint and concrete is flaking off in many areas and is due for resurfacing. It is recommended that these areas be resurfaced by removing the existing paint, sealing the concrete masonry unit blocks and applying a new finished surface of elastomeric paint. This project also provides for repairing the significant damage near the rear driveway by the garage. This work may require some new concrete masonry unit blocks and wall caps as well as resurfacing. | GOVERNOR'S MANSION SITE | 9978 | Admin | PubWorks | B&G | Carson City | 1907 |  | 2018-09-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
9978SIT1 | FRENCH DRAIN INSPECTION | 9978 | Staff reported that the french drains in the rear yard do not drain correctly causing the grass and sidewalks to flood during normal irrigation practices and precipitation events. The reason for this backup was not known at the time of the survey, but was suspected to be blocked or crushed pipes in the drains. This project would provide funding to scope the french drains by a certified inspector to determine the cause of the problem. Any future projects would come from the inspector's report recommendations. | GOVERNOR'S MANSION SITE | 9978 | Admin | PubWorks | B&G | Carson City | 1907 |  | 2018-09-11 | Immediate to Two Years | Currently Critical | 1 | 1000
0151HVA2 | INSULATE ATTIC | 0151 | The attic insulation appears to be original to the building. It has deteriorated and should be replaced. Many locations in the attic are completely missing the insulation or it was not reinstalled after construction work was completed in the past. It is recommended that the entire attic area be reinsulated with R-30 insulation. This will increase energy efficiency and be more resistant to heat loss. The estimate is based on 13" thick blown fiberglass insulation. This project or a portion thereof was previously recommended in the FCA report dated 03/10/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/15/2008. | GOVERNOR'S MANSION | 9978 | Admin | PubWorks | B&G | Carson City | 1908 | 9361 | 2018-09-11 | Immediate to Two Years | Currently Critical | 1 | 12054
0154EXT2 | EXTERIOR FINISHES | 0154 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around flashing, fixtures, and other attachments to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. This project or a portion thereof was previously recommended in the FCA report dated 03/10/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/15/2008. | LLEWELLYN B. GROSS MEMORIAL PAVILION | 9978 | Admin | PubWorks | B&G | Carson City | 1969 | 2827 | 2018-09-11 | Four to Ten Years | Long-Term Needs | 3 | 28270
0154SIT2 | LANDSCAPE WALL REPAIR | 0154 | The concrete landscape wall bearing the name of the pavilion is cracking and flaking. The top layer of paint and concrete is flaking off and is due for resurfacing. It is recommended to resurface the wall by removing the existing paint, sealing the concrete and applying a new finished surface of elastomeric paint. | LLEWELLYN B. GROSS MEMORIAL PAVILION | 9978 | Admin | PubWorks | B&G | Carson City | 1969 | 2827 | 2018-09-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
0153SFT2 | STAIRWAY HANDRAIL INSTALLATION | 0153 | The existing concrete exterior stairs at the entry are lacking a handrail as required in the 2006 IBC Chapter 10, Section 1012. This project would provide for a wood framed handrail to be installed. Material and construction should match the existing guardrail. | GOVERNOR'S MANSION COOK'S COTTAGE | 9978 | Admin | PubWorks | B&G | Carson City | 1965 | 928 | 2018-09-11 | Immediate to Two Years | Currently Critical | 1 | 1500
0153INT4 | INTERIOR FINISHES | 0153 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 03/10/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/15/2008. | GOVERNOR'S MANSION COOK'S COTTAGE | 9978 | Admin | PubWorks | B&G | Carson City | 1965 | 928 | 2018-09-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4640
0153EXT3 | EXTERIOR FINISHES | 0153 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. This project or a portion thereof was previously recommended in the FCA report dated 03/10/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/15/2008. | GOVERNOR'S MANSION COOK'S COTTAGE | 9978 | Admin | PubWorks | B&G | Carson City | 1965 | 928 | 2018-09-11 | Four to Ten Years | Long-Term Needs | 3 | 9280
0152EXT1 | EXTERIOR FINISHES | 0152 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | GOVERNOR'S MANSION GARAGE | 9978 | Admin | PubWorks | B&G | Carson City | 1998 | 912 | 2018-09-11 | Four to Ten Years | Long-Term Needs | 3 | 9120
0151EXT4 | DECK AND PAVER REPAIR | 0151 | The brick pavers that accent the driveway and walkways on the east side of the grounds are failing. Also, the poured deck material on the second floor of the Mansion is cracking and failing. The brick pavers are not tied into the surrounding concrete and they consistently move around independently from the concrete. This is due to moisture infiltration between the bricks and the concrete which contributes to ground heaving and erosion. The bricks are dislodged to the point of causing a tripping hazard and are a constant maintenance problem. The second floor decking material is cracking and no longer provides a waterproof barrier to the plywood decking and the floor below. The plywood is warping and buckling causing the joints to separate which contributes to the failed waterproofing system. This project would provide for removing the brick pavers and replacing them with stamped concrete to resemble the original brick. The new concrete should be tied into the existing concrete with rebar connectors. This project would also provide for replacing the poured deck material and repairing any damaged plywood decking below it. Note: This project has been recommended by the State Public Works Board for the 2009 CIP. | GOVERNOR'S MANSION | 9978 | Admin | PubWorks | B&G | Carson City | 1908 | 9361 | 2018-09-11 | Immediate to Two Years | Currently Critical | 1 | 125000
0151EXT3 | EXTERIOR FINISHES | 0151 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and it is also recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 03/10/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/15/2008. | GOVERNOR'S MANSION | 9978 | Admin | PubWorks | B&G | Carson City | 1908 | 9361 | 2018-09-11 | Four to Ten Years | Long-Term Needs | 3 | 140415
0151INT2 | INTERIOR FINISHES | 0151 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 03/10/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/15/2008. | GOVERNOR'S MANSION | 9978 | Admin | PubWorks | B&G | Carson City | 1908 | 9361 | 2018-09-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 93610
0151SEC1 | SECURITY SYSTEM UPGRADE | 0151 | The current security surveillance system is outdated and ineffective particularly for night surveillance. The surveillance of the mansion and surrounding grounds is inadequate due to poor placement of cameras, outdated cameras and monitoring equipment and not enough cameras overall. This project would provide for replacing the cameras to color low light cameras and upgrading the monitoring equipment. More effective surveillance will be provided to the security staff by adding more cameras and by selecting new camera locations. Note: This project has been recommended by the State Public Works Board for the 2009 CIP. | GOVERNOR'S MANSION | 9978 | Admin | PubWorks | B&G | Carson City | 1908 | 9361 | 2018-09-11 | Immediate to Two Years | Currently Critical | 1 | 200000
0154ADA1 | ADA SIDEWALK REPAIR | 0154 | The concrete sidewalk to the north of the Pavilion is in need of replacement. Settling has created a non-ADA complaint change of level at the upper transition. The concrete in this area also has minor cracking and spalling. This project would provide for the removal and replacement of the concrete sidewalk. 48 SF of 4" thick concrete sidewalk was used for this estimate. IBC - 2006, ICC/ANSI A117.1 - 2003 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2003 were referenced for this project. | LLEWELLYN B. GROSS MEMORIAL PAVILION | 9978 | Admin | PubWorks | B&G | Carson City | 1969 | 2827 | 2018-09-11 | Immediate to Two Years | Currently Critical | 1 | 720
0707INT1 | INTERIOR FINISHES | 0707 | The interior finishes are in good condition. The walls are covered by wallpaper, wood wainscot and wood trim. The coffered ceiling is covered by painted gypsum board and wood trim. It is recommended that the interior wood areas of the walls and the entire ceiling be stained or painted as appropriate at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | GOVERNORS MANSION NORTH HALL | 9978 | Admin | PubWorks | B&G | Carson City | 1998 | 6608 | 2018-09-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 33.04
0707EXT1 | EXTERIOR FINISHES | 0707 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. This project or a portion thereof was previously recommended in the FCA report dated 03/10/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/15/2008. | GOVERNORS MANSION NORTH HALL | 9978 | Admin | PubWorks | B&G | Carson City | 1998 | 6608 | 2018-09-11 | Four to Ten Years | Long-Term Needs | 3 | 66080
0707PLM1 | WATER HEATER REPLACEMENT | 0707 | The average life span of a water heater is eight to ten years. The existing 100 gallon natural gas water heater is original to the building. It is approaching the end of its expected life and should be scheduled for replacement in the next 3 to 5 years. This project would provide for the removal and disposal of the old water heater and installation of a new 100 gallon water heater. | GOVERNORS MANSION NORTH HALL | 9978 | Admin | PubWorks | B&G | Carson City | 1998 | 6608 | 2018-09-11 | Four to Ten Years | Long-Term Needs | 3 | 3500
9831ADA1 | ADA PATH OF TRAVEL UPGRADE | 9831 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. An accessible path of travel from the public way to the entrance of the building is necessary to comply with ADA accessibility requirements. This project would provide for repairing the asphalt portion and replacing the concrete walkway. This will require crack fill and seal of the asphalt, regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2006 IBC, ICC/ANSI A117.1 - 2003 and the most current version of the Americans With Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. 560 square feet of concrete was used for this estimate. It is recommended that this project coincide with the paving project. | BELROSE OFFICE BUILDING SITE | 9831 | Admin | PubWorks | B&G | Las Vegas | 0 |  | 2018-12-10 | Immediate to Two Years | Currently Critical | 1 | 10000
9831ADA2 | ADA PARKING UPGRADE | 9831 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. A compliant concrete parking area and passenger loading area are necessary to comply with ADA requirements. The existing accessible parking spaces do not meet current guidelines. This project would provide for a concrete van accessible ADA parking and loading space, a passenger ADA space and walkway to the existing sidewalk. This will require regrading, installing P.C. concrete, striping, signage and any other necessary upgrades. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | BELROSE OFFICE BUILDING SITE | 9831 | Admin | PubWorks | B&G | Las Vegas | 0 |  | 2018-12-10 | Immediate to Two Years | Currently Critical | 1 | 15000
9831SIT1 | SEAL ASPHALT PAVING | 9831 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the paving site wide including access roads, parking areas and the maintenance yard. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 55,000 square feet of asphalt area was used to generate this estimate. | BELROSE OFFICE BUILDING SITE | 9831 | Admin | PubWorks | B&G | Las Vegas | 0 |  | 2018-12-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 41250
9831SFT1 | SIDEWALK / LANDING REPAIR | 9831 | The sidewalks serving the building are in overall good condition, but there are a couple of areas that require repairs. Some areas have cracks that need to be filled and at least one area has created a tripping hazard where one slab has heaved up next to another slab. This project addresses filling cracks and grinding high areas as necessary to remove tripping hazards and maintain the concrete in good condition. This project would also provide a code compliant landing at the exterior door adjacent to the driveway along the east side of the building. | BELROSE OFFICE BUILDING SITE | 9831 | Admin | PubWorks | B&G | Las Vegas | 0 |  | 2018-12-10 | Immediate to Two Years | Currently Critical | 1 | 2000
9831SIT2 | EXTERIOR SOLAR SITE LIGHTING UPGRADE | 9831 | There are five existing light poles around the site. The lighting fixtures and lamps are the older type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. This project would provide for the installation of 5 solar powered LED exterior light fixtures on the existing poles. | BELROSE OFFICE BUILDING SITE | 9831 | Admin | PubWorks | B&G | Las Vegas | 0 |  | 2018-12-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
0286EXT3 | EXTERIOR FINISHES | 0286 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting the stucco, cleaning and sealing the brick masonry and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BELROSE OFFICE BUILDING | 9831 | Admin | PubWorks | B&G | Las Vegas | 1973 | 41075 | 2018-12-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 205375
0286ENV2 | PEST CONTROL | 0286 | There are numerous signs throughout this building of insect infestation including ants, bees, cockroaches and crickets. Due to the potential risk of disease and damage to the building, this project provides for treatment and clean up of the insects by a licensed pest control business. It is recommended that the building be treated in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain control of the pests. | BELROSE OFFICE BUILDING | 9831 | Admin | PubWorks | B&G | Las Vegas | 1973 | 41075 | 2018-12-10 | Immediate to Two Years | Currently Critical | 1 | 2500
0286HVA2 | EXHAUST FAN REPLACEMENT | 0286 | The exhaust fan in one of the restrooms was not operating at the time of the survey. This project would provide for the removal of the existing exhaust fan assembly and the purchase and installation of a new exhaust fan assembly including connections to utilities. | BELROSE OFFICE BUILDING | 9831 | Admin | PubWorks | B&G | Las Vegas | 1973 | 41075 | 2018-12-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 750
0286INT5 | BREAK ROOM REMODELS | 0286 | The kitchenettes and associated cabinets in the seven employee break rooms are original to the building. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and counter tops are delaminating and failing. This project recommends the replacement of the existing kitchen counters, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) should be incorporated into the design such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. | BELROSE OFFICE BUILDING | 9831 | Admin | PubWorks | B&G | Las Vegas | 1973 | 41075 | 2018-12-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35000
0286ADA5 | ADA SIGNAGE | 0286 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | BELROSE OFFICE BUILDING | 9831 | Admin | PubWorks | B&G | Las Vegas | 1973 | 41075 | 2018-12-10 | Immediate to Two Years | Currently Critical | 1 | 7500
0286INT4 | SUSPENDED CEILING SYSTEM REPLACEMENT | 0286 | The entire building has a suspended acoustical tile ceiling system that is original dating back to 1973. The t-bar framing is bent and rusted in some areas and some of the acoustical tiles are damaged and stained. This project would provide for the replacement of the suspended acoustical tile ceiling system including framing, bracing, acoustical tiles and HVAC grilles. Removal and disposal of the existing ceiling system is included in this estimate. | BELROSE OFFICE BUILDING | 9831 | Admin | PubWorks | B&G | Las Vegas | 1973 | 41075 | 2018-12-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 205375
0286ENV1 | ROOF MAINTENANCE | 0286 | There is a low roof section on the north side of the building that requires maintenance work. It has been overcome by pigeons and holds an abandoned HVAC unit. The pigeon droppings have accumulated to an unsafe level and should be cleaned up and the HVAC unit should be removed and disposed of. This project would provide for cleaning the roof area, removing and disposing of the HVAC unit and installing new pigeon deterrent devices. | BELROSE OFFICE BUILDING | 9831 | Admin | PubWorks | B&G | Las Vegas | 1973 | 41075 | 2018-12-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0286INT3 | INTERIOR FINISHES | 0286 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | BELROSE OFFICE BUILDING | 9831 | Admin | PubWorks | B&G | Las Vegas | 1973 | 41075 | 2018-12-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 205375
0286ELE1 | PROVIDE CLEARANCE AT ELECTRICAL PANELS | 0286 | There are electrical panels in the east electrical room which do not have proper clear floor space around them. The 2006 IFC section 605.3 states that, "A working space of not less than 30 inches in width, 36 inches in depth and 78 inches in height shall be provided in front of electrical service equipment. Where the electrical service equipment is wider than 30 inches, the working space shall not be less than the width of the equipment. No storage of any materials shall be located within the designated working space." This project would provide funds to relocate the fiber optic racks and other items currently blocking the working space. | BELROSE OFFICE BUILDING | 9831 | Admin | PubWorks | B&G | Las Vegas | 1973 | 41075 | 2018-12-10 | Immediate to Two Years | Currently Critical | 1 | 750
0286ADA7 | ADA ACCESSIBLE COUNTER | 0286 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The Youth Parole front office has a service counter for the public to approach which does not meet current codes. Section 7.2 of the Americans with Disabilities Act Accessible Guidelines (ADAAG) states that the counter must have a portion which is at least 36" in length with a maximum height of 36" above the finish floor. This project will provide an accessible counter space in accordance with this requirement as well as replacing the security glass to maintain a secure entrance. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | BELROSE OFFICE BUILDING | 9831 | Admin | PubWorks | B&G | Las Vegas | 1973 | 41075 | 2018-12-10 | Immediate to Two Years | Currently Critical | 1 | 6000
0286ADA6 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0286 | This building contains several drinking water fountains on the first and second floors. The 2006 IBC Section 1109.5 states where a water fountain is provided, at least half should be accessible. Due to the layout of the building and that the various offices are separated from each other, four accessible fountains are required. This project would provide funding for the purchase and installation of four new accessible fixed high/ low ADA drinking fountains, three on the first floor and one on the second floor. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | BELROSE OFFICE BUILDING | 9831 | Admin | PubWorks | B&G | Las Vegas | 1973 | 41075 | 2018-12-10 | Immediate to Two Years | Currently Critical | 1 | 16000
0286ADA4 | ELEVATOR UPGRADE | 0286 | The Department of Rehabilitation has offices on the second floor which are served by an older elevator. The configuration of the elevator and controls does not meet current ADA requirements. Due to the significant number of clients with special needs that the Department serves, a complying elevator should be installed. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 02/10/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2011. | BELROSE OFFICE BUILDING | 9831 | Admin | PubWorks | B&G | Las Vegas | 1973 | 41075 | 2018-12-10 | Immediate to Two Years | Currently Critical | 1 | 100000
0286PLM1 | WATER HEATER REPLACEMENT | 0286 | There are two 50 gallon gas-fired water heaters in the building. One was installed in 2008, the other one is older. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 5-6 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | BELROSE OFFICE BUILDING | 9831 | Admin | PubWorks | B&G | Las Vegas | 1973 | 41075 | 2018-12-10 | Four to Ten Years | Long-Term Needs | 3 | 1500
2162EXT2 | CONSERVE AND PROTECT VACANT BUILDING | 2162 | In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to removing water in the basement or crawlspace, providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #102 INFIRMARY (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1904 | 3000 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 74400
2160EXT2 | EXTERIOR FINISHES | 2160 | The exterior finishes are in poor condition. It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2 - 3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | #070 BARN (B&G STORAGE) | 9971 | Admin | PubWorks | B&G | Stewart | 1910 | 2160 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 21000
2161SIT1 | SEISMIC RETROFIT WALLS | 2161 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current code. Visual analysis during the survey found no indication of seismic strengthening of the URM walls. The walls should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #094 PUMP HOUSE | 9971 | Admin | PubWorks | B&G | Stewart | 1938 | 183 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 13700
2161EXT1 | EXTERIOR FINISHES | 2161 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting the wood finishes, re-pointing the stone where needed and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | #094 PUMP HOUSE | 9971 | Admin | PubWorks | B&G | Stewart | 1938 | 183 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1800
2160EXT1 | ROOF REPLACEMENT | 2160 | The transite shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roof. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #070 BARN (B&G STORAGE) | 9971 | Admin | PubWorks | B&G | Stewart | 1910 | 2160 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 40000
2162SFT1 | SEISMIC RETROFIT WALLS | 2162 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current code. Visual analysis during the survey found no indication of seismic strengthening of the URM walls. The walls should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #102 INFIRMARY (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1904 | 3000 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 225000
2702EXT1 | EXTERIOR FINISHES | 2702 | The exterior finishes are in good condition. It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry, painting the concrete roof eaves and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | #107 GARAGE | 9971 | Admin | PubWorks | B&G | Stewart | 1964 | 676 | 2020-02-07 | Four to Ten Years | Long-Term Needs | 3 | 3400
2163EXT2 | DEMOLISH STRUCTURE | 2163 | The building is an old garage that is no longer in use. It has significant structural failures and the roof has completely deteriorated. It is recommended that this structure be demolished. | #108 GARAGE (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1929 | 750 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
2162SFT2 | SEISMIC RETROFIT ROOF STRUCTURE | 2162 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current codes. Visual analysis during the survey found no indication of seismic strengthening of the roof structure. The roof structure should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #102 INFIRMARY (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1904 | 3000 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 141000
2157EXT2 | ROOF REPLACEMENT | 2157 | The rolled asphalt roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new single-ply membrane roof. This estimate includes removal and disposal of the old roof. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #161 WATER PLANT | 9971 | Admin | PubWorks | B&G | Stewart | 1978 | 938 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18000
2157INT1 | INTERIOR FINISHES | 2157 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #161 WATER PLANT | 9971 | Admin | PubWorks | B&G | Stewart | 1978 | 938 | 2020-02-07 | Four to Ten Years | Long-Term Needs | 3 | 4700
2157EXT1 | EXTERIOR FINISHES | 2157 | The building exterior is in good condition. It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | #161 WATER PLANT | 9971 | Admin | PubWorks | B&G | Stewart | 1978 | 938 | 2020-02-07 | Four to Ten Years | Long-Term Needs | 3 | 4700
2703INT1 | INTERIOR FINISHES | 2703 | The interior finishes are in fair condition. It is recommended that the interior CMU walls be sealed at least once in the next 5 - 6 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | #089 UTILITY ROOM | 9971 | Admin | PubWorks | B&G | Stewart | 2000 | 120 | 2020-02-07 | Four to Ten Years | Long-Term Needs | 3 | 600
2703EXT0 | EXTERIOR FINISHES | 2703 | The exterior finishes are in good condition. It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are painting the wood finishes, cleaning and sealing the concrete masonry units and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | #089 UTILITY ROOM | 9971 | Admin | PubWorks | B&G | Stewart | 2000 | 120 | 2020-02-07 | Four to Ten Years | Long-Term Needs | 3 | 600
2704EXT1 | EXTERIOR FINISHES | 2704 | The finish is in good condition. It is important to maintain the finish, weather resistance and appearance of the water tower. This project would provide for the painting of the water tower and caulking of the joints to maintain it in a good, weather tight condition. It is recommended that this project be implemented in the next 8 - 9 years and is recommended on a cyclical basis based on environmental conditions. | #087 WATER TOWER | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 900 | 2020-02-07 | Four to Ten Years | Long-Term Needs | 3 | 211800
2704SFT1 | STRUCTURAL REPAIR | 2704 | A seismic analysis was performed on the water tower under CIP 03-S04D in which structural improvements were necessary at all levels of water stored in the tower. In order to remain operational and prevent collapse in a major earthquake, the seismic retrofitting will address the tower’s structure and foundations. This project will provide the funding to structurally retrofit the existing water tower and foundation. | #087 WATER TOWER | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 900 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 411400
2702INT1 | INTERIOR FINISHES | 2702 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 5 - 6 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. | #107 GARAGE | 9971 | Admin | PubWorks | B&G | Stewart | 1964 | 676 | 2020-02-07 | Four to Ten Years | Long-Term Needs | 3 | 3380
9971SIT9 | CRACK FILL & SEAL ASPHALT PAVING | 9971 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the paving sitewide including access roads and parking areas. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 300,000 square feet of asphalt area was used to generate this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | STEWART CAMPUS SITE | 9971 | Admin | PubWorks | B&G | Stewart | 1890 |  | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 216000
9971PLM2 | IRRIGATION WATER SYSTEM UPGRADE | 9971 | The existing water tower is still in use to supply irrigation water to the site. Structural upgrades to the water tower have not been done. Structural analysis performed by Melvyn Green and Assoc. defined the need for upgrades based on various water levels in the water tower tank. Based on the analysis, structural upgrades were required for all water levels in the tank. Currently, water tower usage is limited to seasonal irrigation demands. This project recommends upgrading the well pumping infrastructure to replace the water tower's function and permanently remove the water tower from service. | STEWART CAMPUS SITE | 9971 | Admin | PubWorks | B&G | Stewart | 1890 |  | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 75000
9971SIT10 | SIDEWALK REPLACEMENT | 9971 | Some of the sidewalks serving the buildings and recreation areas on this site have deteriorated and are failing. In some areas cracks wider than four inches have been identified, and there is settling in many locations. This project addresses removal and replacement of existing sidewalks as needed. 5,000 SF of 4" thick concrete sidewalk was used for this estimate. | STEWART CAMPUS SITE | 9971 | Admin | PubWorks | B&G | Stewart | 1890 |  | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 62700
0424SIT1 | DRIVEWAY INSTALLATION | 0424 | The driveway is used frequently and is currently not paved. This project would provide for the installation of a new 4" thick concrete slab-on-grade driveway approximately 40'x20' in size. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #009 RESIDENCE (P.O.S.T.) | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 2222 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9500
0424ENR3 | HVAC UPGRADE | 0424 | The existing HVAC system consists of a high efficiency natural gas fired furnace with an A-coil casing and a window mounted evaporative cooler. This project would provide for installing a condensing unit outdoors and inserting a refrigerant coil in the existing A-coil casing. This project includes removal and disposal of the evaporative cooler and all required connections to utilities. | #009 RESIDENCE (P.O.S.T.) | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 2222 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
0424ELE1 | ELECTRICAL UPGRADE | 0424 | The building's wiring appears to be in good condition with GFCIs installed in all wet locations and other outlets are grounded 3 prong type. However, the main breaker panel may be a safety hazard and requires replacement. If the breaker panel is a Sylvania Zinsco or Federal Pacific “Stab-Loc” breaker panel, it should be replaced. This project would fund an audit by a qualified electrician and any required replacement. | #009 RESIDENCE (P.O.S.T.) | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 2222 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 10000
0424INT3 | RESTROOM REMODEL | 0424 | The restroom in the residence is original to the building and in overall poor condition. The finishes, fixtures, cabinet, toilet, shower, and exhaust fan are showing signs of wear and deterioration. This project would provide for a complete remodel of the restroom. The removal and disposal of the existing fixtures and finishes is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #009 RESIDENCE (P.O.S.T.) | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 2222 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 17900
0424SIT2 | SIDEWALK REPLACEMENT | 0424 | The sidewalks serving the building and basement access have deteriorated and are failing. This project addresses removal and replacement of existing sidewalks as needed. 300 SF of 4" thick concrete sidewalk was used for this estimate. | #009 RESIDENCE (P.O.S.T.) | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 2222 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3800
0424PLM1 | WATER HEATER REPLACEMENT | 0424 | There is an 80 gallon electric water heater in the building that is more than ten years old. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed for more efficient use of energy. This estimate includes: 100 feet of gas pipe, fittings, couplers, and labor for installation. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #009 RESIDENCE (P.O.S.T.) | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 2222 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
0425ENV1 | ASBESTOS ABATEMENT, TSI | 0425 | An inspection was performed on this building in 1989 for asbestos containing materials (ACM). Piping insulation was found which is believed to contain asbestos, and this report recommends abatement of this material. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #011 QUARTERS (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1925 | 1182 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11800
0424SFT4 | SEISMIC RETROFIT WALLS | 0424 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current code. Visual analysis during the survey found no indication of seismic strengthening of the URM walls. The walls should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #009 RESIDENCE (P.O.S.T.) | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 2222 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 166600
0426EXT2 | EXTERIOR FINISHES | 0426 | The exterior finishes are in good condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting the wood finishes, re-pointing the stone where needed, and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | #002 MUSEUM WELCOME CENTER | 9971 | Admin | PubWorks | B&G | Stewart | 1926 | 362 | 2020-02-07 | Four to Ten Years | Long-Term Needs | 3 | 2200
0424INT2 | FLOORING REPLACEMENT | 0424 | The VCT (vinyl composite tile) and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT flooring with a 6" base and heavy duty commercial grade carpet in the next 2-3 years. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #009 RESIDENCE (P.O.S.T.) | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 2222 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 21100
0424SFT1 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0424 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #009 RESIDENCE (P.O.S.T.) | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 2222 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 4800
0424EXT3 | EXTERIOR DOOR REPLACEMENT | 0424 | The 2 exterior wood man doors appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement of the wood doors with new metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #009 RESIDENCE (P.O.S.T.) | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 2222 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3600
0424ENR1 | WINDOW REPLACEMENT | 0424 | The windows are original, single pane construction in a wooden frame. These older windows are drafty, not energy efficient and the wooden frames have deteriorated significantly. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 10 units including wooden frames to match the historical style of the building. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #009 RESIDENCE (P.O.S.T.) | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 2222 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11000
0424EXT2 | EXTERIOR FINISHES | 0424 | The exterior painted surfaces are in fair condition. The exterior paint is starting to peel at the eave fascia, which will start a rapid deterioration. These areas should be addressed soon. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting the wood finishes, re-pointing the stone where needed, and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | #009 RESIDENCE (P.O.S.T.) | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 2222 | 2020-02-07 | Four to Ten Years | Long-Term Needs | 3 | 11110
0424INT1 | INTERIOR FINISHES | 0424 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 5 - 6 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | #009 RESIDENCE (P.O.S.T.) | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 2222 | 2020-02-07 | Four to Ten Years | Long-Term Needs | 3 | 13200
0423SFT2 | SEISMIC RETROFIT WALLS | 0423 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current code. Visual analysis during the survey found no indication of seismic strengthening of the URM walls. The walls should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #008 DOIT STORAGE | 9971 | Admin | PubWorks | B&G | Stewart | 1930 | 720 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 54000
0423SFT3 | SEISMIC RETROFIT ROOF STRUCTURE | 0423 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current codes. Visual analysis during the survey found no indication of seismic strengthening of the roof structure. The roof structure should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #008 DOIT STORAGE | 9971 | Admin | PubWorks | B&G | Stewart | 1930 | 720 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 33800
0423SEC1 | CONSERVE AND PROTECT VACANT BUILDING | 0423 | In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to removing water in the basement or crawlspace, providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #008 DOIT STORAGE | 9971 | Admin | PubWorks | B&G | Stewart | 1930 | 720 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 17200
0422ELE1 | GFCI OUTLETS | 0422 | There are several outlets in the restrooms, near drinking fountains, and kitchen which are not GFCI protected. The 2017 NEC 210.8 requires these locations to have GFCI protection. This project would provide for removing the standard receptacles and installing GFCI receptacles. | #006 ADMINISTRATION (P.O.S.T.) | 9971 | Admin | PubWorks | B&G | Stewart | 1930 | 18743 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 1000
0422EXT2 | REPAIR/REPLACE FASCIA AND SOFFITS | 0422 | The fascia and the soffits around the building are weather beaten, peeling, and are showing signs of considerable wear. This project would provide funding to repair the fascia and replace the soffits. Repairs include: replacing if necessary, sanding, scraping, priming, painting, and roof repairs. | #006 ADMINISTRATION (P.O.S.T.) | 9971 | Admin | PubWorks | B&G | Stewart | 1930 | 18743 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 2000
0424SFT2 | SMOKE ALARM INSTALLATION | 0424 | Section 907.2 of the 2018 IFC explains the requirements for smoke alarms in dwelling units including installing and maintaining smoke alarms in each sleeping room and on the ceiling or wall outside of each separate sleeping area in the immediate vicinity of bedrooms. State Fire Marshal NAC 477.915 (3) requires that smoke detectors be connected to the wiring of the building with a battery backup. This project would provide funding for the purchase and installation of smoke alarms in accordance with these codes. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #009 RESIDENCE (P.O.S.T.) | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 2222 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 1200
0422SFT5 | SEISMIC RETROFIT ROOF STRUCTURE | 0422 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current codes. Visual analysis during the survey found no indication of seismic strengthening of the roof structure. The roof structure should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #006 ADMINISTRATION (P.O.S.T.) | 9971 | Admin | PubWorks | B&G | Stewart | 1930 | 18743 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 881000
0430SFT1 | SEISMIC RETROFIT WALLS | 0430 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current code. Visual analysis during the survey found no indication of seismic strengthening of the URM walls. The walls should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #045 BAND ROOM (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1931 | 2373 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 177900
0430EXT2 | CONSERVE AND PROTECT VACANT BUILDING | 0430 | In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to removing water in the basement or crawlspace, providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. | #045 BAND ROOM (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1931 | 2373 | 2020-02-07 | Four to Ten Years | Long-Term Needs | 3 | 56000
0430ENV1 | ASBESTOS ABATEMENT, TSI | 0430 | An inspection was performed on this building in 1989 for asbestos containing materials (ACM). Piping insulation was found which is believed to contain asbestos, and this report recommends abatement of this material. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #045 BAND ROOM (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1931 | 2373 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 56400
0429SFT3 | SEISMIC RETROFIT WALLS | 0429 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current code. Visual analysis during the survey found no indication of seismic strengthening of the URM walls. The walls should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #015 KITCHEN/ DINING (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1923 | 11444 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 858300
0429SFT4 | SEISMIC RETROFIT ROOF STRUCTURE | 0429 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current codes. Visual analysis during the survey found no indication of seismic strengthening of the roof structure. The roof structure should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #015 KITCHEN/ DINING (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1923 | 11444 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 537900
0429EXT2 | CONSERVE AND PROTECT VACANT BUILDING | 0429 | In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to removing water in the basement or crawlspace, providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. | #015 KITCHEN/ DINING (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1923 | 11444 | 2020-02-07 | Four to Ten Years | Long-Term Needs | 3 | 270000
0429ENV1 | ASBESTOS ABATEMENT, TSI | 0429 | An inspection was performed on this building in 1989 for asbestos containing materials (ACM). Piping insulation was found which is believed to contain asbestos, and this report recommends abatement of this material. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #015 KITCHEN/ DINING (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1923 | 11444 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 270000
0428EXT2 | CONSERVE AND PROTECT VACANT BUILDING | 0428 | In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. | #120 PUMP HOUSE (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1925 | 220 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5500
0425SFT1 | SEISMIC RETROFIT WALLS | 0425 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current code. Visual analysis during the survey found no indication of seismic strengthening of the URM walls. The walls should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #011 QUARTERS (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1925 | 1182 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 88600
0425SEC1 | CONSERVE AND PROTECT VACANT BUILDING | 0425 | In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to removing water in the basement or crawlspace, providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #011 QUARTERS (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1925 | 1182 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 28100
0427SFT1 | EXTERIOR CONCRETE STAIR REPLACEMENT | 0427 | The concrete stairs and porch that access the building are deteriorating. Some sections have completely failed and are a safety hazard. The rest of the concrete is spalling and cracking extensively. It appears the concrete is original to the building and should be scheduled for a complete replacement immediately. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #090 AUDITORIUM (B&G) (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1925 | 5857 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 18000
0427EXT2 | CONSERVE AND PROTECT VACANT BUILDING | 0427 | In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to removing water in the basement or crawlspace, providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. | #090 AUDITORIUM (B&G) (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1925 | 5857 | 2020-02-07 | Four to Ten Years | Long-Term Needs | 3 | 140000
0426INT1 | INTERIOR FINISHES | 0426 | The interior finishes are in good condition due to recent complete renovation under CIP 17-C08 & 17-SO2. It is recommended that the interior walls and ceilings be painted at least once in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | #002 MUSEUM WELCOME CENTER | 9971 | Admin | PubWorks | B&G | Stewart | 1926 | 362 | 2020-02-07 | Four to Ten Years | Long-Term Needs | 3 | 2200
0425SFT2 | SEISMIC RETROFIT ROOF STRUCTURE | 0425 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current codes. Visual analysis during the survey found no indication of seismic strengthening of the roof structure. The roof structure should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #011 QUARTERS (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1925 | 1182 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 55500
0427SFT2 | SEISMIC RETROFIT WALLS | 0427 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current code. Visual analysis during the survey found no indication of seismic strengthening of the URM walls. The walls should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #090 AUDITORIUM (B&G) (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1925 | 5857 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 439000
0420EXT5 | EXTERIOR FINISHES | 0420 | The exterior paint is in good condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting the wood finishes, re-pointing the stone where needed, and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | #003 STEWART INDIAN ADMINISTRATION BLDG | 9971 | Admin | PubWorks | B&G | Stewart | 1930 | 5917 | 2020-02-07 | Four to Ten Years | Long-Term Needs | 3 | 35200
0746ENR1 | LIGHTING UPGRADE | 0746 | The existing lighting fixtures are the older incandescent type. Some are broken and they are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. CFL (compact fluorescent lamps) are suggested. Occupancy sensors will be installed in restrooms, closets, and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #118 FAMILY SHELTER | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1198 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
0420SFT2 | EXIT SIGN AND EGRESS LIGHTING INSTALLATION | 0420 | The building does not have any emergency lighting or exit signs. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2018 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #003 STEWART INDIAN ADMINISTRATION BLDG | 9971 | Admin | PubWorks | B&G | Stewart | 1930 | 5917 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 14800
0420EXT3 | WINDOW REPLACEMENT | 0420 | The windows are original, single pane construction in a wooden frame. These older windows are drafty, not energy efficient, and the wooden frames have deteriorated significantly. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 44 units including wooden frames to match the historical style of the building. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #003 STEWART INDIAN ADMINISTRATION BLDG | 9971 | Admin | PubWorks | B&G | Stewart | 1930 | 5917 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 48400
0419SIT2 | CONCRETE APRON REPAIRS | 0419 | The exterior concrete apron outside of the building's west side was placed with an incorrect slope allowing condensate from the HVAC VRF (variable refrigerant flow) outdoor unit and rainwater to flow to the basement wall. This project would provide funding for the demolition of the apron, removal of debris, regrading, and installation of a new apron to prevent this condition. | #001 STEWART INDIAN SCHOOL MUSEUM | 9971 | Admin | PubWorks | B&G | Stewart | 1923 | 5602 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 4000
0419INT1 | INTERIOR FINISHES | 0419 | The interior finishes are in good condition due to the recent complete renovation under CIP 17-C08 & 17-SO2. It is recommended that the interior walls and ceilings be painted at least once in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | #001 STEWART INDIAN SCHOOL MUSEUM | 9971 | Admin | PubWorks | B&G | Stewart | 1923 | 5602 | 2020-02-07 | Four to Ten Years | Long-Term Needs | 3 | 33300
0419EXT2 | EXTERIOR FINISHES | 0419 | The exterior finishes are in good condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting the wood finishes, re-pointing the stone where needed, and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | #001 STEWART INDIAN SCHOOL MUSEUM | 9971 | Admin | PubWorks | B&G | Stewart | 1923 | 5602 | 2020-02-07 | Four to Ten Years | Long-Term Needs | 3 | 33300
0743SFT3 | SEISMIC RETROFIT ROOF STRUCTURE | 0743 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current codes. Visual analysis during the survey found no indication of seismic strengthening of the roof structure. The roof structure should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #114 WAREHOUSE (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1925 | 3200 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 150400
0420SFT6 | SEISMIC RETROFIT WALLS | 0420 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current code. Visual analysis during the survey found no indication of seismic strengthening of the URM walls. The walls should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #003 STEWART INDIAN ADMINISTRATION BLDG | 9971 | Admin | PubWorks | B&G | Stewart | 1930 | 5917 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 443000
0746INT6 | INTERIOR FINISHES | 0746 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | #118 FAMILY SHELTER | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1198 | 2020-02-07 | Four to Ten Years | Long-Term Needs | 3 | 7100
0420SFT4 | FIRE ALARM SYSTEM INSTALLATION | 0420 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1 Section 7 and the 2018 International Fire Code. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #003 STEWART INDIAN ADMINISTRATION BLDG | 9971 | Admin | PubWorks | B&G | Stewart | 1930 | 5917 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 28200
0746INT4 | INTERIOR DOOR REPLACEMENT | 0746 | The interior doors in this building are hollow core units and most are damaged. This project would provide for the installation of new solid core interior doors including frames, lever action door handles, hardware and paint. Removal and disposal of the existing doors is included in this cost estimate. A total of 8 interior doors was used in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #118 FAMILY SHELTER | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1198 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4800
0746SFT1 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0746 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #118 FAMILY SHELTER | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1198 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 5000
0746EXT4 | EXTERIOR DOOR REPLACEMENT | 0746 | The 1 exterior wood man door in the rear appears to be original to the building. It is damaged from age and general wear and tear. This project would provide for the replacement of the wood door with a new wood door, frame and hardware. Removal and disposal of the existing door, and painting of the new door is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #118 FAMILY SHELTER | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1198 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 600
0746EXT3 | EXTERIOR FINISHES | 0746 | The exterior finish is in good condition. It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5 - 6 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | #118 FAMILY SHELTER | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1198 | 2020-02-07 | Four to Ten Years | Long-Term Needs | 3 | 7100
0745INT5 | KITCHEN REMODEL | 0745 | The kitchen is in fair to poor condition. The cabinets and equipment are showing signs of general wear and tear and are approaching the end of their expected life. This project recommends the replacement of the existing kitchen cabinets, countertops, fixtures and equipment with mid range, high quality components. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #117 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1203 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11900
0745INT4 | INTERIOR DOOR REPLACEMENT | 0745 | The interior doors in this building are hollow core units and most are damaged. This project would provide for the installation of new solid core interior doors including frames, lever action door handles, hardware and paint. Removal and disposal of the existing doors is included in this cost estimate. A total of 8 interior doors was used in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #117 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1203 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4800
0745SFT2 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0745 | This building does not have an automatic fire suppression system. It should be retrofitted with fire sprinklers during the next remodel or change of occupancy according to 2018 IEBC 101.4 Applicability provision, 2018 IFC and NAC 477.917. This project would provide funding for the installation of fire sprinklers including backflow prevention devices. | #117 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1203 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 21100
0745ENR1 | LIGHTING UPGRADE | 0745 | The existing lighting fixtures are the older incandescent type. Some are broken and they are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. CFL (compact fluorescent lamps) are suggested. Occupancy sensors will be installed in restrooms, closets, and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #117 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1203 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
0746SFT2 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0746 | This building does not have an automatic fire suppression system. It should be retrofitted with fire sprinklers during the next remodel or change of occupancy according to 2018 IEBC 101.4 Applicability provision, 2018 IFC and NAC 477.917. This project would provide funding for the installation of fire sprinklers including backflow prevention devices. | #118 FAMILY SHELTER | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1198 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 21100
0421SFT2 | SEISMIC RETROFIT ROOF STRUCTURE | 0421 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current codes. Visual analysis during the survey found no indication of seismic strengthening of the roof structure. The roof structure should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #004 STEWART INDIAN COMMISSION (STORAGE) | 9971 | Admin | PubWorks | B&G | Stewart | 1938 | 662 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 31000
0422ADA2 | ADA RAMP REPLACEMENT | 0422 | This facility has ADA accessible ramps located on the east side and the west side of the building. These ramps are on the accessible path of travel from the accessible parking spaces to the front and rear entrances of the building. The ramps do not have proper landings or handrails. This project would provide for removing and replacing both ramps to provide fully ADA compliant access to the building. The 2018 IBC, ICC/ANSI A117.1, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #006 ADMINISTRATION (P.O.S.T.) | 9971 | Admin | PubWorks | B&G | Stewart | 1930 | 18743 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 83000
0422ADA1 | ADA RESTROOM UPGRADE | 0422 | The building does not have an accessible restroom. The existing restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for remodeling the Men's and Women's restrooms into ADA compliant restrooms. These items may include new sinks, toilets, showers, hardware, mirrors, fixtures, flooring and paint. The 2018 IBC, ICC/ANSI A117.1, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #006 ADMINISTRATION (P.O.S.T.) | 9971 | Admin | PubWorks | B&G | Stewart | 1930 | 18743 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 119000
0422ADA4 | ADA SIGNAGE | 0422 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2018 IBC, ICC/ANSI A117.1, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #006 ADMINISTRATION (P.O.S.T.) | 9971 | Admin | PubWorks | B&G | Stewart | 1930 | 18743 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 2700
0422INT2 | ADA KITCHEN REMODEL | 0422 | The kitchenette and associated cabinets in the employee break room are original to the building. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and countertops are delaminating and failing. This project recommends the replacement of the existing kitchen countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2018, ICC/ANSI A117.1 and the most current version of the ADA Standards For Accessible Design should be incorporated into the design such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #006 ADMINISTRATION (P.O.S.T.) | 9971 | Admin | PubWorks | B&G | Stewart | 1930 | 18743 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 41600
0422SFT1 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0422 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2018 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #006 ADMINISTRATION (P.O.S.T.) | 9971 | Admin | PubWorks | B&G | Stewart | 1930 | 18743 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 11300
0422EXT1 | EXTERIOR FINISHES | 0422 | The building's exterior is repainted and in good condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting the wood finishes, re-pointing the stone where needed, and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | #006 ADMINISTRATION (P.O.S.T.) | 9971 | Admin | PubWorks | B&G | Stewart | 1930 | 18743 | 2020-02-07 | Four to Ten Years | Long-Term Needs | 3 | 110000
0422ADA3 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0422 | This building contains three water fountains that are not ADA compliant. The 2018 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of three dual level drinking fountains at three different locations to meet the ADA requirements. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #006 ADMINISTRATION (P.O.S.T.) | 9971 | Admin | PubWorks | B&G | Stewart | 1930 | 18743 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 7500
0422INT3 | JANITORS CLOSET REPAIRS | 0422 | The mop sinks in the Janitors Closets are mounted adjacent to gypsum board and are showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. This is recommended for two Janitors Closets. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #006 ADMINISTRATION (P.O.S.T.) | 9971 | Admin | PubWorks | B&G | Stewart | 1930 | 18743 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3300
0422INT1 | INTERIOR FINISHES | 0422 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | #006 ADMINISTRATION (P.O.S.T.) | 9971 | Admin | PubWorks | B&G | Stewart | 1930 | 18743 | 2020-02-07 | Four to Ten Years | Long-Term Needs | 3 | 93700
0420INT1 | INTERIOR FINISHES | 0420 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4 -5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | #003 STEWART INDIAN ADMINISTRATION BLDG | 9971 | Admin | PubWorks | B&G | Stewart | 1930 | 5917 | 2020-02-07 | Four to Ten Years | Long-Term Needs | 3 | 35200
0421EXT3 | EXTERIOR FINISHES | 0421 | The building exterior paint and masonry is in good condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting the wood finishes, re-pointing the stone where needed, and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | #004 STEWART INDIAN COMMISSION (STORAGE) | 9971 | Admin | PubWorks | B&G | Stewart | 1938 | 662 | 2020-02-07 | Four to Ten Years | Long-Term Needs | 3 | 8300
0420ADA1 | ADA RESTROOM REMODEL | 0420 | The building does not have an accessible restroom. The existing Men's and Women's restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for remodeling the Men's and Women's restrooms into ADA compliant restrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2018 IBC, ICC/ANSI A117.1, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #003 STEWART INDIAN ADMINISTRATION BLDG | 9971 | Admin | PubWorks | B&G | Stewart | 1930 | 5917 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 56000
0421SFT3 | SEISMIC RETROFIT WALLS | 0421 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current code. Visual analysis during the survey found no indication of seismic strengthening of the URM walls. The walls should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #004 STEWART INDIAN COMMISSION (STORAGE) | 9971 | Admin | PubWorks | B&G | Stewart | 1938 | 662 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 49600
0421INT1 | INTERIOR FINISHES | 0421 | Interior finishes are in good condition. It is recommended to paint the interior walls and ceilings at least once in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | #004 STEWART INDIAN COMMISSION (STORAGE) | 9971 | Admin | PubWorks | B&G | Stewart | 1938 | 662 | 2020-02-07 | Four to Ten Years | Long-Term Needs | 3 | 8300
0421SFT1 | EXTERIOR STAIR HANDRAIL INSTALLATION | 0421 | The concrete exterior stairs at the entry are lacking handrails as required in the 2012 IBC Chapter 10, Section 1012. This project would provide for tubular steel framed handrails to be installed. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #004 STEWART INDIAN COMMISSION (STORAGE) | 9971 | Admin | PubWorks | B&G | Stewart | 1938 | 662 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 6000
0420HVA1 | HVAC FLEXIBLE DUCT REPLACEMENT | 0420 | SPWD Adopted Standards, Section 7 Mechanical Standards limits the use of flexible ducting to 5 feet. This project would remove and replace the flexible ductwork located in the unconditioned basement and crawlspace with insulated metal ductwork. This estimate is for the replacement of approximately 100' of ductwork. Removal and disposal of the existing ductwork is included in this estimate. | #003 STEWART INDIAN ADMINISTRATION BLDG | 9971 | Admin | PubWorks | B&G | Stewart | 1930 | 5917 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0420ADA3 | KITCHEN REMODEL | 0420 | The kitchen is in fair to poor condition and does not meet the Americans with Disabilities Act (ADA) requirements. The cabinets and equipment are showing signs of general wear and tear and are approaching the end of their expected life. This project recommends the replacement of the existing kitchen cabinets, countertops, fixtures and equipment with mid-range, high quality components and incorporating ADA elements into the design such as providing an accessible sink and faucet handles. The 2018 IBC, ICC/ANSI A117.1, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #003 STEWART INDIAN ADMINISTRATION BLDG | 9971 | Admin | PubWorks | B&G | Stewart | 1930 | 5917 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 41700
0420ENR1 | LIGHTING UPGRADE | 0420 | The existing lighting fixtures are the older incandescent type and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. CFL (compact fluorescent lamps) are suggested. Occupancy sensors will be installed in restrooms, conference rooms, and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #003 STEWART INDIAN ADMINISTRATION BLDG | 9971 | Admin | PubWorks | B&G | Stewart | 1930 | 5917 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7000
0420STR1 | STRUCTURAL REPAIRS | 0420 | This facility has a cantilevered concrete walkway extending along the south side of the building's exterior approximately 10 feet above grade. The walkway concrete, guard rail and supporting structure appear to be original 1930 construction. The concrete walkway edge has previously failed and is now patched. The deteriorating concrete walkway also supports the guard rail posts raising concern for the structural integrity of the entire walkway and guardrail system. This project recommends a structural redesign and walkway replacement. Removal and disposal of the existing walkway is included in this estimate. | #003 STEWART INDIAN ADMINISTRATION BLDG | 9971 | Admin | PubWorks | B&G | Stewart | 1930 | 5917 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 25000
0420SFT5 | EXTERIOR LANDING INSTALLATION | 0420 | Section 1008.1 of the 2018 IBC describes the requirements for egress doors including floor elevations and landings. Landings shall have a length measured in the direction of travel of not less than 44 inches. There are three doors that do not comply with this code and pose a safety hazard. This project would provide for the installation of compliant landings for three exterior doors. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #003 STEWART INDIAN ADMINISTRATION BLDG | 9971 | Admin | PubWorks | B&G | Stewart | 1930 | 5917 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 8900
0422SFT4 | SEISMIC RETROFIT WALLS | 0422 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current code. Visual analysis during the survey found no indication of seismic strengthening of the URM walls. The walls should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #006 ADMINISTRATION (P.O.S.T.) | 9971 | Admin | PubWorks | B&G | Stewart | 1930 | 18743 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 1405000
0422SFT3 | CONCRETE STAIR REPLACEMENT | 0422 | The concrete stairs that access the building are not code compliant and many areas of the concrete are spalling and cracking. It appears these stairs are original to the building and should be scheduled for replacement. This project would provide for removal and disposal of the existing concrete stairs and handrails and installation of new compliant stairs and handrails. The estimate is for the replacement of 5 separate stairs. 2018 IBC Chapter 10 was used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #006 ADMINISTRATION (P.O.S.T.) | 9971 | Admin | PubWorks | B&G | Stewart | 1930 | 18743 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 35700
0456EXT2 | CONSERVE AND PROTECT VACANT BUILDING | 0456 | In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to removing water in the basement or crawlspace, providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. | #034 WASHOE TRIBE (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 1729 | 2020-02-07 | Four to Ten Years | Long-Term Needs | 3 | 34600
0455INT1 | INTERIOR FINISHES | 0455 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | #033 NON-PROFIT HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 1729 | 2020-02-07 | Four to Ten Years | Long-Term Needs | 3 | 10200
0732SFT5 | SEISMIC RETROFIT WALLS | 0732 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current code. Visual analysis during the survey found no indication of seismic strengthening of the URM walls. The walls should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #060 NON-PROFIT | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 1746 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 130900
0732ENR1 | WINDOW REPLACEMENT | 0732 | The windows are original, single pane construction in a wooden frame. These older windows are drafty, not energy efficient and the wooden frames have deteriorated significantly. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 16 units including wooden frames and additional costs are included due to the historical nature of the building. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #060 NON-PROFIT | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 1746 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
0732ELE1 | ELECTRICAL UPGRADE | 0732 | This building was constructed before the high demand for electrical services were needed for computers and other electrical devices. As time has progressed, the building's electrical demand and system has changed. It is utilized to its current maximum potential. The electrical panels are more than 30 years old, the fuses burn out often and it is difficult to find the correct replacement fuses. It is recommended the entire system be upgraded to meet the evolving needs of the building. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #060 NON-PROFIT | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 1746 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 41500
0732SFT2 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0732 | This building does not have an automatic fire suppression system. It should be retrofitted with fire sprinklers during the next remodel or addition according to 2018 IEBC 101.4 Applicability provision, 2018 IFC and NAC 477.917. This project would provide funding for the installation of fire sprinklers including backflow prevention devices. | #060 NON-PROFIT | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 1746 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 29100
0733EXT3 | ROOF REPLACEMENT | 0733 | The Transite shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayment. This estimate does not include removal and disposal of the old roofing system due to ACM and is a separate project. This project should be implemented concurrently with the ASBESTOS ABATEMENT - ROOFING project. | #061 (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1949 | 1630 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 16000
0456SFT1 | SEISMIC RETROFIT WALLS | 0456 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current code. Visual analysis during the survey found no indication of seismic strengthening of the URM walls. The walls should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #034 WASHOE TRIBE (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 1729 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 129600
0733SFT2 | SEISMIC RETROFIT ROOF STRUCTURE | 0733 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current codes. Visual analysis during the survey found no indication of seismic strengthening of the roof structure. The roof structure should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #061 (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1949 | 1630 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 76600
0455SFT6 | SEISMIC RETROFIT WALLS | 0455 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current code. Visual analysis during the survey found no indication of seismic strengthening of the URM walls. The walls should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #033 NON-PROFIT HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 1729 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 129600
0455ADA2 | ADA RAMP REPLACEMENT | 0455 | This building has an ADA accessible ramp located on the north side of the building. This ramp is on the accessible path of travel from the parking space to the rear entrance of the building. The ramp does not have proper landings, curbs or handrails. This project would provide for replacing the ramp with a fully compliant ramp. The 2018 IBC, ICC/ANSI A117.1, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #033 NON-PROFIT HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 1729 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 17800
0455ADA3 | ADA RESTROOM UPGRADE | 0455 | One side of the duplex has some ADA improvements, but it is due for an upgrade. The existing restroom does not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2018 IBC, ICC/ANSI A117.1, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #033 NON-PROFIT HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 1729 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 17800
0455SFT2 | SMOKE ALARM INSTALLATION | 0455 | Section 907.2.10 of the 2018 IBC and 2018 IFC explains the requirements for smoke alarms in dwelling units including installing and maintaining smoke alarms in each sleeping room and on the ceiling or wall outside of each separate sleeping area in the immediate vicinity of bedrooms. State Fire Marshal NAC 477.915 (3) requires that smoke detectors be connected to the wiring of the building with a battery backup. This project would provide funding for the purchase and installation of smoke alarms in accordance with these codes. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #033 NON-PROFIT HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 1729 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 960
0455SFT3 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0455 | This building does not have an automatic fire suppression system. It should be retrofitted with fire sprinklers during the next remodel or change of occupancy according to 2018 IEBC 101.4 Applicability provision, 2018 IFC and NAC 477.917. This project would provide funding for the installation of fire sprinklers including backflow prevention devices. | #033 NON-PROFIT HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 1729 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 28800
0455ELE1 | ELECTRICAL UPGRADE | 0455 | The kitchens in both residences do not have grounded (3-prong) receptacles or GFCI outlets. This building was constructed before the high demand for electrical services were needed for computers and other electrical devices. As time has progressed, the building's electrical demand and system has changed. It is utilized to its current maximum potential. The electrical panels are more than 30 years old, the fuses burn out often and it is difficult to find the correct replacement fuses. It is recommended the entire system be upgraded to meet the evolving needs of the building. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #033 NON-PROFIT HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 1729 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 41200
0686SFT3 | EGRESS LIGHTING UPGRADE | 0686 | There are older emergency egress lighting units in this building. These units have a finite lifespan, and this project recommends their replacement with new egress lights, and providing additional lights on the main exit routes and in individual rooms as needed. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #012 DORMITORY (P.O.S.T.) | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 14572 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 3000
0456ENV1 | ASBESTOS ABATEMENT, TSI | 0456 | An inspection was performed on this building in 1989 for asbestos containing materials (ACM). Piping insulation was found which is believed to contain asbestos, and this report recommends abatement of this material. | #034 WASHOE TRIBE (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 1729 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 38000
0743SFT2 | SEISMIC RETROFIT WALLS | 0743 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current code. Visual analysis during the survey found no indication of seismic strengthening of the URM walls. The walls should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #114 WAREHOUSE (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1925 | 3200 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 240000
0744INT6 | GYPSUM BOARD REPAIR | 0744 | The ceiling gypsum board is cracked. This project recommends removing the gypsum board, investigating cause of cracking, and replacing the drywall. | #116 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1198 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0744SFT2 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0744 | This building does not have an automatic fire suppression system. It should be retrofitted with fire sprinklers during the next remodel or change of occupancy according to 2018 IEBC 101.4 Applicability provision, 2018 IFC and NAC 477.917. This project would provide funding for the installation of fire sprinklers including backflow prevention devices. | #116 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1198 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 21000
0745EXT4 | EXTERIOR DOOR REPLACEMENT | 0745 | The 1 exterior wood man door in the rear appears to be original to the building. It is damaged from age and general wear and tear. This project would provide for the replacement of the wood door with a new metal door, frame and hardware. Removal and disposal of the existing door, and painting of the new door is included in this estimate. | #117 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1203 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 600
0745INT1 | INTERIOR FINISHES | 0745 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | #117 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1203 | 2020-02-07 | Four to Ten Years | Long-Term Needs | 3 | 6000
0745SFT1 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0745 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #117 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1203 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 5000
0745INT2 | FLOORING REPLACEMENT | 0745 | The VCT (vinyl composite tile) and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT flooring with a 6" base and heavy duty commercial grade carpet in the next 2-3 years. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #117 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1203 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11600
0732SFT1 | SMOKE ALARM INSTALLATION | 0732 | Section 907.2.11 of the 2018 IBC and 2018 IFC explains the requirements for smoke alarms in dwelling units including installing and maintaining smoke alarms in each sleeping room and on the ceiling or wall outside of each separate sleeping area in the immediate vicinity of bedrooms. State Fire Marshal NAC 477.915 (3) requires that smoke detectors be connected to the wiring of the building with a battery backup. This project would provide funding for the purchase and installation of smoke alarms in accordance with these codes. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #060 NON-PROFIT | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 1746 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 1900
0745INT3 | RESTROOM REMODEL | 0745 | The restroom in the residence is original to the building and in overall poor condition. The finishes, fixtures, cabinets, toilet, shower, and exhaust fan are showing signs of wear and deterioration. This project would provide for a complete remodel of the restroom. The removal and disposal of the existing fixtures and finishes is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #117 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1203 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
0455EXT1 | EXTERIOR FINISHES | 0455 | The exterior paint is in poor condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting the wood finishes, re-pointing the stone where needed, and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2 - 3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | #033 NON-PROFIT HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 1729 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10200
0734SFT1 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0734 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #062 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1960 | 1630 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 5000
0734ENV1 | ASBESTOS ABATEMENT, TSI | 0734 | An inspection was performed on this building in 1989 for asbestos containing materials (ACM). Thermal System Insulation was found on the piping and this report recommends abatement of this material. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #062 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1960 | 1630 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 39000
0734INT1 | INTERIOR FINISHES | 0734 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | #062 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1960 | 1630 | 2020-02-07 | Four to Ten Years | Long-Term Needs | 3 | 8150
0733SFT1 | SEISMIC RETROFIT WALLS | 0733 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current code. Visual analysis during the survey found no indication of seismic strengthening of the URM walls. The walls should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #061 (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1949 | 1630 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 122200
0733EXT1 | CONSERVE AND PROTECT VACANT BUILDING | 0733 | In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to removing water in the basement or crawlspace, providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. . | #061 (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1949 | 1630 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8200
0733ENV2 | ASBESTOS ABATEMENT - ROOFING | 0733 | The Transite roofing materials are known to have Asbestos containing materials and shall be removed in an approved manner. This abatement project provides for the safe removal and disposal of the Transite shingles in an approved manner. This project should be implemented concurrently with the SEISMIC RETROFIT ROOF STRUCTURE project. | #061 (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1949 | 1630 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 4900
0745EXT3 | EXTERIOR FINISHES | 0745 | The building exterior is in good condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting, and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | #117 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1203 | 2020-02-07 | Four to Ten Years | Long-Term Needs | 3 | 15100
0686ADA2 | ADA RESTROOM UPGRADE | 0686 | The designated unisex ADA accessible restrooms are not fully compliant. There is no pipe protection, the toilet paper dispenser is not in the correct location, one of the flush handles is on the wrong side and the grab bars are not compliant. A partial retrofit is necessary. This project would provide funding to bring the restrooms into full ADA compliance. The 2018 IBC, ICC/ANSI A117.1, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #012 DORMITORY (P.O.S.T.) | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 14572 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 4000
0455SFT1 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0455 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #033 NON-PROFIT HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 1729 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 4800
0731PLM1 | WATER HEATER REPLACEMENT | 0731 | There are two natural gas-fired water heaters in the building, a 40 gallon and a 50 gallon. The average life span of a water heater is eight to ten years. With the passage of time and constant use, these units are showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that two new natural gas-fired water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #057 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 3000 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3600
0731ENV1 | ASBESTOS ABATEMENT, TSI | 0731 | An inspection was performed on this building in 1989 for asbestos containing materials (ACM). Thermal System Insulation was found on the piping and this report recommends abatement of this material. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #057 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 3000 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 71000
0731SFT4 | SEISMIC RETROFIT ROOF STRUCTURE | 0731 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current codes. Visual analysis during the survey found no indication of seismic strengthening of the roof structure. The roof structure should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #057 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 3000 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 141000
0730EXT2 | CONSERVE AND PROTECT VACANT BUILDINGS | 0730 | In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to removing water in the basement, providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #048 NDOC STORAGE | 9971 | Admin | PubWorks | B&G | Stewart | 1920 | 4070 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 81400
0730EXT1 | ROOF REPLACEMENT | 0730 | The wood shingle roof on this building was in poor condition at the time of the survey and is at the point of failure. It is recommended that this building be re-roofed immediately with a new 50 year asphalt composition shingle roof and new underlayments. This estimate includes removal and disposal of the old roof. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #048 NDOC STORAGE | 9971 | Admin | PubWorks | B&G | Stewart | 1920 | 4070 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 80000
0731ENR1 | LIGHTING UPGRADE | 0731 | The existing lighting fixtures are the older incandescent type, are not energy efficient, and several of the fixtures are damaged. This project will upgrade fixtures to higher efficiency units with a longer life cycle. CFL (compact fluorescent lamps) are suggested. Occupancy sensors will be installed in restrooms, closets, and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #057 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 3000 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
0686SFT1 | FIRE ALARM SYSTEM UPGRADE | 0686 | This building is equipped with an automatic fire detection and alarm system that no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 "If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure". When completed, the new system will provide visual, as well as audible notification, in accordance with the 2018 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #012 DORMITORY (P.O.S.T.) | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 14572 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 58300
0731INT4 | INTERIOR DOOR REPLACEMENT | 0731 | The interior doors in this building are hollow core units and most are damaged. This project would provide for the installation of new solid core interior doors including frames, lever action door handles, hardware and paint. Removal and disposal of the existing doors is included in this cost estimate. A total of 18 interior doors was used in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #057 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 3000 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10800
0686INT2 | RESTROOM REMODEL | 0686 | The two large restrooms in the dormitory have not been remodeled for at least 20 years and are in overall poor condition. The finishes, fixtures, cabinets, toilets, showers, and exhaust fans are showing signs of wear and deterioration. This project would provide for a complete remodel of the restrooms. The removal and disposal of the existing fixtures and finishes is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #012 DORMITORY (P.O.S.T.) | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 14572 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 84000
0686ADA3 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0686 | This building contains 3 water fountains that are not ADA compliant. The 2018 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of three drinking fountains to meet the ADA requirements. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #012 DORMITORY (P.O.S.T.) | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 14572 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 8000
0686ADA4 | ADA SIGNAGE | 0686 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2018 IBC, ICC/ANSI A117.1, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #012 DORMITORY (P.O.S.T.) | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 14572 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 1500
0686INT1 | INTERIOR FINISHES | 0686 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | #012 DORMITORY (P.O.S.T.) | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 14572 | 2020-02-07 | Four to Ten Years | Long-Term Needs | 3 | 72900
0686ELE2 | EXTERIOR LIGHTING REPLACEMENT | 0686 | The building has perimeter lighting on the exterior of the building, but the light fixtures are old, failing, and not energy efficient. This project would provide for the replacement of the exterior lighting fixtures with new LED light fixtures, using existing wiring. | #012 DORMITORY (P.O.S.T.) | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 14572 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0686EXT1 | WINDOW REPLACEMENT | 0686 | The windows are original, single pane construction in a wooden frame. These older windows are drafty, not energy efficient and the wooden frames have deteriorated significantly. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 70 units including wooden frames and additional costs are included due to the historical nature of the building. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #012 DORMITORY (P.O.S.T.) | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 14572 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 175000
0686INT3 | JANITORS CLOSET REPAIRS | 0686 | The mop sinks in the Janitors Closets are mounted adjacent to gypsum board and are showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. This is recommended for two Janitors Closets. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #012 DORMITORY (P.O.S.T.) | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 14572 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3500
0686EXT4 | EXTERIOR FINISHES | 0686 | The exterior finishes are in fair condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting the wood finishes, re-pointing the stone where needed, and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | #012 DORMITORY (P.O.S.T.) | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 14572 | 2020-02-07 | Four to Ten Years | Long-Term Needs | 3 | 72900
0732ENV1 | ASBESTOS ABATEMENT, TSI | 0732 | An inspection was performed on this building in 1989 for asbestos containing materials (ACM). Thermal System Insulation was found on the piping and this report recommends abatement of this material. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #060 NON-PROFIT | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 1746 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 41500
0455ADA1 | ADA ACCESSIBLE PATH OF TRAVEL | 0455 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the entrance are necessary to comply with ADA accessibility requirements. This project would provide for a concrete van accessible ADA parking and loading space and concrete walkway to the existing entrance. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2018 IBC, ICC/ANSI A117.1, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. 750 square feet of concrete was used for this estimate. It is recommended that this project coincide with the paving project. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #033 NON-PROFIT HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 1729 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 35700
0455ENV1 | ASBESTOS ABATEMENT, TSI | 0455 | An inspection was performed on this building in 1989 for asbestos containing materials (ACM). Thermal System Insulation was found on the piping and this report recommends abatement of this material. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #033 NON-PROFIT HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 1729 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 41200
0455SFT5 | EXIT SIGN AND EGRESS LIGHTING INSTALLATION | 0455 | The building does not have any emergency lighting or exit signs. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems, as well as emergency egress lighting, to provide illumination along the egress route. IBC - 2018 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #033 NON-PROFIT HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 1729 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 5200
0455SFT7 | SEISMIC RETROFIT ROOF STRUCTURE | 0455 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current codes. Visual analysis during the survey found no indication of seismic strengthening of the roof structure. The roof structure should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #033 NON-PROFIT HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 1729 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 81200
0454ADA4 | ADA RESTROOM UPGRADE | 0454 | The building does not have an accessible restroom. The existing restroom does not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2018 IBC, ICC/ANSI A117.1, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #032 NON-PROFIT OFFICE | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 1800 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 17900
0732INT1 | INTERIOR FINISHES | 0732 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | #060 NON-PROFIT | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 1746 | 2020-02-07 | Four to Ten Years | Long-Term Needs | 3 | 8700
0731ENR2 | HVAC EQUIPMENT REPLACEMENT | 0731 | The existing HVAC system consists of wall mounted hydronic radiators and there is no cooling equipment. This project would provide for replacing the existing equipment with exterior ground mounted packaged units that provide natural gas-fired heating as well as air conditioning. Ducting and vents will need to be installed in either the attic or the crawlspace as well. This project includes removal and disposal of the existing HVAC equipment and all required connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #057 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 3000 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 54000
0732PLM1 | WATER HEATER REPLACEMENT | 0732 | There are two 40 gallon natural gas-fired water heaters in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, these units are showing signs of wear and should be scheduled for replacement in the next 1 - 2 years. It is recommended that two new natural gas-fired water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #060 NON-PROFIT | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 1746 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 3000
0744INT5 | KITCHEN REMODEL | 0744 | The kitchen is in fair to poor condition. The cabinets and equipment are showing signs of general wear and tear and are approaching the end of their expected life. This project recommends the replacement of the existing kitchen cabinets, countertops, fixtures, and equipment with mid range, high quality components. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #116 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1198 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11900
0732SFT6 | SEISMIC RETROFIT ROOF STRUCTURE | 0732 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current codes. Visual analysis during the survey found no indication of seismic strengthening of the roof structure. The roof structure should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #060 NON-PROFIT | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 1746 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 82000
0731ELE1 | ELECTRICAL UPGRADE | 0731 | The building's wiring appears to be in good order with GFCIs installed in all wet locations and other outlets are grounded 3 prong type. However, the main breaker panel may be a safety hazard and require replacement. If the breaker panel is a Sylvania Zinsco or Federal Pacific “Stab-Loc” breaker panel, it should be replaced. This project would fund an audit by a qualified electrician and any required replacement. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #057 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 3000 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
0731SFT3 | SEISMIC RETROFIT WALLS | 0731 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current code. Visual analysis during the survey found no indication of seismic strengthening of the URM walls. The walls should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #057 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 3000 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 225000
0731INT6 | RESTROOM REMODEL | 0731 | The two restrooms in the residence are original to the building and in overall poor condition. The finishes, fixtures, cabinets, toilets, showers, and exhaust fans are showing signs of wear and deterioration. This project would provide for a complete remodel of the restrooms. While not required, it is recommended the design of one restroom be compliant with the 2018 IBC, ICC/ANSI A117.1, NRS 338.180, and the most current version of the ADA Standards for Accessible Design. The removal and disposal of the existing fixtures and finishes is included in this estimate. | #057 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 3000 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 24000
0734INT3 | RESTROOM REMODEL | 0734 | The two restrooms in the duplex are more than 20 years old and in overall poor condition. The finishes, fixtures, cabinets, toilets, showers, and exhaust fans are showing signs of wear and deterioration. This project would provide for a complete remodel of both restrooms in the duplex. The removal and disposal of the existing fixtures and finishes is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #062 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1960 | 1630 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24000
0731EXT2 | EXTERIOR FINISHES | 0731 | The exterior finishes are in good condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting the wood finishes, re-pointing the stone where needed, and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | #057 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 3000 | 2020-02-07 | Four to Ten Years | Long-Term Needs | 3 | 15000
0731INT3 | FLOORING REPLACEMENT | 0731 | The sheet vinyl and wood plank flooring in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be upgraded. This project would provide for removal and disposal of the existing sheet vinyl flooring and installation of new 12x12 VCT flooring with a 6" base in its place as well as covering the wood planks with VCT. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #057 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 3000 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 29000
0732EXT1 | EXTERIOR FINISHES | 0732 | The exterior paint is in poor condition including roof rafters and fascia. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting the wood finishes, re-pointing the stone where needed, and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the 2 - 3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | #060 NON-PROFIT | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 1746 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10400
0737INT2 | INTERIOR FINISHES | 0737 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | #084 B&G SHOP | 9971 | Admin | PubWorks | B&G | Stewart | 1931 | 4581 | 2020-02-07 | Four to Ten Years | Long-Term Needs | 3 | 22905
0744EXT5 | EXTERIOR FINISHES | 0744 | The exterior is in good condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting, and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | #116 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1198 | 2020-02-07 | Four to Ten Years | Long-Term Needs | 3 | 15000
0736SFT6 | SEISMIC RETROFIT WALLS | 0736 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current code. Visual analysis during the survey found no indication of seismic strengthening of the URM walls. The walls should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #067 NON-PROFIT | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 4862 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 364600
0736SFT3 | SMOKE ALARM INSTALLATION | 0736 | Section 907.2.9 and 907.2.10 of the 2018 IBC and 2018 IFC explains the requirements for smoke alarms in dwelling units including installing and maintaining smoke alarms in each sleeping room and on the ceiling or wall outside of each separate sleeping area in the immediate vicinity of bedrooms. State Fire Marshal NAC 477.915 (3) requires that smoke detectors be connected to the wiring of the building with a battery backup. This project would provide funding for the purchase and installation of smoke alarms in accordance with these codes. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #067 NON-PROFIT | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 4862 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 3800
0736ADA1 | ADA RESTROOM UPGRADE | 0736 | The restrooms in this triplex dwelling are not ADA accessible. The existing restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom for one of the units in the triplex. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2018 IBC, ICC/ANSI A117.1, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #067 NON-PROFIT | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 4862 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 17800
0736INT2 | RESTROOM REMODEL | 0736 | The four restrooms in the building that are more than 20 years old and in overall poor condition. The finishes, fixtures, cabinets, toilets, showers, and exhaust fans are showing signs of wear and deterioration. This project would provide for a complete remodel of three of the restrooms. The removal and disposal of the existing fixtures and finishes is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #067 NON-PROFIT | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 4862 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 36000
0736ELE1 | ELECTRICAL UPGRADE | 0736 | This building was constructed before the high demand for electrical services were needed for computers and other electrical devices. As time has progressed, the building's electrical demand and system has changed. It is utilized to its current maximum potential. The electrical panels are more than 30 years old and the fuses burn out often and it is difficult to find the correct replacement fuses. All wet locations should have GFCI outlets. It is recommended the entire system be upgraded to meet the evolving needs of the building. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #067 NON-PROFIT | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 4862 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 97200
0736SFT1 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0736 | This building does not have an automatic fire suppression system. It should be retrofitted with fire sprinklers during the next remodel or change of occupancy according to 2018 IEBC 101.4 Applicability provision, 2018 IFC and NAC 477.917. This project would provide funding for the installation of fire sprinklers including backflow prevention devices. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #067 NON-PROFIT | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 4862 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 81000
0737SFT2 | FIRE ALARM SYSTEM INSTALLATION | 0737 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1 Section 7 and the 2018 International Fire Code. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #084 B&G SHOP | 9971 | Admin | PubWorks | B&G | Stewart | 1931 | 4581 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 23000
0736SFT2 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0736 | This project would provide for the installation of two seismic gas shut-off valves on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #067 NON-PROFIT | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 4862 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 9500
0737EXT5 | EXTERIOR FINISHES | 0737 | The exterior finishes are in good condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting the wood finishes, re-pointing the stone where needed, and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | #084 B&G SHOP | 9971 | Admin | PubWorks | B&G | Stewart | 1931 | 4581 | 2020-02-07 | Four to Ten Years | Long-Term Needs | 3 | 22905
0737SFT7 | SEISMIC RETROFIT WALLS | 0737 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current code. Visual analysis during the survey found no indication of seismic strengthening of the URM walls. The walls should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #084 B&G SHOP | 9971 | Admin | PubWorks | B&G | Stewart | 1931 | 4581 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 343500
0737ENR1 | WINDOW REPLACEMENT | 0737 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 10 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #084 B&G SHOP | 9971 | Admin | PubWorks | B&G | Stewart | 1931 | 4581 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18000
0737ADA1 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0737 | This building contains a water fountain that is not ADA compliant. The 2018 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #084 B&G SHOP | 9971 | Admin | PubWorks | B&G | Stewart | 1931 | 4581 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 5000
0734ELE1 | ELECTRICAL UPGRADE | 0734 | The building's wiring appears to be in fair condition with GFCIs installed in all wet locations and most other outlets are grounded 3 prong type. Some 2 prong non-grounded outlets do remain and should be replaced. However, the main breaker panel is a Federal Pacific “Stab-Loc” panel and is recognized as a safety hazard and requires replacement. This project would fund a review by a qualified electrician and fund replacement. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #062 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1960 | 1630 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
0734ENR1 | FURNACE REPLACEMENT | 0734 | The duplex building is heated by natural gas-fired furnaces. One is a newer 90% condensing type while the other is an older 80% standard efficiency unit. The older unit is more than 15 years old and is reaching the end of its useful life. This project provides for the removal and disposal of the existing unit, and replacement with a new natural gas-fired unit including connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #062 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1960 | 1630 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
0737SFT5 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0737 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2018 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #084 B&G SHOP | 9971 | Admin | PubWorks | B&G | Stewart | 1931 | 4581 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 2300
0737EXT2 | STAIR REPLACEMENT | 0737 | There is a set of wood stairs that accesses the north side of the building which serves as a means of egress. They are in poor condition and do not meet current codes. Also, the guardrail on the exterior deck area is missing and / or not to code. This project would provide for the removal of the existing stairs and installation of a new set of wood stairs which comply with Chapter 10 of the 2018 IBC and a wood framed guardrail along the deck area. A 3'x3' concrete landing at the bottom of the stairs is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #084 B&G SHOP | 9971 | Admin | PubWorks | B&G | Stewart | 1931 | 4581 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 7500
0735ELE1 | ELECTRICAL UPGRADE | 0735 | This building was constructed before the high demand for electrical services were needed for computers and other electrical devices. As time has progressed, the building's electrical demand and system has changed. It is utilized to its current maximum potential. The electrical panels are more than 30 years old, the fuses burn out often and it is difficult to find the correct replacement fuses. It is recommended the entire system be upgraded to meet the evolving needs of the building. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #065 NON-PROFIT | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 2102 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
0734INT2 | INTERIOR DOOR REPLACEMENT | 0734 | The interior doors in this building are hollow core units and most are damaged. This project would provide for the installation of new solid core interior doors including frames, lever action door handles, hardware and paint. Removal and disposal of the existing doors is included in this cost estimate. A total of 12 interior doors was used in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #062 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1960 | 1630 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7200
0734EXT2 | EXTERIOR FINISHES | 0734 | The building exterior is in fair condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting, and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | #062 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1960 | 1630 | 2020-02-07 | Four to Ten Years | Long-Term Needs | 3 | 8150
0734SFT4 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0734 | The building is an R-3 occupancy per the 2018 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as an R occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #062 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1960 | 1630 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 28000
0735SFT7 | SEISMIC RETROFIT ROOF STRUCTURE | 0735 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current codes. Visual analysis during the survey found no indication of seismic strengthening of the roof structure. The roof structure should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #065 NON-PROFIT | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 2102 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 98700
0735INT1 | INTERIOR FINISHES | 0735 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | #065 NON-PROFIT | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 2102 | 2020-02-07 | Four to Ten Years | Long-Term Needs | 3 | 10500
0735SFT1 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0735 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing Unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #065 NON-PROFIT | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 2102 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 5000
0736ADA2 | ADA ACCESSIBLE PATH OF TRAVEL | 0736 | This building is not ADA accessible. The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the building entrance are necessary to comply with ADA accessibility requirements. This project would provide for a concrete van accessible ADA parking and loading space and concrete walkway to the existing sidewalk. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2018 IBC, ICC/ANSI A117.1, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. 750 square feet of concrete was used for this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #067 NON-PROFIT | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 4862 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 23500
0735ENV1 | ASBESTOS ABATEMENT, TSI | 0735 | An inspection was performed on this building in 1989 for asbestos containing materials (ACM). Thermal System Insulation was found on the piping and this report recommends abatement of this material. Additionally, the basement of this building is in use for laundry and general storage. The piping that is suspected to contain ACM has a small area of damage. Also, the unfaced fiberglass insulation on the HVAC ductwork is damaged and in need of removal and/ or replacement with faced insulation. This project recommends an additional ACM inspection/ testing, removal/ encapsulation of ACM and unfaced fiberglass, and thorough cleaning of the basement area. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #065 NON-PROFIT | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 2102 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 50500
0738EXT2 | EXTERIOR FINISHES | 0738 | The exterior finishes are in poor condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting the wood finishes, re-pointing the stone where needed, and caulking of the windows, flashing, fixtures and all other penetrations to maintain the building in good, weather tight condition. It is recommended that the building be painted in the next 2 -3 years and that this project be done on a cyclical basis based on environmental conditions and exposure to the elements. | #092 CENTRAL HEAT PLANT | 9971 | Admin | PubWorks | B&G | Stewart | 1924 | 3825 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 38300
0735SFT3 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0735 | This building does not have an automatic fire suppression system. It should be retrofitted with fire sprinklers during the next remodel or addition according to 2018 IEBC 101.4 Applicability provision, 2018 IFC and NAC 477.917. This project would provide funding for the installation of fire sprinklers including backflow prevention devices. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #065 NON-PROFIT | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 2102 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 35000
0735SFT6 | SEISMIC RETROFIT WALLS | 0735 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current code. Visual analysis during the survey found no indication of seismic strengthening of the URM walls. The walls should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #065 NON-PROFIT | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 2102 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 157600
0735SFT2 | SMOKE ALARM INSTALLATION | 0735 | Section 907.2.11 of the 2018 IBC and 2018 IFC explains the requirements for smoke alarms in dwelling units including installing and maintaining smoke alarms in each sleeping room and on the ceiling or wall outside of each separate sleeping area in the immediate vicinity of bedrooms. State Fire Marshal NAC 477.915 (3) requires that smoke detectors be connected to the wiring of the building with a battery backup. This project would provide funding for the purchase and installation of smoke alarms in accordance with these codes. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #065 NON-PROFIT | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 2102 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 1000
0736SFT7 | SEISMIC RETROFIT ROOF STRUCTURE | 0736 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current codes. Visual analysis during the survey found no indication of seismic strengthening of the roof structure. The roof structure should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #067 NON-PROFIT | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 4862 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 228500
0736INT1 | INTERIOR FINISHES | 0736 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | #067 NON-PROFIT | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 4862 | 2020-02-07 | Four to Ten Years | Long-Term Needs | 3 | 24300
0736EXT1 | EXTERIOR FINISHES | 0736 | The exterior paint is in fair condition. It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting the wood finishes, re-pointing the stone where needed and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | #067 NON-PROFIT | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 4862 | 2020-02-07 | Four to Ten Years | Long-Term Needs | 3 | 24300
0736ENV1 | ASBESTOS ABATEMENT, TSI | 0736 | An inspection was performed on this building in 1989 for asbestos containing materials (ACM). Thermal System Insulation was found on the piping and this report recommends abatement of this material. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #067 NON-PROFIT | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 4862 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 97200
0735EXT1 | EXTERIOR FINISHES | 0735 | The exterior paint is in poor condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting the wood finishes, re-pointing the stone where needed, and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2 - 3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | #065 NON-PROFIT | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 2102 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12500
0743EXT2 | CONSERVE AND PROTECT VACANT BUILDING | 0743 | In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to removing water in the basement or crawlspace, providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #114 WAREHOUSE (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1925 | 3200 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 64000
0741EXT2 | CONCRETE PATIO REPLACEMENT | 0741 | The exterior concrete patio has extensive cracking and is due for replacement. This project would provide for the installation of a new 4" thick concrete slab-on-grade patio on the west side of the house. Removal and disposal of the existing concrete is included in this estimate. | #110 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 2000 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 5100
0741PLM1 | WATER HEATER REPLACEMENT | 0741 | There are two 30 gallon electric water heaters in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, these units are showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that new gas-fired water heaters be installed for more efficient use of energy. This estimate includes: 100 feet of gas pipe, fittings, couplers, and labor for installation. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #110 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 2000 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3600
0741ENR1 | EVAPORATIVE COOLER REPLACEMENT | 0741 | An evaporative cooler is installed on the side of this building. It is severely scaled and has reached the end of its useful and expected life. This project would provide for a new evaporative cooler to be installed including all required connections to utilities. The estimate includes removal and disposal of the old cooler. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #110 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 2000 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3600
0741SFT2 | INTERIOR STAIRWAY REPLACEMENT | 0741 | The stairway does not meet code. It is not required to be replaced unless a change of occupancy occurs or the dwelling undergoes a significant alteration. However, there are no handrails. This project would provide funding to install a handrail. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #110 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 2000 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
0742SFT2 | SEISMIC RETROFIT ROOF STRUCTURE | 0742 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current codes. Visual analysis during the survey found no indication of seismic strengthening of the roof structure. The roof structure should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #112 BARN (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1925 | 2450 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 115100
0742EXT2 | CONSERVE AND PROTECT VACANT BUILDING | 0742 | In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to removing water in the basement or crawlspace, providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #112 BARN (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1925 | 2450 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 49000
0738SFT4 | SEISMIC RETROFIT ROOF STRUCTURE | 0738 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current codes. Visual analysis during the survey found no indication of seismic strengthening of the roof structure. The roof structure should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #092 CENTRAL HEAT PLANT | 9971 | Admin | PubWorks | B&G | Stewart | 1924 | 3825 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 179700
0727SFT1 | FIRE ALARM SYSTEM INSTALLATION | 0727 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1 Section 7 and the 2018 International Fire Code. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #044 CAPITOL POLICE SUBSTATION | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 650 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 5200
0741INT4 | KITCHEN REMODEL | 0741 | The kitchen and associated cabinets are original to the residence. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and countertops are delaminating and failing. This project recommends the replacement of the existing kitchen countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product over a moisture resistant underlayment to minimize swelling and damage from water exposure. While not required, ADA compliance is recommended according to NRS 338.180, IBC - 2018, ICC/ANSI A117.1 and the most current version of the ADA Standards for Accessible Design should be incorporated into the design such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. | #110 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 2000 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 18600
0744INT1 | INTERIOR FINISHES | 0744 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | #116 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1198 | 2020-02-07 | Four to Ten Years | Long-Term Needs | 3 | 7100
0744INT2 | FLOORING REPLACEMENT | 0744 | The VCT (vinyl composite tile) and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT flooring with a 6" base and heavy duty commercial grade carpet in the next 2-3 years. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #116 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1198 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11400
0744SFT1 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0744 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #116 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1198 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 5000
0744EXT4 | EXTERIOR DOOR REPLACEMENT | 0744 | The 1 exterior wood man door in the rear appears to be original to the building. It is damaged from age and general wear and tear. This project would provide for the replacement of the wood door with a new wood door, frame and hardware. Removal and disposal of the existing door, and painting of the new door is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #116 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1198 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 600
0744ENR1 | LIGHTING UPGRADE | 0744 | The existing lighting fixtures are the older incandescent type. Some are broken and they are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. CFL (compact fluorescent lamps) are suggested. Occupancy sensors will be installed in restrooms, closets, and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #116 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1198 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0744INT4 | INTERIOR DOOR REPLACEMENT | 0744 | The interior doors in this building are hollow core units and most are damaged. This project would provide for the installation of new solid core interior doors including frames, lever action door handles, hardware and paint. Removal and disposal of the existing doors is included in this cost estimate. A total of 8 interior doors was used in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #116 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1198 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4800
0731INT2 | INTERIOR FINISHES | 0731 | The interior finishes are in poor condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2 - 3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | #057 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 3000 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0742SFT1 | SEISMIC RETROFIT WALLS | 0742 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current code. Visual analysis during the survey found no indication of seismic strengthening of the URM walls. The walls should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #112 BARN (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1925 | 2450 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 183700
0740EXT2 | CONSERVE AND PROTECT VACANT BUILDING | 0740 | In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to removing water in the basement or crawlspace, providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #056 GARAGE (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 2075 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 41500
0744INT3 | RESTROOM REMODEL | 0744 | The restroom in the residence is original to the building and in overall poor condition. The finishes, fixtures, cabinets, toilet, shower, and exhaust fan are showing signs of wear and deterioration. This project would provide for a complete remodel of the restroom. The removal and disposal of the existing fixtures and finishes is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #116 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1198 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
0738SFT2 | INSTALL SEISMIC GAS SHUT-OFF VALVE | 0738 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel brace. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #092 CENTRAL HEAT PLANT | 9971 | Admin | PubWorks | B&G | Stewart | 1924 | 3825 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 5000
0738SFT3 | SEISMIC RETROFIT WALLS | 0738 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current code. Visual analysis during the survey found no indication of seismic strengthening of the URM walls. The walls should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #092 CENTRAL HEAT PLANT | 9971 | Admin | PubWorks | B&G | Stewart | 1924 | 3825 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 286800
0739SFT3 | SEISMIC RETROFIT ROOF STRUCTURE | 0739 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current codes. Visual analysis during the survey found no indication of seismic strengthening of the roof structure. The roof structure should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #096 B&G WAREHOUSE | 9971 | Admin | PubWorks | B&G | Stewart | 1940 | 2710 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 127300
0739EXT2 | EXTERIOR FINISHES | 0739 | The exterior finishes are in poor condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting the wood finishes, re-pointing the stone where needed, and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2 - 3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | #096 B&G WAREHOUSE | 9971 | Admin | PubWorks | B&G | Stewart | 1940 | 2710 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 13600
0747INT1 | INTERIOR FINISHES | 0747 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | #119 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1203 | 2020-02-07 | Four to Ten Years | Long-Term Needs | 3 | 7200
0739SFT1 | INTERIOR STAIR HANDRAIL REPLACEMENT | 0739 | The interior stair handrails in the building are older and do not meet code for safety. The gripping surfaces are incorrect, they are not continuous from the top to bottom landings and/ or they are installed on only one side of the stairs. This project recommends the installation of handrails on both sides of the stairs, with proper returns and supports in accordance with the 2018 IBC Chapter 10, Section 1012. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #096 B&G WAREHOUSE | 9971 | Admin | PubWorks | B&G | Stewart | 1940 | 2710 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 7500
0741SFT4 | SEISMIC RETROFIT WALLS | 0741 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current code. Visual analysis during the survey found no indication of seismic strengthening of the URM walls. The walls should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #110 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 2000 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 150000
0739INT1 | INTERIOR FINISHES | 0739 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | #096 B&G WAREHOUSE | 9971 | Admin | PubWorks | B&G | Stewart | 1940 | 2710 | 2020-02-07 | Four to Ten Years | Long-Term Needs | 3 | 13600
0741SFT3 | EXIT SIGN AND EGRESS LIGHTING INSTALLATION | 0741 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. | #110 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 2000 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 2600
0740EXT1 | ROOF REPLACEMENT | 0740 | The wood shake shingle and asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition shingle roof and new underlayments. This estimate includes removal and disposal of the old roof. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #056 GARAGE (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 2075 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 39000
0741SFT50 | SEISMIC RETROFIT ROOF STRUCTURE | 0741 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current codes. Visual analysis during the survey found no indication of seismic strengthening of the roof structure. The roof structure should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #110 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 2000 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 94000
0741SFT1 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0741 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #110 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 2000 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 5000
0741INT1 | INTERIOR FINISHES | 0741 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | #110 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 2000 | 2020-02-07 | Four to Ten Years | Long-Term Needs | 3 | 10000
0741EXT3 | TREE REMOVAL | 0741 | The building has two trees which are growing up against the structure. The trees move in windy conditions, rubbing the roofs, which can cause premature failure of the roof system and voiding roof warranties. The root systems are causing shifting and heaving of the foundation and sidewalks, creating unsafe conditions. This project recommends removing the trees. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #110 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 2000 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0741EXT1 | EXTERIOR FINISHES | 0741 | The exterior paint is in fair condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting the wood finishes, re-pointing the stone where needed, and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4 -5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | #110 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 2000 | 2020-02-07 | Four to Ten Years | Long-Term Needs | 3 | 10000
0738INT1 | REMOVE AND SALVAGE EXISTING EQUIPMENT | 0738 | The existing equipment in this building has been abandoned and is no longer required or in use. There are 4 boilers, holding tanks, piping and ancillary equipment inside that should be removed to allow for a different and efficient use of this facility. Some of the piping contains asbestos insulation based on a previous environmental report conducted in 1989. This project would provide for the removal, disposal and / or salvaging of the equipment currently inside of the building including asbestos removal. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #092 CENTRAL HEAT PLANT | 9971 | Admin | PubWorks | B&G | Stewart | 1924 | 3825 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 60000
0739SFT2 | SEISMIC RETROFIT WALLS | 0739 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current code. Visual analysis during the survey found no indication of seismic strengthening of the URM walls. The walls should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #096 B&G WAREHOUSE | 9971 | Admin | PubWorks | B&G | Stewart | 1940 | 2710 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 203200
0444SFT1 | SEISMIC RETROFIT WALLS | 0444 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current code. Visual analysis during the survey found no indication of seismic strengthening of the URM walls. The walls should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #022 DMV & PS STORAGE (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 6395 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 479700
0449SFT2 | SEISMIC RETROFIT ROOF STRUCTURE | 0449 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current codes. Visual analysis during the survey found no indication of seismic strengthening of the roof structure. The roof structure should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #027 WASHOE TRIBE (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 2254 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 105900
0447EXT2 | CONSERVE AND PROTECT VACANT BUILDING | 0447 | In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to removing water in the basement or crawlspace, providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. | #025 DORMITORY (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 6395 | 2020-02-07 | Four to Ten Years | Long-Term Needs | 3 | 150000
0447ENV1 | ASBESTOS ABATEMENT, ACOUSTICAL CEILING & TSI | 0447 | An inspection was performed on this building in 1989 for asbestos containing materials (ACM). Spray acoustical ceiling material was found which is believed to contain asbestos, and this report recommends abatement of this material. Piping insulation also was found which is believed to contain asbestos, and this report recommends abatement of this material. | #025 DORMITORY (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 6395 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 150000
0447SFT1 | SEISMIC RETROFIT WALLS | 0447 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current code. Visual analysis during the survey found no indication of seismic strengthening of the URM walls. The walls should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #025 DORMITORY (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 6395 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 479700
0446ENV1 | ASBESTOS ABATEMENT, ACOUSTICAL CEILING & TSI | 0446 | An inspection was performed on this building in 1989 for asbestos containing materials (ACM). Spray acoustical ceiling material was found which is believed to contain asbestos, and this report recommends abatement of this material. Piping insulation also was found which is believed to contain asbestos, and this report recommends abatement of this material. | #024 DORMITORY (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 6395 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 150000
0446SFT10 | SEISMIC RETROFIT WALLS | 0446 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current code. Visual analysis during the survey found no indication of seismic strengthening of the URM walls. The walls should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #024 DORMITORY (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 6395 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 479700
0446EXT2 | CONSERVE AND PROTECT VACANT BUILDING | 0446 | In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to removing water in the basement or crawlspace, providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. | #024 DORMITORY (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 6395 | 2020-02-07 | Four to Ten Years | Long-Term Needs | 3 | 150000
0445SFT1 | SEISMIC RETROFIT WALLS | 0445 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current code. Visual analysis during the survey found no indication of seismic strengthening of the URM walls. The walls should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #023 DORMITORY (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 6395 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 479700
0441SFT2 | SEISMIC RETROFIT WALLS | 0441 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current code. Visual analysis during the survey found no indication of seismic strengthening of the URM walls. The walls should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #068A & 068B SHOPS (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1931 | 8588 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 644000
0445EXT2 | CONSERVE AND PROTECT VACANT BUILDING | 0445 | In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to removing water in the basement or crawlspace, providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. | #023 DORMITORY (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 6395 | 2020-02-07 | Four to Ten Years | Long-Term Needs | 3 | 150000
0449SFT1 | SEISMIC RETROFIT WALLS | 0449 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current code. Visual analysis during the survey found no indication of seismic strengthening of the URM walls. The walls should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only | #027 WASHOE TRIBE (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 2254 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 169000
0444EXT2 | CONSERVE AND PROTECT VACANT BUILDING | 0444 | In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to removing water in the basement or crawlspace, providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. | #022 DMV & PS STORAGE (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 6395 | 2020-02-07 | Four to Ten Years | Long-Term Needs | 3 | 150000
0444ENV1 | ASBESTOS ABATEMENT, ACOUSTICAL CEILING & TSI | 0444 | An inspection was performed on this building in 1989 for asbestos containing materials (ACM). Spray acoustical ceiling material was found which is believed to contain asbestos, and this report recommends abatement of this material. Piping insulation also was found which is believed to contain asbestos, and this report recommends abatement of this material. | #022 DMV & PS STORAGE (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 6395 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 150000
0443SFT1 | SEISMIC RETROFIT WALLS | 0443 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current code. Visual analysis during the survey found no indication of seismic strengthening of the URM walls. The walls should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #021 DORMITORY (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 8662 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 649600
0443EXT2 | CONSERVE AND PROTECT VACANT BUILDING | 0443 | In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to removing water in the basement or crawlspace, providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. | #021 DORMITORY (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 8662 | 2020-02-07 | Four to Ten Years | Long-Term Needs | 3 | 205000
0443ENV1 | ASBESTOS ABATEMENT, ACOUSTICAL CEILING & TSI | 0443 | An inspection was performed on this building in 1989 for asbestos containing materials (ACM). Spray acoustical ceiling material was found which is believed to contain asbestos, and this report recommends abatement of this material. Piping insulation also was found which is believed to contain asbestos, and this report recommends abatement of this material. . | #021 DORMITORY (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 8662 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 205000
0442SFT1 | SEISMIC RETROFIT WALLS | 0442 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current code. Visual analysis during the survey found no indication of seismic strengthening of the URM walls. The walls should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #019 OLD POST OFFICE | 9971 | Admin | PubWorks | B&G | Stewart | 1926 | 1646 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 123400
0442ENV1 | ASBESTOS ABATEMENT, TSI | 0442 | An inspection was performed on this building in 1989 for asbestos containing materials (ACM). Piping insulation was found which is believed to contain asbestos, and this report recommends abatement of this material. | #019 OLD POST OFFICE | 9971 | Admin | PubWorks | B&G | Stewart | 1926 | 1646 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19500
0725EXT2 | CONSERVE AND PROTECT VACANT BUILDING | 0725 | In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to removing water in the basement or crawlspace, providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. | #036 WASHOE TRIBE (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1942 | 1500 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 30000
0445ENV1 | ASBESTOS ABATEMENT, ACOUSTICAL CEILING & TSI | 0445 | An inspection was performed on this building in 1989 for asbestos containing materials (ACM). Spray acoustical ceiling material was found which is believed to contain asbestos, and this report recommends abatement of this material. Piping insulation also was found which is believed to contain asbestos, and this report recommends abatement of this material. | #023 DORMITORY (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 6395 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 150000
0452EXT2 | CONSERVE AND PROTECT VACANT BUILDING | 0452 | In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to removing water in the basement or crawlspace, providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. | #030 WASHOE TRIBE (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 2569 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 51400
0725SFT2 | SEISMIC RETROFIT WALLS | 0725 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current code. Visual analysis during the survey found no indication of seismic strengthening of the URM walls. The walls should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #036 WASHOE TRIBE (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1942 | 1500 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 112500
0726SFT2 | SEISMIC RETROFIT ROOF STRUCTURE | 0726 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current codes. Visual analysis during the survey found no indication of seismic strengthening of the roof structure. The roof structure should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #037 QUARTERS (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1956 | 1433 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 67300
0686SFT4 | SEISMIC RETROFIT WALLS | 0686 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current code. Visual analysis during the survey found no indication of seismic strengthening of the URM walls. The walls should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #012 DORMITORY (P.O.S.T.) | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 14572 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 1093000
0726EXT2 | CONSERVE AND PROTECT VACANT BUILDING | 0726 | In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to removing water in the basement or crawlspace, providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. | #037 QUARTERS (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1956 | 1433 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 28700
0731INT5 | KITCHEN REMODEL | 0731 | The kitchen is in fair to poor condition. The cabinets and equipment are showing signs of general wear and tear and are approaching the end of their expected life. This project recommends the replacement of the existing kitchen cabinets, countertops, fixtures and equipment with mid range, high quality components. | #057 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 3000 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 43500
0726SFT1 | SEISMIC RETROFIT WALLS | 0726 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current code. Visual analysis during the survey found no indication of seismic strengthening of the URM walls. The walls should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #037 QUARTERS (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1956 | 1433 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 107400
0727SFT4 | SEISMIC RETROFIT ROOF STRUCTURE | 0727 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current codes. Visual analysis during the survey found no indication of seismic strengthening of the roof structure. The roof structure should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #044 CAPITOL POLICE SUBSTATION | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 650 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 30500
0727EXT4 | EXTERIOR FINISHES | 0727 | The wood framed portion of the building is in very poor condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting the wood finishes, re-pointing the stone where needed, and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2 - 3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | #044 CAPITOL POLICE SUBSTATION | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 650 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 13000
0449EXT2 | CONSERVE AND PROTECT VACANT BUILDING | 0449 | In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to removing water in the basement or crawlspace, providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. | #027 WASHOE TRIBE (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 2254 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 45000
0452ENV1 | ASBESTOS ABATEMENT, TSI | 0452 | An inspection was performed on this building in 1989 for asbestos containing materials (ACM). Piping insulation was found which is believed to contain asbestos, and this report recommends abatement of this material. | #030 WASHOE TRIBE (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 2569 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 56000
0449ENV1 | ASBESTOS ABATEMENT, TSI | 0449 | An inspection was performed on this building in 1989 for asbestos containing materials (ACM). Piping insulation was found which is believed to contain asbestos, and this report recommends abatement of this material. | #027 WASHOE TRIBE (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 2254 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 49000
0452SFT2 | SEISMIC RETROFIT ROOF STRUCTURE | 0452 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current codes. Visual analysis during the survey found no indication of seismic strengthening of the roof structure. The roof structure should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #030 WASHOE TRIBE (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 2569 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 120700
0451SFT1 | SEISMIC RETROFIT WALLS | 0451 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current code. Visual analysis during the survey found no indication of seismic strengthening of the URM walls. The walls should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #029 WASHOE TRIBE (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 3231 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 242300
0451ENV1 | ASBESTOS ABATEMENT, TSI | 0451 | An inspection was performed on this building in 1989 for asbestos containing materials (ACM). Piping insulation was found which is believed to contain asbestos, and this report recommends abatement of this material. | #029 WASHOE TRIBE (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 3231 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 70000
0451EXT2 | CONSERVE AND PROTECT VACANT BUILDING | 0451 | In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to removing water in the basement or crawlspace, providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. | #029 WASHOE TRIBE (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 3231 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 64600
0451SFT2 | SEISMIC RETROFIT ROOF STRUCTURE | 0451 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current codes. Visual analysis during the survey found no indication of seismic strengthening of the roof structure. The roof structure should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #029 WASHOE TRIBE (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 3231 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 151800
0450SFT1 | SEISMIC RETROFIT WALLS | 0450 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current code. Visual analysis during the survey found no indication of seismic strengthening of the URM walls. The walls should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #028 WASHOE TRIBE (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 3523 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 264200
0450EXT2 | CONSERVE AND PROTECT VACANT BUILDINGS | 0450 | In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to removing water in the basement, providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. | #028 WASHOE TRIBE (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 3523 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 70500
0450SFT2 | SEISMIC RETROFIT ROOF STRUCTURE | 0450 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current codes. Visual analysis during the survey found no indication of seismic strengthening of the roof structure. The roof structure should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #028 WASHOE TRIBE (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 3523 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 165500
0441EXT2 | CONSERVE AND PROTECT VACANT BUILDING | 0441 | In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to removing water in the basement or crawlspace, providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. | #068A & 068B SHOPS (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1931 | 8588 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 205000
0452SFT1 | SEISMIC RETROFIT WALLS | 0452 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current code. Visual analysis during the survey found no indication of seismic strengthening of the URM walls. The walls should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #030 WASHOE TRIBE (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 2569 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 192600
0436SEC1 | CONSERVE AND PROTECT VACANT BUILDING | 0436 | In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to removing water in the basement or crawlspace, providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #014 QUARTERS (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 1430 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 28600
0437SFT2 | SEISMIC RETROFIT WALLS | 0437 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current code. Visual analysis during the survey found no indication of seismic strengthening of the URM walls. The walls should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #016 DORMITORY (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1942 | 8416 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 631200
0437SEC1 | CONSERVE AND PROTECT VACANT BUILDING | 0437 | In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to removing water in the basement or crawlspace, providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #016 DORMITORY (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1942 | 8416 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 200000
0442EXT2 | CONSERVE AND PROTECT VACANT BUILDING | 0442 | In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to removing water in the basement or crawlspace, providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. | #019 OLD POST OFFICE | 9971 | Admin | PubWorks | B&G | Stewart | 1926 | 1646 | 2020-02-07 | Four to Ten Years | Long-Term Needs | 3 | 39000
0436SFT1 | SEISMIC RETROFIT WALLS | 0436 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current code. Visual analysis during the survey found no indication of seismic strengthening of the URM walls. The walls should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #014 QUARTERS (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 1430 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 107700
0437ENV1 | ASBESTOS ABATEMENT, TSI | 0437 | An inspection was performed on this building in 1989 for asbestos containing materials (ACM). Piping insulation was found which is believed to contain asbestos, and this report recommends abatement of this material. | #016 DORMITORY (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1942 | 8416 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 200000
0440ADA5 | ADA DOOR HARDWARE | 0440 | The 2010 ADA Standards for Accessible Design states that handles, pulls, latches, locks and other operable parts on doors and gates shall be operable with one hand and shall not require tight grasping, pinching, or twisting of the wrist. The force to activate operable parts shall be 5 pounds maximum. It is recommended that proper lever hardware be installed on all of the interior doors in this building to meet these requirements. The 2018 IBC, ICC/ANSI A117.1, NRS 338.180 and sections 309.4 and 404.2.7 of the 2010 ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #160 NEW GYM | 9971 | Admin | PubWorks | B&G | Stewart | 1973 | 37150 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 31500
0441SFT3 | SEISMIC RETROFIT ROOF STRUCTURE | 0441 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current codes. Visual analysis during the survey found no indication of seismic strengthening of the roof structure. The roof structure should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #068A & 068B SHOPS (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1931 | 8588 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 403600
0440ELE1 | EXTERIOR LIGHTING REPLACEMENT | 0440 | The building has perimeter lighting on the exterior of the building, but the light fixtures are old, failing and not energy efficient. This project would provide for the replacement of the exterior lighting fixtures with new LED light fixtures, using existing wiring. | #160 NEW GYM | 9971 | Admin | PubWorks | B&G | Stewart | 1973 | 37150 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24000
0440SFT4 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0440 | The building is over 12,000 square feet in area. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, every building owned or occupied by the state which is designated as an R occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #160 NEW GYM | 9971 | Admin | PubWorks | B&G | Stewart | 1973 | 37150 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 660000
0440HVA1 | EXHAUST FAN REPLACEMENT | 0440 | Many of the exhaust fans in the restrooms and shower areas were inoperative and should be scheduled for replacement. Due to excessive humidity concerns, high volume commercial units should be installed. Additionally, the gymnasium's exhaust fans are inoperative and should be replaced with new ones. It is recommended that this project coincide with the HVAC system upgrade project. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #160 NEW GYM | 9971 | Admin | PubWorks | B&G | Stewart | 1973 | 37150 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 27000
0440EXT4 | EXTERIOR DOOR REPLACEMENT | 0440 | The exterior metal doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the 13 metal man doors with new metal doors, frames, and ADA compliant hardware. Removal and disposal of the existing doors is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #160 NEW GYM | 9971 | Admin | PubWorks | B&G | Stewart | 1973 | 37150 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 23400
0440SFT1 | FIRE ALARM SYSTEM UPGRADE | 0440 | This building is equipped with an automatic fire detection and alarm system that no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 "If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure". When completed, the new system will provide visual, as well as audible notification, in accordance with the 2018 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #160 NEW GYM | 9971 | Admin | PubWorks | B&G | Stewart | 1973 | 37150 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 175000
0440PLM1 | WATER HEATER REPLACEMENT | 0440 | There is a 100 gallon natural gas-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 3-4 years. It is recommended that a new natural gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #160 NEW GYM | 9971 | Admin | PubWorks | B&G | Stewart | 1973 | 37150 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3600
0440ADA3 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0440 | This building contains a water fountain that is not ADA compliant. The 2018 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #160 NEW GYM | 9971 | Admin | PubWorks | B&G | Stewart | 1973 | 37150 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 5000
0440ENR2 | HVAC SYSTEM UPGRADE | 0440 | The HVAC system consists of two natural gas-fired boilers that were installed in 2000 and three large air handlers that are original to the building. There is no central cooling in the building. The system is not energy efficient and has reached the end of its expected and useful life. This project would provide for installation of a new HVAC system including cooling equipment and cleaning of the existing duct work and grilles. The new system shall be designed to significantly reduce electrical and natural gas usage in order to comply with the 2018 IECC and ASHRAE 90.1 and to reduce utility costs. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #160 NEW GYM | 9971 | Admin | PubWorks | B&G | Stewart | 1973 | 37150 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 670000
0440EXT3 | STOREFRONT SYSTEM REPLACEMENT | 0440 | There are three sets of exterior aluminum entrance storefront systems that appear to be original to the building. They are damaged from age and general wear and tear and are a constant maintenance problem. This project would provide for the replacement and installation of three new exterior aluminum entrance storefront systems including ADA compliant hardware. Removal and disposal of the existing storefronts is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #160 NEW GYM | 9971 | Admin | PubWorks | B&G | Stewart | 1973 | 37150 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 54000
0440ADA1 | ADA RESTROOM UPGRADE | 0440 | The Men's and Women's locker rooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for remodeling the Men's and Women's locker rooms for accessibility upgrades. These items may include new sinks, water closets, urinals, showers, partitions, hardware, mirrors, fixtures, flooring and paint. The 2018 IBC, ICC/ANSI A117.1, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #160 NEW GYM | 9971 | Admin | PubWorks | B&G | Stewart | 1973 | 37150 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 220000
0440INT1 | INTERIOR FINISHES | 0440 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | #160 NEW GYM | 9971 | Admin | PubWorks | B&G | Stewart | 1973 | 37150 | 2020-02-07 | Four to Ten Years | Long-Term Needs | 3 | 185750
0440EXT2 | EXTERIOR FINISHES | 0440 | The exterior is in fair condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the open faced downspouts and other painted finishes, and caulking of the pre-cast stone panels, windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | #160 NEW GYM | 9971 | Admin | PubWorks | B&G | Stewart | 1973 | 37150 | 2020-02-07 | Four to Ten Years | Long-Term Needs | 3 | 185800
0440EXT1 | ROOF REPLACEMENT | 0440 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #160 NEW GYM | 9971 | Admin | PubWorks | B&G | Stewart | 1973 | 37150 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 695000
0439SFT1 | SEISMIC RETROFIT WALLS | 0439 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current codes. It should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #020 OLD GYM (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1938 | 11933 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 894900
0439SEC1 | CONSERVE AND PROTECT VACANT BUILDING | 0439 | In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to removing water in the basement or crawlspace, providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. | #020 OLD GYM (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1938 | 11933 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 60000
0726ENV1 | ASBESTOS ABATEMENT, TSI | 0726 | An inspection was performed on this building in 1989 for asbestos containing materials (ACM). Piping insulation was found which is believed to contain asbestos, and this report recommends abatement of this material. | #037 QUARTERS (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1956 | 1433 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 31000
0440ADA4 | ADA SIGNAGE | 0440 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2018 IBC, ICC/ANSI A117.1, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #160 NEW GYM | 9971 | Admin | PubWorks | B&G | Stewart | 1973 | 37150 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 2700
0454ELE1 | ELECTRICAL UPGRADE | 0454 | This building was constructed before the high demand for electrical services were needed for computers and other electrical devices. As time has progressed, the building's electrical demand and system has changed. It is utilized to its current maximum potential. The electrical panels are more than 30 years old, the fuses burn out often and it is difficult to find the correct replacement fuses. It is recommended the entire system be upgraded to meet the evolving needs of the building. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #032 NON-PROFIT OFFICE | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 1800 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 42800
0453SFT1 | SEISMIC RETROFIT WALLS | 0453 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current code. Visual analysis during the survey found no indication of seismic strengthening of the URM walls. The walls should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #031 WASHOE TRIBE (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 2388 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 179100
0727INT3 | RESTROOM REMODEL | 0727 | The restroom in the building is in overall poor condition. The finishes, fixtures, cabinets, toilets, and exhaust fan are showing signs of wear and deterioration. This project would provide for a complete remodel of the restroom. The removal and disposal of the existing fixtures and finishes is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #044 CAPITOL POLICE SUBSTATION | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 650 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
0727EXT2 | WINDOW REPLACEMENT | 0727 | The windows are original, single pane construction in a wooden frame. These older windows are drafty, not energy efficient and the wooden frames have deteriorated significantly. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 12 units including wooden frames and additional costs are included due to the historical nature of the building. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #044 CAPITOL POLICE SUBSTATION | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 650 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0727INT1 | INTERIOR FINISHES | 0727 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. . | #044 CAPITOL POLICE SUBSTATION | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 650 | 2020-02-07 | Four to Ten Years | Long-Term Needs | 3 | 5200
0727ENV1 | ASBESTOS ABATEMENT, TSI | 0727 | An inspection was performed on this building in 1989 for asbestos containing materials (ACM). Thermal System Insulation was found on the piping and this report recommends abatement of this material. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #044 CAPITOL POLICE SUBSTATION | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 650 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 13000
0454SFT2 | INTERIOR STAIRWAY REPLACEMENT | 0454 | The stairs and handrails between the first floor and the second floor do not meet the requirements in the 2018 International Building Code sections 1009 and 1012. This project would provide funding to remove and replace the stairway and handrail. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #032 NON-PROFIT OFFICE | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 1800 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 10700
0454SFT6 | EXIT SIGN AND EGRESS LIGHTING INSTALLATION | 0454 | The building does not have any emergency lighting and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems, as well as emergency egress lighting, to provide illumination along the egress route. IBC - 2018 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #032 NON-PROFIT OFFICE | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 1800 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 5400
0454SFT7 | SEISMIC RETROFIT WALLS | 0454 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current code. Visual analysis during the survey found no indication of seismic strengthening of the URM walls. The walls should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #032 NON-PROFIT OFFICE | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 1800 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 135000
0727EXT5 | EXTERIOR DOOR REPLACEMENT | 0727 | The 2 exterior wood man doors are damaged from age and general wear and tear. This project would provide for the replacement of the wood doors with new metal doors, frames and hardware. Removal and disposal of the existing doors, and painting of the new doors is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #044 CAPITOL POLICE SUBSTATION | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 650 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0454SIT1 | SIDEWALK REPLACEMENT | 0454 | The sidewalks serving the building and recreation areas on this site have deteriorated and are failing. There is settling in many locations. This project addresses removal and replacement of existing sidewalks as needed. 300 SF of 4" thick concrete sidewalk was used for this estimate. NRS 338.180, IBC - 2018, ICC/ANSI A117.1 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | #032 NON-PROFIT OFFICE | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 1800 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3800
0727SFT3 | SEISMIC RETROFIT WALLS | 0727 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current code. Visual analysis during the survey found no indication of seismic strengthening of the URM walls. The walls should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #044 CAPITOL POLICE SUBSTATION | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 650 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 48700
0454SFT3 | FIRE ALARM SYSTEM INSTALLATION | 0454 | This building is lacking a fire detection and alarm system and only has one smoke detector. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1 Section 7 and the 2018 International Fire Code. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #032 NON-PROFIT OFFICE | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 1800 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 8600
0454ADA3 | INTERIOR ACCESSIBILITY UPGRADES | 0454 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. An accessible path of travel throughout the interior of the building is necessary to comply with ADA accessibility requirements. There are at least two areas of the building that have a change in level greater than 1/2". This project would provide for raising the floor level to match or installing compliant ramps at these locations. The 2018 IBC, ICC/ANSI A117.1, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #032 NON-PROFIT OFFICE | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 1800 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 29800
0725ENV1 | ASBESTOS ABATEMENT, TSI | 0725 | An inspection was performed on this building in 1989 for asbestos containing materials (ACM). Piping insulation was found which is believed to contain asbestos, and this report recommends abatement of this material. | #036 WASHOE TRIBE (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1942 | 1500 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 33000
0454SFT1 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0454 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #032 NON-PROFIT OFFICE | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 1800 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 4800
0454INT1 | INTERIOR FINISHES | 0454 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | #032 NON-PROFIT OFFICE | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 1800 | 2020-02-07 | Four to Ten Years | Long-Term Needs | 3 | 10700
0454ENV1 | ASBESTOS ABATEMENT, TSI | 0454 | An inspection was performed on this building in 1989 for asbestos containing materials (ACM). Thermal System Insulation was found on the piping and this report recommends abatement of this material. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #032 NON-PROFIT OFFICE | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 1800 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 42900
0454SFT8 | SEISMIC RETROFIT ROOF STRUCTURE | 0454 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current codes. Visual analysis during the survey found no indication of seismic strengthening of the roof structure. The roof structure should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #032 NON-PROFIT OFFICE | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 1800 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 84600
0453EXT2 | CONSERVE AND PROTECT VACANT BUILDING | 0453 | In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to removing water in the basement or crawlspace, providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. | #031 WASHOE TRIBE (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 2388 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 47800
0453ENV1 | ASBESTOS ABATEMENT, TSI | 0453 | An inspection was performed on this building in 1989 for asbestos containing materials (ACM). Piping insulation was found which is believed to contain asbestos, and this report recommends abatement of this material. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #031 WASHOE TRIBE (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 2388 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 52000
0454SFT5 | ADA DOOR HARDWARE REPLACEMENT | 0454 | The 2010 ADA Standards for Accessible Design states that handles, pulls, latches, locks and other operable parts on doors and gates shall be operable with one hand and shall not require tight grasping, pinching, or twisting of the wrist. The force to activate operable parts shall be 5 pounds maximum. It is recommended that proper lever hardware be installed on all of the interior doors in this building to meet these requirements. The 2018 IBC, ICC/ANSI A117.1, NRS 338.180 and sections 309.4 and 404.2.7 of the 2010 ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #032 NON-PROFIT OFFICE | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 1800 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 5300
0687INT3 | RESTROOM REMODEL | 0687 | The two large restrooms in the dormitory have not been remodeled for at least 20 years and are in overall poor condition. The finishes, fixtures, cabinets, toilets, showers, and exhaust fans are showing signs of wear and deterioration. This project would provide for a complete remodel of the restrooms. The removal and disposal of the existing fixtures and finishes is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #013 DORM (DMV & PS) | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 14572 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 84000
0686HVA1 | EXHAUST FAN INSTALLATION | 0686 | There are two rooms in the building with laundry facilities. These rooms are not equipped with any type of exhaust system to ventilate the rooms. When the laundry machines are running, heat and moisture build up in the rooms and the occupants prop open the fire rated doors. This compromises the fire safety design for the building. This project would provide for the purchase and installation of exhaust fan assemblies in each room including connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #012 DORMITORY (P.O.S.T.) | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 14572 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
0687ENR1 | WINDOW REPLACEMENT | 0687 | The windows are original, single pane construction in a wooden frame. These older windows are drafty, not energy efficient and the wooden frames have deteriorated significantly. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 70 units including wooden frames and additional costs are included due to the historical nature of the building. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #013 DORM (DMV & PS) | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 14572 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 116900
0687INT1 | INTERIOR FINISHES | 0687 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4- 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | #013 DORM (DMV & PS) | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 14572 | 2020-02-07 | Four to Ten Years | Long-Term Needs | 3 | 72900
0687SFT4 | SEISMIC RETROFIT WALLS | 0687 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current code. Visual analysis during the survey found no indication of seismic strengthening of the URM walls. The walls should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #013 DORM (DMV & PS) | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 14572 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 1093000
0687SIT1 | CONCRETE PATIO REPLACEMENT | 0687 | The exterior concrete patio has extensive cracking and spalling and is due for replacement. This project would provide for the installation of a new 4" thick concrete slab-on-grade patio at the center courtyard. Removal and disposal of the existing concrete is included in this estimate. | #013 DORM (DMV & PS) | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 14572 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0687ELE1 | EXTERIOR LIGHTING REPLACEMENT | 0687 | The building has perimeter lighting on the exterior of the building, but the light fixtures are old, failing and not energy efficient. This project would provide for the replacement of the exterior lighting fixtures with new LED light fixtures, using existing wiring. | #013 DORM (DMV & PS) | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 14572 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0687EXT3 | EXTERIOR FINISHES | 0687 | The exterior finishes are in fair condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting the wood finishes, re-pointing the stone where needed, and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | #013 DORM (DMV & PS) | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 14572 | 2020-02-07 | Four to Ten Years | Long-Term Needs | 3 | 72900
0687SFT1 | FIRE ALARM SYSTEM UPGRADE | 0687 | This building is equipped with an automatic fire detection and alarm system that no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 "If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure". When completed, the new system will provide visual, as well as audible notification, in accordance with the 2018 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #013 DORM (DMV & PS) | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 14572 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 58300
0727INT2 | FLOORING REPLACEMENT | 0727 | The carpet in the building is showing signs of extreme wear and should be scheduled for replacement. It is recommended that the carpet be replaced with 12x12 VCT flooring with a 6" base in the next 2-3 years. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #044 CAPITOL POLICE SUBSTATION | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 650 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6500
0687SFT3 | EGRESS LIGHTING UPGRADE | 0687 | There are older emergency egress lighting units in this building. These units have a finite lifespan, and this project recommends their replacement with new egress lights, and providing additional lights on the main exit routes and in individual rooms as needed. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #013 DORM (DMV & PS) | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 14572 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 3000
0454EXT1 | EXTERIOR FINISHES | 0454 | The exterior paint is in fair condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting the wood finishes, re-pointing the stone where needed, and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | #032 NON-PROFIT OFFICE | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 1800 | 2020-02-07 | Four to Ten Years | Long-Term Needs | 3 | 10700
0687ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0687 | This building contains 3 water fountains that are not ADA compliant. The 2018 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of three drinking fountains to meet the ADA requirements. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #013 DORM (DMV & PS) | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 14572 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 8000
0687INT4 | JANITORS CLOSET REPAIRS | 0687 | The mop sinks in the Janitors Closets are mounted adjacent to gypsum board and are showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. This is recommended for two Janitors Closets. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #013 DORM (DMV & PS) | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 14572 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3500
0687HVA1 | EXHAUST FAN INSTALLATION | 0687 | There are two rooms in the building with laundry facilities. These rooms are not equipped with any type of exhaust system to ventilate the rooms. When the laundry machines are running, heat and moisture build up in the rooms and the occupants prop open the fire rated doors. This compromises the fire safety design for the building. This project would provide for the purchase and installation of exhaust fan assemblies in each room including connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #013 DORM (DMV & PS) | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 14572 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
0687ADA3 | ADA SIGNAGE | 0687 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2018 IBC, ICC/ANSI A117.1, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #013 DORM (DMV & PS) | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 14572 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 1500
0729SFT0 | SEISMIC RETROFIT WALLS | 0729 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current code. Visual analysis during the survey found no indication of seismic strengthening of the URM walls. The walls should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #047 GARAGE (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1930 | 2183 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 163700
0729EXT2 | CONSERVE AND PROTECT VACANT BUILDINGS | 0729 | In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to removing water in the basement, providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. | #047 GARAGE (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1930 | 2183 | 2020-02-07 | Four to Ten Years | Long-Term Needs | 3 | 43700
0728SFT0 | SEISMIC RETROFIT WALLS | 0728 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current code. Visual analysis during the survey found no indication of seismic strengthening of the URM walls. The walls should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #046 STORAGE | 9971 | Admin | PubWorks | B&G | Stewart | 1938 | 2590 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 233000
0728EXT2 | CONSERVE AND PROTECT VACANT BUILDING | 0728 | In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to removing water in the basement or crawlspace, providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. | #046 STORAGE | 9971 | Admin | PubWorks | B&G | Stewart | 1938 | 2590 | 2020-02-07 | Four to Ten Years | Long-Term Needs | 3 | 51800
0728SFT1 | FIRE EXTINGUISHER INSTALLATION | 0728 | The building does not have a portable fire extinguisher available. The building is currently used for storage and staff enters and exits the building. International Fire Code Section 906 requires that portable fire extinguishers shall be installed in S occupancies. They shall be provided for employee use and selected and distributed based on the classes of anticipated workplace fires and on the size and degree of hazard which would affect their use. This project would provide funding for the purchase and installation of 2 fire extinguishers, cabinets, and the hardware necessary to install them. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #046 STORAGE | 9971 | Admin | PubWorks | B&G | Stewart | 1938 | 2590 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 1000
0687ADA1 | ADA RESTROOM UPGRADE | 0687 | The designated unisex ADA accessible restrooms are not fully compliant. There is no pipe protection, the toilet paper dispenser is not in the correct location, one of the flush handles is on the wrong side and the grab bars are not compliant. A partial retrofit is necessary. This project would provide funding to bring the restrooms into full ADA compliance. The 2018 IBC, ICC/ANSI A117.1, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #013 DORM (DMV & PS) | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 14572 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 4000
0747EXT3 | EXTERIOR FINISHES | 0747 | The exterior finishes are in good condition. It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | #119 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1203 | 2020-02-07 | Four to Ten Years | Long-Term Needs | 3 | 6000
0454SFT4 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0454 | The building is a B occupancy per the 2018 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 or R-2 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #032 NON-PROFIT OFFICE | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 1800 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 30000
0747INT2 | FLOORING REPLACEMENT | 0747 | The VCT (vinyl composite tile) and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT flooring with a 6" base and heavy duty commercial grade carpet in the next 2-3 years. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #119 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1203 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11500
0453SFT2 | SEISMIC RETROFIT ROOF STRUCTURE | 0453 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current codes. Visual analysis during the survey found no indication of seismic strengthening of the roof structure. The roof structure should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #031 WASHOE TRIBE (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 2388 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 112200
0747ENR1 | LIGHTING UPGRADE | 0747 | The existing lighting fixtures are the older incandescent type. Some are broken and they are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. CFL (compact fluorescent lamps) are suggested. Occupancy sensors will be installed in restrooms, closets, and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #119 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1203 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
0747PLM1 | WATER HEATER REPLACEMENT | 0747 | There is a 40 gallon gas-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #119 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1203 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1800
0747EXT4 | EXTERIOR DOOR REPLACEMENT | 0747 | The exterior wood man door in the rear appears to be original to the building. It is damaged from age and general wear and tear. This project would provide for the replacement of the wood door with a new wood door, frame and hardware. Removal and disposal of the existing door and painting of the new door is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #119 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1203 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 600
0747SFT1 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0747 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #119 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1203 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 5000
0724EXT2 | CONSERVE AND PROTECT VACANT BUILDING | 0724 | In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to removing water in the basement or crawlspace, providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. | #035 WASHOE TRIBE (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 1500 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 30000
0747INT4 | INTERIOR DOOR REPLACEMENT | 0747 | The interior doors in this building are hollow core units and most are damaged. This project would provide for the installation of new solid core interior doors including frames, lever action door handles, hardware, and paint. Removal and disposal of the existing doors is included in this cost estimate. A total of 8 interior doors was used in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #119 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1203 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4800
0724SFT2 | SEISMIC RETROFIT ROOF STRUCTURE | 0724 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current codes. Visual analysis during the survey found no indication of seismic strengthening of the roof structure. The roof structure should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #035 WASHOE TRIBE (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 1500 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 70500
0725SFT3 | SEISMIC RETROFIT ROOF STRUCTURE | 0725 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current codes. Visual analysis during the survey found no indication of seismic strengthening of the roof structure. The roof structure should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #036 WASHOE TRIBE (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1942 | 1500 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 70500
0747INT5 | KITCHEN REMODEL | 0747 | The kitchen and associated cabinets are original to the building. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and countertops are delaminating and failing. This project recommends the replacement of the existing kitchen countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #119 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1203 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11900
0724SFT1 | SEISMIC RETROFIT WALLS | 0724 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current code. Visual analysis during the survey found no indication of seismic strengthening of the URM walls. The walls should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #035 WASHOE TRIBE (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 1500 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 112500
0724ENV1 | ASBESTOS ABATEMENT, TSI | 0724 | An inspection was performed on this building in 1989 for asbestos containing materials (ACM). Piping insulation was found which is believed to contain asbestos, and this report recommends abatement of this material. | #035 WASHOE TRIBE (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 1500 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 33000
0747SFT2 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0747 | This building does not have an automatic fire suppression system. It should be retrofitted with fire sprinklers during the next remodel or change of occupancy according to 2018 IEBC 101.4 Applicability provision, 2018 IFC and NAC 477.917. This project would provide funding for the installation of fire sprinklers including backflow prevention devices. | #119 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1203 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 21100
2312INT1 | INTERIOR FINISHES | 2312 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 8 to 9 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | BUILDINGS & GROUNDS GARAGE | 9956 | Admin | PubWorks | B&G | Carson City | 1990 | 2400 | 2020-05-15 | Four to Ten Years | Long-Term Needs | 3 | 7200
2312HVA1 | HVAC UPGRADE | 2312 | The small office area has only an electric baseboard heater which is in poor condition and no cooling system. It is recommended to install upgraded heating equipment and an evaporative cooler in this occupied area to ensure a comfortable work environment. This project would provide for the purchase and installation of a natural gas fired heater and a wall mounted evaporative cooler including all required connections to existing utilities. This project or a portion thereof was previously recommended in the FCA report dated 11/25/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/15/2020. | BUILDINGS & GROUNDS GARAGE | 9956 | Admin | PubWorks | B&G | Carson City | 1990 | 2400 | 2020-05-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
2315EXT5 | CMU BLOCK REPAIR | 2315 | There is a hole in the CMU block wall on the exterior of the east wall. It appears that a crack is progressing vertically from this hole and could possibly be a structural concern. An analysis of this issue and subsequent repairs; if needed, is recommended. This project recommends a structural review and CMU block repair or replacement. | B & G OFFICE GARAGE ADDITION | 9956 | Admin | PubWorks | B&G | Carson City | 1960 | 2200 | 2020-05-15 | Immediate to Two Years | Currently Critical | 1 | 15000
2315ENV1 | DUST COLLECTION SYSTEM, WOOD SHOP | 2315 | The building has a woodshop which does not have a complete dust collection system. In order to reduce the possibility of damage or injury, each piece of equipment should have complete collection capability. This project recommends installing a new dust collection system. This project or a portion thereof was previously recommended in the FCA report dated 11/25/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/15/2020. | B & G OFFICE GARAGE ADDITION | 9956 | Admin | PubWorks | B&G | Carson City | 1960 | 2200 | 2020-05-15 | Immediate to Two Years | Currently Critical | 1 | 18000
2315EXT1 | EXTERIOR FINISHES | 2315 | The exterior painted surfaces and caulking joints are in poor condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining or other applied finishes, and caulking around windows, flashing, fixtures and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 2 to 3 years and is recommended on a cyclical basis to maintain the integrity of the structure. | B & G OFFICE GARAGE ADDITION | 9956 | Admin | PubWorks | B&G | Carson City | 1960 | 2200 | 2020-05-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 22000
2315INT1 | INTERIOR FINISHES | 2315 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4 to 5 years and every 4 to 5 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | B & G OFFICE GARAGE ADDITION | 9956 | Admin | PubWorks | B&G | Carson City | 1960 | 2200 | 2020-05-15 | Four to Ten Years | Long-Term Needs | 3 | 6600
2315EXT3 | ROOF REPLACEMENT | 2315 | The single-ply roof on this building was reported in fair condition at the time of the survey. This existing single-ply roofing system was installed in 1998. The statewide roofing program estimates the useful life of an average roof at 15 years. The roof warranty expires at the end of the same time frame. This building should be re-roofed in the next five to six years, consistent with the roofing program guidelines and the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 11/25/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/15/2020. | B & G OFFICE GARAGE ADDITION | 9956 | Admin | PubWorks | B&G | Carson City | 1960 | 2200 | 2020-05-15 | Four to Ten Years | Long-Term Needs | 3 | 41400
2312EXT2 | ROOF REPLACEMENT | 2312 | The asphalt composition shingle roof on this building was in poor condition with multiple roof leaks discussed at the time of the survey. It is recommended that this building be re-roofed in the next couple of years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing system. This project or a portion thereof was previously recommended in the FCA report dated 11/25/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/15/2020. | BUILDINGS & GROUNDS GARAGE | 9956 | Admin | PubWorks | B&G | Carson City | 1990 | 2400 | 2020-05-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 45200
2312EXT1 | EXTERIOR FINISHES | 2312 | The painted wood surfaces on the exterior are in poor condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining or other applied finishes, and caulking around windows, flashing, fixtures and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 2 -3 years and is recommended on a cyclical basis to maintain the integrity of the structure. | BUILDINGS & GROUNDS GARAGE | 9956 | Admin | PubWorks | B&G | Carson City | 1990 | 2400 | 2020-05-15 | Immediate to Two Years | Currently Critical | 1 | 12000
2312ADA1 | ADA RESTROOM UPGRADE | 2312 | The unisex restroom does not meet the Americans with Disabilities Act (ADA) regulations. A retrofit is necessary to comply with 2018 IBC Chapter 11, ICC/ANSI A117.1 and the Americans with Disabilities Act Accessibility Guidelines (ADAAG). Given the current configuration of the restroom, the work will include the installation of a new toilet, sink, grab bars, faucets, mirrors, dispensers and hardware. Some minor design work will be required and may impact the final cost estimate. This estimate is for one ADA unisex restroom facility. The removal and disposal of the old restroom fixtures is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 11/25/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/15/2020. | BUILDINGS & GROUNDS GARAGE | 9956 | Admin | PubWorks | B&G | Carson City | 1990 | 2400 | 2020-05-15 | Immediate to Two Years | Currently Critical | 1 | 18000
2315EXT2 | WINDOW REPLACEMENT | 2315 | The windows are original, single pane construction in wood frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 2 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 11/25/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/15/2020. | B & G OFFICE GARAGE ADDITION | 9956 | Admin | PubWorks | B&G | Carson City | 1960 | 2200 | 2020-05-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
9956ADA2 | SIDEWALK / CURB REPLACEMENT - PARKING LOT | 9956 | The concrete sidewalks and curbs surrounding the parking lot are in poor condition. There are damaged curbs, spalling concrete, and non-conforming ADA curb cuts at street crossings. This project would provide for the removal and replacement of the concrete sidewalks and curbing around the parking lot. Four ADA compliant curb cuts, 3,000 square feet of concrete sidewalk, and 275 lineal feet of concrete curbing was used to generate this estimate. The sidewalk along Stewart Street was not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 11/25/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/15/2020. | BUILDINGS AND GROUNDS OFFICE SITE | 9956 | Admin | PubWorks | B&G | Carson City | 0 |  | 2020-05-15 | Immediate to Two Years | Currently Critical | 1 | 48300
9956SIT4 | LOADING DOCK / APRON REPLACEMENT - PAINT SHOP | 9956 | The concrete loading dock and concrete aprons at the overhead doors are in poor condition and failing. This project would provide for the installation of a new concrete loading dock and aprons. Removal and disposal of the existing concrete is included in this estimate. A total of 1,050 square feet was used to generate this estimate. This project or a portion thereof was previously recommended in the FCA report dated 11/25/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/15/2020. | BUILDINGS AND GROUNDS OFFICE SITE | 9956 | Admin | PubWorks | B&G | Carson City | 0 |  | 2020-05-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18900
9956ENV1 | INSTALL DOMESTIC WATER BACKFLOW PREVENTION | 9956 | There is a two inch domestic water line located in the southwest corner of the parking lot which feeds the B & G office buildings. It does not have any backflow prevention. This project would provide for a two inch double check backflow assembly device to be installed at this location. A below grade installation including a vault with a traffic rated lid is also included in this project. The existing shut-off or isolation valve would remain and a new isolation valve should be installed just outside of the building where the water service is located. This is also included in the estimate. This project or a portion thereof was previously recommended in the FCA report dated 11/25/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/15/2020. | BUILDINGS AND GROUNDS OFFICE SITE | 9956 | Admin | PubWorks | B&G | Carson City | 0 |  | 2020-05-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15600
9956ADA1 | ADA ACCESSIBLE PARKING INSTALLATION - PARKING LOT | 9956 | The ADA accessible parking stalls in the south parking lot do not meet slope requirements due to root damaged asphalt. This project would provide for the removal of the existing asphalt and installation of 5 new ADA compliant parking and loading zones. One shall be a van accessible space. Signage is included in this estimate. 900 square feet of paving was used to generate this estimate. This project or a portion thereof was previously recommended in the FCA report dated 11/25/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/15/2020. | BUILDINGS AND GROUNDS OFFICE SITE | 9956 | Admin | PubWorks | B&G | Carson City | 0 |  | 2020-05-15 | Immediate to Two Years | Currently Critical | 1 | 18000
9956SIT1 | REPLACE ASPHALT PAVING - B & G BUILDINGS | 9956 | The asphalt around the side and rear of the B&G buildings is failing with significant alligatoring and cracks observed. The paving has deteriorated to the point that it is no longer viable. This project covers the removal and replacement of all existing asphalt paving around and between the B & G buildings. This project should be done concurrently with the sidewalk replacement project. This project or a portion thereof was previously recommended in the FCA report dated 11/25/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/15/2020. | BUILDINGS AND GROUNDS OFFICE SITE | 9956 | Admin | PubWorks | B&G | Carson City | 0 |  | 2020-05-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 54000
9956SEC1 | INSTALL EXTERIOR SITE LIGHTING IN PARKING LOT | 9956 | This project would provide for the installation of general security lighting fixtures around the parking lot. Cost includes light fixtures, wiring, trenching and installation based on a 20 foot pole. This project should be done prior to any pavement projects. This project or a portion thereof was previously recommended in the FCA report dated 11/25/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/15/2020. | BUILDINGS AND GROUNDS OFFICE SITE | 9956 | Admin | PubWorks | B&G | Carson City | 0 |  | 2020-05-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 79200
9956SIT2 | CRACK FILL AND SEAL ASPHALT PAVING - PARKING LOT | 9956 | The parking lot south of the B & G buildings is in fair condition. There are numerous cracks that are in need of filling. This project would provide for crack fill and sealing of the parking lot including striping. This project should be done concurrently with the ADA parking and sidewalk replacement projects. It is recommended that this project be done on a cyclical basis every three to five years to maintain the integrity of the pavement. This project or a portion thereof was previously recommended in the FCA report dated 11/25/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/15/2020. | BUILDINGS AND GROUNDS OFFICE SITE | 9956 | Admin | PubWorks | B&G | Carson City | 0 |  | 2020-05-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 37500
0239SFT5 | EXIT SIGN AND EGRESS LIGHTING INSTALLATION | 0239 | The emergency egress lighting in the north shop area is insufficient and the exit sign does not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC 2018 Chapter 10 was referenced for this project. | B & G PAINT SHOP | 9956 | Admin | PubWorks | B&G | Carson City | 1948 | 5000 | 2020-05-15 | Immediate to Two Years | Currently Critical | 1 | 500
0239HVA1 | INSTALL EVAPORATIVE COOLERS | 0239 | The building has no central cooling system and is uncomfortably warm in the summer. It is recommended to install three evaporative coolers in the building to ensure a comfortable work environment in the shop areas. This project would provide for the purchase and installation of three evaporative coolers including all required connections to existing utilities. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2003, 11/25/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/15/2020. | B & G PAINT SHOP | 9956 | Admin | PubWorks | B&G | Carson City | 1948 | 5000 | 2020-05-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0239EXT1 | EXTERIOR FINISHES | 0239 | The exterior finishes are in poor condition. The paint finish has failed in multiple locations. It is important to maintain the finish, weather resistance, and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining or other applied finishes, and caulking around windows, flashing, fixtures and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 2 - 3 years and is recommended on a cyclical basis to maintain the integrity of the structure. | B & G PAINT SHOP | 9956 | Admin | PubWorks | B&G | Carson City | 1948 | 5000 | 2020-05-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
0239SFT4 | GUARDRAIL INSTALLATION | 0239 | The mezzanine guardrail in the shop area is not contiguous. This project would provide for a wood framed guardrail to be installed. Material and construction should match the existing guardrail. | B & G PAINT SHOP | 9956 | Admin | PubWorks | B&G | Carson City | 1948 | 5000 | 2020-05-15 | Immediate to Two Years | Currently Critical | 1 | 2000
0239EXT5 | OVERHEAD DOOR REPLACEMENT | 0239 | There are 3 overhead rollup doors which are damaged and do not function properly. They should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead doors and replacement with motorized doors. | B & G PAINT SHOP | 9956 | Admin | PubWorks | B&G | Carson City | 1948 | 5000 | 2020-05-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 29800
0239ELE2 | EXTERIOR LIGHTING REPLACEMENT | 0239 | The building has perimeter HPS lighting on the exterior of the building which is old, failing, and not energy efficient. This project would provide for the replacement of the exterior lighting fixtures with new LED light fixtures using existing wiring. | B & G PAINT SHOP | 9956 | Admin | PubWorks | B&G | Carson City | 1948 | 5000 | 2020-05-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
0239HVA2 | INSTALL HVAC SYSTEM | 0239 | The offices and restroom do not currently have any HVAC systems as required by the Mechanical Code and 2018 IBC. This project would provide for a new gas fired furnace with A/C coil, an air cooled condensing unit, and all required ductwork and utility connections for a complete system in these areas. This project or a portion thereof was previously recommended in the FCA report dated 11/25/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/15/2020. | B & G PAINT SHOP | 9956 | Admin | PubWorks | B&G | Carson City | 1948 | 5000 | 2020-05-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0239ELE1 | PROVIDE CLEARANCE AT ELECTRICAL PANELS | 0239 | There are electrical panels in the building which do not have proper clear floor space around them. The 2017 NEC Article 110-26 stipulates working clearances around electrical equipment. Working space should be at least 30" wide, 36"-42" depth and 72" high. This project would provide funds to relocate the tables, microwaves, and other items currently blocking the working space. This project or a portion thereof was previously recommended in the FCA report dated 11/25/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/15/2020. | B & G PAINT SHOP | 9956 | Admin | PubWorks | B&G | Carson City | 1948 | 5000 | 2020-05-15 | Immediate to Two Years | Currently Critical | 1 | 500
0239EXT3 | EXTERIOR DOOR REPLACEMENT | 0239 | The three existing exterior metal doors and frames are damaged from age, general wear and tear, and have reached the end of their expected life. This project would provide for the replacement of the south double door assembly and the north single door assembly with new metal doors, frames, and ADA accessible hardware and thresholds. Removal and disposal of the existing doors is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 11/25/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/15/2020. | B & G PAINT SHOP | 9956 | Admin | PubWorks | B&G | Carson City | 1948 | 5000 | 2020-05-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5400
0239EXT4 | ROOF DRAIN DOWNSPOUT MODIFICATIONS | 0239 | The building currently does not have rain gutters and has one abandoned downspout. This is causing rainwater to run down the building and pool next to the foundation causing damage to the foundation and stucco walls. This project would provide for the installation of rain gutters, full length downspouts to grade, and extensions away from the perimeter of the building to prevent pooling and damage to the building. | B & G PAINT SHOP | 9956 | Admin | PubWorks | B&G | Carson City | 1948 | 5000 | 2020-05-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
0239SFT3 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0239 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. | B & G PAINT SHOP | 9956 | Admin | PubWorks | B&G | Carson City | 1948 | 5000 | 2020-05-15 | Immediate to Two Years | Currently Critical | 1 | 5000
0239EXT2 | ROOF REPLACEMENT | 0239 | The existing roof consists of corrugated transite and single-ply with the corrugated roofing covering about three-fourths of the building. The roofing material has reached the end of its expected life. It is recommended that this building be re-roofed in the next 2 to 3 years with a standing seam metal roofing system in place of the corrugated transite as well as a new single-ply membrane roofing system on the low slope roof area. This estimate includes removal and disposal of the old roofing system, an increased square footage cost for asbestos abatement, gutters, and downspouts. This project should be implemented concurrently with the SEISMIC RETROFIT WALLS & ROOF STRUCTURE project. This project or a portion thereof was previously recommended in the FCA report dated 11/25/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/15/2020. | B & G PAINT SHOP | 9956 | Admin | PubWorks | B&G | Carson City | 1948 | 5000 | 2020-05-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 119000
0239INT1 | INTERIOR FINISHES | 0239 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4 - 5 years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | B & G PAINT SHOP | 9956 | Admin | PubWorks | B&G | Carson City | 1948 | 5000 | 2020-05-15 | Four to Ten Years | Long-Term Needs | 3 | 25000
0239SFT6 | SEISMIC RETROFIT WALLS & ROOF STRUCTURE | 0239 | This building appears to be an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current code. Visual analysis during the survey found no indication of seismic strengthening of the URM walls or roof structure. The walls and roof should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | B & G PAINT SHOP | 9956 | Admin | PubWorks | B&G | Carson City | 1948 | 5000 | 2020-05-15 | Four to Ten Years | Long-Term Needs | 3 | 610000
0239ADA1 | ADA RESTROOM UPGRADE | 0239 | The unisex restroom does not meet the Americans with Disabilities Act (ADA) regulations. A retrofit is necessary to comply with 2018 IBC Chapter 11, ICC/ANSI A117.1Sections 603 - 604 and the Americans with Disabilities Act Accessibility Guidelines (ADAAG). Given the current configuration of the restrooms, the work will include the installation of a new toilet, sink, grab bars, faucets, mirrors, dispensers and hardware. Some minor design work will be required and may impact the final cost estimate. This estimate is for one ADA unisex restroom facility. The removal and disposal of the old restroom fixtures is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 11/25/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/15/2020. | B & G PAINT SHOP | 9956 | Admin | PubWorks | B&G | Carson City | 1948 | 5000 | 2020-05-15 | Immediate to Two Years | Currently Critical | 1 | 18000
0391ADA3 | ADA SIGNAGE | 0391 | Americans with Disabilities Act (ADA) regulations pertaining to building access, route of travel, and restrooms has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances, route of travel inside the building, and restrooms. Americans with Disabilities Act Accessibility Guidelines (ADAAG) was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 11/25/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/15/2020. | BUILDINGS & GROUNDS OFFICE | 9956 | Admin | PubWorks | B&G | Carson City | 1900 | 7800 | 2020-05-15 | Immediate to Two Years | Currently Critical | 1 | 1200
0391EXT3 | EXTERIOR FINISHES | 0391 | Painted wood trim and architectural details are cracking and painted surfaces are in poor condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including sealing the stone, painting, staining or other applied finishes, and caulking around windows, flashing, fixtures and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 2 - 3 years and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BUILDINGS & GROUNDS OFFICE | 9956 | Admin | PubWorks | B&G | Carson City | 1900 | 7800 | 2020-05-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 39000
0391SFT3 | SEISMIC RETROFIT WALLS | 0391 | This building is an unreinforced sandstone masonry structure which requires seismic strengthening to meet current building and life safety codes. An initial study was done under CIP 07-M46 which provided detailed recommendations for a seismic retrofit. The planning and design were requested under CIP 09-P05 and the construction cost was requested for the 2011 CIP. The estimate is for the construction costs only. This project should coincide with a complete remodel of the interior of the building. This project or a portion thereof was previously recommended in the FCA report dated 11/25/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/15/2020. | BUILDINGS & GROUNDS OFFICE | 9956 | Admin | PubWorks | B&G | Carson City | 1900 | 7800 | 2020-05-15 | Immediate to Two Years | Currently Critical | 1 | 585000
0391SFT8 | STORAGE AREA GUARDRAIL / HANDRAIL INSTALLATION | 0391 | The upper level storage area contains numerous levels with a mix of stairs and handrails / guardrails that do not meet the intent of the building code. This project would provide for new stairs, handrails and guardrails to be installed. The 2018 IBC Chapter 10 was used for reference. Removal and disposal of the existing stairs and guardrails is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 11/25/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/15/2020. | BUILDINGS & GROUNDS OFFICE | 9956 | Admin | PubWorks | B&G | Carson City | 1900 | 7800 | 2020-05-15 | Immediate to Two Years | Currently Critical | 1 | 10000
0391ADA2 | ADA ACCESSIBLE COUNTER | 0391 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. This building contains a counter which does not meet current codes. Section 7.2 of the Americans with Disabilities Act Accessible Guidelines (ADAAG) states that the counter must have a portion which is at least 36" in length with a maximum height of 36" above the finish floor. This project will provide an accessible counter space in accordance with this requirement. IBC - 2018, ICC/ANSI A117.1 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) were referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 11/25/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/15/2020. | BUILDINGS & GROUNDS OFFICE | 9956 | Admin | PubWorks | B&G | Carson City | 1900 | 7800 | 2020-05-15 | Immediate to Two Years | Currently Critical | 1 | 3600
0391ADA1 | ACCESSIBLE WATER FOUNTAIN | 0391 | This building contains a water fountain. The 2018 IBC Section 1109.5 states where a water fountain is provided, at least half should be accessible. This project would provide funding for the purchase and replacement of a new accessible fixed high / low ADA accessible drinking fountain. This project or a portion thereof was previously recommended in the FCA report dated 11/25/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/15/2020. | BUILDINGS & GROUNDS OFFICE | 9956 | Admin | PubWorks | B&G | Carson City | 1900 | 7800 | 2020-05-15 | Immediate to Two Years | Currently Critical | 1 | 4800
0391HVA1 | REPLACE HVAC EQUIPMENT | 0391 | The HVAC system consists of two hot water boilers, a few isolated evaporative coolers, and window mounted air conditioning units. There is no central cooling system; although, the radiant heating from the boilers is sufficient. The boilers were replaced in 2001. This project would provide for installation of a central cooling system including duct work and grills throughout the building. This project includes removal and disposal of the existing cooling units and all required connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 11/25/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/15/2020. | BUILDINGS & GROUNDS OFFICE | 9956 | Admin | PubWorks | B&G | Carson City | 1900 | 7800 | 2020-05-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 172000
0391SFT9 | SEISMIC RETROFIT ROOF STRUCTURE | 0391 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current codes. Visual analysis during the survey found no indication of seismic strengthening of the roof structure. The roof structure should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | BUILDINGS & GROUNDS OFFICE | 9956 | Admin | PubWorks | B&G | Carson City | 1900 | 7800 | 2020-05-15 | Immediate to Two Years | Currently Critical | 1 | 366000
0391ADA4 | REPLACE STAIR HANDRAILS | 0391 | The stair handrails are older and do not meet code for safety or accessibility. The gripping surfaces are incorrect and they are not continuous from the top to bottom landings. This project recommends the installation of handrails on both sides of the stairs with proper returns and supports. Removal and disposal of the existing railing is included. 2018 IBC Chapter 10, Section 1012, ICC/ANSI A117.1 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) were referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 11/25/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/15/2020. | BUILDINGS & GROUNDS OFFICE | 9956 | Admin | PubWorks | B&G | Carson City | 1900 | 7800 | 2020-05-15 | Immediate to Two Years | Currently Critical | 1 | 20000
0391INT1 | INTERIOR FINISHES | 0391 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2 to 3 years and every 4 - 5 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | BUILDINGS & GROUNDS OFFICE | 9956 | Admin | PubWorks | B&G | Carson City | 1900 | 7800 | 2020-05-15 | Four to Ten Years | Long-Term Needs | 3 | 39000
0391EXT4 | WINDOW REPLACEMENT | 0391 | The existing window systems in the building are of original wood frames and single pane glazing. Many of the window openings have been modified to accommodate air conditioning units. These units are not energy efficient. This project would provide for the removal of the existing window units and replacement with new energy efficient glazing that would match the historical nature of the existing windows. This building is on the State Historical Register and approval of this project may be required by the Nevada State Historical Preservation Office. This project or a portion thereof was previously recommended in the FCA report dated 11/25/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/15/2020. | BUILDINGS & GROUNDS OFFICE | 9956 | Admin | PubWorks | B&G | Carson City | 1900 | 7800 | 2020-05-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 150000
2303INT1 | INTERIOR FINISHES | 2303 | The interior finishes were not examined and access not provided. The building is not occupied and is used for storage. It is recommended that the interior walls be painted at least once in the next 8 - 9 years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | MODULAR STORAGE #2-EAST | 9916 | Admin | PubWorks | B&G | Carson City | 1960 | 1152 | 2020-10-07 | Four to Ten Years | Long-Term Needs | 3 | 5800
2304EXT3 | INSTALL EXTERIOR DOOR LANDING | 2304 | The exterior door on the north side of the building does not have a landing as required by the 2018 IBC Chapter 10. The step from finish floor to grade is about 12". This project would provide for the installation of a concrete landing at the exterior door. This project or a portion thereof was previously recommended in the FCA report dated 03/31/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/07/2020. | STORAGE #3 | 9916 | Admin | PubWorks | B&G | Carson City | 1960 | 600 | 2020-10-07 | Immediate to Two Years | Currently Critical | 1 | 750
2304EXT2 | SIDING AND ROOF REPAIRS | 2304 | There is damage to the metal siding and the metal roof which is compromising the weather resistance of the building. The siding has been punctured and is exposing the framing of the building. It is recommended to repair the damage immediately in order to protect the framing and the interior of the building. This project or a portion thereof was previously recommended in the FCA report dated 03/31/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/07/2020. | STORAGE #3 | 9916 | Admin | PubWorks | B&G | Carson City | 1960 | 600 | 2020-10-07 | Immediate to Two Years | Currently Critical | 1 | 10000
2303SFT2 | FIRE ALARM SYSTEM UPGRADE | 2303 | This building is equipped with an automatic fire detection and alarm system that is no longer operable. According to 2018 IFC 907.8.5 Inspection, testing and maintenance, the building owner shall be responsible to maintain the fire and life safety systems in an operable condition at all times. It is recommended the fire alarm AHJ (Authority Having Jurisdiction) be notified and make a determination on the disposition of the existing system, whether to demolish / decommission or upgrade and make operational. This estimate includes the cost of replacing the existing system with a new system that will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1 Section 7 and the 2018 International Fire Code. | MODULAR STORAGE #2-EAST | 9916 | Admin | PubWorks | B&G | Carson City | 1960 | 1152 | 2020-10-07 | Immediate to Two Years | Currently Critical | 1 | 5800
2303EXT1 | EXTERIOR FINISHES | 2303 | The exterior finishes are in good condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding, priming, painting, and caulking of the windows, flashing, fixtures and all other penetrations. This project also includes an allowance for the replacement of damaged fascia and trim. It is recommended that the building be painted in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MODULAR STORAGE #2-EAST | 9916 | Admin | PubWorks | B&G | Carson City | 1960 | 1152 | 2020-10-07 | Four to Ten Years | Long-Term Needs | 3 | 8000
2303EXT4 | REPLACE EXTERIOR STAIRS, DECK AND DOOR | 2303 | The existing deck and stairs on the north side of the building are in poor condition and do not meet current building code requirements. This project would provide for the removal of the existing stairs and deck and replacement with a new wood framed deck and stair system including handrails and guardrails, landing and route of travel to the paved parking area. Also included is the replacement of the exterior door, frame, and hardware. This project or a portion thereof was previously recommended in the FCA report dated 03/31/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/07/2020. | MODULAR STORAGE #2-EAST | 9916 | Admin | PubWorks | B&G | Carson City | 1960 | 1152 | 2020-10-07 | Immediate to Two Years | Currently Critical | 1 | 19500
2303ADA1 | REPLACE ACCESSIBLE ENTRANCE RAMP / ENTRY DECK | 2303 | This facility has a wood ramp and entry deck located on the south side of the building. The ramp and deck are deteriorating and do not have proper landings, guardrails or handrails. This project would provide for an upgrade to the ramp to make it fully ADA compliant including new decking, handrails, guardrails, signage, and landings. The 2018 IBC Chapter 10 and 11, ICC/ANSI A117.1 and the most current version of the Americans With Disabilities Act Accessible Guidelines (ADAAG) was used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 03/31/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/07/2020. | MODULAR STORAGE #2-EAST | 9916 | Admin | PubWorks | B&G | Carson City | 1960 | 1152 | 2020-10-07 | Immediate to Two Years | Currently Critical | 1 | 22000
2304EXT1 | EXTERIOR FINISHES | 2304 | The exterior painted wood finished portions are in poor condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is the sealing and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2 - 3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | STORAGE #3 | 9916 | Admin | PubWorks | B&G | Carson City | 1960 | 600 | 2020-10-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1800
9862SIT1 | PATCH, CRACK & SLURRY SEAL ASPHALT PAVING | 9862 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor replacement of deteriorated paving, minor crack filling, and slurry sealing of the paving site wide. Striping is included in this estimate. Slurry seal should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 22,789 square feet of asphalt area was used to generate this estimate. This project should be implemented concurrently with the DRAINAGE IMPROVEMENTS project. This project or a portion thereof was previously recommended in the FCA report dated 01/24/2012. It has been amended accordingly to reflect conditions observed during the most recent survey date of10/07/2020. | CARSON CITY MOTOR POOL SITE | 9862 | Admin | PubWorks | B&G | Carson City | 0 |  | 2020-10-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 31900
9862SIT2 | DRAINAGE IMPROVEMENTS | 9862 | There are several drainage problems around the site. On the perimeter of the site, the runoff is directed across the public sidewalk creating a slip and fall hazard especially when it freezes. Several areas have standing water which causes premature deterioration of the paving. This project would create positive flow away from the building and to the storm drain system by regrading and adding additional storm drain connections. This project should be implemented concurrently with the PATCH, CRACK & SLURRY SEAL ASPHALT PAVING project. This project or a portion thereof was previously recommended in the FCA report dated 01/24/2012. It has been amended accordingly to reflect conditions observed during the most recent survey date of10/07/2020. | CARSON CITY MOTOR POOL SITE | 9862 | Admin | PubWorks | B&G | Carson City | 0 |  | 2020-10-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
9916SIT3 | SEAL ASPHALT PAVING | 9916 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the paving site wide including access roads, parking areas, and the maintenance yard. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 50,000 square feet of asphalt area was used to generate this estimate. | EDUCATION/ STATE MAIL SERVICES SITE | 9916 | Admin | PubWorks | B&G | Carson City | 0 |  | 2020-10-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 62500
9916ENV1 | IRRIGATION RELOCATION AND TURF REMOVAL | 9916 | There is a large area of irrigated turf along the south and east side of the Mail Services Building. There are sprinkler heads adjacent to the brick masonry exterior of the building which are wetting the brick and is causing damage. Water may also infiltrate the walls which could lead to mold growth and other environmental issues with the structure. This project would provide for the removal of the turf to about 5 feet away from the structure and relocate all sprinkler heads to prevent water from spraying the side of the building. This project or a portion thereof was previously recommended in the FCA report dated 03/31/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/07/2020. | EDUCATION/ STATE MAIL SERVICES SITE | 9916 | Admin | PubWorks | B&G | Carson City | 0 |  | 2020-10-07 | Immediate to Two Years | Currently Critical | 1 | 5000
9916SIT6 | UNDERGROUND PLUMBING REPLACEMENT | 9916 | The site's underground domestic water and waste systems are older and in poor condition. Multiple leaks have been repaired under the parking lot. Most of the systems appear to be original to the building and should be scheduled for replacement. This project would provide for replacement all of the water and sewer lines from the street to the building. This estimate includes removal and disposal of the existing systems as required. | EDUCATION/ STATE MAIL SERVICES SITE | 9916 | Admin | PubWorks | B&G | Carson City | 0 |  | 2020-10-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 125000
9916SIT5 | TRAFFIC RATED VAULT LID REPLACEMENT | 9916 | The traffic rated vault lid in the driveway on the northwest corner of the Mail Services building is corroded and appears to be failing and in need of replacement. In addition, it appears that contributing to the vault lid failure is a rain gutter downspout discharging water directly onto the vault lid. This project provides funding to replace the vault lid and relocate the downspout. | EDUCATION/ STATE MAIL SERVICES SITE | 9916 | Admin | PubWorks | B&G | Carson City | 0 |  | 2020-10-07 | Immediate to Two Years | Currently Critical | 1 | 7500
9916SIT4 | PARKING LOT REPLACEMENT | 9916 | The concrete public parking area, sidewalk and curbs on the south side of the Mail Services Building is failing and in need of replacement. This project provides funding to replace the concrete paving, curbs and the adjacent sidewalk. Striping for safety and parking is included in this estimate. | EDUCATION/ STATE MAIL SERVICES SITE | 9916 | Admin | PubWorks | B&G | Carson City | 0 |  | 2020-10-07 | Four to Ten Years | Long-Term Needs | 3 | 31400
9916SFT1 | PARKING LOT REPAIRS | 9916 | A portion of the parking lot pavement was removed north of the Mail Services Building to repair an underground water main leak. The opening in the pavement is a safety concern for vehicles and employees. A temporary gravel patch is recommended as a short term repair until an asphalt paving solution is available. This project would fund the cost of the asphalt repair and the temporary fix. | EDUCATION/ STATE MAIL SERVICES SITE | 9916 | Admin | PubWorks | B&G | Carson City | 0 |  | 2020-10-07 | Immediate to Two Years | Currently Critical | 1 | 5500
9864SIT2 | SEAL ASPHALT PAVING | 9864 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the paving site wide including access roads, parking areas, and the maintenance yard. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 30,000 square feet of asphalt area were used to generate this estimate. | CARSON CITY STATE OFFICES SITE | 9864 | Admin | PubWorks | B&G | Carson City | 1959 |  | 2020-10-07 | Four to Ten Years | Long-Term Needs | 3 | 37500
9862SIT3 | EXTERIOR LIGHTING REPLACEMENT | 9862 | There are five lighting poles on the site. Three have been upgraded with LED fixtures. Two are non-LED fixtures, possibly HPS (high pressure sodium). This project would provide for the replacement of the two fixtures with new LED light fixtures using existing wiring and poles. | CARSON CITY MOTOR POOL SITE | 9862 | Admin | PubWorks | B&G | Carson City | 0 |  | 2020-10-07 | Four to Ten Years | Long-Term Needs | 3 | 2000
0204ADA2 | INSTALL LEVER HARDWARE | 0204 | Section 4.13.9 of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) states that handles, pulls, latches, locks and other operating devices on accessible doors shall have a shape that is easy to grasp with one hand and does not require tight grasping, tight pinching, or twisting of the wrist to operate. It is recommended that compliant hardware be installed on all doors in this building to meet these guidelines. The estimate is based on purchase and installation of hardware for 12 doors. This project or a portion thereof was previously recommended in the FCA report dated 01/24/2012. It has been amended accordingly to reflect conditions observed during the most recent survey date of10/07/2020. | CARSON CITY MOTOR POOL | 9862 | Admin | PubWorks | B&G | Carson City | 1988 | 3987 | 2020-10-07 | Immediate to Two Years | Currently Critical | 1 | 3600
0204ENR4 | REPLACE INSULATION | 0204 | The ceiling in the vehicle bays have insulation bats that have fallen or been removed. Other insulation bats are resting on the head of the fire sprinklers and are a safety issue. This project recommends the missing insulation bats be replaced with R-30 and the installed insulation be repaired, as required, to prevent them from falling or resting on the fire sprinklers. | CARSON CITY MOTOR POOL | 9862 | Admin | PubWorks | B&G | Carson City | 1988 | 3987 | 2020-10-07 | Immediate to Two Years | Currently Critical | 1 | 2500
0204ELE1 | GFCI OUTLET INSTALLATION | 0204 | The existing receptacles in the breakroom and restrooms appear to be standard duplex receptacles and may not be GFCI protected. The 2017 NEC 210.8 requires all locations within 6 feet of a water source, garages, accessory buildings, and outdoors shall have GFCI protection. This project would provide for removing the standard receptacles and installing GFCI receptacles. | CARSON CITY MOTOR POOL | 9862 | Admin | PubWorks | B&G | Carson City | 1988 | 3987 | 2020-10-07 | Immediate to Two Years | Currently Critical | 1 | 100
0204ENR3 | EXTERIOR LIGHTING REPLACEMENT | 0204 | The building has perimeter lighting on the exterior of the building, but the light fixtures are HPS (high pressure sodium) and not energy efficient. This project would provide for the replacement of the exterior lighting fixtures with new LED light fixtures using existing wiring. | CARSON CITY MOTOR POOL | 9862 | Admin | PubWorks | B&G | Carson City | 1988 | 3987 | 2020-10-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0204INT4 | FLOORING REPLACEMENT | 0204 | The carpet, sheet vinyl, and painted concrete floors in the building are worn and are reaching the end of their useful life. It is recommended that the flooring be replaced and the concrete stripped and recoated with a clear sealer. This project would provide for coating the concrete, removal and disposal of the existing vinyl and carpet, and installation of new 12x12 VCT (vinyl composite tile) with a 6" base and heavy duty commercial grade carpet in the next 2-3 years. Additional costs may be necessary to repair the concrete floor in the shop area. This project or a portion thereof was previously recommended in the FCA report dated 01/24/2012. It has been amended accordingly to reflect conditions observed during the most recent survey date of10/07/2020. . | CARSON CITY MOTOR POOL | 9862 | Admin | PubWorks | B&G | Carson City | 1988 | 3987 | 2020-10-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 40000
0204EXT3 | EXTERIOR FINISHES | 0204 | The exterior finishes are in good condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry, painting the stucco, and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. In addition, this project would repair damaged areas of the stucco and slump stone masonry. | CARSON CITY MOTOR POOL | 9862 | Admin | PubWorks | B&G | Carson City | 1988 | 3987 | 2020-10-07 | Four to Ten Years | Long-Term Needs | 3 | 30000
0204INT3 | INTERIOR FINISHES | 0204 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | CARSON CITY MOTOR POOL | 9862 | Admin | PubWorks | B&G | Carson City | 1988 | 3987 | 2020-10-07 | Four to Ten Years | Long-Term Needs | 3 | 28000
0204INT5 | JANITORS CLOSET REPAIRS | 0204 | The mop sink in the Janitors Closet is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. This project or a portion thereof was previously recommended in the FCA report dated 01/24/2012. It has been amended accordingly to reflect conditions observed during the most recent survey date of10/07/2020. | CARSON CITY MOTOR POOL | 9862 | Admin | PubWorks | B&G | Carson City | 1988 | 3987 | 2020-10-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1700
0395EXT1 | EXTERIOR FINISHES | 0395 | The exterior finishes are in good condition with the exception of the EIFS system at the front entry which will be addressed as a separate project. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the brick masonry, painting, staining or other applied finishes, and caulking around windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted, and caulked in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project also includes the repair and / or replacement of missing and damaged brick masonry units. | STATE MAIL SERVICES BUILDING | 9916 | Admin | PubWorks | B&G | Carson City | 1953 | 8137 | 2020-10-07 | Four to Ten Years | Long-Term Needs | 3 | 57000
0395INT4 | MOP SINK REPAIRS | 0395 | The mop sink on the mail sorting floor near the north wall is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide FRP to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | STATE MAIL SERVICES BUILDING | 9916 | Admin | PubWorks | B&G | Carson City | 1953 | 8137 | 2020-10-07 | Immediate to Two Years | Currently Critical | 1 | 500
0395HVA2 | MECHANICAL ROOM UPGRADE | 0395 | The mechanical room is overheating due to lack of ventilation caused by heat generated from the air compressors. This project would provide funding to install an exhaust ventilation fan to remove heat from the room. | STATE MAIL SERVICES BUILDING | 9916 | Admin | PubWorks | B&G | Carson City | 1953 | 8137 | 2020-10-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0395EXT7 | LOADING DOCK REFURBISHMENT | 0395 | The concrete vehicle ramp and curbs at the loading dock are failing and need replacement. Additionally, the columns supporting the dock awning are unprotected from vehicular and pallet truck traffic. This project would provide funding to remove and replace the failing concrete, add metal bollards protecting the awning support columns, and add additional dock bumpers as required. | STATE MAIL SERVICES BUILDING | 9916 | Admin | PubWorks | B&G | Carson City | 1953 | 8137 | 2020-10-07 | Four to Ten Years | Long-Term Needs | 3 | 23000
0395INT1 | INTERIOR FINISHES | 0395 | The interior finishes are in poor condition. It is recommended that the interior walls be painted at least once in the next 2 - 3 years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | STATE MAIL SERVICES BUILDING | 9916 | Admin | PubWorks | B&G | Carson City | 1953 | 8137 | 2020-10-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 81000
0395EXT3 | REPLACE WINDOWS | 0395 | The windows on the north side of the building and clerestory are original, single pane construction. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. Additionally, two exterior doors have been permanently closed and should be completely removed as part of this work scope. This estimate is for the replacement of 109 units and two abandoned doors. Removal and disposal of the existing windows is included in this estimate. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. This project or a portion thereof was previously recommended in the FCA report dated 03/31/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/07/2020. | STATE MAIL SERVICES BUILDING | 9916 | Admin | PubWorks | B&G | Carson City | 1953 | 8137 | 2020-10-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 109000
0395EXT6 | ROOF REPLACEMENT | 0395 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1996. It is recommended that this building be re-roofed in the next 2 - 3 years to be consistent with the roofing program and the end of the warranty period. | STATE MAIL SERVICES BUILDING | 9916 | Admin | PubWorks | B&G | Carson City | 1953 | 8137 | 2020-10-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 104000
0395SFT2 | INSTALL SEISMIC GAS SHUT-OFF VALVE | 0395 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 03/31/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/07/2020. | STATE MAIL SERVICES BUILDING | 9916 | Admin | PubWorks | B&G | Carson City | 1953 | 8137 | 2020-10-07 | Immediate to Two Years | Currently Critical | 1 | 5000
0397ELE2 | ELECTRICAL UPGRADE | 0397 | At the time of the survey, it was noted that the electrical service entrance switchgear has been replaced. However, some distribution boards in the basement appear to be original to the construction of the building. It is recommended that an electrical coordination and arc flash study be performed to ensure electrical safety. Electrical hardware infrastructure upgrades have not been included in this estimate. | CARSON CITY STATE OFFICES BUILDING | 9864 | Admin | PubWorks | B&G | Carson City | 1959 | 42550 | 2020-10-07 | Immediate to Two Years | Currently Critical | 1 | 80000
0395HVA1 | HVAC EQUIPMENT REPLACEMENT | 0395 | There are 6 rooftop packaged HVAC units that are approximately 24 years old and are not energy efficient and have reached the end of their useful life. Additionally, the rooftop units contain R-22 refrigerant which has been phased out of production. The six HVAC roof top units should be scheduled for replacement in the next 3 - 4 years. This project would provide for installation of six new HVAC packaged units, curb adapters, TCS (temperature control system), cleaning of the existing duct work and grilles, and commissioning. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 03/31/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/07/2020. | STATE MAIL SERVICES BUILDING | 9916 | Admin | PubWorks | B&G | Carson City | 1953 | 8137 | 2020-10-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 270000
0395ADA4 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0395 | This building contains a water fountain. The 2018 IBC Section 1109.5 states where a water fountain is provided, at least half should be accessible. This project would provide funding for the purchase and installation of a new accessible fixed high/ low ADA drinking fountain. The 2018 IBC Chapter 11, ICC/ANSI A117.1 and the most current version of the Americans With Disabilities Act Accessible Guidelines (ADAAG) was used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 03/31/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/07/2020. | STATE MAIL SERVICES BUILDING | 9916 | Admin | PubWorks | B&G | Carson City | 1953 | 8137 | 2020-10-07 | Immediate to Two Years | Currently Critical | 1 | 5000
0395ADA3 | INSTALL ADA SIGNAGE | 0395 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2018 IBC Chapter 11, ICC/ANSI A117.1 and the most current version of the Americans With Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 03/31/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/07/2020. | STATE MAIL SERVICES BUILDING | 9916 | Admin | PubWorks | B&G | Carson City | 1953 | 8137 | 2020-10-07 | Immediate to Two Years | Currently Critical | 1 | 1200
0395INT2 | RESURFACE CONCRETE FLOOR | 0395 | The painted concrete floor in the building is worn and cracked and should be resurfaced. This project provides for stripping existing floor paint, repairing the existing floor, and applying an appropriate clear concrete sealer. This project or a portion thereof was previously recommended in the FCA report dated 03/31/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/07/2020. | STATE MAIL SERVICES BUILDING | 9916 | Admin | PubWorks | B&G | Carson City | 1953 | 8137 | 2020-10-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 65000
0395SFT1 | INSTALL DUST COLLECTION SYSTEM | 0395 | The building has automated OCR mail sorters, which generate an observable amount of fine paper dust. The mail sorters do not have dust collection systems. This project recommends the installation of dust collection systems for the mail sorters including vacuum tubing and all required connections to existing utilities. This project or a portion thereof was previously recommended in the FCA report dated 03/31/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/07/2020. | STATE MAIL SERVICES BUILDING | 9916 | Admin | PubWorks | B&G | Carson City | 1953 | 8137 | 2020-10-07 | Immediate to Two Years | Currently Critical | 1 | 50000
0395SFT6 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0395 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated LED style exit signs with battery-backed internal systems, as well as emergency egress lighting, to provide illumination along the egress route. IBC 2018 Chapter 10 was referenced for this project. | STATE MAIL SERVICES BUILDING | 9916 | Admin | PubWorks | B&G | Carson City | 1953 | 8137 | 2020-10-07 | Immediate to Two Years | Currently Critical | 1 | 10200
0395PLM1 | WATER HEATER REPLACEMENT | 0395 | There is a 53 gallon gas-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2 - 3 years. It is recommended that a new gas-fired water heater be installed. This project or a portion thereof was previously recommended in the FCA report dated 03/31/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/07/2020. | STATE MAIL SERVICES BUILDING | 9916 | Admin | PubWorks | B&G | Carson City | 1953 | 8137 | 2020-10-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
0397INT7 | ROOF LEAK REPAIRS | 0397 | Roof leaks are evident on the ceiling of the 4th floor penthouse mechanical room need to be repaired. This project will fund the investigation and repair of the single ply roofing system. | CARSON CITY STATE OFFICES BUILDING | 9864 | Admin | PubWorks | B&G | Carson City | 1959 | 42550 | 2020-10-07 | Immediate to Two Years | Currently Critical | 1 | 1500
0395ELE1 | EXTERIOR LIGHTING REPLACEMENT | 0395 | The building has exterior lighting on the north side of the building and the 3 existing light fixtures are old, failing, and not energy efficient. This project would provide for augmenting site lighting on the north side and replacement of the exterior lighting fixtures with new LED light fixtures using existing wiring circuits. | STATE MAIL SERVICES BUILDING | 9916 | Admin | PubWorks | B&G | Carson City | 1953 | 8137 | 2020-10-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0395EXT5 | EXTERIOR DOOR REPLACEMENT | 0395 | The exterior metal doors on the north side are damaged from age, general wear and tear, and have reached the end of their expected life. This project would provide for the replacement of the double door assembly and two single door assemblies on the north side with new metal insulated doors, frames, and hardware. Removal and disposal of the existing doors is included in this estimate. | STATE MAIL SERVICES BUILDING | 9916 | Admin | PubWorks | B&G | Carson City | 1953 | 8137 | 2020-10-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14900
0395INT3 | FLOORING INSTALLATION / REPLACEMENT | 0395 | All of the support function offices along the south wall currently do not have any floor covering. It is recommended that carpet tile be installed in these office spaces and also the main office circulation area outside the restrooms similar to the private offices and conference room. This project would enhance the acoustical attenuation in the office area needed due to the noise generated by the mail sorting machines. 1,500 square feet of flooring was used for this estimate. | STATE MAIL SERVICES BUILDING | 9916 | Admin | PubWorks | B&G | Carson City | 1953 | 8137 | 2020-10-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 13000
0395ADA6 | RESTROOM REMODEL | 0395 | The restrooms in the building date back to the original construction in 1953. They are old and reaching the end of their expected and useful life. An entire remodel is recommended. This project would provide funding for remodeling the men's and women's restrooms per ADA regulations. Task items include demolition and replacement of under slab waste lines, all interior finishes and fixtures. The 2018 IBC, ICC/ANSI A117.1, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as a reference for this project. | STATE MAIL SERVICES BUILDING | 9916 | Admin | PubWorks | B&G | Carson City | 1953 | 8137 | 2020-10-07 | Four to Ten Years | Long-Term Needs | 3 | 120000
0395ENR2 | LIGHTING UPGRADE | 0395 | It is recommended that the existing lighting fixtures be re-lamped with T-8 LED lamps resulting in increased efficiency and reduced costs associated with illumination. | STATE MAIL SERVICES BUILDING | 9916 | Admin | PubWorks | B&G | Carson City | 1953 | 8137 | 2020-10-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0397SIT1 | BUILDING DRAINAGE UPGRADES | 0397 | The grade on the west side of the building does not slope away from the building effectively which could allow water to infiltrate the basement window openings. This project would create positive flow away from the building by regrading and reinstallation of landscaping as needed. | CARSON CITY STATE OFFICES BUILDING | 9864 | Admin | PubWorks | B&G | Carson City | 1959 | 42550 | 2020-10-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
0395EXT4 | EIFS REPAIRS | 0395 | The EIFS (Exterior Insulating Finish System) at the front entry of the building is damaged and in need of repair and the EIFS finish has deteriorated. This project would provide for the repair of the EIFS system and re-coating all of the EIFS surfaces. | STATE MAIL SERVICES BUILDING | 9916 | Admin | PubWorks | B&G | Carson City | 1953 | 8137 | 2020-10-07 | Immediate to Two Years | Currently Critical | 1 | 2000
0397INT5 | INTERIOR FINISHES | 0397 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | CARSON CITY STATE OFFICES BUILDING | 9864 | Admin | PubWorks | B&G | Carson City | 1959 | 42550 | 2020-10-07 | Four to Ten Years | Long-Term Needs | 3 | 212750
0397ADA1 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0397 | This building contains water fountains on the 1st and 2nd floors that are not ADA compliant. The 2018 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of accessible drinking fountains to meet the ADA requirements on the first two floors. If drinking fountains are located in an exit access, it is recommended to review exit access requirements for projections into exit access width. This project or a portion thereof was previously recommended in the FCA report dated 01/19/2012. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/07/2020. | CARSON CITY STATE OFFICES BUILDING | 9864 | Admin | PubWorks | B&G | Carson City | 1959 | 42550 | 2020-10-07 | Immediate to Two Years | Currently Critical | 1 | 15000
0397ADA3 | ADA ACCESSIBLE COUNTERS | 0397 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The front offices on the 2nd and 3rd floors have a service counter for the public to approach which does not meet current codes. Section 7.2 of the Americans with Disabilities Act Accessible Guidelines (ADAAG) states that the counter must have a portion which is at least 36" in length with a maximum height of 36" above the finish floor. This project will provide an accessible counter space on the 2nd and 3rd floor in accordance with this requirement. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 01/19/2012. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/07/2020. | CARSON CITY STATE OFFICES BUILDING | 9864 | Admin | PubWorks | B&G | Carson City | 1959 | 42550 | 2020-10-07 | Immediate to Two Years | Currently Critical | 1 | 2000
0397EXT2 | EXTERIOR FINISHES | 0397 | The exterior finishes are in good condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is priming, painting, and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CARSON CITY STATE OFFICES BUILDING | 9864 | Admin | PubWorks | B&G | Carson City | 1959 | 42550 | 2020-10-07 | Four to Ten Years | Long-Term Needs | 3 | 212750
0397ENR1 | WINDOW REPLACEMENT | 0397 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units including frames. This estimate is for the replacement of 10,270 square feet of glazing and associated frames. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 01/19/2012. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/07/2020. Also, referenced CIP #21044. | CARSON CITY STATE OFFICES BUILDING | 9864 | Admin | PubWorks | B&G | Carson City | 1959 | 42550 | 2020-10-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 700000
0395SFT5 | FIRE ALARM SYSTEM UPGRADE | 0395 | This building is lacking a fire alarm annunciation system. The existing fire alarm is connected to the flow switch in the fire suppression system but lacks notification to occupants within the building. It is recommended that a fire alarm annunciator system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1 Section 7 and the 2018 International Fire Code. | STATE MAIL SERVICES BUILDING | 9916 | Admin | PubWorks | B&G | Carson City | 1953 | 8137 | 2020-10-07 | Immediate to Two Years | Currently Critical | 1 | 16300
0397INT6 | JANITORS CLOSET REPAIRS | 0397 | The mop sinks in the Janitors Closets are mounted adjacent to gypsum board and are showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. A total for 4 closets was used for this estimate. This project or a portion thereof was previously recommended in the FCA report dated 01/19/2012. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/07/2020. | CARSON CITY STATE OFFICES BUILDING | 9864 | Admin | PubWorks | B&G | Carson City | 1959 | 42550 | 2020-10-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6800
0397SFT1 | SPRINKLER HEAD OBSTRUCTIONS | 0397 | The upright sprinkler heads do not appear to have the correct clearance to obstructions as required by NFPA 13 as referenced in 2018 IFC Section 903.3.1. It is recommended that 18" of clearance be provided to combustibles; however, there are exceptions to this requirement and consultation with the AHJ (Authority Having Jurisdiction, in this case State Fire Marshal) is recommended. This project would fund the purchase of additional storage cabinets and relayout of the storage area to accommodate the required fire sprinkler clearance. | CARSON CITY STATE OFFICES BUILDING | 9864 | Admin | PubWorks | B&G | Carson City | 1959 | 42550 | 2020-10-07 | Immediate to Two Years | Currently Critical | 1 | 5000
9845SIT4 | MOTORIZED GATE INSTALLATION | 9845 | The site has a perimeter fence that has vehicle access gates off Galletti and Barnett. They are mechanically operated, have been problematic, and are difficult to open and close. This project recommends the gates be upgraded to a motorized track system that can handle heavy equipment traffic. The gates will be required to meet UL Standard 325, per NRS 405.270. This project or a portion thereof was previously recommended in the FCA report dated 07/15/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/12/2011. | RENO PURCHASING WAREHOUSE SITE | 9845 | Admin | PubWorks | B&G | Reno | 0 |  | 2021-01-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
3098EXT1 | EXTERIOR FINISHES | 3098 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | STORAGE BUILDING | 9845 | Admin | PubWorks | B&G | Reno | 2000 | 1250 | 2021-01-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 750
9845SIT3 | DRAINAGE UPGRADES | 9845 | The site has several areas with inadequate drainage due to deteriorated asphalt and clogged drains. The standing water causes premature deterioration of the paving and other site improvements. This project would provide for drainage upgrades which may include pumping existing drains, installing new french drains and re-grading to ensure proper water flows. This project should be implemented concurrently with the ASPHALT PAVING REPLACEMENT project. This project or a portion thereof was previously recommended in the FCA report dated 07/15/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/12/2011. | RENO PURCHASING WAREHOUSE SITE | 9845 | Admin | PubWorks | B&G | Reno | 0 |  | 2021-01-12 | Immediate to Two Years | Currently Critical | 1 | 35000
9845SIT2 | ASPHALT PAVING REPLACEMENT | 9845 | The asphalt around the building has failed, with significant alligatoring, settling, cracks and complete erosion. This project covers the removal and replacement of the existing asphalt for parking and site access. Striping for safety, parking and loading zones is included in this estimate. 120,000 square feet was used to generate this estimate. This project should be implemented concurrently with the DRAINAGE UPGRADES project. | RENO PURCHASING WAREHOUSE SITE | 9845 | Admin | PubWorks | B&G | Reno | 0 |  | 2021-01-12 | Immediate to Two Years | Currently Critical | 1 | 1200000
9845SIT1 | SLURRY SEAL ASPHALT PAVING | 9845 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site wide. Striping is included in this estimate. The ASPHALT PAVING project should be done prior to this long term cyclical maintenance work. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 120,000 square feet of asphalt area was used to generate this estimate. This project or a portion thereof was previously recommended in the FCA report dated 07/15/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/12/2011. | RENO PURCHASING WAREHOUSE SITE | 9845 | Admin | PubWorks | B&G | Reno | 0 |  | 2021-01-12 | Four to Ten Years | Long-Term Needs | 3 | 90000
9845ADA2 | ADA SIGNAGE | 9845 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | RENO PURCHASING WAREHOUSE SITE | 9845 | Admin | PubWorks | B&G | Reno | 0 |  | 2021-01-12 | Immediate to Two Years | Currently Critical | 1 | 1250
9845ADA1 | ADA PARKING UPGRADE | 9845 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The existing ADA parking space does not entirely meet the requirements of the code. This project provides funding to bring the existing ADA parking space up to code including removal of the asphalt and replacement with P.C. concrete, updated signage, re-striping, re-grading and any other necessary upgrades. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | RENO PURCHASING WAREHOUSE SITE | 9845 | Admin | PubWorks | B&G | Reno | 0 |  | 2021-01-12 | Immediate to Two Years | Currently Critical | 1 | 2500
0399EXT4 | LOADING DOCK REPAIRS | 0399 | The main loading dock on the west side of the building is damaged and due for major repairs. The concrete is cracked and failing to the point of exposing the reinforcing steel and jeopardizing the integrity of the structure. The stairs from the parking lot also have significant deterioration and require complete replacement. This project would provide for repairs to the loading dock including removing and replacing concrete, replacement of the stairs and rails and refurbishing the lifts. | RENO PURCHASING WAREHOUSE | 9845 | Admin | PubWorks | B&G | Reno | 1960 | 58428 | 2021-01-12 | Immediate to Two Years | Currently Critical | 1 | 125000
0399HVA2 | HVAC UPGRADES, B&G SHOP | 0399 | The B&G shop is located at the north west corner of the building. An office was built in this area that has no ventilation as required by Section 1203 of the 2006 International Building Code. This project would provide for the purchase and installation of a wall mounted heat pump to provide cooling, heating and ventilation in the office area of the shop including all required connections to existing utilities. This project or a portion thereof was previously recommended in the FCA report dated 07/15/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/12/2011. | RENO PURCHASING WAREHOUSE | 9845 | Admin | PubWorks | B&G | Reno | 1960 | 58428 | 2021-01-12 | Immediate to Two Years | Currently Critical | 1 | 3000
0399INT3 | RESTROOM REMODEL - B&G SHOP | 0399 | The restroom in the B&G Shop is in overall poor condition and does not meet code for safety. The finishes, fixtures, cabinets, toilet, shower and exhaust fan are showing signs of wear and deterioration. Section 1008.1 of the 2006 International Building Code describes the requirements for landings at doors. There is no proper landing at the door. This project would provide for a complete remodel of the restroom and installation of a compliant landing. The removal and disposal of the existing fixtures and finishes is included in this estimate. | RENO PURCHASING WAREHOUSE | 9845 | Admin | PubWorks | B&G | Reno | 1960 | 58428 | 2021-01-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
0399EXT3 | EXTERIOR FINISHES | 0399 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is scraping, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | RENO PURCHASING WAREHOUSE | 9845 | Admin | PubWorks | B&G | Reno | 1960 | 58428 | 2021-01-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 300000
0399SFT2 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0399 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2006 Chapter 10 was referenced for this project. | RENO PURCHASING WAREHOUSE | 9845 | Admin | PubWorks | B&G | Reno | 1960 | 58428 | 2021-01-12 | Immediate to Two Years | Currently Critical | 1 | 15000
0399ADA5 | ADA SIGNAGE | 0399 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | RENO PURCHASING WAREHOUSE | 9845 | Admin | PubWorks | B&G | Reno | 1960 | 58428 | 2021-01-12 | Immediate to Two Years | Currently Critical | 1 | 1500
0399ADA4 | ADA RESTROOM UPGRADE | 0399 | The existing restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for remodeling the Men's and Women's restrooms into ADA compliant restrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | RENO PURCHASING WAREHOUSE | 9845 | Admin | PubWorks | B&G | Reno | 1960 | 58428 | 2021-01-12 | Immediate to Two Years | Currently Critical | 1 | 30000
0399ENR2 | WINDOW REPLACEMENT | 0399 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 7 units. Removal and disposal of the existing windows is included in this estimate. | RENO PURCHASING WAREHOUSE | 9845 | Admin | PubWorks | B&G | Reno | 1960 | 58428 | 2021-01-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5250
0399ELE2 | EXTERIOR OUTLET REPLACEMENT | 0399 | There is an electrical outlet on the exterior of the building that does not meet code. This outlet should be changed to a GFCI type outlet per the 2005 NEC. This project would provide for the purchase and installation of one GFCI duplex outlet with a weatherproof cover. | RENO PURCHASING WAREHOUSE | 9845 | Admin | PubWorks | B&G | Reno | 1960 | 58428 | 2021-01-12 | Immediate to Two Years | Currently Critical | 1 | 300
0399INT1 | INTERIOR FINISHES | 0399 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings in the offices and the B&G shop be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | RENO PURCHASING WAREHOUSE | 9845 | Admin | PubWorks | B&G | Reno | 1960 | 58428 | 2021-01-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 17500
0399ENV1 | 4" BACKFLOW PREVENTION | 0399 | State Health Law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of back siphonage or backpressure. This project allows for the installation of a 4" double check valve or reduced pressure principle backflow preventer for the main domestic water line. Costs include an above ground vault, and allowance for 200 feet of 1" conduit to provide power for freeze protection. This project or a portion thereof was previously recommended in the FCA report dated 07/15/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/12/2011. | RENO PURCHASING WAREHOUSE | 9845 | Admin | PubWorks | B&G | Reno | 1960 | 58428 | 2021-01-12 | Immediate to Two Years | Currently Critical | 1 | 25000
0399EXT2 | OVERHEAD DOOR REPLACEMENTS | 0399 | There are six overhead coiling doors throughout the facility in various stages of disrepair. Three of the doors are damaged and do not function properly. Exposure, wind and general wear and tear have caused the doors to bend, crack and lose their finish. They are original to the building and should be scheduled for replacement. The other three doors are in need of new weather seals to minimize air and debris infiltration. This project would provide for the removal and disposal of the doors and installing new weather seals. This project or a portion thereof was previously recommended in the FCA report dated 07/15/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/12/2011. | RENO PURCHASING WAREHOUSE | 9845 | Admin | PubWorks | B&G | Reno | 1960 | 58428 | 2021-01-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0399STR2 | STRUCTURAL ASSESSMENT, STORAGE AREA | 0399 | A storage area has been constructed over the B&G office, accessed via non-complying stairs in the shop. There is no record of a CIP project for this work or of any structural evaluations having been conducted. This project recommends that a licensed engineer perform a structural investigation to assess the load bearing capacity of the structure. Future projects would be based on this report. This project or a portion thereof was previously recommended in the FCA report dated 07/15/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/12/2011. | RENO PURCHASING WAREHOUSE | 9845 | Admin | PubWorks | B&G | Reno | 1960 | 58428 | 2021-01-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0399ENR1 | LIGHTING UPGRADE | 0399 | The existing interior and exterior lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. T-5 High Output high bay lamps with electronic ballasts and compact fluorescent lights (CFL's) are suggested. Occupancy sensors will be installed in restrooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 07/15/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/12/2011. | RENO PURCHASING WAREHOUSE | 9845 | Admin | PubWorks | B&G | Reno | 1960 | 58428 | 2021-01-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 86904
0399HVA3 | BOILER REPLACEMENT | 0399 | The hot water boiler servicing the building was installed almost 20 years ago and should be scheduled for replacement. The life expectancy of this unit is 20 to 25 years with proper maintenance and water treatment programs. Replacement parts for performing routine and emergency maintenance are hard to find for this older equipment. The controls and mixing valves should be replaced for the same reasons. There are currently several areas of the building which have stand alone electric heaters. It is recommended to remove those units and replace them with fan coil units serviced by the boiler. This project would provide for the removal and disposal of the existing boiler, controls and mixing valves and replacement with new equipment including all required connections to utilities and equipment. The estimate is based on a 1,700 MBH maximum output hot water boiler, associated equipment and new equipment to replace the electric heaters. The existing chemical water treatment system will need to be tested and adjusted once equipment is operational. $2,000 is included in this estimate for testing of the chemical water treatment system. This project or a portion thereof was previously recommended in the FCA report dated 07/15/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/12/2011. | RENO PURCHASING WAREHOUSE | 9845 | Admin | PubWorks | B&G | Reno | 1960 | 58428 | 2021-01-12 | Four to Ten Years | Long-Term Needs | 3 | 85000
0399ENV2 | 3" BACKFLOW PREVENTION | 0399 | State Health Law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of back siphonage or backpressure. This project allows for the installation of a 3" double check valve or reduced pressure principle backflow preventer for the automatic fire suppression system. Costs include an above ground vault, and allowance for 200 feet of 1" conduit to provide power for freeze protection. This project or a portion thereof was previously recommended in the FCA report dated 07/15/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/12/2011. | RENO PURCHASING WAREHOUSE | 9845 | Admin | PubWorks | B&G | Reno | 1960 | 58428 | 2021-01-12 | Immediate to Two Years | Currently Critical | 1 | 20000
0200SFT4 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0200 | The emergency egress lighting is insufficient and most of the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2006 Chapter 10 was referenced for this project. | BLASDEL OFFICE BUILDING | 9860 | Admin | PubWorks | B&G | Carson City | 1957 | 41680 | 2021-01-26 | Immediate to Two Years | Currently Critical | 1 | 41680
0200ADA1 | SIDEWALK REPAIRS | 0200 | The concrete sidewalk on the south side of the building appears to have heaved significantly since it was installed. The transition from the sidewalk concrete to the existing concrete adjacent to the buildings south entrance has an elevation change of more than 1/2". This is on the accessible means of egress and should be remedied immediately. The concrete should be ground down to reduce the elevation change to less than 1/4". NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2003 were referenced for this project. | BLASDEL OFFICE BUILDING | 9860 | Admin | PubWorks | B&G | Carson City | 1957 | 41680 | 2021-01-26 | Immediate to Two Years | Currently Critical | 1 | 1000
0200INT2 | INTERIOR FINISHES | 0200 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | BLASDEL OFFICE BUILDING | 9860 | Admin | PubWorks | B&G | Carson City | 1957 | 41680 | 2021-01-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 208400
0200ELE2 | EMERGENCY GENERATOR REPLACEMENT | 0200 | The existing generator which provides emergency power to the building is old and under-powered for the increased electrical load. This project would provide for the replacement of the generator with a new 550 kw generator including new auto switchgear. It is recommended that this project be done in conjunction with the electrical upgrade project. | BLASDEL OFFICE BUILDING | 9860 | Admin | PubWorks | B&G | Carson City | 1957 | 41680 | 2021-01-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 250000
0200SFT2 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0200 | The building is a B occupancy per the 2006 IBC. It does not have a fire suppression system on the first, second or third floors. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. Costs are lower on this project because there is a fire suppression system installed in the basement and a 4" dry standpipe that supplies the fire hoses on the upper floors with fire department connections at the roof, basement, and at grade. This project or a portion thereof was previously recommended in the FCA report dated 4/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 8/3/2010. | BLASDEL OFFICE BUILDING | 9860 | Admin | PubWorks | B&G | Carson City | 1957 | 41680 | 2021-01-26 | Immediate to Two Years | Currently Critical | 1 | 333440
0200INT1 | FLOORING REPLACEMENT | 0200 | The VCT (vinyl composite tile) and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the next 3-4 years. This estimate is for all three floors with the exception of the main floor lobby tile, which is in good shape. This project or a portion thereof was previously recommended in the FCA report dated 4/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 8/3/2010. | BLASDEL OFFICE BUILDING | 9860 | Admin | PubWorks | B&G | Carson City | 1957 | 41680 | 2021-01-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 190000
0200INT5 | JANITOR CLOSET REPAIRS | 0200 | The mop sinks in the Janitor Closets are mounted adjacent to painted concrete wall board and are showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. A total for 3 closets was used for this estimate. | BLASDEL OFFICE BUILDING | 9860 | Admin | PubWorks | B&G | Carson City | 1957 | 41680 | 2021-01-26 | Immediate to Two Years | Currently Critical | 1 | 4200
0200INT3 | CEILING SYSTEM REPLACEMENT | 0200 | The second and third floors of this building have a dated suspended acoustical tile ceiling system. The t-bar framing is bent and rusted in many areas and a number of the ceiling tiles are damaged and stained. This project would provide for the replacement of the suspended acoustical tile ceiling system. Removal and disposal of the existing ceiling system is included in this estimate. | BLASDEL OFFICE BUILDING | 9860 | Admin | PubWorks | B&G | Carson City | 1957 | 41680 | 2021-01-26 | Four to Ten Years | Long-Term Needs | 3 | 200000
0200EXT2 | EXTERIOR FINISHES | 0200 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the concrete and tile, repairing cracks in the concrete and granite, and caulking of the windows, flashing, fixtures, and all other penetrations. Special attention should be paid to the penthouse where the cooling tower has caused moss and mildew growth. It is recommended that the building be cleaned, sealed, and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BLASDEL OFFICE BUILDING | 9860 | Admin | PubWorks | B&G | Carson City | 1957 | 41680 | 2021-01-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 208400
0200ENR2 | HVAC SYSTEM REPLACEMENT | 0200 | The building has an older HVAC system, most of which is original to the building. The boiler is approximately 22 years old, with radiant heaters under the windows. This project recommends replacing the HVAC system for improved comfort and efficiency. This project would provide for the removal and disposal of the existing air handler, cooling tower, boiler, radiators and controls, and replacement with new equipment including a new boiler, air handler, cooling tower, controls, all required connections to utilities, ductwork, and required equipment. The existing chemical water treatment system will need to be tested and adjusted once equipment is operational. $2,000 is included in this estimate for testing of the chemical water treatment system. This project or a portion thereof was previously recommended in the FCA report dated 4/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 8/3/2010. | BLASDEL OFFICE BUILDING | 9860 | Admin | PubWorks | B&G | Carson City | 1957 | 41680 | 2021-01-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1667200
0200SFT3 | SEAL PENETRATIONS | 0200 | There are a number of penetrations through the chases and corridor walls for plumbing, data cables and cable trays. Many of these penetrations do not have smoke and fire sealing which corrupts the fire rated wall separations. This project provides funds to hire a qualified contractor to address penetration problems throughout the building. This project or a portion thereof was previously recommended in the FCA report dated 4/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 8/3/2010. | BLASDEL OFFICE BUILDING | 9860 | Admin | PubWorks | B&G | Carson City | 1957 | 41680 | 2021-01-26 | Immediate to Two Years | Currently Critical | 1 | 10000
0200SFT5 | REPLACE EMERGENCY DISCONNECTS | 0200 | There is an emergency shutoff for the boiler and a remote purge control for the chiller located on the east side of the building. These switches are not secured and could be activated by unauthorized persons resulting in loss of building heating and cooling capacity. This project recommends replacing the existing switches with newer models and/or relocating them to a more secure location. This project or a portion thereof was previously recommended in the FCA report dated 4/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 8/3/2010. | BLASDEL OFFICE BUILDING | 9860 | Admin | PubWorks | B&G | Carson City | 1957 | 41680 | 2021-01-26 | Immediate to Two Years | Currently Critical | 1 | 1500
0200ADA3 | ADA IMPROVEMENTS | 0200 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. This building contains a drinking fountain on the second floor that is missing cane detection equipment and elevator car controls that do not meet current codes. The car controls outside and inside the elevator should comply with ADAAG 4.10.12 which describes button sizes, Braille requirements, mounting heights and control locations. This project will provide cane detection and new car controls in accordance with ADA requirements. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2003 were referenced for this project. | BLASDEL OFFICE BUILDING | 9860 | Admin | PubWorks | B&G | Carson City | 1957 | 41680 | 2021-01-26 | Immediate to Two Years | Currently Critical | 1 | 7500
0200ENR1 | LIGHTING UPGRADE | 0200 | The existing lighting fixtures are the older T-8 fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in janitor closets, restrooms, conference rooms, and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | BLASDEL OFFICE BUILDING | 9860 | Admin | PubWorks | B&G | Carson City | 1957 | 41680 | 2021-01-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 145880
0200SFT1 | MODIFY REFRIGERANT ALARM SYSTEM | 0200 | The refrigerant alarm system appears to be improperly installed, with the horn located in the room, and the exhaust system is piped into the chimney for the abandoned incinerator. A project is recommended to provide proper signage, relocate the exhaust system to the exterior, and related repairs. This project or a portion thereof was previously recommended in the FCA report dated 4/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 8/3/2010. | BLASDEL OFFICE BUILDING | 9860 | Admin | PubWorks | B&G | Carson City | 1957 | 41680 | 2021-01-26 | Immediate to Two Years | Currently Critical | 1 | 6000
0200ELE1 | ELECTRICAL UPGRADE | 0200 | This building was constructed before the high demand for electrical services were needed for computers and other electrical devices. As time has progressed, the building's electrical demand and system has changed. It is utilized to its current maximum potential. The electrical panels, wiring and receptacles are at their limit. It is recommended the entire system be upgraded to meet the evolving needs of the building. At the time of the 2010 survey, a CIP project 09-M18 to replace the main switchgear and transformer in the basement was funded but not completed. The costs were not included as part of this project. This project or a portion thereof was previously recommended in the FCA report dated 4/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 8/3/2010. | BLASDEL OFFICE BUILDING | 9860 | Admin | PubWorks | B&G | Carson City | 1957 | 41680 | 2021-01-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 625200
0200INT4 | INTERIOR DOOR REPLACEMENT | 0200 | The majority of the interior doors in this building are damaged, difficult to operate, and have reached the end of their useful life. This project would provide for the installation of new interior doors including frames, lever action door handles, hardware, and paint. Removal and disposal of the existing doors is included in this cost estimate. A total of 100 interior doors was used in this estimate. | BLASDEL OFFICE BUILDING | 9860 | Admin | PubWorks | B&G | Carson City | 1957 | 41680 | 2021-01-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 350000
0200ADA2 | ADA RESTROOM REMODEL | 0200 | The Men's and Women's designated ADA restrooms on the first floor do not fully meet the Americans with Disabilities Act (ADA) requirements. The restrooms on the second and third floors should be remodeled to comply with the ADA as well. A complete retrofit is necessary on all four restrooms on the second and third levels including new partitions, water closets, urinals, lavatories, faucets, handles and any other necessary fixtures and finishes and minor modifications to the first floor designated ADA restrooms. This project would provide funding to bring all of the restrooms into ADA compliance. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2003 were referenced for this project. | BLASDEL OFFICE BUILDING | 9860 | Admin | PubWorks | B&G | Carson City | 1957 | 41680 | 2021-01-26 | Immediate to Two Years | Currently Critical | 1 | 150000
0200ENR3 | WINDOW REPLACEMENT | 0200 | The windows are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 144 units consisting of one large pane with two operable windows below. Removal and disposal of the existing windows is included in this estimate. | BLASDEL OFFICE BUILDING | 9860 | Admin | PubWorks | B&G | Carson City | 1957 | 41680 | 2021-01-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 792000
1675INT3 | CARPET REPLACEMENT | 1675 | The carpet in the Records Management Office is showing signs of extreme wear. It is recommended that the carpet be replaced with heavy duty commercial grade carpet in the next 2-3 years. | NEVADA STATE LIBRARY & ARCHIVES | 9866 | Admin | PubWorks | B&G | Carson City | 1992 | 130000 | 2021-02-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1050
1675INT8 | JANITORS CLOSET REPAIRS | 1675 | The mop sink in the basement Janitors Closet is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | NEVADA STATE LIBRARY & ARCHIVES | 9866 | Admin | PubWorks | B&G | Carson City | 1992 | 130000 | 2021-02-02 | Immediate to Two Years | Currently Critical | 1 | 1000
1675ENR2 | CHILLER REPLACEMENT | 1675 | The building is cooled by a chiller and cooling tower system. The chiller is original to the building and is reaching the end of its useful life. It is recommended to schedule replacement of the chiller in the next 9-10 years. This project provides for disposal of the existing unit and replacement with a new 400 ton water cooled centrifugal chiller including connections to utilities. | NEVADA STATE LIBRARY & ARCHIVES | 9866 | Admin | PubWorks | B&G | Carson City | 1992 | 130000 | 2021-02-02 | Four to Ten Years | Long-Term Needs | 3 | 200000
1675ENR4 | LIGHTING UPGRADE | 1675 | The existing lighting fixtures are older T-8's, T-12's and sodium vapor HID's, and are not energy efficient. This project will upgrade T-8 lamps to super T-8 lamps with electronic ballasts and upgrade the HID (high intensity discharge) lamps to current standards, resulting in increased efficiency and reduced costs associated with illumination and HVAC load. Occupancy sensors will be installed in restrooms, conference rooms, individual offices and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | NEVADA STATE LIBRARY & ARCHIVES | 9866 | Admin | PubWorks | B&G | Carson City | 1992 | 130000 | 2021-02-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 130000
1675SFT2 | FM 200 SUPPRESSION SYSTEM | 1675 | The building has Halon extinguishing systems for the Microfilm, Archives and Rare Documents rooms. The EPA banned manufacture of Halon in 1998, and this project addresses the replacement of the system. A water-based fire suppression system is not recommended for this location due to building contents. This project will provide for the design and installation of an FM 200 or equivalent system and disposal of the existing equipment and chemicals. The existing Halon could be sold to help offset the cost of this project. The current area appears to be constructed of fire resistive components but should be field verified prior to installation of this system. This project or a portion thereof was previously recommended in the FCA report dated 07/25/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/11/2011. | NEVADA STATE LIBRARY & ARCHIVES | 9866 | Admin | PubWorks | B&G | Carson City | 1992 | 130000 | 2021-02-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 60000
1675ELE1 | ELECTRICAL UPGRADE, CONFERENCE ROOM | 1675 | The electrical outlets in Conference Room A are located on a single breaker. This results in frequent tripping of the breaker when several pieces of equipment are in use. This project will provide additional capacity for branch circuits for the outlets. This project or a portion thereof was previously recommended in the FCA report dated 07/25/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/11/2011. | NEVADA STATE LIBRARY & ARCHIVES | 9866 | Admin | PubWorks | B&G | Carson City | 1992 | 130000 | 2021-02-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7000
1675ENR5 | BOILER REPLACEMENT | 1675 | There are two hot water boilers that provide heating and process hot water to the building. They are original to the building and were manufactured in 1991. The life expectancy of these units is 20 to 25 years with proper maintenance and water treatment programs. Replacement parts for performing routine and emergency maintenance are hard to find for this old equipment. The controls and mixing valves should be replaced for the same reasons. This project would provide for the removal and disposal of the existing boilers, controls and mixing valves and replacement with new equipment including all required connections to utilities and equipment. The estimate is based on a 2,000 MBH output steel, natural gas fired, packaged water tube heating boiler. The existing chemical water treatment system will need to be tested and adjusted once equipment is operational. $2,000 is included in this estimate for testing of the chemical water treatment system. This project or a portion thereof was previously recommended in the FCA report dated 07/25/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/11/2011. | NEVADA STATE LIBRARY & ARCHIVES | 9866 | Admin | PubWorks | B&G | Carson City | 1992 | 130000 | 2021-02-02 | Four to Ten Years | Long-Term Needs | 3 | 90000
1675EXT2 | EXTERIOR FINISHES | 1675 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry, caulking of the windows, flashing, fixtures and all other penetrations and removing all of the climbing vines from the walls. It is recommended that the building be sealed and caulked in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Re-pointing of the sandstone masonry on an as needed basis is included in this estimate. | NEVADA STATE LIBRARY & ARCHIVES | 9866 | Admin | PubWorks | B&G | Carson City | 1992 | 130000 | 2021-02-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 260000
1675ENR1 | COOLING TOWER REPLACEMENT | 1675 | The building is cooled by a chiller and cooling tower system. The cooling tower and its associated equipment is non-operational and should be scheduled for replacement. Rust and water freezing in the pipes has greatly reduced the efficiency of the equipment. Three incidents of the heat transfer coil freezing have occurred since the tower was installed. This project provides for disposal of the existing equipment and replacement with a new cooling tower, heat exchanger and piping including connections to utilities. This project is currently funded under CIP 09-M01 but the contract had not been executed at the time of the survey of 2011.. | NEVADA STATE LIBRARY & ARCHIVES | 9866 | Admin | PubWorks | B&G | Carson City | 1992 | 130000 | 2021-02-02 | Immediate to Two Years | Currently Critical | 1 | 250000
1675ENR3 | TEMPERATURE CONTROLS UPGRADE | 1675 | The existing temperature control system is obsolete and the manufacturer is no longer in business. Spare parts are no longer available, it is increasingly more difficult to maintain the equipment and it is not compatible with current computer operating systems. It is recommended to schedule replacement of the temperature control system in the next 2-3 years. This project provides for disposal of the existing equipment and replacement with a new temperature control system including connections to utilities. This project is currently funded under CIP 09-M14 but the contract had not been executed. | NEVADA STATE LIBRARY & ARCHIVES | 9866 | Admin | PubWorks | B&G | Carson City | 1992 | 130000 | 2021-02-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 650000
1675INT7 | DOOR HARDWARE REPLACEMENT | 1675 | The interior wood doors are in good shape, but staff has had continuous problems with the hardware. The handles, tumblers and locks on the doors are damaged from age and general wear and tear and have reached the end of their useful life. This project would provide for the replacement of the hardware on 173 doors. Removal and disposal of the existing hardware is included in this estimate. | NEVADA STATE LIBRARY & ARCHIVES | 9866 | Admin | PubWorks | B&G | Carson City | 1992 | 130000 | 2021-02-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 86500
1675ADA1 | ACCESSIBLE DRINKING FOUNTAIN INSTALLATION | 1675 | This building contains four water fountains, one on the basement floor, two on the first floor and one on the second floor. Section 4.1.3 (10) of the Americans with Disabilities Act Accessible Guidelines (ADAAG) states where one water fountain is provided on a floor it shall be accessible and where more than one is provided on a floor, 50% of those shall be accessible. This project would provide funding for the purchase and installation of three new accessible fixed high/ low ADA drinking fountains. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | NEVADA STATE LIBRARY & ARCHIVES | 9866 | Admin | PubWorks | B&G | Carson City | 1992 | 130000 | 2021-02-02 | Immediate to Two Years | Currently Critical | 1 | 12000
1675INT9 | SHELVING REPLACEMENT | 1675 | The static shelving in the State Records Center and in the State Archives room is reaching capacity and will no longer be able meet storage demands. In order to maintain control and security of the records it is recommended to replace the existing shelving with a new compact shelving system as opposed to utilizing offsite storage facilities. The new system will store twice as much material in the same amount of space. The estimate includes removal and disposal of existing shelving and purchase and installation of new compact shelving. | NEVADA STATE LIBRARY & ARCHIVES | 9866 | Admin | PubWorks | B&G | Carson City | 1992 | 130000 | 2021-02-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1100000
1675ADA2 | ADA RESTROOM UPGRADES | 1675 | The designated ADA restrooms on the first floor of the Library are not compliant. The doors do not meet space requirements, the flush handles are on the wrong side of the water closets and the pipes under the sinks are not protected. This project would provide for an automatic door opener for each door, automatic flush valves for the water closets and pipe protection. A survey by an ADA professional should be conducted to verify these findings and determine whether any additional work is required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | NEVADA STATE LIBRARY & ARCHIVES | 9866 | Admin | PubWorks | B&G | Carson City | 1992 | 130000 | 2021-02-02 | Immediate to Two Years | Currently Critical | 1 | 15000
1675ADA4 | ADA SIGNAGE | 1675 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | NEVADA STATE LIBRARY & ARCHIVES | 9866 | Admin | PubWorks | B&G | Carson City | 1992 | 130000 | 2021-02-02 | Immediate to Two Years | Currently Critical | 1 | 5000
1675SIT1 | LOADING DOCK REPAIR | 1675 | The existing loading dock on the west side of the building is damaged. There is exposed rebar and severely cracked concrete including the stairs and side retaining walls. This project would provide for the removal and replacement of the damaged steel, concrete walls, sidewalk and handrails. The existing lift is not included in this estimate. | NEVADA STATE LIBRARY & ARCHIVES | 9866 | Admin | PubWorks | B&G | Carson City | 1992 | 130000 | 2021-02-02 | Immediate to Two Years | Currently Critical | 1 | 100000
1675SFT4 | FUME HOOD / VENTING MODIFICATIONS | 1675 | The existing fume hood is non-operational and the existing venting for the microfiche machine does not work properly. This project will provide funds for the repair of the fume hood exhaust fan and microfiche venting system. | NEVADA STATE LIBRARY & ARCHIVES | 9866 | Admin | PubWorks | B&G | Carson City | 1992 | 130000 | 2021-02-02 | Immediate to Two Years | Currently Critical | 1 | 2500
1675ENR6 | HUMIDIFICATION SYSTEM REPLACEMENT - ARCHIVES | 1675 | The Archives/ Records Center has six individual humidifiers mounted on the wall. They are original to the building, require frequent maintenance and only two or three of them are currently operating. The humidification system should be scheduled for replacement. It is recommended to re-engineer the entire system and install a new system based on the new design. The new design may include integration with the existing HVAC system or utilizing evaporative cooling for increased energy efficiency. This project or a portion thereof was previously recommended in the FCA report dated 07/25/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/11/2011. | NEVADA STATE LIBRARY & ARCHIVES | 9866 | Admin | PubWorks | B&G | Carson City | 1992 | 130000 | 2021-02-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 45000
1675PLM1 | WATER HEATER INSTALLATION | 1675 | The building's process hot water is supplied by the two boilers. The main purpose of the boilers is to heat the conditioned spaces during cold weather. The boilers run year round to support this configuration. It would be more economical and energy efficient to install a separate water heater for the process hot water supply. This would enable the boilers to be shut down when building heat is not necessary, reducing utility costs and extending the life of the boilers. There is a 73 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed for more efficient use of energy. This estimate includes: 100 feet of gas pipe, fittings, couplers, and labor for installation. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 07/25/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/11/2011. | NEVADA STATE LIBRARY & ARCHIVES | 9866 | Admin | PubWorks | B&G | Carson City | 1992 | 130000 | 2021-02-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
9918SIT4 | DRAINAGE IMPROVEMENTS | 9918 | There is a drainage problem on the west side of the Capitol building resulting in water leaking into the basement. Two roof drain downspouts and landscaping are just outside of the subject area and it is suspected that the water is pooling up in this area instead of running off away from the building. It is recommended to extend the downspouts underground to a dry well or similar drainage feature to carry the water away from the building and regrade the landscaped area to provide a positive slope away from the building. | NEVADA STATE CAPITOL SITE | 9918 | Admin | PubWorks | B&G | Carson City | 0 |  | 2021-02-02 | Immediate to Two Years | Currently Critical | 1 | 5000
9918ADA1 | SIDEWALK / CONCRETE REPAIRS | 9918 | Some of the sidewalks around the building are deteriorated and failing and some do not meet ADA requirements. In some areas there is extensive cracking, heaving and settling. The concrete landings at the bottom of the three steel exterior exit stairs are too small and one is missing. This project addresses removal and replacement of existing sidewalks as needed particularly for the ADA path of travel on the east side of the site and installing new landings for the exit stairs. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | NEVADA STATE CAPITOL SITE | 9918 | Admin | PubWorks | B&G | Carson City | 0 |  | 2021-02-02 | Immediate to Two Years | Currently Critical | 1 | 15000
9918SFT1 | CONCRETE STAIR REPAIRS | 9918 | The south side concrete stairs and landing at the breezeway between the Annex and Capitol are severely deteriorated. Spalling and cracking have occurred to the extent that the stairs need to be replaced and the landing resurfaced. It is currently a tripping hazard especially during inclement weather. This project addresses removal and replacement of the entire stair structure and resurfacing the concrete landing. The existing handrails do not meet current building codes and may need to be replaced in kind or altered to bring them into compliance. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. Section 1012 of the 2006 IBC was referenced for this project. | NEVADA STATE CAPITOL SITE | 9918 | Admin | PubWorks | B&G | Carson City | 0 |  | 2021-02-02 | Immediate to Two Years | Currently Critical | 1 | 15000
9918SIT3 | SLURRY SEAL ASPHALT PAVING | 9918 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving including the access road and parking area on the south side of the Capitol. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 10,000 square feet of asphalt area was used to generate this estimate. | NEVADA STATE CAPITOL SITE | 9918 | Admin | PubWorks | B&G | Carson City | 0 |  | 2021-02-02 | Four to Ten Years | Long-Term Needs | 3 | 7500
0203EXT2 | EXTERIOR FINISHES | 0203 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are sanding, priming and painting, cleaning and sealing the sandstone masonry and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted, sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | STATE CAPITOL ANNEX | 9918 | Admin | PubWorks | B&G | Carson City | 1905 | 9864 | 2021-02-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 49320
0203PLM1 | WATER HEATER REPLACEMENT | 0203 | There is a 30 gallon electric water heater in the building that was installed in 2005. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 4-5 years. It is recommended that a new on-demand electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | STATE CAPITOL ANNEX | 9918 | Admin | PubWorks | B&G | Carson City | 1905 | 9864 | 2021-02-02 | Four to Ten Years | Long-Term Needs | 3 | 2500
0203ADA1 | ADA KITCHENETTE UPGRADES | 0203 | The kitchenette in the employee break room does not entirely meet the Americans with Disabilities Act (ADA) requirements. Minor modifications are necessary. This project would provide funding for upgrades to the kitchenette to remove architectural barriers. These items may include a new sink, modifications to the casework to provide clearances, hardware, relocating the microwave and moving furniture to provide clearances. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | STATE CAPITOL ANNEX | 9918 | Admin | PubWorks | B&G | Carson City | 1905 | 9864 | 2021-02-02 | Immediate to Two Years | Currently Critical | 1 | 2500
0203INT2 | INTERIOR FINISHES | 0203 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | STATE CAPITOL ANNEX | 9918 | Admin | PubWorks | B&G | Carson City | 1905 | 9864 | 2021-02-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 49320
0235EXT2 | REMOVE VINE GROWTH FROM BUILDING | 0235 | There is extensive vine growth on the exterior sandstone masonry of the building. This will damage the sandstone masonry and grout joints. This project will provide for the removal of all vines from the exterior of the building including the actual plant itself along the perimeter of the structure. | NEVADA STATE CAPITOL | 9918 | Admin | PubWorks | B&G | Carson City | 1870 | 54778 | 2021-02-02 | Immediate to Two Years | Currently Critical | 1 | 2000
0203ADA4 | ADA SIGNAGE | 0203 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. This project or a portion thereof was previously recommended in the FCA report dated 09/03/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/23/2011. | STATE CAPITOL ANNEX | 9918 | Admin | PubWorks | B&G | Carson City | 1905 | 9864 | 2021-02-02 | Immediate to Two Years | Currently Critical | 1 | 1500
0235ADA3 | ADA RESTROOM UPGRADES | 0235 | The building has several ADA accessible restrooms, some of which are not fully compliant. For instance, the unisex ADA restroom on the 2nd floor is missing pipe protection under the sink and the water closet is lower than the required 17" height for the seat. Also, the countertop in the Men's restroom on the 1st floor does not meet height requirements and the water closet flush handle in the Men's restroom in the basement is on the wrong side of the water closet. This project would provide funding for these specific repairs and any other necessary upgrades to bring the restrooms into full compliance. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | NEVADA STATE CAPITOL | 9918 | Admin | PubWorks | B&G | Carson City | 1870 | 54778 | 2021-02-02 | Immediate to Two Years | Currently Critical | 1 | 15000
0235INT3 | JANITORS CLOSET REPAIRS | 0235 | The mop sink in the basement Janitors Closet is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | NEVADA STATE CAPITOL | 9918 | Admin | PubWorks | B&G | Carson City | 1870 | 54778 | 2021-02-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
0235EXT1 | EXTERIOR FINISHES | 0235 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are sanding, priming and painting, cleaning and pointing the sandstone masonry as needed and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be repaired in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NEVADA STATE CAPITOL | 9918 | Admin | PubWorks | B&G | Carson City | 1870 | 54778 | 2021-02-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 273890
0235ADA2 | ADA SIGNAGE | 0235 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. This project or a portion thereof was previously recommended in the FCA report dated 09/03/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/23/2011. | NEVADA STATE CAPITOL | 9918 | Admin | PubWorks | B&G | Carson City | 1870 | 54778 | 2021-02-02 | Immediate to Two Years | Currently Critical | 1 | 3000
0235INT2 | INTERIOR FINISHES | 0235 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | NEVADA STATE CAPITOL | 9918 | Admin | PubWorks | B&G | Carson City | 1870 | 54778 | 2021-02-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 273890
0235SFT5 | GUARD REPAIRS | 0235 | The guardrail on the 2nd floor of the building around the stairwell is older and does not meet code for safety. Being a historic building, the guard is only required to meet a level of protection for a means of egress. It does not meet this level of protection because it is not at least 42 inches in height. This project provides for attaching a new top rail to the existing guard in order to raise the overall height to more than 42 inches. The new rail will be designed and built to match the style of the existing historic guard. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. Section 1003.1 of the 2006 International Existing Building Code and section 1013.2 of the 2006 International Building Code were used as a reference for this project. | NEVADA STATE CAPITOL | 9918 | Admin | PubWorks | B&G | Carson City | 1870 | 54778 | 2021-02-02 | Immediate to Two Years | Currently Critical | 1 | 5000
0235SFT1 | GFCI DUPLEX OUTLET REPLACEMENTS | 0235 | There are two outlets in the Governor's Office kitchen which are not GFCI. One is above the countertop near the sink and the other is in the cabinet directly under the sink. These outlets should be changed to GFCI type outlets per the NEC. This project would provide for the purchase and installation of two GFCI duplex outlets. | NEVADA STATE CAPITOL | 9918 | Admin | PubWorks | B&G | Carson City | 1870 | 54778 | 2021-02-02 | Immediate to Two Years | Currently Critical | 1 | 600
0235INT4 | BASEMENT CARPET REPLACEMENT | 0235 | The carpet in the staff offices in the Basement is showing signs of extreme wear. It is recommended that the carpet be replaced with heavy duty commercial grade carpet in the next 2-3 years. | NEVADA STATE CAPITOL | 9918 | Admin | PubWorks | B&G | Carson City | 1870 | 54778 | 2021-02-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2800
0235SFT4 | INTERIOR STAIR HANDRAIL REPLACEMENT | 0235 | There are two exit stairwells on the west side of the building. The handrails are older and do not meet code for safety or accessibility. The gripping surfaces are incorrect, they do not have proper returns, they are on only one side of the stairway and they are not continuous from the top to bottom landings. This project recommends the installation of handrails on both sides of the stairs, with proper gripping surfaces, returns and supports. Removal and disposal of the existing railing is included. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. NRS 338.180, 2006 IBC Chapter 10, Section 1012, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | NEVADA STATE CAPITOL | 9918 | Admin | PubWorks | B&G | Carson City | 1870 | 54778 | 2021-02-02 | Immediate to Two Years | Currently Critical | 1 | 15000
0235ADA1 | ADA ACCESSIBLE COUNTER | 0235 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The security desk near the entrance to the building has a counter for the public to approach which does not meet current codes. Section 7.2 of the Americans with Disabilities Act Accessible Guidelines (ADAAG) states that the counter must have a portion which is at least 36" in length with a maximum height of 36" above the finish floor. This project will provide an accessible counter space in accordance with this requirement. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. This project or a portion thereof was previously recommended in the FCA report dated 09/03/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/23/2011. | NEVADA STATE CAPITOL | 9918 | Admin | PubWorks | B&G | Carson City | 1870 | 54778 | 2021-02-02 | Immediate to Two Years | Currently Critical | 1 | 1500
0235PLM1 | WATER HEATER REPLACEMENT | 0235 | There is a 100 gallon natural gas-fired water heater in the basement mechanical room. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 3-4 years. It is recommended that a new natural gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | NEVADA STATE CAPITOL | 9918 | Admin | PubWorks | B&G | Carson City | 1870 | 54778 | 2021-02-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0235ELE2 | ELEVATOR UPGRADES | 0235 | The elevator was built in 1979 and requires periodic repairs. It is currently due for a refurbishment of all mechanical parts to maintain the elevator in a safe working order. The maintenance staff has acquired a bid for the work in the amount of $190,000 which also includes a regenerative elevator drive that generates its own electricity. | NEVADA STATE CAPITOL | 9918 | Admin | PubWorks | B&G | Carson City | 1870 | 54778 | 2021-02-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 190000
0235ADA4 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0235 | This building contains a water fountain on each floor. The basement floor and 1st floor drinking fountains are not accessible. The 2006 IBC Section 1109.5 states where a water fountain is provided, at least half should be accessible. This project would provide funding for the purchase and installation of two new accessible fixed high/ low ADA drinking fountains for the basement and 1st floor. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | NEVADA STATE CAPITOL | 9918 | Admin | PubWorks | B&G | Carson City | 1870 | 54778 | 2021-02-02 | Immediate to Two Years | Currently Critical | 1 | 8000
3113SFT2 | FIRE ALARM REPAIRS | 3113 | This building is equipped with an automatic fire detection and alarm system that needs to be inspected and cleaned before occupancy. This project would provide for a complete system inspection by a qualified inspector, cleaning of the smoke and heat detectors and replacement of 5 detectors. | AGRICULTURE LAS VEGAS | 9793 | Agricult | Agri |  | Las Vegas | 1978 | 16154 | 2012-04-10 | Immediate to Two Years | Currently Critical | 1 | 3000
3113EXT2 | ROOF REPLACEMENT | 3113 | The roof on this building was in poor to fair condition at the time of the survey. The roof is probably original to the building dating back to the late 1970's. The built-up roofing system has had at least one coating applied over the top and there is evidence of past leaks. Natural gas lines are supported by damaged wood members and the HVAC units are not on proper curbs. The flat roof has signs of cracking and the sealant is in poor condition. The clay tile areas have broken tiles throughout and mastic repairs around vents and roof scuppers. Numerous apparent leaks were observed on the interior ceiling. It is recommended that this building be re-roofed in the next 1-2 years to prevent further damage to the building. | AGRICULTURE LAS VEGAS | 9793 | Agricult | Agri |  | Las Vegas | 1978 | 16154 | 2012-04-10 | Immediate to Two Years | Currently Critical | 1 | 193848
3113ENR2 | EXTERIOR INSULATION & FINISH SYSTEM | 3113 | The building is constructed with exterior unisulated CMU / slumpstone masonry and does not meet today's energy code requirements. This project would provide for the installation of an exterior insulation and finish system (EIFS) over the exterior walls. | AGRICULTURE LAS VEGAS | 9793 | Agricult | Agri |  | Las Vegas | 1978 | 16154 | 2012-04-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 105001
3113ADA3 | ADA RESTROOM UPGRADE | 3113 | The building does not have fully compliant ADA accessible restrooms. The existing restrooms do not meet all of the Americans with Disabilities Act (ADA) requirements. A complete retrofit may be necessary. This project would provide funding for remodeling the Men's and Women's restrooms into ADA compliant restrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | AGRICULTURE LAS VEGAS | 9793 | Agricult | Agri |  | Las Vegas | 1978 | 16154 | 2012-04-10 | Immediate to Two Years | Currently Critical | 1 | 30000
3113ENR1 | LIGHTING UPGRADE | 3113 | The existing lighting fixtures in the warehouse are the older T-12 fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed for additional savings. Any electrical wiring upgrades are not included in this estimate. | AGRICULTURE LAS VEGAS | 9793 | Agricult | Agri |  | Las Vegas | 1978 | 16154 | 2012-04-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9750
3113ADA1 | ADA SIGNAGE | 3113 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | AGRICULTURE LAS VEGAS | 9793 | Agricult | Agri |  | Las Vegas | 1978 | 16154 | 2012-04-10 | Immediate to Two Years | Currently Critical | 1 | 1500
3113INT1 | INTERIOR FINISHES | 3113 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | AGRICULTURE LAS VEGAS | 9793 | Agricult | Agri |  | Las Vegas | 1978 | 16154 | 2012-04-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 80770
3113ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 3113 | This building contains a water fountain near the main entrance. The 2006 IBC Section 1109.5 states where a water fountain is provided, at least half should be accessible. This project would provide funding for the purchase and installation of a new accessible fixed high/ low ADA drinking fountain. | AGRICULTURE LAS VEGAS | 9793 | Agricult | Agri |  | Las Vegas | 1978 | 16154 | 2012-04-10 | Immediate to Two Years | Currently Critical | 1 | 4000
3113INT3 | JANITOR'S CLOSET REPAIRS | 3113 | The mop sink in the Janitor's Closet is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | AGRICULTURE LAS VEGAS | 9793 | Agricult | Agri |  | Las Vegas | 1978 | 16154 | 2012-04-10 | Immediate to Two Years | Currently Critical | 1 | 1400
3113INT4 | CEILING TILE REPLACEMENT | 3113 | There are several areas of stained and / or damaged ceiling tiles in the building. This project would provide for the replacement of stained or missing tiles throughout the building. It is recommended that this project be executed after the roof is replaced. | AGRICULTURE LAS VEGAS | 9793 | Agricult | Agri |  | Las Vegas | 1978 | 16154 | 2012-04-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
3113HVA1 | REPLACE COOLING MEDIA | 3113 | There are 4 roof mounted evaporative cooling units on the warehouse roof which are missing the cooling media. This project would provide for new cooling media to be installed. | AGRICULTURE LAS VEGAS | 9793 | Agricult | Agri |  | Las Vegas | 1978 | 16154 | 2012-04-10 | Immediate to Two Years | Currently Critical | 1 | 2000
3113ADA4 | ACCESSIBLE ENTRANCE MODIFICATIONS | 3113 | The current entrance to the building is on the north elevation and is not ADA compliant. There were no accessible entrances to the building at the time of the survey. The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. In order to comply with the ADA, it is recommended to modify the building and site to provide a compliant entrance from the ADA parking spaces and from the public right of way. The 2006 IBC, ICC/ANSI A117.1 - 2003 and the most current version of the Americans With Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. This project should be implemented concurrently with the ADA PARKING SPACES AND PATH OF TRAVEL project. | AGRICULTURE LAS VEGAS | 9793 | Agricult | Agri |  | Las Vegas | 1978 | 16154 | 2012-04-10 | Immediate to Two Years | Currently Critical | 1 | 100000
3113SFT1 | FIRE SUPPRESSION SYSTEM INSTALLATION | 3113 | The building is a B occupancy per the 2006 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 or R-2 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. This estimate is based on a $9.00/SF for sprinkler installation and a lump sum of $20,000 for connection to water supply including backflow prevention. | AGRICULTURE LAS VEGAS | 9793 | Agricult | Agri |  | Las Vegas | 1978 | 16154 | 2012-04-10 | Immediate to Two Years | Currently Critical | 1 | 165386
3113PLM3 | WATER HEATER / ROOF ACCESS MODIFICATIONS | 3113 | The existing gas fired water heater appears to not have proper combustion air and is larger that needed. The closet where it is located used to contain the roof access ladder which has been modified and no longer is usable. This project would provide for the removal of the gas fired water heater, installation of a gas fired tankless water heater and a new roof access ladder including all required gypsum board repairs and painting. | AGRICULTURE LAS VEGAS | 9793 | Agricult | Agri |  | Las Vegas | 1978 | 16154 | 2012-04-10 | Immediate to Two Years | Currently Critical | 1 | 9500
9793ENV1 | ABANDON FUEL TANK MONITORING SYSTEM | 9793 | An underground fuel storage tank was removed in 1993 and minor contamination was discovered. The contamination was remediated but an electronic monitoring system and passive venting system were installed and are still in place. The systems were never properly abandoned after the issuance of the closure letter by the Clark County Health District. This project would provide for abandoning the systems including the passive venting system and the monitoring wells. | AGRICULTURE LAS VEGAS SITE | 9793 | Agricult | Agri |  | Las Vegas | 1978 |  | 2012-04-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8500
9793SIT1 | SLURRY SEAL ASPHALT PAVING | 9793 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site-wide including the access road and parking areas. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 75,000 square feet of asphalt area was used to generate this estimate. | AGRICULTURE LAS VEGAS SITE | 9793 | Agricult | Agri |  | Las Vegas | 1978 |  | 2012-04-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 56250
9793ADA1 | ADA PARKING SPACES AND PATH OF TRAVEL | 9793 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. Concrete parking spaces, a passenger loading area and path of travel to the accessible entrance are necessary to comply with ADA accessibility requirements. This project would provide for two ADA parking spaces including a concrete van accessible ADA parking and loading space and walkway to the existing sidewalk. This will require regrading, installing P.C. concrete, striping, signage and any other necessary upgrades. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. This project should be implemented concurrently with the ACCESSIBLE ENTRANCE MODIFICATIONS project. | AGRICULTURE LAS VEGAS SITE | 9793 | Agricult | Agri |  | Las Vegas | 1978 |  | 2012-04-10 | Immediate to Two Years | Currently Critical | 1 | 25000
3113INT2 | CARPET REPLACEMENT | 3113 | The carpet in the warehouse offices is showing signs of extreme wear. It is recommended that the carpet be replaced with heavy duty commercial grade carpet in the next 2-3 years. 1,000 square feet of floor area was used to generate this estimate. | AGRICULTURE LAS VEGAS | 9793 | Agricult | Agri |  | Las Vegas | 1978 | 16154 | 2012-04-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
9793SIT2 | LANDSCAPING AND IRRIGATION UPGRADE | 9793 | The existing landscaping consists of a few plantings, rocks, dirt and old irrigation lines. These features have reached the end of their expected life and should be scheduled for replacement. This project would provide for the removal of the existing plantings and irrigation lines and the purchase and installation of new plants, irrigation lines and hardscape features. | AGRICULTURE LAS VEGAS SITE | 9793 | Agricult | Agri |  | Las Vegas | 1978 |  | 2012-04-10 | Four to Ten Years | Long-Term Needs | 3 | 7500
3113EXT1 | EXTERIOR FINISHES | 3113 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the brick masonry and stucco and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | AGRICULTURE LAS VEGAS | 9793 | Agricult | Agri |  | Las Vegas | 1978 | 16154 | 2012-04-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 80770
9793ENR1 | EXTERIOR SOLAR SITE LIGHTING UPGRADE | 9793 | There are four existing light poles in the parking lot. They are the older metal halide type fixtures and are not energy efficient. This project would provide for the purchase and installation of 4 solar powered LED exterior light fixtures on the existing poles. | AGRICULTURE LAS VEGAS SITE | 9793 | Agricult | Agri |  | Las Vegas | 1978 |  | 2012-04-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 26000
9793SFT1 | EXTERIOR OUTLET REPLACEMENT | 9793 | There is an electrical outlet on the exterior of the building near the front entrance that does not meet code. This outlet should be changed to a GFCI type outlet per the 2005 NEC. This project would provide for the purchase and installation of one GFCI duplex outlet with a weatherproof cover. | AGRICULTURE LAS VEGAS SITE | 9793 | Agricult | Agri |  | Las Vegas | 1978 |  | 2012-04-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 300
2558EXT1 | EXTERIOR FINISHES | 2558 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are repairing damaged stucco fascia areas, painting, and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted, sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. An acrylic paint should be utilized on the stucco areas for durability. | ELKO AGRICULTURE REGIONAL OFFICE | 9822 | Agricult | Agri |  | Elko | 1997 | 5700 | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 39900
2558ADA1 | ADA IMPROVEMENTS | 2558 | The restrooms in the building are not 100% ADA compliant. This project would provide for improvements including but not limited to flush valve relocation and relocation of toilet tissue dispensers and signage. The conference / break room casework is also not 100% ADA compliant. This project would also provide for required modifications to the casework to provide ADA accessibility. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | ELKO AGRICULTURE REGIONAL OFFICE | 9822 | Agricult | Agri |  | Elko | 1997 | 5700 | 2014-07-22 | Immediate to Two Years | Currently Critical | 1 | 3000
2558INT1 | INTERIOR FINISHES | 2558 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. A satin or semi-gloss paint should be utilized in wet areas for durability. | ELKO AGRICULTURE REGIONAL OFFICE | 9822 | Agricult | Agri |  | Elko | 1997 | 5700 | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 28500
2558SFT1 | OVERHEAD COILING DOOR REPAIR | 2558 | The existing power operated overhead coiling door does not operate properly according to staff. This project would provide for required repairs to the door motor and controls as needed. | ELKO AGRICULTURE REGIONAL OFFICE | 9822 | Agricult | Agri |  | Elko | 1997 | 5700 | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
2558ENR1 | LED LIGHTING UPGRADE | 2558 | The majority of the existing lighting in the building is older fluorescent T-8 lamps in recessed fixtures. This project would provide for re-lamping the existing fixtures with LED tubes. This project would result in energy savings. | ELKO AGRICULTURE REGIONAL OFFICE | 9822 | Agricult | Agri |  | Elko | 1997 | 5700 | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 17100
9822SIT2 | AUTOMATIC GATE REPAIR | 9822 | The existing automatic sliding gate has been problematic for years. It sometimes opens and will not close. This project would provide for a new electronic gate motor and wiring to be installed including connections and testing of the new system. | ELKO AGRICULTURE REGIONAL OFFICE SITE | 9822 | Agricult | Agri |  | Elko | 1997 |  | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
9822SIT3 | LANDSCAPING MAINTENANCE | 9822 | The site has some grass areas that are in need of regular maintenance, mowing and trimming. There are also numerous areas of weeds and brush which are in need of removal as they may damage the retaining walls and fencing. This project would provide for regular maintenance of the site including mowing and trimming, weed and brush removal on an annual basis. This is a one time estimate but should be scheduled in the agency's operating budget. A $200 monthly allowance is a recommended amount for budgeting. during the warmer months. | ELKO AGRICULTURE REGIONAL OFFICE SITE | 9822 | Agricult | Agri |  | Elko | 1997 |  | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
9822SIT1 | AC PAVING SEAL - CRACK FILL - REPAIR | 9822 | The existing AC paving on site is due for crack filling, sealing and re-striping. There are also some areas that are alligatoring and in need of removal and replacement. This project would provide for a crack fill and slurry seal as well as repair of damaged AC paving. Striping including ADA accessible parking and loading zones is included in this estimate. This project should be scheduled every 4-5 years based on environmental conditions. | ELKO AGRICULTURE REGIONAL OFFICE SITE | 9822 | Agricult | Agri |  | Elko | 1997 |  | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 42000
1475EXT3 | OVERHEAD DOOR REPLACEMENT | 1475 | There is a 16'x20' overhead door which is damaged and does not function properly. It is original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead door and replacement with a motorized door. | AGRICULTURE WAREHOUSE | 9868 | Agricult | Agri |  | Sparks | 1960 | 1300 | 2014-11-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
1475INT2 | RESTROOM REMODEL | 1475 | The restroom in the building was out of service at the time of the survey. It is original to the building and is due for a complete remodel. This project would provide for a complete remodel of the restroom fixtures, hardware, floor and wall finishes. | AGRICULTURE WAREHOUSE | 9868 | Agricult | Agri |  | Sparks | 1960 | 1300 | 2014-11-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
1475ENR1 | LIGHTING UPGRADE | 1475 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in all areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | AGRICULTURE WAREHOUSE | 9868 | Agricult | Agri |  | Sparks | 1960 | 1300 | 2014-11-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1950
1475PLM2 | WATER HEATER REPLACEMENT | 1475 | There is a 30 gallon gas-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | AGRICULTURE WAREHOUSE | 9868 | Agricult | Agri |  | Sparks | 1960 | 1300 | 2014-11-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
1475EXT2 | EXTERIOR DOOR REPLACEMENT | 1475 | The exterior metal man door is damaged from age and general wear and tear and has reached the end of its expected life. This project would provide for the replacement of the door assembly with a new metal door, frame and hardware. Removal and disposal of the existing door is included in this estimate. | AGRICULTURE WAREHOUSE | 9868 | Agricult | Agri |  | Sparks | 1960 | 1300 | 2014-11-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
1475INT1 | INTERIOR FINISHES | 1475 | The interior finishes are in poor condition. It is recommended to repair the insulation and paint the gypsum board walls at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | AGRICULTURE WAREHOUSE | 9868 | Agricult | Agri |  | Sparks | 1960 | 1300 | 2014-11-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6500
1475EXT1 | EXTERIOR FINISHES | 1475 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | AGRICULTURE WAREHOUSE | 9868 | Agricult | Agri |  | Sparks | 1960 | 1300 | 2014-11-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1300
1475SFT1 | FIRE ALARM SYSTEM INSTALLATION | 1475 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2009 Section 7 and the 2012 International Fire Code. | AGRICULTURE WAREHOUSE | 9868 | Agricult | Agri |  | Sparks | 1960 | 1300 | 2014-11-05 | Immediate to Two Years | Currently Critical | 1 | 5200
1475SFT2 | FIRE EXTINGUISHER INSTALLATION | 1475 | The building does not have a portable fire extinguisher available. International Fire Code Section 906 requires that portable fire extinguishers shall be installed in S occupancies. They shall be provided for employee use and selected and distributed based on the classes of anticipated workplace fires and on the size and degree of hazard which would affect their use. This project would provide funding for the purchase and installation of 2 fire extinguishers, cabinets, and the hardware necessary to install them. | AGRICULTURE WAREHOUSE | 9868 | Agricult | Agri |  | Sparks | 1960 | 1300 | 2014-11-05 | Immediate to Two Years | Currently Critical | 1 | 1000
1475SFT3 | ELECTRICAL UPGRADE | 1475 | This building was constructed before the high demand for electrical services were needed for computers and other electrical devices. As time has progressed, the buildings electrical demand and system has changed. It is utilized to its current maximum potential. The electrical panels and receptacles are at their limit. It is recommended the entire system be upgraded to meet the evolving needs of the building including three-phase power. | AGRICULTURE WAREHOUSE | 9868 | Agricult | Agri |  | Sparks | 1960 | 1300 | 2014-11-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 26000
1475SFT4 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 1475 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. | AGRICULTURE WAREHOUSE | 9868 | Agricult | Agri |  | Sparks | 1960 | 1300 | 2014-11-05 | Immediate to Two Years | Currently Critical | 1 | 4000
2990EXT1 | EXTERIOR FINISHES | 2990 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | CENTRAL PLANT | 9868 | Agricult | Agri |  | Sparks | 2009 | 920 | 2014-11-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4600
2992EXT1 | EXTERIOR FINISHES | 2992 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the translucent panels, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | GREEN HOUSE | 9868 | Agricult | Agri |  | Sparks | 2009 | 1274 | 2014-11-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6370
2989EXT1 | EXTERIOR FINISHES | 2989 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | HEADQUARTERS & LAB | 9868 | Agricult | Agri |  | Sparks | 2009 | 25913 | 2014-11-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 129565
2991EXT1 | EXTERIOR FINISHES | 2991 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | STORAGE/CARPORT BUILDING | 9868 | Agricult | Agri |  | Sparks | 2009 | 7151 | 2014-11-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35755
2991INT1 | INTERIOR FINISHES | 2991 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | STORAGE/CARPORT BUILDING | 9868 | Agricult | Agri |  | Sparks | 2009 | 7151 | 2014-11-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 13650
2989INT1 | INTERIOR FINISHES | 2989 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HEADQUARTERS & LAB | 9868 | Agricult | Agri |  | Sparks | 2009 | 25913 | 2014-11-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 129565
2990INT1 | INTERIOR FINISHES | 2990 | The interior finishes are in fair condition. It is recommended to repair and seal the interior concrete block walls at least once in the 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. | CENTRAL PLANT | 9868 | Agricult | Agri |  | Sparks | 2009 | 920 | 2014-11-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4600
2992INT1 | INTERIOR FINISHES | 2992 | The interior finishes are in fair condition. It is recommended to repair and seal the interior concrete block walls at least once in the 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to sealing, all surfaces should be repaired and prepped. | GREEN HOUSE | 9868 | Agricult | Agri |  | Sparks | 2009 | 1274 | 2014-11-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6370
9868SIT4 | RELOCATE MAIN ENTRY | 9868 | The main entry to the site is very close to the intersection of Galletti Way and Kietzke Lane. This project would relocate the entry south along Galletti to make access in and out of the site safer during heavy traffic. The project would provide new curb and gutter, concrete apron, fencing, and a new gate. This project should be implemented concurrently with the Fence Replacement project. This project or a portion thereof was previously recommended in the FCA report dated 10/28/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/05/2014. | AGRICULTURE HEADQUARTERS OFFICE SITE | 9868 | Agricult | Agri |  | Sparks |  |  | 2014-11-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
9868ADA1 | ADA SIGNAGE & STRIPING | 9868 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The accessible parking spaces and passenger loading areas in front of the Measurement Standards building are missing proper signage and striping to comply with ADA requirements. This project would provide for striping, signage and any other necessary upgrades to the parking space. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | AGRICULTURE HEADQUARTERS OFFICE SITE | 9868 | Agricult | Agri |  | Sparks |  |  | 2014-11-05 | Immediate to Two Years | Currently Critical | 1 | 2500
9868SIT1 | CRACK FILL & SEAL ASPHALT PAVING | 9868 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the paving site wide including access roads and parking areas. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 34,000 square feet of asphalt area was used to generate this estimate. | AGRICULTURE HEADQUARTERS OFFICE SITE | 9868 | Agricult | Agri |  | Sparks |  |  | 2014-11-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20400
9868SIT3 | FENCE REPLACEMENT | 9868 | The majority of the fencing around the Warehouse/ Equipment Yard has failed and is due for replacement. This project recommends the installation of a 6 foot high 6 gauge wire perimeter chain link fence around the entire site with two 14' wide gates with hardware. The cost estimate also includes demolition and disposal of the existing fence. This project should be implemented concurrently with the Relocate Main Entry project. This project or a portion thereof was previously recommended in the FCA report dated 10/28/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/05/2014. | AGRICULTURE HEADQUARTERS OFFICE SITE | 9868 | Agricult | Agri |  | Sparks |  |  | 2014-11-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 45500
2996EXT1 | EXTERIOR FINISHES | 2996 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | PLANT PATHOLOGY/ELECTRICAL | 9868 | Agricult | Agri |  | Sparks | 2009 | 2175 | 2014-11-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10875
2996INT1 | INTERIOR FINISHES | 2996 | The interior finishes are in fair condition. It is recommended to repair and seal the interior concrete block walls at least once in the 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. | PLANT PATHOLOGY/ELECTRICAL | 9868 | Agricult | Agri |  | Sparks | 2009 | 2175 | 2014-11-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10875
0274SFT2 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0274 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. | MEASUREMENT STANDARDS | 9868 | Agricult | Agri |  | Sparks | 1971 | 6622 | 2014-11-05 | Immediate to Two Years | Currently Critical | 1 | 4000
0274EXT2 | EXTERIOR FINISHES | 0274 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | MEASUREMENT STANDARDS | 9868 | Agricult | Agri |  | Sparks | 1971 | 6622 | 2014-11-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 33110
0274INT2 | INTERIOR FINISHES | 0274 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | MEASUREMENT STANDARDS | 9868 | Agricult | Agri |  | Sparks | 1971 | 6622 | 2014-11-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 33110
0274EXT4 | ROOF REPLACEMENT | 0274 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. | MEASUREMENT STANDARDS | 9868 | Agricult | Agri |  | Sparks | 1971 | 6622 | 2014-11-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 78504
0274SFT1 | EXIT SIGN UPGRADE | 0274 | The existing exit signs in this building are older types and should be replaced with new self-illuminated or LED style signs with battery-backed internal systems. IBC - 2012 Chapter 10 was referenced for this project. | MEASUREMENT STANDARDS | 9868 | Agricult | Agri |  | Sparks | 1971 | 6622 | 2014-11-05 | Immediate to Two Years | Currently Critical | 1 | 3150
0274INT3 | EMPLOYEE LOUNGE INSTALLATION | 0274 | The building was not originally equipped with an Employee Lounge for the employees. This project recommends installing cabinets, a sink, GFCI outlets for small appliances and tables and chairs. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. | MEASUREMENT STANDARDS | 9868 | Agricult | Agri |  | Sparks | 1971 | 6622 | 2014-11-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0274PLM2 | WATER HEATER REPLACEMENT | 0274 | There is a 30 gallon gas-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 5-6 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | MEASUREMENT STANDARDS | 9868 | Agricult | Agri |  | Sparks | 1971 | 6622 | 2014-11-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0274EXT3 | EXTERIOR DOOR REPLACEMENT | 0274 | The exterior man doors on the original structure are damaged from age and general wear and tear. This includes the front entrance door and three metal man doors on the east elevation. This project would provide for the replacement of four exterior doors with new metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | MEASUREMENT STANDARDS | 9868 | Agricult | Agri |  | Sparks | 1971 | 6622 | 2014-11-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16000
0274ADA1 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0274 | This building contains a water fountain that is not ADA compliant and is not working. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | MEASUREMENT STANDARDS | 9868 | Agricult | Agri |  | Sparks | 1971 | 6622 | 2014-11-05 | Immediate to Two Years | Currently Critical | 1 | 4000
5015ADA1 | ADA RESTROOM UPGRADE | 5015 | The building does not have an accessible restroom. A complete retrofit is necessary. This project would provide for remodeling the men's and women's restrooms per ADA regulations. Items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | ADMINISTRATION BUILDING | 5010 | Agricult | Agri |  | Reno | 1931 | 6000 | 2018-02-06 | Immediate to Two Years | Currently Critical | 1 | 40000
5010SIT3 | CONCRETE REPAIRS | 5010 | The concrete sidewalks, curbs, stairs and ramps serving the buildings on this site have areas that are deteriorated and failing. In some areas the concrete has heaved or settled and some is pitted and spalling. The stairs and ADA ramp in front of the Main Arena have failing concrete around the handrail supports which poses a significant safety hazard. This project addresses repairs or replacement of existing sidewalks, curbs, stairs and ramps as needed. IBC 2012 and the ICC A117.1 - 2009 were used as a reference for this project. | RENO SPARKS LIVESTOCK EVENTS CTR SITE | 5010 | Agricult | Agri |  | Reno | 0 |  | 2018-02-06 | Immediate to Two Years | Currently Critical | 1 | 50000
5010SIT1 | ASPHALT REPLACEMENT | 5010 | The asphalt in the large parking area on the north side of the site is failing. Extensive block cracking, alligatoring, settling and potholes were observed. It is at least 15 years old and has had minimal maintenance over the years. This project covers the removal and replacement of the existing asphalt for parking and site access. Striping for safety, parking and loading zones is included in this estimate. 600,000 square feet was used to generate this estimate and is based on pulverizing the existing asphalt and reusing it on site. | RENO SPARKS LIVESTOCK EVENTS CTR SITE | 5010 | Agricult | Agri |  | Reno | 0 |  | 2018-02-06 | Immediate to Two Years | Currently Critical | 1 | 1800000
5010EXT1 | EXTERIOR FINISHES - BARNS | 5010 | There are 18 metal barns on the site which are 3,500 s.f. each for a total of 63,000 square feet. It is important to maintain the weather resistance, finish, and appearance of the buildings. This project would provide for protecting the exterior envelope of the buildings excluding the roofs. The work shall include caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended to do the work in the next 3-4 years and to schedule this project on a cyclical basis to maintain the integrity of the structure. | RENO SPARKS LIVESTOCK EVENTS CTR SITE | 5010 | Agricult | Agri |  | Reno | 0 |  | 2018-02-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 141120
5010SIT2 | CRACK FILL & SEAL ASPHALT PAVING | 5010 | The asphalt in the smaller parking areas including the RV parking on the east side of the site was mostly re-done in 2016. It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the paving in these areas including access roads, parking areas and the RV parking area. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 620,000 square feet of asphalt area was used to generate this estimate. | RENO SPARKS LIVESTOCK EVENTS CTR SITE | 5010 | Agricult | Agri |  | Reno | 0 |  | 2018-02-06 | Four to Ten Years | Long-Term Needs | 3 | 620000
5012EXT2 | ROOF REPLACEMENT | 5012 | The single ply and standing seam metal roofs on the structures that make up the Rodeo Arena were in poor condition at the time of the survey. The seams and penetrations have been patched and caulked numerous times but there are still active leaks. It is recommended that these structures be re-roofed in the next 2-3 years. | RODEO ARENA | 5010 | Agricult | Agri |  | Reno | 0 | 65000 | 2018-02-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 420000
5011INT4 | SCOREBOARD REPLACEMENT | 5011 | There is a large scoreboard/ message center mounted to the roof trusses in the center of the arena. The scoreboard is outdated, hard to maintain and is due for replacement. This project recommends removal and disposal of the old scoreboard and purchase and installation of a new scoreboard. | MAIN ARENA | 5010 | Agricult | Agri |  | Reno | 1987 | 124215 | 2018-02-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
5013ELE1 | ELECTRICAL UPGRADE | 5013 | This building was constructed before the high demand for electrical services was needed. As time has progressed, the building’s electrical demand and systems have changed. The electrical panels and receptacles are at their limit. It is recommended to have the entire system upgraded to meet current and future needs. | LIVESTOCK PAVILION | 5010 | Agricult | Agri |  | Reno | 1969 | 30000 | 2018-02-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 300000
5013ELE2 | LIGHTING UPGRADE | 5013 | The existing lighting fixtures in the building are the older metal halide and fluorescent types and are not energy efficient. This project will upgrade the older lighting components to LED’s. This type of lighting will provide better illumination, energy savings and a reduction of normal maintenance. Occupancy sensors will be installed in low occupancy areas for additional savings. | LIVESTOCK PAVILION | 5010 | Agricult | Agri |  | Reno | 1969 | 30000 | 2018-02-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 75000
5013PLM1 | WATER HEATER REPLACEMENT | 5013 | There is a 50 gallon electric water heater in the building that was installed in 2002. The average life span of a water heater is eight to ten years. With the passage of time, this unit is showing signs of wear and should be scheduled for replacement in the next 1-2 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | LIVESTOCK PAVILION | 5010 | Agricult | Agri |  | Reno | 1969 | 30000 | 2018-02-06 | Immediate to Two Years | Currently Critical | 1 | 2000
5013EXT3 | OVERHEAD DOOR REPLACEMENT | 5013 | There are 3 overhead coiling doors which are damaged and do not function properly. 1 door is motorized and the other 2 are manual. Exposure and wind have caused the doors to bend, crack and lose their finish. They are original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the overhead coiling doors and replacement with new overhead coiling doors. | LIVESTOCK PAVILION | 5010 | Agricult | Agri |  | Reno | 1969 | 30000 | 2018-02-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 26880
5013SFT1 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 5013 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention, an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | LIVESTOCK PAVILION | 5010 | Agricult | Agri |  | Reno | 1969 | 30000 | 2018-02-06 | Immediate to Two Years | Currently Critical | 1 | 10000
5013INT1 | INTERIOR FINISHES | 5013 | It is recommended to paint the interior walls at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | LIVESTOCK PAVILION | 5010 | Agricult | Agri |  | Reno | 1969 | 30000 | 2018-02-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 150000
5012INT1 | INTERIOR FINISHES | 5012 | It is recommended to paint the interior walls and ceilings of the buildings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | RODEO ARENA | 5010 | Agricult | Agri |  | Reno | 0 | 65000 | 2018-02-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 250000
5012EXT1 | EXTERIOR FINISHES | 5012 | It is important to maintain the weather resistance, finish, and appearance of the structures that make up the Rodeo Arena. This project would provide for protecting the exterior of the metal buildings and the stands excluding the roofs. The work shall include sanding and painting the wood bleachers and the caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended to do the work in the next 2-3 years and to schedule this project on a cyclical basis to maintain the integrity of the structure. | RODEO ARENA | 5010 | Agricult | Agri |  | Reno | 0 | 65000 | 2018-02-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 325000
5012PLM1 | WATER HEATER REPLACEMENT | 5012 | There are several water heaters in the buildings. The average lifespan of a water heater is eight to ten years. It is recommended that 3 new electric water heaters, seismic straps, braided steel hose, expansion tanks and pans be installed in the next 2-3 years. Removal and disposal of the existing equipment is included in this estimate. | RODEO ARENA | 5010 | Agricult | Agri |  | Reno | 0 | 65000 | 2018-02-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
5012HVA1 | HVAC EQUIPMENT REPLACEMENT | 5012 | The existing HVAC systems consist of unit heaters and window mounted evaporative coolers. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for replacing the HVAC units throughout the Rodeo Arena. | RODEO ARENA | 5010 | Agricult | Agri |  | Reno | 0 | 65000 | 2018-02-06 | Four to Ten Years | Long-Term Needs | 3 | 168000
5013EXT1 | EXTERIOR FINISHES | 5013 | It is important to maintain the weather resistance, finish, and appearance of the building. This project would provide for protecting the exterior envelope of the building excluding the roof. The work shall include painting the CMU walls as well as caulking the windows, flashing, fixtures and all other penetrations. It is recommended to do the work in the next 3-4 years and to schedule this project on a cyclical basis to maintain the integrity of the structure. | LIVESTOCK PAVILION | 5010 | Agricult | Agri |  | Reno | 1969 | 30000 | 2018-02-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 67200
5012ELE2 | LIGHTING UPGRADE | 5012 | The existing lighting fixtures in the facility are the older fluorescent type and are not energy efficient. This project will upgrade the T-12 components to LED’s. This type of lighting will provide better illumination, energy savings and a reduction of normal maintenance. Occupancy sensors will be installed in low occupancy areas for additional savings. | RODEO ARENA | 5010 | Agricult | Agri |  | Reno | 0 | 65000 | 2018-02-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 224000
5013EXT2 | ROOF REPLACEMENT | 5013 | The standing seam metal roof on this building was in poor condition at the time of the survey. The seams and penetrations have been patched and caulked numerous times but there are still active leaks. It is recommended that this building be re-roofed in the next 1-2 years with a new standing seam metal roofing system as well as a new roof hatch and replacement of the skylights. | LIVESTOCK PAVILION | 5010 | Agricult | Agri |  | Reno | 1969 | 30000 | 2018-02-06 | Immediate to Two Years | Currently Critical | 1 | 504000
5012ELE1 | ELECTRICAL UPGRADE | 5012 | This building was constructed before the high demand for electrical services were needed. As time has progressed, the building’s electrical demand and systems have changed. The electrical panels and receptacles are at their limit. It is recommended to have the entire system upgraded to meet current and future needs. | RODEO ARENA | 5010 | Agricult | Agri |  | Reno | 0 | 65000 | 2018-02-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500000
5011INT2 | CEILING SYSTEM REPLACEMENT | 5011 | Several areas of the building have suspended acoustical tile ceiling systems. The t-bar framing is old, bent and rusted in many areas and many ceiling tiles are damaged and stained. This project would provide for the replacement of the suspended acoustical tile ceiling system including the framing, acoustical tile and seismic bracing assemblies. Removal and disposal of the existing ceiling system is included in this estimate. | MAIN ARENA | 5010 | Agricult | Agri |  | Reno | 1987 | 124215 | 2018-02-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 300000
5011SFT1 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 5011 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention, an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MAIN ARENA | 5010 | Agricult | Agri |  | Reno | 1987 | 124215 | 2018-02-06 | Immediate to Two Years | Currently Critical | 1 | 10000
5011EXT1 | EXTERIOR FINISHES | 5011 | It is important to maintain the weather resistance, finish, and appearance of the building. This project would provide for protecting the exterior envelope of the building excluding the roof. The work shall include caulking and sealing the windows, flashing, fixtures and all other penetrations. It is recommended to do the work in the next 3-4 years and to schedule this project on a cyclical basis to maintain the integrity of the structure. | MAIN ARENA | 5010 | Agricult | Agri |  | Reno | 1987 | 124215 | 2018-02-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 278242
5011INT1 | INTERIOR FINISHES | 5011 | It is recommended to paint the interior walls and ceilings of the building at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | MAIN ARENA | 5010 | Agricult | Agri |  | Reno | 1987 | 124215 | 2018-02-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1242150
5011ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 5011 | This building contains water fountains that are not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide for the purchase and installation of four drinking fountains to meet the ADA requirements, one set on each end of the arena. | MAIN ARENA | 5010 | Agricult | Agri |  | Reno | 1987 | 124215 | 2018-02-06 | Immediate to Two Years | Currently Critical | 1 | 8960
5011ELE1 | ELECTRICAL UPGRADE | 5011 | This building was constructed before the high demand for electrical services was needed for control systems, computers and other electrical devices. The electrical system is utilized to its current maximum potential. It is recommended the entire system be upgraded to meet current and future needs. | MAIN ARENA | 5010 | Agricult | Agri |  | Reno | 1987 | 124215 | 2018-02-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2484300
5011EXT2 | ROOF REPLACEMENT | 5011 | The standing seam metal roof on this building was in poor condition at the time of the survey. The seams and penetrations have been patched and caulked numerous times but there are still active leaks. It is recommended that this building be re-roofed in the next 1-2 years with a new standing seam metal roofing system as well as a new roof hatch and replacement of the skylights. | MAIN ARENA | 5010 | Agricult | Agri |  | Reno | 1987 | 124215 | 2018-02-06 | Immediate to Two Years | Currently Critical | 1 | 2086812
5011PLM1 | WATER HEATER REPLACEMENTS | 5011 | There are at least 8 water heaters in the building ranging from 20 gallons to 80 gallons. The average lifespan of a water heater is eight to ten years. All of the units were installed more than 8 years ago. It is recommended that 8 new electric water heaters, seismic straps, braided steel hose, expansion tanks and pans be installed in the next 1-2 years. Removal and disposal of the existing equipment is included in this estimate. | MAIN ARENA | 5010 | Agricult | Agri |  | Reno | 1987 | 124215 | 2018-02-06 | Immediate to Two Years | Currently Critical | 1 | 15000
5011ELE2 | LIGHTING UPGRADE | 5011 | The existing lighting fixtures in the building are the older metal halide and fluorescent type and are not energy efficient. This project will upgrade the metal halide and T-12 components to LED’s. This type of lighting will provide better illumination, energy savings and a reduction of normal maintenance. Occupancy sensors will be installed in low occupancy areas for additional savings. | MAIN ARENA | 5010 | Agricult | Agri |  | Reno | 1987 | 124215 | 2018-02-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 310537
5011ADA1 | ADA RESTROOM UPGRADES | 5011 | There are 6 restrooms in the building with some ADA features, but they are not fully compliant. A partial retrofit is necessary for each restroom. This project would provide for construction of 6 ADA compliant restrooms. These items may include new partitions to provide the required 60" width of the water closet room, new sinks, toilets, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC and the ICC/ANSI A117.1 - 2009 were used as a reference for this project. | MAIN ARENA | 5010 | Agricult | Agri |  | Reno | 1987 | 124215 | 2018-02-06 | Immediate to Two Years | Currently Critical | 1 | 72000
5011HVA1 | HVAC SYSTEM REPLACEMENT | 5011 | There are 24 rooftop make up air units and several small air conditioners and refrigerator compressors that are original to the building. The rooftop units have indirect fired heaters and evaporative cooling. The metal housing for the equipment has been patched numerous times but still leaks. The refrigerator condensers use R-22 refrigerant which is no longer allowed per EPA requirements. The HVAC units around the building have reached the end of their expected and useful life. The pneumatic controls are original to the building and have reached the end of their useful life. This project would provide for the installation of 24 new rooftop packaged HVAC units, a new Direct Digital Control system, cleaning of the existing duct work and grilles and replacing the refrigerator condensers. This project includes removal and disposal of the existing equipment and all required connections to utilities. | MAIN ARENA | 5010 | Agricult | Agri |  | Reno | 1987 | 124215 | 2018-02-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1560000
5012ADA1 | ADA SEATING UPGRADE | 5012 | The Rodeo Arena is open to the public for viewing events. The designated ADA access and seating does not meet current requirements. An additional ADA section is needed. This project would provide for an ADA accessible path of travel and seating area on the north side of the arena and any other necessary ADA upgrades. The 2012 IBC and the ICC A117.1 - 2009 were used as a reference for this project. | RODEO ARENA | 5010 | Agricult | Agri |  | Reno | 0 | 65000 | 2018-02-06 | Immediate to Two Years | Currently Critical | 1 | 35000
5016ADA1 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 5016 | This building contains water fountains that are not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide for the purchase and installation of two drinking fountains to meet the ADA requirements. | EXHIBIT HALL | 5010 | Agricult | Agri |  | Reno | 1968 | 20000 | 2018-02-06 | Immediate to Two Years | Currently Critical | 1 | 8000
5036ELE1 | LIGHTING UPGRADE | 5036 | The existing lighting fixtures in the structure are older high pressure sodium and are not energy efficient. This project will upgrade the fixtures to LED’s. This type of lighting will provide better illumination, energy savings and a reduction of normal maintenance. | OPEN BARN | 5010 | Agricult | Agri |  | Reno | 2005 | 36000 | 2018-02-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 54000
5035PLM1 | WATER HEATER REPLACEMENT | 5035 | There is a 100 gallon gas-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | COMFORT STATION | 5010 | Agricult | Agri |  | Reno | 1987 | 1000 | 2018-02-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6500
5035INT1 | INTERIOR FINISHES | 5035 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | COMFORT STATION | 5010 | Agricult | Agri |  | Reno | 1987 | 1000 | 2018-02-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
5035HVA1 | HVAC EQUIPMENT REPLACEMENT | 5035 | The existing HVAC system consists of a natural gas fired furnace and does not have any cooling equipment. The furnace was installed in 1987 and has reached the end of its life cycle. This project would provide for replacing the furnace and cleaning the ductwork and grilles. | COMFORT STATION | 5010 | Agricult | Agri |  | Reno | 1987 | 1000 | 2018-02-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6720
5035EXT1 | EXTERIOR FINISHES | 5035 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide for protecting the exterior of the building excluding the roof. Included in the cost is caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | COMFORT STATION | 5010 | Agricult | Agri |  | Reno | 1987 | 1000 | 2018-02-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2240
5035ELE1 | LIGHTING UPGRADE | 5035 | The existing lighting fixtures in the building are the older fluorescent type and are not energy efficient. This project will upgrade the T-12 components to LED’s. This type of lighting will provide better illumination, energy savings and a reduction of normal maintenance. Occupancy sensors will be installed in low occupancy areas for additional savings. | COMFORT STATION | 5010 | Agricult | Agri |  | Reno | 1987 | 1000 | 2018-02-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8960
5035ADA1 | ADA RESTROOM UPGRADE | 5035 | The men's and women's restrooms do not meet ADA requirements. The stall has grab bars, but does not have a clear width of 60", there is no under sink protection and some of the appliances are not within the allowable reach range. A partial retrofit is necessary. This project would provide for remodeling the men's and women's restrooms per ADA requirements. Items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC and the ICC A117.1 - 2009 were used as a reference for this project. | COMFORT STATION | 5010 | Agricult | Agri |  | Reno | 1987 | 1000 | 2018-02-06 | Immediate to Two Years | Currently Critical | 1 | 40000
5016EXT1 | EXTERIOR FINISHES | 5016 | It is important to maintain the weather resistance, finish, and appearance of the building. This project would provide for protecting the exterior envelope of the building excluding the roof. The work shall include caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended to do the work in the next 3-4 years and to schedule this project on a cyclical basis to maintain the integrity of the structure. | EXHIBIT HALL | 5010 | Agricult | Agri |  | Reno | 1968 | 20000 | 2018-02-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 44800
5016EXT2 | ROOF REPLACEMENT | 5016 | The standing seam metal roof on this building was in poor condition at the time of the survey. The seams and penetrations have been patched and caulked numerous times but there are still active leaks. It is recommended that this building be re-roofed in the next 1-2 years with a new standing seam metal roofing system. | EXHIBIT HALL | 5010 | Agricult | Agri |  | Reno | 1968 | 20000 | 2018-02-06 | Immediate to Two Years | Currently Critical | 1 | 336000
5016ELE1 | LIGHTING UPGRADE | 5016 | The existing lighting fixtures in the building are the older metal halide and fluorescent types and are not energy efficient. This project will upgrade the older lighting components to LED’s. This type of lighting will provide better illumination, energy savings and a reduction of normal maintenance. Occupancy sensors will be installed in low occupancy areas for additional savings. | EXHIBIT HALL | 5010 | Agricult | Agri |  | Reno | 1968 | 20000 | 2018-02-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
5016SFT1 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 5016 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention, an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | EXHIBIT HALL | 5010 | Agricult | Agri |  | Reno | 1968 | 20000 | 2018-02-06 | Immediate to Two Years | Currently Critical | 1 | 10000
5013HVA1 | HVAC EQUIPMENT REPLACEMENT | 5013 | The existing HVAC system consists of ceiling mounted natural gas radiant heaters, exhaust vents, a natural gas fired furnace for the restrooms and does not have any cooling equipment. The radiant heaters are missing exhaust piping and the large exhaust vents in the roof do not work. This project would provide for replacing the existing heaters and exhaust vents. This project includes removal and disposal of the existing HVAC system and all required connections to utilities. | LIVESTOCK PAVILION | 5010 | Agricult | Agri |  | Reno | 1969 | 30000 | 2018-02-06 | Immediate to Two Years | Currently Critical | 1 | 90000
5016INT1 | INTERIOR FINISHES | 5016 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | EXHIBIT HALL | 5010 | Agricult | Agri |  | Reno | 1968 | 20000 | 2018-02-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 100000
5015ADA3 | ADA ACCESSIBLE PATH OF TRAVEL | 5015 | The ADA provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the office are necessary to comply with ADA accessibility requirements. This project would provide for a concrete van accessible ADA parking and loading space and concrete walkway to the existing sidewalk. This will require regrading, placement of concrete, signage, striping and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. 750 square feet of concrete was used for this estimate. | ADMINISTRATION BUILDING | 5010 | Agricult | Agri |  | Reno | 1931 | 6000 | 2018-02-06 | Immediate to Two Years | Currently Critical | 1 | 30000
5015INT2 | FLOORING REPLACEMENT | 5015 | The carpet in the office areas and the ceramic tile in the shop are showing signs of extreme wear and should be scheduled for replacement in the next 2-3 years. It is recommended to replace the carpet with heavy duty commercial grade carpet. | ADMINISTRATION BUILDING | 5010 | Agricult | Agri |  | Reno | 1931 | 6000 | 2018-02-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19600
5015ADA4 | ADA DOOR & THRESHOLD REPLACEMENT | 5015 | The existing exterior entrance doors and thresholds to the Offices are not accessible. The thresholds are too high and the hardware is not compliant. This project would provide for two new accessible doors and threshold assemblies including removal of the existing door assemblies and installation of the new accessible door assemblies. ADA compliant signage is also included in this project. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | ADMINISTRATION BUILDING | 5010 | Agricult | Agri |  | Reno | 1931 | 6000 | 2018-02-06 | Immediate to Two Years | Currently Critical | 1 | 3000
5010ELE1 | LIGHT POLE FIXTURE UPGRADE | 5010 | There are 27 light poles throughout the site that have 4 lamps each. These fixtures are an older style and not energy efficient. This project would provide for retrofitting the fixtures for LED lamps and the purchase and installation of 108 LED lamps for the light poles. The cost includes the removal and the disposal of the existing lamps and fixtures. | RENO SPARKS LIVESTOCK EVENTS CTR SITE | 5010 | Agricult | Agri |  | Reno | 0 |  | 2018-02-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 162000
5015ADA2 | ADA ACCESSIBLE COUNTER | 5015 | The ADA provides for accessibility to sites and services for people with physical limitations. The lobby at the entrance of the Junior Livestock Show Board Office has a service counter for the public to approach which does not meet current requirements. Section 904.4 of the ADA Standards For Accessible Design states that a portion of the counter surface that is 36" long minimum and 36" high maximum above the finish floor shall be provided. This project will provide an accessible counter space in accordance with this requirement. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | ADMINISTRATION BUILDING | 5010 | Agricult | Agri |  | Reno | 1931 | 6000 | 2018-02-06 | Immediate to Two Years | Currently Critical | 1 | 4500
5015SFT3 | EXIT SIGN AND EGRESS LIGHTING INSTALLATION | 5015 | The building does not have emergency lighting and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC 2012 Chapter 10 was referenced for this project. | ADMINISTRATION BUILDING | 5010 | Agricult | Agri |  | Reno | 1931 | 6000 | 2018-02-06 | Immediate to Two Years | Currently Critical | 1 | 33600
5015SFT2 | FIRE ALARM SYSTEM INSTALLATION | 5015 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2009 Section 7 and the 2012 International Fire Code. | ADMINISTRATION BUILDING | 5010 | Agricult | Agri |  | Reno | 1931 | 6000 | 2018-02-06 | Immediate to Two Years | Currently Critical | 1 | 26880
5015PLM1 | WATER HEATER REPLACEMENT | 5015 | There is a 19 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. This unit was installed in 2015 and should be scheduled for replacement in the next 6-7 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | ADMINISTRATION BUILDING | 5010 | Agricult | Agri |  | Reno | 1931 | 6000 | 2018-02-06 | Four to Ten Years | Long-Term Needs | 3 | 1200
5015EXT1 | EXTERIOR FINISHES | 5015 | It is important to maintain the weather resistance, finish, and appearance of the building. This project would provide for protecting the exterior envelope of the building excluding the roof. The work shall include sanding, priming and painting the existing painted surfaces as well as caulking the windows, flashing, fixtures and all other penetrations. It is recommended to do the work in the next 3-4 years and to schedule this project on a cyclical basis to maintain the integrity of the structure. | ADMINISTRATION BUILDING | 5010 | Agricult | Agri |  | Reno | 1931 | 6000 | 2018-02-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 67200
5015ELE2 | LIGHTING UPGRADE | 5015 | The existing lighting fixtures in the building are the older fluorescent type and are not energy efficient. This project will upgrade the T-12 components to LED’s. This type of lighting will provide better illumination, energy savings and a reduction of normal maintenance. Occupancy sensors will be installed in low occupancy areas for additional savings. | ADMINISTRATION BUILDING | 5010 | Agricult | Agri |  | Reno | 1931 | 6000 | 2018-02-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 53760
5015ELE1 | ELECTRICAL UPGRADE | 5015 | This building was constructed before the high demand for electrical services was needed for computers and other electrical devices. As time has progressed, the building's electrical demand and system has changed. It is utilized to its current maximum potential. The electrical panels and receptacles are at their limit. It is recommended the entire system be upgraded to meet the evolving needs of the building including three-phase power. | ADMINISTRATION BUILDING | 5010 | Agricult | Agri |  | Reno | 1931 | 6000 | 2018-02-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 134400
5014EXT1 | EXTERIOR/ INTERIOR FINISHES | 5014 | It is important to maintain the weather resistance, finish and appearance of the structure. The work shall include sanding, priming and painting the existing painted surfaces. It is recommended to do the work in the next 3-4 years and to schedule this project on a cyclical basis to maintain the integrity of the structure. | CUTTING ARENA | 5010 | Agricult | Agri |  | Reno | 1969 | 10000 | 2018-02-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
5014ELE1 | LIGHTING UPGRADE | 5014 | The existing lighting fixtures in the structure are the older high pressure sodium type and are not energy efficient. This project will upgrade the lighting components to LED’s. This type of lighting will provide better illumination, energy savings and a reduction of normal maintenance. | CUTTING ARENA | 5010 | Agricult | Agri |  | Reno | 1969 | 10000 | 2018-02-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 150000
5016HVA1 | HVAC EQUIPMENT REPLACEMENT | 5016 | There are 4 rooftop HVAC units that are over 15 years old. The rooftop units have indirect fired heaters and evaporative cooling. The metal housing for the equipment has been patched numerous times but still leaks. The HVAC units around the building have reached the end of their expected and useful life. This project would provide for the installation of 4 new rooftop packaged HVAC units, a new Direct Digital Control system and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing equipment and all required connections to utilities. | EXHIBIT HALL | 5010 | Agricult | Agri |  | Reno | 1968 | 20000 | 2018-02-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 200000
5011ELE3 | GENERATOR REPLACEMENT | 5011 | There is a 125 KVA diesel generator on site that has reached the end of its expected life. The generator provides backup power for the building which is a high priority based on the function of the building. This project provides for the purchase and installation of a 125 KVA diesel-engine-driven generator set. This estimate includes removal and disposal of the existing equipment. | MAIN ARENA | 5010 | Agricult | Agri |  | Reno | 1987 | 124215 | 2018-02-06 | Four to Ten Years | Long-Term Needs | 3 | 150000
5011INT3 | FLOORING REPLACEMENT | 5011 | The carpet in the offices and the Doc Bar is showing signs of extreme wear and should be scheduled for replacement in the next 2-3 years. It is recommended that the carpet be replaced with heavy duty commercial grade carpet. | MAIN ARENA | 5010 | Agricult | Agri |  | Reno | 1987 | 124215 | 2018-02-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 156800
5010ADA1 | ADA UPGRADES | 5010 | The ADA provides for accessibility to sites and services for people with physical limitations. Additional concrete parking areas, passenger loading areas and paths of travel to the program areas around the site are necessary to comply with ADA accessibility requirements. There are accessible spaces for the Main Arena and the Exhibit Hall, but there are no accessible spaces for the RV parking area, the barns or the Rodeo Arena. This project would provide for 24 new concrete accessible ADA parking and loading spaces and concrete walkways to the existing sidewalks. This will require regrading, placement of concrete, signage, striping and any other necessary upgrades. IBC 2012 and the ICC A117.1 - 2009 were used as a reference for this project. | RENO SPARKS LIVESTOCK EVENTS CTR SITE | 5010 | Agricult | Agri |  | Reno | 0 |  | 2018-02-06 | Immediate to Two Years | Currently Critical | 1 | 240000
5015INT1 | INTERIOR FINISHES | 5015 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and to schedule this project on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | ADMINISTRATION BUILDING | 5010 | Agricult | Agri |  | Reno | 1931 | 6000 | 2018-02-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 60000
5011INT5 | KITCHEN EQUIPMENT REPLACEMENT | 5011 | There are four concession stands in the building with various types of kitchen equipment in them. Two only have counters, sinks, ice makers and soda fountains. The other two also have refrigerators, freezers, ovens and grills. All of the equipment is old and due for replacement. This project recommends the replacement of the existing kitchen countertops and associated equipment with heavy duty, quality components. The countertops should be constructed of a highly durable product, such as stainless steel. ADA compliance according to IBC - 2012 and ICC A117.1 - 2009 should be incorporated into the design such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. | MAIN ARENA | 5010 | Agricult | Agri |  | Reno | 1987 | 124215 | 2018-02-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 40000
2311SFT5 | PANIC HARDWARE INSTALLATION | 2311 | There is a door at the bottom of the north stairwell that does not have proper exiting hardware on the door. It is recommended that the door be retrofitted with new exiting hardware to ensure the safety of the occupants in the event of a fire. This project would provide for installing panic hardware on the door. | HEROES MEMORIAL ANNEX | 9917 | AttGen | B&G |  | Carson City | 1951 | 6819 | 2021-01-26 | Immediate to Two Years | Currently Critical | 1 | 2000
2311INT2 | INTERIOR FINISHES | 2311 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HEROES MEMORIAL ANNEX | 9917 | AttGen | B&G |  | Carson City | 1951 | 6819 | 2021-01-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 34095
2950ADA1 | ADA SIGNAGE | 2950 | Americans with Disabilities Act (ADA) regulations pertaining to building access, route of travel and restrooms has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances, route of travel inside the building and restrooms. Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 1998 was referenced for this project. | SERVICE CUBE BUILDING | 9917 | AttGen | B&G |  | Carson City | 1994 | 4800 | 2021-01-26 | Immediate to Two Years | Currently Critical | 1 | 900
2311SFT2 | SEISMIC RETROFIT | 2311 | This building is an unreinforced masonry structure which requires seismic strengthening to meet current life safety codes. An initial study was done under CIP 07-M46 which provided detailed recommendations for a seismic retrofit. The planning and design will be requested under CIP 09-P04 and the construction cost will be requested for the 2011 CIP. The estimate is for the construction costs only. This project should coincide with a complete remodel of the interior of the building. | HEROES MEMORIAL ANNEX | 9917 | AttGen | B&G |  | Carson City | 1951 | 6819 | 2021-01-26 | Immediate to Two Years | Currently Critical | 1 | 238665
2311EXT2 | WINDOW REPLACEMENT | 2311 | The windows are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 20 units. Removal and disposal of the existing windows is included in this estimate. | HEROES MEMORIAL ANNEX | 9917 | AttGen | B&G |  | Carson City | 1951 | 6819 | 2021-01-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
2950EXT1 | EXTERIOR FINISHES | 2950 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis to maintain the integrity of the structure. | SERVICE CUBE BUILDING | 9917 | AttGen | B&G |  | Carson City | 1994 | 4800 | 2021-01-26 | Four to Ten Years | Long-Term Needs | 3 | 48000
2950ADA2 | ADA RESTROOM UPGRADE | 2950 | The Men's and Women's designated ADA restrooms do not meet the Americans with Disabilities Act (ADA) regulations. A retrofit is necessary to comply with 2006 IBC Chapter 11, ICC/ANSI A117.1-1998 Sections 603 - 604 and the Americans with Disabilities Act Accessibility Guidelines (ADAAG). Given the current configuration of the restrooms, the work will include modifying the lavatory counter to ensure that there is enough legroom under the counter to comply with ADAAG 4.19. Currently, the counter does not provide a clearance of 29 in. above the finish floor nor does it provide a clearance of 8 in. in depth under the counter. This estimate is for two Men's and two Women's restrooms. The removal and disposal of the old restroom fixtures is included in this estimate. | SERVICE CUBE BUILDING | 9917 | AttGen | B&G |  | Carson City | 1994 | 4800 | 2021-01-26 | Immediate to Two Years | Currently Critical | 1 | 2000
2311EXT1 | EXTERIOR FINISHES | 2311 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis to maintain the integrity of the structure. | HEROES MEMORIAL ANNEX | 9917 | AttGen | B&G |  | Carson City | 1951 | 6819 | 2021-01-26 | Four to Ten Years | Long-Term Needs | 3 | 68190
2950INT1 | INTERIOR FINISHES | 2950 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SERVICE CUBE BUILDING | 9917 | AttGen | B&G |  | Carson City | 1994 | 4800 | 2021-01-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24000
2311SFT4 | REPLACE STAIR HANDRAILS | 2311 | The handrails in several stairwells do not meet code for safety. The gripping surfaces are incorrect, the handrails do not have proper returns and they are not continuous from the top to bottom of the stairs. This project recommends the installation of handrails on both sides of stairwells, with proper returns and supports. IBC - 2006 Chapter 10 - Section 1012 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/09/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/10/2008. | HEROES MEMORIAL ANNEX | 9917 | AttGen | B&G |  | Carson City | 1951 | 6819 | 2021-01-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
2311ENR1 | LIGHTING UPGRADE | 2311 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts to current standards, resulting in increased efficiency and reduced costs associated with illumination. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/09/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/10/2008. | HEROES MEMORIAL ANNEX | 9917 | AttGen | B&G |  | Carson City | 1951 | 6819 | 2021-01-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20457
2311ADA3 | SIGNAGE FOR ADA COMPLIANCE | 2311 | Americans with Disabilities Act (ADA) regulations pertaining to building access, route of travel and restrooms has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances, route of travel inside the building and restrooms. Signage on the second floor should direct occupants to the new ADA Unisex restroom on the first floor. Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 1998 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/09/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/10/2008. | HEROES MEMORIAL ANNEX | 9917 | AttGen | B&G |  | Carson City | 1951 | 6819 | 2021-01-26 | Immediate to Two Years | Currently Critical | 1 | 1800
2311SFT1 | INSTALL EMERGENCY EGRESS LIGHTING | 2311 | There is inadequate emergency egress lighting in the building and the existing lights do not meet current standards. This project would provide for the purchase and installation of emergency egress lighting to provide illumination along the egress route. IBC - 2006 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/09/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/10/2008. | HEROES MEMORIAL ANNEX | 9917 | AttGen | B&G |  | Carson City | 1951 | 6819 | 2021-01-26 | Immediate to Two Years | Currently Critical | 1 | 5000
2311SFT3 | EXIT SIGN UPGRADE | 2311 | The existing exit signs in this building are older types and should be replaced with new self-illuminated or LED style signs with battery-backed internal systems. Additional signs are also needed to ensure a safe escape in case of a fire. IBC - 2006 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/09/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/10/2008. | HEROES MEMORIAL ANNEX | 9917 | AttGen | B&G |  | Carson City | 1951 | 6819 | 2021-01-26 | Immediate to Two Years | Currently Critical | 1 | 6000
9917SIT1 | SITE DRAINAGE PROJECT | 9917 | There are several site drainage problems around the complex including flooding from the street to the West, improper roof drains and window wells without drains. The site is fairly flat and the grading slopes toward the building in several locations, most noticeably at the Heroes Memorial and Heroes Memorial Annex. Several reports of water seeping into the building's basement have been reported over the past few years. Some of the roof drains do not drain to the storm drain system resulting in pooling against the buildings and leaking into the building. There have been reports of water accumulation in several of the window wells on the Attorney General's Office due to drainage problems. This project recommends grading the site, and installing a system of drains, catch basins and storm drain connections to minimize recurring flooding, water movement and accumulations. It would be most beneficial if this project be incorporated with the fence project that is also included in this report. This project or a portion thereof was previously recommended in the FCA report dated 09/09/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/10/2008. | ATTORNEY GENERAL OFFICES COMPLEX | 9917 | AttGen | B&G |  | Carson City | 0 |  | 2021-01-26 | Immediate to Two Years | Currently Critical | 1 | 250000
9917SFT3 | REPLACE STAIR HANDRAILS/ GUARDRAILS | 9917 | The handrails and guardrails at some of the exterior stairs, including the fire escapes, do not meet code for safety or accessibility. The gripping surfaces are incorrect, the handrails do not have proper returns and/or there are improper or missing guardrails. This project recommends the installation of new handrails on both sides of the stairs, with proper guardrails, returns and supports. The rails should be replaced at the Heroes Memorial monument stairs, Heroes Memorial fire escape and the Heroes Memorial Annex fire escape. The 2006 IBC Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/09/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/10/2008. | ATTORNEY GENERAL OFFICES COMPLEX | 9917 | AttGen | B&G |  | Carson City | 0 |  | 2021-01-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 37500
9917SIT3 | FENCE INSTALLATION | 9917 | The west side of the complex between the Attorney General's Office and the Heroes Memorial contains electrical equipment and the backup generator. Portions of the area are not blocked from view from the street and equipment switches and shutoffs are in plain view. This project recommends the installation of a wrought iron fence along the west side of the site, similar in design to the one at the Capitol building to keep unauthorized personnel out, and provide a secure outdoor break area for employees. It would be most beneficial if this project is incorporated with the SITE DRAINAGE project that is also included in this report. This fence could be mounted on a curb or stem wall that would help divert water that comes from the west during occasional flooding. This area has to be lined with sand bags during these floods and a wall type item would help mitigate this issue. The estimate is for 300 linear feet of fencing mounted on a concrete stem wall. This project or a portion thereof was previously recommended in the FCA report dated 09/09/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/10/2008. | ATTORNEY GENERAL OFFICES COMPLEX | 9917 | AttGen | B&G |  | Carson City | 0 |  | 2021-01-26 | Immediate to Two Years | Currently Critical | 1 | 60000
9917SIT5 | SIDEWALK REPLACEMENT | 9917 | The existing sidewalks around the site range from new to poor condition. Some of the sidewalks have deteriorated and are failing. This project addresses removal and replacement of existing sidewalks as needed including those on the North side of the Attorney General's Office, some areas in the rear courtyard and along 2nd street. The sidewalks should include flared curb cuts for site ADA accessibility. | ATTORNEY GENERAL OFFICES COMPLEX | 9917 | AttGen | B&G |  | Carson City | 0 |  | 2021-01-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
9917SIT6 | CRACK FILL AND SEAL ASPHALT PAVING | 9917 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the northwest parking lot within the next 2-3 years. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 9,736 square feet of asphalt area was used to generate this estimate. | ATTORNEY GENERAL OFFICES COMPLEX | 9917 | AttGen | B&G |  | Carson City | 0 |  | 2021-01-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7302
0261PLM1 | MODIFY ROOF DRAIN PLUMBING | 0261 | The majority of the roof drain plumbing system is located inside the building and it exits the building near ground level. The building has decorative spouts mounted to the building exterior that do not do a very good job of draining the water away from the building. These drains also allow the wind to push the drain water back against the building. Poor site drainage causes many problems with buildings such as water infiltration. This project recommends that the drains be modified to deliver the drain water away from the building and that collection drain systems be installed to catch the roof drain water and carry it to the storm drain system. This project would be best served if coupled with the site drainage project located in the site report for this building. This project or a portion thereof was previously recommended in the FCA report dated 09/09/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/10/2008. | FRANKIE SUE DEL PAPA BUILDING | 9917 | AttGen | B&G |  | Carson City | 1920 | 14680 | 2021-01-26 | Immediate to Two Years | Currently Critical | 1 | 30000
0244SFT1 | EXIT SIGN UPGRADE | 0244 | The existing exit signs in this building are older types and should be replaced with new self-illuminated or LED style signs with battery-backed internal systems. Additional signs are also needed to ensure a safe escape in case of a fire. IBC - 2006 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/09/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/10/2008. | HEROES MEMORIAL BUILDING | 9917 | AttGen | B&G |  | Carson City | 1920 | 13992 | 2021-01-26 | Immediate to Two Years | Currently Critical | 1 | 5400
0244STR1 | SEISMIC RETROFIT | 0244 | This building is an unreinforced masonry structure which requires seismic strengthening to meet current life safety codes. An initial study was done under CIP 07-M46 which provided detailed recommendations for a seismic retrofit. The planning and design will be requested under CIP 09-P04and the construction cost will be requested for the 2011 CIP. The estimate is for the construction costs only. This project should coincide with a complete remodel of the interior of the building. | HEROES MEMORIAL BUILDING | 9917 | AttGen | B&G |  | Carson City | 1920 | 13992 | 2021-01-26 | Immediate to Two Years | Currently Critical | 1 | 489720
0244ENR1 | LIGHTING UPGRADE | 0244 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts to current standards, resulting in increased efficiency and reduced costs associated with illumination. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/09/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/10/2008. | HEROES MEMORIAL BUILDING | 9917 | AttGen | B&G |  | Carson City | 1920 | 13992 | 2021-01-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 41976
0244ADA2 | SIGNAGE FOR ADA COMPLIANCE | 0244 | Americans with Disabilities Act (ADA) regulations pertaining to building access, route of travel and restrooms has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances, route of travel inside the building and restrooms. Signage on the second floor should direct occupants to the new ADA Unisex restroom on the first floor. Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 1998 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/09/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/10/2008. | HEROES MEMORIAL BUILDING | 9917 | AttGen | B&G |  | Carson City | 1920 | 13992 | 2021-01-26 | Immediate to Two Years | Currently Critical | 1 | 1800
0306INT2 | INTERIOR FINISHES | 0306 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | ATTORNEY GENERAL'S OFFICE | 9917 | AttGen | B&G |  | Carson City | 1937 | 23100 | 2021-01-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 115500
0261INT1 | INTERIOR FINISHES | 0261 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | FRANKIE SUE DEL PAPA BUILDING | 9917 | AttGen | B&G |  | Carson City | 1920 | 14680 | 2021-01-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 73400
0261EXT2 | EXTERIOR ARCHITRAVE REPAIR | 0261 | It is important to maintain the finish, weather resistance and appearance of the building. There is visible damage to the finish on the architrave section of the entablature. This project recommends work to repair the substrate and finish at this area in order to maintain the building in good, weather tight condition. | FRANKIE SUE DEL PAPA BUILDING | 9917 | AttGen | B&G |  | Carson City | 1920 | 14680 | 2021-01-26 | Immediate to Two Years | Currently Critical | 1 | 1500
0306ADA2 | SIGNAGE FOR ADA COMPLIANCE | 0306 | Americans with Disabilities Act (ADA) regulations pertaining to building access, route of travel and restrooms has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances, route of travel inside the building and restrooms. Signage on the second floor should direct occupants to the new ADA Unisex restroom on the first floor. Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 1998 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/09/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/10/2008. | ATTORNEY GENERAL'S OFFICE | 9917 | AttGen | B&G |  | Carson City | 1937 | 23100 | 2021-01-26 | Immediate to Two Years | Currently Critical | 1 | 3000
0306ADA3 | REPLACE STAIR HANDRAILS | 0306 | The handrails in several stairwells do not meet code for safety or accessibility. The gripping surfaces are incorrect, the handrails do not have proper returns and they are not continuous from the top to bottom of the stairs. The east stairwell near the main entrance has an overhead hazard at the cane detection area under the stairs. This project recommends the installation of handrails on both sides of stairwells, with proper returns and supports as well as installing a barrier under the stairs. IBC - 2006 Section 1012 and ADAAG 4.4.2 were referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/09/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/10/2008. | ATTORNEY GENERAL'S OFFICE | 9917 | AttGen | B&G |  | Carson City | 1937 | 23100 | 2021-01-26 | Immediate to Two Years | Currently Critical | 1 | 35000
0306SFT4 | INSTALL MAGNETIC DOOR HOLDERS | 0306 | There are doors in the AG's office which have been propped open. In the event of a fire or other emergency, these doors would remain open, creating a possible hazard. This project recommends the installation of magnetic door holders, with closers, tied into the fire alarm, which would hold the doors open. In the event of a fire, the alarm would release the doors, allowing them to close. This applies to the one hour doors into the corridors. This project or a portion thereof was previously recommended in the FCA report dated 09/09/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/10/2008. | ATTORNEY GENERAL'S OFFICE | 9917 | AttGen | B&G |  | Carson City | 1937 | 23100 | 2021-01-26 | Immediate to Two Years | Currently Critical | 1 | 20000
0306SFT1 | INSTALL EMERGENCY EGRESS LIGHTING | 0306 | There is inadequate emergency egress lighting in the building and the existing lights do not meet current standards. This project would provide for the purchase and installation of emergency egress lighting to provide illumination along the egress route. IBC - 2006 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/09/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/10/2008. | ATTORNEY GENERAL'S OFFICE | 9917 | AttGen | B&G |  | Carson City | 1937 | 23100 | 2021-01-26 | Immediate to Two Years | Currently Critical | 1 | 3000
0306ENR1 | LIGHTING UPGRADE | 0306 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts to current standards, resulting in increased efficiency and reduced costs associated with illumination. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/09/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/10/2008. | ATTORNEY GENERAL'S OFFICE | 9917 | AttGen | B&G |  | Carson City | 1937 | 23100 | 2021-01-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 69300
0244SFT3 | REPLACE INTERIOR STAIR HANDRAILS | 0244 | The handrails in several stairwells do not meet code for safety. The gripping surfaces are incorrect, the handrails do not have proper returns and they are not continuous from the top to bottom of the stairs. This project recommends the installation of handrails on both sides of stairwells, with proper returns and supports. IBC - 2006 Section 1012 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/09/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/10/2008. | HEROES MEMORIAL BUILDING | 9917 | AttGen | B&G |  | Carson City | 1920 | 13992 | 2021-01-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0306EXT1 | EXTERIOR FINISHES | 0306 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis to maintain the integrity of the structure. | ATTORNEY GENERAL'S OFFICE | 9917 | AttGen | B&G |  | Carson City | 1937 | 23100 | 2021-01-26 | Four to Ten Years | Long-Term Needs | 3 | 231000
0306SFT2 | EXIT SIGN UPGRADE | 0306 | The existing exit signs in this building are older types and should be replaced with new self-illuminated or LED style signs with battery-backed internal systems. Additional signs are also needed to ensure a safe escape in case of a fire. IBC - 2006 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/09/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/10/2008. | ATTORNEY GENERAL'S OFFICE | 9917 | AttGen | B&G |  | Carson City | 1937 | 23100 | 2021-01-26 | Immediate to Two Years | Currently Critical | 1 | 3000
0261EXT1 | EXTERIOR FINISHES | 0261 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, masonry sealing, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis to maintain the integrity of the structure. | FRANKIE SUE DEL PAPA BUILDING | 9917 | AttGen | B&G |  | Carson City | 1920 | 14680 | 2021-01-26 | Four to Ten Years | Long-Term Needs | 3 | 146800
0244SFT5 | INSTALL MAGNETIC DOOR HOLDERS | 0244 | There are doors in the building which have been propped open. In the event of a fire or other emergency, these doors would remain open, creating a possible hazard. This project recommends the installation of magnetic door holders, with closers, tied into the fire alarm, which would hold the doors open. In the event of a fire, the alarm would release the doors, allowing them to close. This project or a portion thereof was previously recommended in the FCA report dated 09/09/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/10/2008. | HEROES MEMORIAL BUILDING | 9917 | AttGen | B&G |  | Carson City | 1920 | 13992 | 2021-01-26 | Immediate to Two Years | Currently Critical | 1 | 20000
0244SFT6 | PANIC HARDWARE INSTALLATION | 0244 | There are two doors along the fire exit path that do not have panic hardware. It is recommended that the doors be retrofitted with panic hardware to ensure the safety of the occupants in the event of a fire. This project would provide for installing panic hardware on two exit doors. | HEROES MEMORIAL BUILDING | 9917 | AttGen | B&G |  | Carson City | 1920 | 13992 | 2021-01-26 | Immediate to Two Years | Currently Critical | 1 | 2000
0244EXT3 | EXTERIOR FINISHES | 0244 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, masonry sealing, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis to maintain the integrity of the structure. | HEROES MEMORIAL BUILDING | 9917 | AttGen | B&G |  | Carson City | 1920 | 13992 | 2021-01-26 | Four to Ten Years | Long-Term Needs | 3 | 139920
0244INT2 | INTERIOR FINISHES | 0244 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HEROES MEMORIAL BUILDING | 9917 | AttGen | B&G |  | Carson City | 1920 | 13992 | 2021-01-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 69960
0244INT3 | JANITORS CLOSET REPAIRS | 0244 | The mop sinks in the Janitor Closets are mounted adjacent to gypsum board and are showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. Typical of two Janitor Closets. | HEROES MEMORIAL BUILDING | 9917 | AttGen | B&G |  | Carson City | 1920 | 13992 | 2021-01-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2800
0244INT4 | REPAIR MARBLE FLOORING | 0244 | The marble flooring at the entry area is damaged as well as the door threshold adjacent to the marble. Some of the marble tile is completely missing and some is cracked and will continue deteriorating. The damaged area is near a wood door threshold that is deteriorating which has probably contributed to the marble becoming damaged. This project would provide for removing damaged materials and replacing them with new matching marble and a new door threshold. | HEROES MEMORIAL BUILDING | 9917 | AttGen | B&G |  | Carson City | 1920 | 13992 | 2021-01-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0244SFT2 | INSTALL EMERGENCY EGRESS LIGHTING | 0244 | There is inadequate emergency egress lighting in the building and the existing lights do not meet current standards. This project would provide for the purchase and installation of emergency egress lighting to provide illumination along the egress route. IBC - 2006 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/09/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/10/2008. | HEROES MEMORIAL BUILDING | 9917 | AttGen | B&G |  | Carson City | 1920 | 13992 | 2021-01-26 | Immediate to Two Years | Currently Critical | 1 | 5400
0244EXT1 | WINDOW REPLACEMENT | 0244 | The exterior windows appear to be original to the building. They are single pane, not energy efficient and the wood is in very poor condition. Many windows are no longer operational and have been screwed shut. This project recommends replacing the windows with Pella Monumental Clad Commercial Architect "Classic" model, to match the windows installed in the Frankie Sue Del Papa Building at the opposite end of the block. Costs were developed from information provided by the manufacturer's representative. This project or a portion thereof was previously recommended in the FCA report dated 09/09/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/10/2008. | HEROES MEMORIAL BUILDING | 9917 | AttGen | B&G |  | Carson City | 1920 | 13992 | 2021-01-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 150000
0306PLM1 | FOUNTAIN PUMP REPLACEMENT | 0306 | There is a decorative fountain in front of the building that is no longer operating. The water pump has reached the end of its expected life and is due for replacement. It is recommended to replace the pump with a new 1/2 H.P. fountain water pump. This project includes removal and disposal of the existing pump and all required connections to utilities. | ATTORNEY GENERAL'S OFFICE | 9917 | AttGen | B&G |  | Carson City | 1937 | 23100 | 2021-01-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
9969SIT1 | REPAIR AND RESEAL ASPHALT PARKING AREAS | 9969 | The existing paving is in good condition. Climate and constant use will accelerate deterioration. For proper maintenance it is recommended the entire parking area and driveway be resealed and re-striped. This type of maintenance will extend the life of the asphalt. | THREE LAKES VALLEY NDF CON. CAMP SITE | 9969 | CNR | Forestry |  | Indian Springs |  |  | 2001-12-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3089.9999
9969ADA1 | ADA PARKING STRIPING AND SIGN | 9969 | The accessible parking area striping is fading, and is becoming difficult to identify. The area also does not have a sign designating the parking space as accessible. CABO/ANSI A117.1 - 1992 Section 4.6.2 states, "...accessible parking spaces shall be identified by a sign showing the international symbol of accessibility..." The area should be re-striped and complying signage installed. | THREE LAKES VALLEY NDF CON. CAMP SITE | 9969 | CNR | Forestry |  | Indian Springs |  |  | 2001-12-01 | Immediate to Two Years | Currently Critical | 1 | 791.2824
0864INT1 | INTERIOR FINISHES | 0864 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next four to six years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | NDF OFFICE/SHOPS | 9969 | CNR | Forestry |  | Indian Springs | 1988 | 7050 | 2001-12-01 | Four to Ten Years | Long-Term Needs | 3 | 15256.4185
0864ADA1 | ADA REMODEL | 0864 | The office is open to the public, and the building does not fully comply with the Americans with Disabilities Act (ADA) regulations. A retrofit is necessary to comply with CABO/ANSI A117.1-1992 Sections 4.15 - 4.20 and 1997 UBC Chapter 11. | NDF OFFICE/SHOPS | 9969 | CNR | Forestry |  | Indian Springs | 1988 | 7050 | 2001-12-01 | Immediate to Two Years | Currently Critical | 1 | 10762.2477
0864ELE1 | LIGHTING UPGRADE | 0864 | Existing building lighting fixtures, T-12s, are older fluorescent types and not energy efficient. This project will upgrade lighting fixtures to T-8 lamps with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. | NDF OFFICE/SHOPS | 9969 | CNR | Forestry |  | Indian Springs | 1988 | 7050 | 2001-12-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 13690.4624
0864SFT2 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0864 | The existing exit signs in this building are older types and should be replaced with new self-illuminated or LED style signs with battery-backed internal systems. Emergency exit lighting should be installed and/or replaced to provide illumination along the egress route. | NDF OFFICE/SHOPS | 9969 | CNR | Forestry |  | Indian Springs | 1988 | 7050 | 2001-12-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11475.8824
0864SFT1 | FIRE ALARM SYSTEM UPGRADE | 0864 | This building is equipped with an automatic fire detection and alarm system, but the system is antiquated. It is recommended that the fire detection and alarm system be upgraded. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements. | NDF OFFICE/SHOPS | 9969 | CNR | Forestry |  | Indian Springs | 1988 | 7050 | 2001-12-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12047.6658
2007INT3 | INTERIOR FINISHES | 2007 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | NDF ADMINISTRATION BUILDING | 9984 | CNR | Forestry |  | Carson City | 1994 | 1875 | 2008-05-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9375
2007EXT2 | EXTERIOR FINISHES | 2007 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | NDF ADMINISTRATION BUILDING | 9984 | CNR | Forestry |  | Carson City | 1994 | 1875 | 2008-05-12 | Four to Ten Years | Long-Term Needs | 3 | 18750
2007HVA1 | EVAPORATIVE COOLER REPLACEMENT | 2007 | This building is cooled by two evaporative coolers, one on grade on the north side and one on the roof. This equipment will reach the end of its expected life in the next 5 to 6 years and should be scheduled for replacement in that time frame. The estimate includes removal and disposal of the existing equipment. | NDF ADMINISTRATION BUILDING | 9984 | CNR | Forestry |  | Carson City | 1994 | 1875 | 2008-05-12 | Four to Ten Years | Long-Term Needs | 3 | 8000
2007EXT1 | REPLACE ROOF | 2007 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. The extreme temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next two to four years with a 50 year asphalt composition roofing shingle and new underlayments. This project or a portion thereof was previously recommended in the FCA report dated 8/22/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/12/2008. | NDF ADMINISTRATION BUILDING | 9984 | CNR | Forestry |  | Carson City | 1994 | 1875 | 2008-05-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18750
1581SEC1 | WINDOW REPLACEMENT | 1581 | The rear exit door has a wire glass window that is broken. This project would provide funding for the removal and replacement of the wire glass window. This project or a portion there of was previously recommended in the FCA report dated 9/29/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/17/2013. | NDF ADMINISTRATION OFFICE | 9973 | CNR | Forestry |  | Carlin | 1988 | 3544 | 2013-09-17 | Immediate to Two Years | Currently Critical | 1 | 500
1581ADA2 | SIGNAGE FOR ADA COMPLIANCE | 1581 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with these criteria. This project would provide funding for the purchase and installation of new signage to meet the criteria for ADA. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 09/19/2000 and 9/29/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/17/2013. | NDF ADMINISTRATION OFFICE | 9973 | CNR | Forestry |  | Carlin | 1988 | 3544 | 2013-09-17 | Immediate to Two Years | Currently Critical | 1 | 2000
1581ENR2 | REPLACE WATER HEATER | 1581 | The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear. It is recommended that a new gas fired water heater be installed for more efficient use of energy. This estimate includes: 100 feet of gas pipe, fittings, couplers, bracing and labor for installation. This project or a portion there of was previously recommended in the FCA report dated 09/19/2000 and 9/29/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date 09/17/2013. | NDF ADMINISTRATION OFFICE | 9973 | CNR | Forestry |  | Carlin | 1988 | 3544 | 2013-09-17 | Immediate to Two Years | Currently Critical | 1 | 2750
1581ADA4 | INSTALL LEVER ACTION DOOR HANDLES | 1581 | The existing door handles in the building are older round type and do not meet the ADA requirements for grasping. This project would provide for new lever action door hardware to be installed on all doors. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 09/19/2000 and 9/29/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/17/2013. | NDF ADMINISTRATION OFFICE | 9973 | CNR | Forestry |  | Carlin | 1988 | 3544 | 2013-09-17 | Immediate to Two Years | Currently Critical | 1 | 3000
1581ADA5 | ACCESSIBLE BUILDING ENTRANCE | 1581 | The building has a ramp and a step leading into the main entrance. This configuration does not meet the requirements for ADA Accessibility This project would provide funding for an accessible concrete ramp, including upper and lower landing areas, handrails, curbing, and replacement of the door hardware and threshold for ADA compliance. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 9/29/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 9/17/2013. | NDF ADMINISTRATION OFFICE | 9973 | CNR | Forestry |  | Carlin | 1988 | 3544 | 2013-09-17 | Immediate to Two Years | Currently Critical | 1 | 15000
1581SFT2 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 1581 | The existing exit signs in this building are non-illuminated or the older type style and should be replaced with new self-illuminated or LED style signs with a battery-backup. Emergency exit lighting should be installed and/or replaced to provide illumination along the egress route. This project would provide for 3 emergency lights and three exit signs including required electrical connections and installation. This project or a portion there of was previously recommended in the FCA report dated 09/19/2000 and 9/29/2005. It has been amended accordingly to reflect conditions observed during the recent survey date of 09/17/2013. | NDF ADMINISTRATION OFFICE | 9973 | CNR | Forestry |  | Carlin | 1988 | 3544 | 2013-09-17 | Immediate to Two Years | Currently Critical | 1 | 3000
1581ADA1 | ADA RESTROOM REMODEL | 1581 | A restroom is present in this building. It does not meet the Americans with Disabilities Act (ADA) regulations. A retrofit is necessary to comply with ADA accessibility. This project would provide funding for construction of a unisex ADA restroom. These items may include new sinks, toilets, urinals, partitions, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 09/19/2000 and 9/29/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/17/2013. | NDF ADMINISTRATION OFFICE | 9973 | CNR | Forestry |  | Carlin | 1988 | 3544 | 2013-09-17 | Immediate to Two Years | Currently Critical | 1 | 25000
1581INT1 | INTERIOR FINISHES | 1581 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next four to six years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA report dated 09/19/2000 and 9/29/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/17/2013. | NDF ADMINISTRATION OFFICE | 9973 | CNR | Forestry |  | Carlin | 1988 | 3544 | 2013-09-17 | Four to Ten Years | Long-Term Needs | 3 | 8860
1581ADA3 | ACCESSIBLE COUNTERTOP | 1581 | The plastic laminate countertop at the public information window in the building does not meet ADA requirements. This project addresses removal and replacement of the plastic laminate countertop. This will bring the reception counter into conformance with ADA requirements. The project includes the removal of the countertop, casework modifications, replacement of countertop, and gypsum board repair and painting. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 9/29/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 9/17/2013. | NDF ADMINISTRATION OFFICE | 9973 | CNR | Forestry |  | Carlin | 1988 | 3544 | 2013-09-17 | Immediate to Two Years | Currently Critical | 1 | 2000
2154EXT1 | EXTERIOR FINISHES | 2154 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | NDF TOOL SHED | 9973 | CNR | Forestry |  | Carlin | 1997 | 180 | 2013-09-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
2155SFT1 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 2155 | The existing exit signs in this building are non-illuminated and should be replaced with new self-illuminated or LED style signs with a battery-backup. Emergency exit lighting should be installed and/or replaced to provide illumination along the egress route. This project would provide for two emergency lights and one exit sign including required electrical connections and installation. This project or a portion there of was previously recommended in the FCA report dated 09/19/2000 and 9/29/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 9/17/2013. | NDF WOOD SHOP | 9973 | CNR | Forestry |  | Carlin | 1998 | 1050 | 2013-09-17 | Immediate to Two Years | Currently Critical | 1 | 1500
2156INT1 | INTERIOR FINISHES | 2156 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next three to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | NDF SHOP | 9973 | CNR | Forestry |  | Carlin | 1988 | 2692 | 2013-09-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 13460
2156EXT1 | EXTERIOR FINISHES | 2156 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | NDF SHOP | 9973 | CNR | Forestry |  | Carlin | 1988 | 2692 | 2013-09-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2692
2155EXT1 | EXTERIOR FINISHES | 2155 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | NDF WOOD SHOP | 9973 | CNR | Forestry |  | Carlin | 1998 | 1050 | 2013-09-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1050
2148EXT1 | EXTERIOR FINISHES | 2148 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | NDF CHAIN LINK STORAGE SHED | 9973 | CNR | Forestry |  | Carlin | 1990 | 385 | 2013-09-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
2154ELE1 | ELECTRICAL WIRING | 2154 | The building wiring is a nonmetallic sheathed cable. Nevada State Public Works Board Adopted Standards requires "All building interior power, telephone, signal and other low voltage wiring (whether plenum-rated or not) shall be installed in raceways" 8.4.1. This project would provide funding to rewire the electrical outlets in raceways. This project or a portion there of was previously recommended in the FCA report dated 9/29/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 9/17/2013. | NDF TOOL SHED | 9973 | CNR | Forestry |  | Carlin | 1997 | 180 | 2013-09-17 | Immediate to Two Years | Currently Critical | 1 | 1500
2549EXT1 | EXTERIOR FINISHES | 2549 | It is important to maintain the finish, weather resistance and appearance of the water tank on a cyclical basis. This project recommends work to protect the exterior tank envelope including sand blasting, painting, staining, or other applied finishes to maintain the tank in good, weather tight condition. | CCC WATER TANK | 9973 | CNR | Forestry |  | Carlin | 1988 |  | 2013-09-17 | Four to Ten Years | Long-Term Needs | 3 | 50000
2149EXT2 | EXTERIOR ELEVATIONS | 2149 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | CUBIE/EUREKA COUNTY STORAGE SHED | 9973 | CNR | Forestry |  | Carlin | 1989 | 385 | 2013-09-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1155
2150SFT1 | SAFETY CABINETS | 2150 | Flammable or combustible liquids in drums or other containers (including flammable aerosols) not exceeding 60 gallons individual capacity and those portable tanks not exceeding 660 gallons individual capacity, shall have a proper storage container, reference OSHA 1910.106 (7) (d). This project will provide one OSHA approved storage cabinet for gasoline, aerosol cans, and other flammable items. This project or a portion there of was previously recommended in the FCA report dated 9/29/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 9/17/2013. | NDF PAINT STORAGE SHED | 9973 | CNR | Forestry |  | Carlin | 1995 | 64 | 2013-09-17 | Immediate to Two Years | Currently Critical | 1 | 3000
2150EXT1 | EXTERIOR FINISHES | 2150 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | NDF PAINT STORAGE SHED | 9973 | CNR | Forestry |  | Carlin | 1995 | 64 | 2013-09-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
2151EXT1 | EXTERIOR FINISHES | 2151 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | NDF HERBICIDE STORAGE SHED | 9973 | CNR | Forestry |  | Carlin | 1988 | 48 | 2013-09-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
2152EXT1 | EXTERIOR FINISHES | 2152 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | NDF PROPANE STORAGE SHED | 9973 | CNR | Forestry |  | Carlin | 1988 | 48 | 2013-09-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
2155ENV1 | INSTALL DUST COLLECTION SYSTEM | 2155 | The existing wood working equipment has partial dust collection capacity. In order to reduce the possibility of damage or injury, each piece of equipment should have complete collection capability. This project will provide for the replacement of the existing system and installation of additional capacity to minimize explosion hazard and disruption to production. This project or a portion there of was previously recommended in the FCA report dated 09/19/2000 and 9/29/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 9/17/2013. | NDF WOOD SHOP | 9973 | CNR | Forestry |  | Carlin | 1998 | 1050 | 2013-09-17 | Immediate to Two Years | Currently Critical | 1 | 13000
2107ELE2 | PROVIDE CLEARANCE AT ELECTRICAL PANEL | 2107 | There is an electrical panel in the building which does not have proper clear floor space around it. A metal shelving system is partially blocking the panel. The 2012 IFC section 605.3 states that, "A working space of not less than 30 inches in width, 36 inches in depth and 78 inches in height shall be provided in front of electrical service equipment. Where the electrical service equipment is wider than 30 inches, the working space shall not be less than the width of the equipment. No storage of any materials shall be located within the designated working space." This project would provide funds to relocate the shelving system currently blocking the working space. | ELKO INTERAGENCY DISPATCH CENTER | 9824 | CNR | Forestry |  | Elko | 2000 | 9143 | 2013-09-19 | Immediate to Two Years | Currently Critical | 1 | 250
2323ENV1 | BACKFLOW PREVENTION | 2323 | The existing Lath House structure includes an irrigation system to water the plants and trees. State Health Law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of backsiphonage or backpressure. This project allows for the installation of double check valves or reduced pressure principle backflow preventers as appropriate to the hazard and in appropriate locations near the potential source of contamination. Costs include an above ground vault, and allowance for 200 feet of 1" conduit to provide power for freeze protection. This project or a portion thereof was previously recommended in the FCA reports dated 08/21/2002 and 09/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/19/2013. | NDF LATH HOUSE | 9934 | CNR | Forestry |  | Elko | 1981 | 3000 | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
2323SFT1 | LATH HOUSE REPAIRS | 2323 | The Lath House is deteriorated and requires basic maintenance and some structural repairs. There is earth to wood contact, warping of the boards and dry rot. It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for repairs and painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA reports dated 08/21/2002 and 09/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/19/2013. | NDF LATH HOUSE | 9934 | CNR | Forestry |  | Elko | 1981 | 3000 | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
2107ELE1 | ELECTRICAL UPGRADE, DISPATCH | 2107 | The dispatch areas have a higher electrical demand than the building was designed for. The electrical system is currently utilized to its maximum potential. The electrical panels and receptacles are at their limit and extension cords are being used for permanent power. It is recommended the system be upgraded to meet the evolving needs of the dispatch area. This project or a portion thereof was previously recommended in the FCA report dated 08/19/2002. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/19/2013. | ELKO INTERAGENCY DISPATCH CENTER | 9824 | CNR | Forestry |  | Elko | 2000 | 9143 | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 60000
2107HVA1 | HVAC SYSTEM REPAIRS | 2107 | The HVAC system has received minimal maintenance since the building was commissioned and some repairs and upgrades are necessary. Staff reports that the system does not provide adequate cooling during warmer weather and the temperature controls are inaccurate. The individual thermostats around the building do not display the same temperature as the energy management system. The server and communications rooms are not cooled sufficiently and staff has employed fans and propping doors open for adequate cooling and ventilation. There was at least one heat pump that was inoperable at the time of the survey as well as air filters that had not been replaced recently and clogged screens in the water lines. This project recommends evaluating the HVAC system and performing necessary repairs including re-balancing the system based on current needs. It is also recommended to contract an HVAC maintenance company to service the equipment on a continual basis. This project or a portion thereof was previously recommended in the FCA report dated 08/19/2002. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/19/2013. | ELKO INTERAGENCY DISPATCH CENTER | 9824 | CNR | Forestry |  | Elko | 2000 | 9143 | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12500
2107SFT1 | VISUAL NOTIFICATION UPGRADE, DISPATCH | 2107 | The building has a fire alarm system throughout, but there are no visual notification devices in the dispatch areas. This project recommends replacing several of the annunciators with combination visual/ auditory notification devices in these areas. This project or a portion thereof was previously recommended in the FCA report dated 08/19/2002. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/19/2013. | ELKO INTERAGENCY DISPATCH CENTER | 9824 | CNR | Forestry |  | Elko | 2000 | 9143 | 2013-09-19 | Immediate to Two Years | Currently Critical | 1 | 2500
2107INT1 | INTERIOR FINISHES | 2107 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | ELKO INTERAGENCY DISPATCH CENTER | 9824 | CNR | Forestry |  | Elko | 2000 | 9143 | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 45715
2107ADA3 | ADA SIGNAGE | 2107 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required and that the restroom ADA signs be relocated off of the doors. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | ELKO INTERAGENCY DISPATCH CENTER | 9824 | CNR | Forestry |  | Elko | 2000 | 9143 | 2013-09-19 | Immediate to Two Years | Currently Critical | 1 | 2500
2107INT2 | CARPET REPLACEMENT | 2107 | The carpet in the building is showing signs of extreme wear and should be scheduled for replacement. It is recommended that the carpet be replaced with heavy duty commercial grade carpet in the next 4-5 years. | ELKO INTERAGENCY DISPATCH CENTER | 9824 | CNR | Forestry |  | Elko | 2000 | 9143 | 2013-09-19 | Four to Ten Years | Long-Term Needs | 3 | 56000
2107INT3 | CABINET REPAIRS | 2107 | The cabinetry in the break rooms and the desk at the reception area has been damaged and are delaminating. This project recommends the replacement of the finishes with heavy duty, quality melamine finishes which encapsulates the door, frame, and shelving. This estimate includes disposal of the existing materials. | ELKO INTERAGENCY DISPATCH CENTER | 9824 | CNR | Forestry |  | Elko | 2000 | 9143 | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
2107SFT2 | EGRESS LIGHTING REPLACEMENT | 2107 | The emergency egress lighting design is sufficient, but there are 5 wall packs that are inoperable. This project would provide for the purchase and installation of 5 emergency egress light packs to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. | ELKO INTERAGENCY DISPATCH CENTER | 9824 | CNR | Forestry |  | Elko | 2000 | 9143 | 2013-09-19 | Immediate to Two Years | Currently Critical | 1 | 2500
2107EXT1 | EXTERIOR FINISHES | 2107 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | ELKO INTERAGENCY DISPATCH CENTER | 9824 | CNR | Forestry |  | Elko | 2000 | 9143 | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 45715
2107PLM1 | WATER TREATMENT VENDOR | 2107 | The existing water softening/ chemical water treatment systems in the building have not been properly maintained. This project would provide for a chemical treatment program including an updated chemicals control system, service and employee training provided by a qualified water treatment vendor. The annual maintenance fee charged by the water treatment vendor would be determined after an investigation of the water system is complete. | ELKO INTERAGENCY DISPATCH CENTER | 9824 | CNR | Forestry |  | Elko | 2000 | 9143 | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
9934PLM1 | SANITARY SEWER LINE REPLACEMENT | 9934 | The sanitary sewer line leading from the Shop to the Office is failing and should be scheduled for replacement. The pipe is not sloped properly which causes backups and clogging. In cold temperatures, the pipe has frozen and broken at least twice. This project would provide for the complete replacement of the sanitary sewer line from the Shop to the Office. | ELKO NORTHERN REGION 2 NDF HDQS. SITE | 9934 | CNR | Forestry |  | Elko |  |  | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
9934ELE1 | GENERATOR INSTALLATION | 9934 | The site does not have an emergency back-up generator. As an emergency management facility, it is important to have backup power to the buildings. This project would provide for a new diesel powered 150 KVA generator including required connections to utility systems. | ELKO NORTHERN REGION 2 NDF HDQS. SITE | 9934 | CNR | Forestry |  | Elko |  |  | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 75000
9934ADA1 | MEMORIAL TREE GROVE ACCESSIBILITY | 9934 | The site has a public trail system for the Mike P. Jordan Memorial Tree Grove located adjacent to the Lath House. The 36" wide trail consists of 2"x6" wood curbing filled with pea gravel. This area is frequented by the public including school children on field trips. The trail is not accessible and does not meet the criteria for Americans with Disability Act (ADA). This project would provide for the installation of a 2" thick polymer based pavement system for the trail system to provide accessibility through the tree grove. A product under the brand name PolyPavement was used as a pricing guide for this project. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/19/2013. | ELKO NORTHERN REGION 2 NDF HDQS. SITE | 9934 | CNR | Forestry |  | Elko |  |  | 2013-09-19 | Immediate to Two Years | Currently Critical | 1 | 9000
9824SIT2 | TREE TRIMMING | 9824 | The site has trees which are growing up against the structure. The trees move in windy conditions, rubbing the roofs and wall finishes, which can cause damage to the building. The root systems are causing shifting and heaving of foundations and sidewalks, creating unsafe conditions. This lack of maintenance could become a safety issue. This project recommends that these issues be addressed by either trimming or removing trees before additional damage is done. | ELKO INTERAGENCY DISPATCH CENTER SITE | 9824 | CNR | Forestry |  | Elko | 2000 |  | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
9934SIT9 | CRACK FILL & SEAL ASPHALT PAVING | 9934 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the paving site wide including access roads, parking areas and the maintenance yard. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 50,000 square feet of asphalt area was used to generate this estimate. It is recommended that this project coincide with the ADA Parking Space project. | ELKO NORTHERN REGION 2 NDF HDQS. SITE | 9934 | CNR | Forestry |  | Elko |  |  | 2013-09-19 | Four to Ten Years | Long-Term Needs | 3 | 30000
9824SIT1 | CRACK FILL & SEAL ASPHALT PAVING | 9824 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the paving site wide including access roads, parking areas and the heli-tack pad. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 100,000 square feet of asphalt area was used to generate this estimate. | ELKO INTERAGENCY DISPATCH CENTER SITE | 9824 | CNR | Forestry |  | Elko | 2000 |  | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 60000
9934ADA2 | ADA PARKING SPACE | 9934 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The existing ADA parking space does not entirely meet the requirements of the code. This project provides funding to bring the existing ADA parking space up to code including removal of the asphalt and replacement with P.C. concrete, updated signage, re-striping, re-grading and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | ELKO NORTHERN REGION 2 NDF HDQS. SITE | 9934 | CNR | Forestry |  | Elko |  |  | 2013-09-19 | Immediate to Two Years | Currently Critical | 1 | 5000
9934SIT2 | SIDEWALK REPLACEMENT | 9934 | The sidewalks serving the buildings and vehicle storage areas on this site are deteriorated and failing. In some areas cracks wider than four inches have been identified, and there is settling in many locations. The accessible route from the parking space to the entrance of the building is also compromised by the failing concrete. This project addresses removal and replacement of existing sidewalks as needed. 1,200 SF of 4" thick concrete sidewalk was used for this estimate. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA reports dated 08/21/2002 and 09/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/19/2013. | ELKO NORTHERN REGION 2 NDF HDQS. SITE | 9934 | CNR | Forestry |  | Elko |  |  | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
9934SIT8 | WHEEL STOPS | 9934 | The Regional Office building has parking for employees along the west side of the apparatus bay portion of the building. The parking spaces lack wheel stops to prevent vehicles from damaging the structure. This project would provide for the installation of concrete wheel stops along the parking area. This project or a portion thereof was previously recommended in the FCA report dated 09/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/19/2013. | ELKO NORTHERN REGION 2 NDF HDQS. SITE | 9934 | CNR | Forestry |  | Elko |  |  | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
9934SIT7 | SITE BOLLARDS | 9934 | The Regional Office building has three large apparatus bay doors for fire fighting equipment. The paved approach does not have any protection to prevent vehicles from damaging the building. This project would provide for six 8" diameter pipe bollards, filled with concrete at each side of the apparatus bay doors. This project or a portion thereof was previously recommended in the FCA report dated 09/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/19/2013. | ELKO NORTHERN REGION 2 NDF HDQS. SITE | 9934 | CNR | Forestry |  | Elko |  |  | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
9934SIT3 | DRAINAGE UPGRADES | 9934 | The grade across the site does not slope away from the buildings effectively which allows water to infiltrate the buildings to some extent. Water also pools up next to the buildings and damages the exterior finishes and foundations. Sand bags have been used during heavy rains to protect the buildings. This project would create positive flow away from the buildings by regrading, paving and installing additional drainage swales as needed. This project or a portion thereof was previously recommended in the FCA report dated 09/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/19/2013. | ELKO NORTHERN REGION 2 NDF HDQS. SITE | 9934 | CNR | Forestry |  | Elko |  |  | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0619EXT1 | EXTERIOR FINISHES | 0619 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting the metal panels and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended to paint the building in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NDF NORTHERN REGION 2 SHOP | 9934 | CNR | Forestry |  | Elko | 1981 | 4880 | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24400
0620ADA2 | KITCHENETTE REPLACEMENT | 0620 | The sink, faucet and associated cabinets in the hallway are original to the building. This project recommends the replacement of the existing kitchenette with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards For Accessible Design should be incorporated into the design such as providing an accessible sink. This estimate includes disposal of the existing materials. | NDF NORTHERN REGION 2 OFFICE/GARAGE | 9934 | CNR | Forestry |  | Elko | 1980 | 5084 | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0619EXT4 | OVERHEAD DOOR REPLACEMENT | 0619 | There is one 12'x14' and two 10'x10' overhead garage doors which are damaged and do not function properly. Exposure and wind have caused the doors to bend, crack and lose their finish. The springs, rollers and hinges are worn from general wear and tear. They are original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead garage doors and replacement with new manually operated overhead garage doors. | NDF NORTHERN REGION 2 SHOP | 9934 | CNR | Forestry |  | Elko | 1981 | 4880 | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16000
0619INT2 | INTERIOR FINISHES | 0619 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | NDF NORTHERN REGION 2 SHOP | 9934 | CNR | Forestry |  | Elko | 1981 | 4880 | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24400
0619SFT1 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0619 | The building is an H-4 occupancy per the 2012 International Building Code. Pursuant to IBC 903.2.5.1, an automatic sprinkler system shall be installed in Group H occupancies. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. This project or a portion thereof was previously recommended in the FCA reports dated 08/21/2002 and 09/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/19/2013. | NDF NORTHERN REGION 2 SHOP | 9934 | CNR | Forestry |  | Elko | 1981 | 4880 | 2013-09-19 | Immediate to Two Years | Currently Critical | 1 | 68320
0619INT3 | VCT FLOORING REPLACEMENT | 0619 | The VCT (vinyl composite tile) flooring in the office space is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. | NDF NORTHERN REGION 2 SHOP | 9934 | CNR | Forestry |  | Elko | 1981 | 4880 | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
0619INT4 | CONCRETE FLOORING REHABILITATION | 0619 | The concrete flooring in the building has extensive cracking and is due for repairs. This project would provide for crack-filling, patching and sealing the concrete flooring in the building. | NDF NORTHERN REGION 2 SHOP | 9934 | CNR | Forestry |  | Elko | 1981 | 4880 | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 21900
0619SFT7 | FIRE ALARM SYSTEM INSTALLATION | 0619 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2009 Section 7 and the 2012 International Fire Code. | NDF NORTHERN REGION 2 SHOP | 9934 | CNR | Forestry |  | Elko | 1981 | 4880 | 2013-09-19 | Immediate to Two Years | Currently Critical | 1 | 19520
0619SFT8 | SAFETY CABINETS | 0619 | The Shop contains many different paints, stains, oils, vehicle repair fluids, cleaning products and other hazardous products on open shelves and on the floor. This does not meet OSHA standards for hazardous materials containment. This project would provide two hazardous storage containers in the building and install placards on the building exterior in accordance with OSHA 1910.106 (d). | NDF NORTHERN REGION 2 SHOP | 9934 | CNR | Forestry |  | Elko | 1981 | 4880 | 2013-09-19 | Immediate to Two Years | Currently Critical | 1 | 10000
0619ENV4 | SPILL CONTAINMENT | 0619 | The Shop does not have a method for containing spills or leakage from oil drums. This project would add secondary containment pallets for all containers in the building and install placards on the building exterior. | NDF NORTHERN REGION 2 SHOP | 9934 | CNR | Forestry |  | Elko | 1981 | 4880 | 2013-09-19 | Immediate to Two Years | Currently Critical | 1 | 3500
0620INT0 | FLOORING REPLACEMENT | 0620 | The VCT (vinyl composite tile) and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the next 2-3 years. This project or a portion thereof was previously recommended in the FCA reports dated 08/21/2002 and 09/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/19/2013. | NDF NORTHERN REGION 2 OFFICE/GARAGE | 9934 | CNR | Forestry |  | Elko | 1980 | 5084 | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0620INT1 | INTERIOR FINISHES | 0620 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | NDF NORTHERN REGION 2 OFFICE/GARAGE | 9934 | CNR | Forestry |  | Elko | 1980 | 5084 | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25420
0620EXT4 | WINDOW REPLACEMENT | 0620 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 12 units. Removal and disposal of the existing windows is included in this estimate. | NDF NORTHERN REGION 2 OFFICE/GARAGE | 9934 | CNR | Forestry |  | Elko | 1980 | 5084 | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
0620SFT1 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0620 | The building is a B occupancy per the 2012 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 or R-2 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. This project or a portion thereof was previously recommended in the FCA report dated 09/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/19/2013. | NDF NORTHERN REGION 2 OFFICE/GARAGE | 9934 | CNR | Forestry |  | Elko | 1980 | 5084 | 2013-09-19 | Immediate to Two Years | Currently Critical | 1 | 71176
0620EXT1 | EXTERIOR FINISHES | 0620 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NDF NORTHERN REGION 2 OFFICE/GARAGE | 9934 | CNR | Forestry |  | Elko | 1980 | 5084 | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5084
0620SFT2 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0620 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. | NDF NORTHERN REGION 2 OFFICE/GARAGE | 9934 | CNR | Forestry |  | Elko | 1980 | 5084 | 2013-09-19 | Immediate to Two Years | Currently Critical | 1 | 2542
0619EXT6 | COOK SHED DEMOLITION | 0619 | The Shop has a small Cook Shed addition on the north side of the structure. It contains numerous code and safety issues including but not limited to broken windows, broken or missing electrical fixtures, temporary metal and wood flooring, dry rot, cooking and washing dishes without proper equipment or ventilation and no life safety systems. The addition is dilapidated and deteriorating and has reached the end of its useful life. This project would provide funding for the demolition of the addition. | NDF NORTHERN REGION 2 SHOP | 9934 | CNR | Forestry |  | Elko | 1981 | 4880 | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2800
0620ADA1 | ADA RESTROOM REMODEL | 0620 | The building does not have an accessible restroom. The existing restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for remodeling the Men's and Women's restrooms into ADA compliant restrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, exhaust fans, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA reports dated 08/21/2002 and 09/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/19/2013. | NDF NORTHERN REGION 2 OFFICE/GARAGE | 9934 | CNR | Forestry |  | Elko | 1980 | 5084 | 2013-09-19 | Immediate to Two Years | Currently Critical | 1 | 30000
0619ENV2 | RESTROOM REMODEL | 0619 | The restroom in the building is original to the building and in overall poor condition. The finishes, fixtures, toilet, sink and shower are showing signs of wear and deterioration. This project would provide for a complete remodel of the restroom. The removal and disposal of the existing fixtures and finishes is included in this estimate. This project or a portion thereof was previously recommended in the FCA reports dated 08/21/2002 and 09/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/19/2013. | NDF NORTHERN REGION 2 SHOP | 9934 | CNR | Forestry |  | Elko | 1981 | 4880 | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0620EXT2 | EXTERIOR DOOR REPLACEMENT | 0620 | The exterior metal doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the doors with new metal doors, frames and hardware. Removal and disposal of the existing doors is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/19/2013. | NDF NORTHERN REGION 2 OFFICE/GARAGE | 9934 | CNR | Forestry |  | Elko | 1980 | 5084 | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
0620HVA2 | AIR CONDITIONER INSTALLATION | 0620 | The server room is not sufficiently cooled by the existing HVAC system. If the room is too warm, the computer equipment will prematurely age and may fail due to overheating. It is recommended to install an air conditioning system in the room to ensure that the temperature is properly regulated. This project would provide for the purchase and installation of an air conditioner including all required connections to existing utilities. | NDF NORTHERN REGION 2 OFFICE/GARAGE | 9934 | CNR | Forestry |  | Elko | 1980 | 5084 | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0620ADA3 | ADA SIGNAGE | 0620 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | NDF NORTHERN REGION 2 OFFICE/GARAGE | 9934 | CNR | Forestry |  | Elko | 1980 | 5084 | 2013-09-19 | Immediate to Two Years | Currently Critical | 1 | 1500
0620PLM1 | WATER HEATER REPLACEMENT | 0620 | There is a 10 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new on-demand electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | NDF NORTHERN REGION 2 OFFICE/GARAGE | 9934 | CNR | Forestry |  | Elko | 1980 | 5084 | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0620ENV1 | ABANDON SEPTIC TANK | 0620 | The Office building was connected to the city sewer system in 1998 and disconnected from the on-site septic system. There is no record of the existing septic system having been demolished. This project provides funds to pump and fill the old tank in compliance with state health regulations. This project or a portion thereof was previously recommended in the FCA reports dated 08/21/2002 and 09/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/19/2013. | NDF NORTHERN REGION 2 OFFICE/GARAGE | 9934 | CNR | Forestry |  | Elko | 1980 | 5084 | 2013-09-19 | Immediate to Two Years | Currently Critical | 1 | 5000
0620ENR1 | LIGHTING UPGRADE | 0620 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, conference rooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA reports dated 08/21/2002 and 09/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/19/2013. | NDF NORTHERN REGION 2 OFFICE/GARAGE | 9934 | CNR | Forestry |  | Elko | 1980 | 5084 | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12620
0620SFT3 | FIRE ALARM SYSTEM INSTALLATION | 0620 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2009 Section 7 and the 2012 International Fire Code. | NDF NORTHERN REGION 2 OFFICE/GARAGE | 9934 | CNR | Forestry |  | Elko | 1980 | 5084 | 2013-09-19 | Immediate to Two Years | Currently Critical | 1 | 20336
0619EXT2 | ROOF REPLACEMENT | 0619 | The standing seam metal roof on this building was in poor condition at the time of the survey and had active leaks. It is recommended that this building be re-roofed in the next 1-2 years with a new single-ply roofing system which will be installed directly over the existing metal roof. This will allow the roof to qualify for the statewide roofing program warranty and preventative maintenance agreement. | NDF NORTHERN REGION 2 SHOP | 9934 | CNR | Forestry |  | Elko | 1981 | 4880 | 2013-09-19 | Immediate to Two Years | Currently Critical | 1 | 58560
0620ELE1 | MINOR ELECTRICAL REPAIRS | 0620 | The building has several electrical outlets and switches missing covers, extension cords being used to supply electrical power, and nonmetallic sheathed cable being used in the attic. This project would provide funding to replace broken or missing covers, install a dedicated electrical outlet to the computer server and to replace the nonmetallic sheathed cable being used in the attic. This project or a portion thereof was previously recommended in the FCA report dated 09/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/19/2013. | NDF NORTHERN REGION 2 OFFICE/GARAGE | 9934 | CNR | Forestry |  | Elko | 1980 | 5084 | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
0619INT5 | INTERIOR DOOR REPLACEMENT | 0619 | The interior doors in this building are damaged and do not function properly. There are 3 hollow core wood doors and 3 hollow core metal doors. This project would provide for the installation of new metal solid core interior doors including frames, lever action door handles, hardware and paint. Removal and disposal of the existing doors is included in this cost estimate. A total of 6 interior doors was used in this estimate. | NDF NORTHERN REGION 2 SHOP | 9934 | CNR | Forestry |  | Elko | 1981 | 4880 | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
0619EXT5 | CONCRETE APRON REPAIRS | 0619 | The 3 exterior concrete aprons and sidewalks around the building have extensive cracking and are due for repairs. This project would provide for crack-filling, patching and sealing the concrete aprons at the vehicle garage doors and the sidewalks and pads around the building. | NDF NORTHERN REGION 2 SHOP | 9934 | CNR | Forestry |  | Elko | 1981 | 4880 | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
0619ELE1 | ELECTRICAL REPAIRS | 0619 | There are many safety issues throughout the building having to do with electrical fixtures and equipment. There are numerous electrical outlets and switches which are missing covers or are broken, extension cords being used to supply permanent electrical power, the GFCI outlet in the restroom is broken and the exterior outlets are not GFCI protected and are missing covers. This project would provide for repairs and/ or replacement of the damaged electrical outlets and removing extension cords from permanent locations. This project or a portion thereof was previously recommended in the FCA report dated 09/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/19/2013. | NDF NORTHERN REGION 2 SHOP | 9934 | CNR | Forestry |  | Elko | 1981 | 4880 | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
0619HVA1 | RESTROOM EXHAUST FAN | 0619 | The existing exhaust fan in the restroom is original equipment and does not provide adequate ventilation. This project would provide for the removal of the existing exhaust fan assembly and the purchase and installation of a new exhaust fan assembly including connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 09/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/19/2013. | NDF NORTHERN REGION 2 SHOP | 9934 | CNR | Forestry |  | Elko | 1981 | 4880 | 2013-09-19 | Immediate to Two Years | Currently Critical | 1 | 3000
0619HVA2 | HVAC REPLACEMENT | 0619 | The existing HVAC system consists of ceiling mounted heaters and does not have any cooling equipment other than a small wall-mounted air conditioner for the office. The equipment is not energy efficient and has reached the end of its expected and useful life. There is a need for cooling equipment as well to provide a comfortable work environment in the summer. The new system shall be designed to significantly reduce electrical and propane gas usage in order to comply with the 2009 IECC and ASHRAE 90.1 and to reduce utility costs. This project would provide for replacing the existing heaters and installing evaporative coolers for cooling. This project or a portion thereof was previously recommended in the FCA reports dated 08/21/2002 and 09/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/19/2013. | NDF NORTHERN REGION 2 SHOP | 9934 | CNR | Forestry |  | Elko | 1981 | 4880 | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 29280
0620HVA3 | HEATING UPGRADES | 0620 | The radiant heating equipment in the Garage is insufficient for the extreme temperatures in the area. The Garage is uncomfortably cold in the winter. It is recommended to install additional propane-fired heating equipment in the Garage to ensure a comfortable work environment. This project would provide for the purchase and installation of three natural gas fired heaters including all required connections to existing utilities. | NDF NORTHERN REGION 2 OFFICE/GARAGE | 9934 | CNR | Forestry |  | Elko | 1980 | 5084 | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
0619STR1 | STRUCTURAL ASSESSMENT | 0619 | A storage area has been constructed inside of the metal shop building accessed via a wood stair case. The 2003 ICC has a minimum requirement of 125 p.s.f. for light storage in non-residential spaces. There is no record of a CIP project or structural plans for this construction and could be a potential safety issue due to collapse. This project recommends that a licensed engineer perform a structural investigation to assess the load carrying capacity of this area. Future projects would be based on this report. | NDF NORTHERN REGION 2 SHOP | 9934 | CNR | Forestry |  | Elko | 1981 | 4880 | 2013-09-19 | Immediate to Two Years | Currently Critical | 1 | 5000
0619SFT3 | INTERIOR STAIRWAY REPLACEMENT | 0619 | The stairs and handrails between the first floor and the storage mezzanine do not meet the requirements in the 2012 International Building Code sections 1009 and 1012. This project would provide funding to remove and replace the stairway and handrail. This project or a portion thereof was previously recommended in the FCA reports dated 08/21/2002 and 09/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/19/2013. | NDF NORTHERN REGION 2 SHOP | 9934 | CNR | Forestry |  | Elko | 1981 | 4880 | 2013-09-19 | Immediate to Two Years | Currently Critical | 1 | 9000
0619EXT3 | EXTERIOR DOOR REPLACEMENT | 0619 | The 5 exterior wood man doors appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement of the wood doors with new metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | NDF NORTHERN REGION 2 SHOP | 9934 | CNR | Forestry |  | Elko | 1981 | 4880 | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
0619SFT6 | VEHICLE EXHAUST EXTRACTION SYSTEM | 0619 | The Shop Building services and repairs vehicles for use by NDF. There is no exhaust extraction system which removes toxic exhaust fumes. Table 403.7 in the 2012 Uniform Mechanical Code states that "Auto repair rooms where engines are run shall have exhaust systems that directly connect to the engine exhaust and prevent escape of fumes". This project would provide for the purchase and installation of a vehicle exhaust extraction system including, hoses, automatic shut off, electrical connections and roof mounted exhaust fans and equipment as provided by the manufacturer. This project or a portion thereof was previously recommended in the FCA report dated 09/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/19/2013. | NDF NORTHERN REGION 2 SHOP | 9934 | CNR | Forestry |  | Elko | 1981 | 4880 | 2013-09-19 | Immediate to Two Years | Currently Critical | 1 | 50000
0619ENR2 | WINDOW REPLACEMENT | 0619 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 7 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/19/2013. | NDF NORTHERN REGION 2 SHOP | 9934 | CNR | Forestry |  | Elko | 1981 | 4880 | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5250
0619ENR1 | LIGHTING UPGRADE | 0619 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, closets and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA reports dated 08/21/2002 and 09/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/19/2013. | NDF NORTHERN REGION 2 SHOP | 9934 | CNR | Forestry |  | Elko | 1981 | 4880 | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7320
0619ENV3 | GREASE/ SAND INTERCEPTOR INSTALLATION | 0619 | The shop has a wash area for vehicles which drains into the city sewer. There is no evidence that a grease/ sand interceptor is provided. This project recommends installing a grease/ sand interceptor in accordance with state health regulations. This project or a portion thereof was previously recommended in the FCA reports dated 08/21/2002 and 09/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/19/2013. | NDF NORTHERN REGION 2 SHOP | 9934 | CNR | Forestry |  | Elko | 1981 | 4880 | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 22500
0619SFT2 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0619 | The emergency egress lighting is insufficient and the exit signs are made of paper and do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA reports dated 08/21/2002 and 09/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/19/2013. | NDF NORTHERN REGION 2 SHOP | 9934 | CNR | Forestry |  | Elko | 1981 | 4880 | 2013-09-19 | Immediate to Two Years | Currently Critical | 1 | 2440
0619INT1 | INTERIOR LANDING INSTALLATION | 0619 | The west side of the shop has an exit door with an interior landing approximately 6" below the exterior landing. Section 1008.1 of the 2012 IBC describes the requirements for doors including floor elevations and landings. The floor or landing shall be at the same elevation on each side of the door. There is a wood ramp constructed to eliminate the step down but it has created a tripping hazard and does not meet code. This project would provide funding to pour a 3'-0"x3'-0" concrete landing on the interior of the building to eliminate the tripping hazard. This project or a portion thereof was previously recommended in the FCA report dated 09/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/19/2013. | NDF NORTHERN REGION 2 SHOP | 9934 | CNR | Forestry |  | Elko | 1981 | 4880 | 2013-09-19 | Immediate to Two Years | Currently Critical | 1 | 2500
0620EXT3 | GUTTER REPLACEMENT | 0620 | The existing gutters and downspouts on the building are damaged and should be scheduled for replacement. They have numerous joints that have proven impossible to seal against leaks and have been bent and broken over time. The leaking gutters will cause premature deterioration to the building finishes and the site hardscape. This project would replace the existing segmented gutter with seamless gutter and new downspouts. It is recommended to extend the downspouts at least 5'-0" away from the building exterior. | NDF NORTHERN REGION 2 OFFICE/GARAGE | 9934 | CNR | Forestry |  | Elko | 1980 | 5084 | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 17500
2490ADA3 | BREAK ROOM REMODEL | 2490 | The employee lounge does not meet the Americans with Disabilities Act (ADA) requirements. It is recommended to upgrade some of the features of the room for compliance with accessibility standards for employees (Title I). This project would provide funding for construction of an accessible sink and faucet, an accessible space at one of the dining tables and an accessible path of travel throughout the room. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | SIERRA FRONT INTERAGENCY DISPATCH CENTER | 9900 | CNR | Forestry |  | Minden | 1991 | 6500 | 2013-11-12 | Immediate to Two Years | Currently Critical | 1 | 2000
2491EXT2 | FOLD-UP DOOR REPAIRS | 2491 | The large fold-up door on the north side of the Hangar is no longer operating and due for maintenance. The cables are fraying and the pulleys and other hardware are worn. This project would provide for the inspection and maintenance of the door including replacing the cables, greasing the hardware and replacing any other parts as necessary. | SIERRA FRONT INTERAGENCY HANGAR | 9900 | CNR | Forestry |  | Minden | 1991 | 7700 | 2013-11-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
2491HVA2 | EXHAUST FAN REPLACEMENT | 2491 | The existing exhaust fan that serves the restroom on the second floor is original equipment and is not operating. This project would provide for the removal of the existing exhaust fan assembly and the purchase and installation of a new exhaust fan assembly including connections to utilities. | SIERRA FRONT INTERAGENCY HANGAR | 9900 | CNR | Forestry |  | Minden | 1991 | 7700 | 2013-11-12 | Immediate to Two Years | Currently Critical | 1 | 1500
2491INT3 | INTERIOR FINISHES | 2491 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings in the office areas at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 12/14/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/12/2013. | SIERRA FRONT INTERAGENCY HANGAR | 9900 | CNR | Forestry |  | Minden | 1991 | 7700 | 2013-11-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 17000
2491INT1 | CARPET REPLACEMENT | 2491 | The carpet in the building is showing signs of extreme wear and should be scheduled for replacement. It is recommended that the carpet be replaced with heavy duty commercial grade carpet in the next 2-3 years. This project or a portion thereof was previously recommended in the FCA report dated 07/07/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/12/2013. | SIERRA FRONT INTERAGENCY HANGAR | 9900 | CNR | Forestry |  | Minden | 1991 | 7700 | 2013-11-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11900
2491SFT1 | FIRE SPRINKLER SYSTEM UPGRADE | 2491 | The Hangar has had an addition built on the taxiway side of the hangar that did not receive sprinkler protection. Also, a combustible shed roof has been constructed on the East side of the building over the existing emergency generator exhaust and the indoor fuel tank vent. This project would design and install sprinkler protection throughout the building. The cost does not include a possible fire pump or equipment storage building for the facility. This project or a portion thereof was previously recommended in the FCA report dated 12/14/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/12/2013. | SIERRA FRONT INTERAGENCY HANGAR | 9900 | CNR | Forestry |  | Minden | 1991 | 7700 | 2013-11-12 | Immediate to Two Years | Currently Critical | 1 | 25000
2491EXT1 | EXTERIOR FINISHES | 2491 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SIERRA FRONT INTERAGENCY HANGAR | 9900 | CNR | Forestry |  | Minden | 1991 | 7700 | 2013-11-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7700
2490ADA4 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 2490 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | SIERRA FRONT INTERAGENCY DISPATCH CENTER | 9900 | CNR | Forestry |  | Minden | 1991 | 6500 | 2013-11-12 | Immediate to Two Years | Currently Critical | 1 | 4000
2491ELE1 | ELECTRICAL UPGRADE | 2491 | This building was constructed before the high demand for electrical services were needed for computers, mechanical equipment and tools and other electrical devices. As time has progressed, the buildings electrical demand and system has changed. It is utilized to its current maximum potential. The electrical panels and receptacles are at their limit. It is recommended the entire system be upgraded to meet the evolving needs of the building including three-phase power. This project or a portion thereof was previously recommended in the FCA report dated 12/14/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/12/2013. | SIERRA FRONT INTERAGENCY HANGAR | 9900 | CNR | Forestry |  | Minden | 1991 | 7700 | 2013-11-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 77000
2490ELE2 | ATTIC LIGHTING INSTALLATION | 2490 | The building has HVAC equipment in the attic that requires maintenance. Section 210.70(C) of the 2012 Uniform Mechanical Code states that attics containing equipment requiring servicing, at least one lighting outlet containing a switch or controlled by a wall switch shall be installed in such places. This project would add permanent lighting in the attic to support maintenance. This project or a portion thereof was previously recommended in the FCA report dated 12/14/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/12/2013. | SIERRA FRONT INTERAGENCY DISPATCH CENTER | 9900 | CNR | Forestry |  | Minden | 1991 | 6500 | 2013-11-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3500
2490PLM3 | WATER HEATER REPLACEMENT | 2490 | There is a 100 gallon gas-fired water heater in the building that was installed in 1991. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | SIERRA FRONT INTERAGENCY DISPATCH CENTER | 9900 | CNR | Forestry |  | Minden | 1991 | 6500 | 2013-11-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
2490SEC1 | SECURITY SYSTEM INSTALLATION | 2490 | The building does not have a security system. This project recommends video surveillance, motion detection, door switches, access control and related items be installed and interfaced with the fire alarm. | SIERRA FRONT INTERAGENCY DISPATCH CENTER | 9900 | CNR | Forestry |  | Minden | 1991 | 6500 | 2013-11-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 75000
2490ENR1 | OCCUPANCY SENSOR INSTALLATION | 2490 | There are no occupancy sensors installed in the building to control lighting. It is recommended to install sensors in order to reduce energy costs. Occupancy sensors will be installed in restrooms, conference rooms, utility rooms and other low occupancy areas for additional savings. This project provides for purchase and installation of 10 sensors. | SIERRA FRONT INTERAGENCY DISPATCH CENTER | 9900 | CNR | Forestry |  | Minden | 1991 | 6500 | 2013-11-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
2490HVA1 | HVAC REPLACEMENT | 2490 | The HVAC system was installed in 1991 and is original to the building. It consists of a natural gas-fired boiler and chiller system with fan coil units in the attic. The system is not energy efficient and has reached the end of its expected and useful life. This project would provide for installation of a new HVAC system and cleaning of the existing duct work and grilles. The new system shall be designed to significantly reduce electrical and natural gas usage in order to comply with the 2009 IECC and ASHRAE 90.1 and to reduce utility costs. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 12/14/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/12/2013. | SIERRA FRONT INTERAGENCY DISPATCH CENTER | 9900 | CNR | Forestry |  | Minden | 1991 | 6500 | 2013-11-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 97500
2490INT5 | KITCHENETTE REPLACEMENT | 2490 | The small kitchenette for the sleeping quarters is in fair to poor condition. The cabinets and equipment are showing signs of general wear and tear and are approaching the end of their expected life. The sink and refrigerator are no longer operating. This project recommends the replacement of the existing kitchen cabinets, countertops, fixtures and equipment with mid range, high quality components. | SIERRA FRONT INTERAGENCY DISPATCH CENTER | 9900 | CNR | Forestry |  | Minden | 1991 | 6500 | 2013-11-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8500
2490ADA2 | ADA ENTRANCE REPAIRS | 2490 | The main ADA entrance is no longer compliant possibly due to the concrete settling and causing the elevation change into the building to exceed the limits. This project would provide for removing the concrete in front of the door and installing new concrete within the accessible limits to approach the entrance door. ADA compliant signage is also included in this project. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | SIERRA FRONT INTERAGENCY DISPATCH CENTER | 9900 | CNR | Forestry |  | Minden | 1991 | 6500 | 2013-11-12 | Immediate to Two Years | Currently Critical | 1 | 5500
2490ELE3 | ELECTRICAL UPGRADE | 2490 | This building was constructed before the high demand for electrical services were needed for computers and other electrical devices. As time has progressed, the buildings electrical demand and system has changed. It is utilized to its current maximum potential. The electrical panels and receptacles are at their limit and several of the exterior lighting fixtures are no longer operating. It is recommended the entire system be upgraded to meet the evolving needs of the building including repairing the exterior lighting. This project or a portion thereof was previously recommended in the FCA report dated 12/14/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/12/2013. | SIERRA FRONT INTERAGENCY DISPATCH CENTER | 9900 | CNR | Forestry |  | Minden | 1991 | 6500 | 2013-11-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 130000
2490INT2 | INTERIOR FINISHES | 2490 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 12/14/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/12/2013. | SIERRA FRONT INTERAGENCY DISPATCH CENTER | 9900 | CNR | Forestry |  | Minden | 1991 | 6500 | 2013-11-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 32500
2490EXT5 | ATTIC ACCESS DOOR REPLACEMENT | 2490 | The north east attic access door has a broken hinge and the lock is not operational. This project would replace the door and hardware. In addition, the project would install a barrel bolt on the roof access hatch for security. This project or a portion thereof was previously recommended in the FCA report dated 12/14/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/12/2013. | SIERRA FRONT INTERAGENCY DISPATCH CENTER | 9900 | CNR | Forestry |  | Minden | 1991 | 6500 | 2013-11-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
2490EXT2 | EXTERIOR FINISHES | 2490 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SIERRA FRONT INTERAGENCY DISPATCH CENTER | 9900 | CNR | Forestry |  | Minden | 1991 | 6500 | 2013-11-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 32500
2490SIT5 | PATIO UPGRADES | 2490 | The patio on the west side of the building is due for upgrades to protect the integrity of the building. The patio is not sloped away from the building allowing water to pool up next to the building, infiltrate the windows and damage the concrete foundation walls. In cold weather, the water freezes at the entrance door and is a slipping hazard. A temporary ramp has been installed at the entrance door which is not compliant with the building code. There is a roof drain that terminates near the entrance and contributes to the problems. This project would create positive flow away from the building by removing the existing concrete, regrading, installing French drains as needed, installing a new concrete patio and extending the roof drains away from the building. The new patio elevation should meet the threshold of the entrance door and allow the temporary ramp to be removed. | SIERRA FRONT INTERAGENCY DISPATCH CENTER | 9900 | CNR | Forestry |  | Minden | 1991 | 6500 | 2013-11-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35000
2490INT4 | JANITORS CLOSET REPAIRS | 2490 | The mop sink in the Janitors Closet is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | SIERRA FRONT INTERAGENCY DISPATCH CENTER | 9900 | CNR | Forestry |  | Minden | 1991 | 6500 | 2013-11-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
2490INT1 | FLOORING REPLACEMENT | 2490 | The carpet and floor tiles in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new heavy duty commercial grade carpet and padded carpet tiles for the raised floor in the Dispatch area in the next 2-3 years. This project excludes porcelain floor tile in restrooms. This project or a portion thereof was previously recommended in the FCA report dated 12/14/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/12/2013. | SIERRA FRONT INTERAGENCY DISPATCH CENTER | 9900 | CNR | Forestry |  | Minden | 1991 | 6500 | 2013-11-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 49500
9900ENV1 | ABOVE GROUND FUEL TANK UPGRADES | 9900 | The existing above ground fuel tanks are located on a concrete slab with no curbs or proper drains to contain spills, no lighting and the emergency shut-off switch is in the wrong building. This project would install a concrete curb around the tanks to prevent soil contamination, a drain with a sand/ oil separator, outdoor lighting around the tanks and provisions to relocate the emergency shut-off switch from the Wildlife hangar to the Forestry hangar. | SIERRA FRONT INTERAGENCY DISPATCH CENTER | 9900 | CNR | Forestry |  | Minden | 0 |  | 2013-11-12 | Immediate to Two Years | Currently Critical | 1 | 31000
9900SIT3 | SITE BOLLARDS | 9900 | There is a filling station on the helicopter apron to distribute water or fire retardant. It is not protected by concrete bollards and has been backed into at least once. This area is in need of bollards to protect the filling station equipment. This project would provide funding for 8 - eight inch diameter bollards to be located on each corner of the filling station. | SIERRA FRONT INTERAGENCY DISPATCH CENTER | 9900 | CNR | Forestry |  | Minden | 0 |  | 2013-11-12 | Immediate to Two Years | Currently Critical | 1 | 4000
9900SIT2 | EXTERIOR SOLAR SITE LIGHTING INSTALLATION | 9900 | There is very little site lighting for the access road, parking area and around the buildings which is a security and safety concern. This project would provide for the installation of 10 solar powered LED exterior light fixtures, 20 foot tall poles and 30" diameter raised concrete bases. This installation will eliminate the need for trenching and electrical connections. | SIERRA FRONT INTERAGENCY DISPATCH CENTER | 9900 | CNR | Forestry |  | Minden | 0 |  | 2013-11-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 65000
9900SIT1 | SLURRY SEAL ASPHALT PAVING | 9900 | It is important to maintain the asphalt concrete paving on the site. This project would provide for crack filling and slurry sealing of the paving site wide including access roads, parking areas and the helicopter apron. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 250,000 square feet of asphalt area was used to generate this estimate. | SIERRA FRONT INTERAGENCY DISPATCH CENTER | 9900 | CNR | Forestry |  | Minden | 0 |  | 2013-11-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 187500
9900SIT4 | PUMP-OUT LIFT STATION | 9900 | The sanitary sewer lift station is clogged with dirt submerging the pumps. This project would pump-out and clean the lift station. It is recommended that this project be scheduled on a cyclical basis based on usage. This project or a portion thereof was previously recommended in the FCA report dated 12/14/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/12/2013. | SIERRA FRONT INTERAGENCY DISPATCH CENTER | 9900 | CNR | Forestry |  | Minden | 0 |  | 2013-11-12 | Immediate to Two Years | Currently Critical | 1 | 1500
9900PLM1 | IRRIGATION SYSTEM REPLACEMENT | 9900 | The existing landscape irrigation lines throughout the site are reaching the end of their expected life and should be scheduled for replacement. This project would provide for the removal of the existing irrigation lines and the purchase and installation of new lines. 4,000 linear feet was used to generate this estimate. | SIERRA FRONT INTERAGENCY DISPATCH CENTER | 9900 | CNR | Forestry |  | Minden | 0 |  | 2013-11-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
1989INT1 | INTERIOR FINISHES | 1989 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 10/12/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | WAREHOUSE/SHOP | 9878 | CNR | Forestry |  | Las Vegas | 2000 | 4500 | 2014-01-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 13500
2033EXT3 | ROOF REPLACEMENT | 2033 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. Repairs have been made recently as shingles have broken or blown off in the wind. The wood eaves have lost their finish and the wood has dried out. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayments. Additional costs are provided to replace the wood eaves. This estimate includes removal and disposal of the old roofing. | NDF/STATE PARKS OFFICE BUILDING | 9878 | CNR | Forestry |  | Las Vegas | 2000 | 5974 | 2014-01-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 56000
1989ELE2 | ENCAPSULATE GROUNDING WIRE | 1989 | There is a copper grounding wire in the north west corner of the warehouse that is laying on the floor and exposed. The maintenance staff was unsure of where the wire came from and what its purpose is. The wire should be encapsulated in conduit and terminated near the wall for safety. This project would provide for a licensed electrician to encapsulate and terminate the wire properly and determine what its purpose is. | WAREHOUSE/SHOP | 9878 | CNR | Forestry |  | Las Vegas | 2000 | 4500 | 2014-01-30 | Immediate to Two Years | Currently Critical | 1 | 1500
1989SFT1 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 1989 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 10/12/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | WAREHOUSE/SHOP | 9878 | CNR | Forestry |  | Las Vegas | 2000 | 4500 | 2014-01-30 | Immediate to Two Years | Currently Critical | 1 | 4000
2033PLM2 | WATER HEATER REPLACEMENT | 2033 | There is a 40 gallon gas-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | NDF/STATE PARKS OFFICE BUILDING | 9878 | CNR | Forestry |  | Las Vegas | 2000 | 5974 | 2014-01-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
2033LGT2 | CARPET REPLACEMENT | 2033 | The carpet in the building is showing signs of extreme wear and should be scheduled for replacement. It is recommended that the carpet be replaced with heavy duty commercial grade carpet in the next 2-3 years. This project or a portion thereof was previously recommended in the FCA report dated 10/12/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | NDF/STATE PARKS OFFICE BUILDING | 9878 | CNR | Forestry |  | Las Vegas | 2000 | 5974 | 2014-01-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 31500
2033INT1 | INTERIOR FINISHES | 2033 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 10/12/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | NDF/STATE PARKS OFFICE BUILDING | 9878 | CNR | Forestry |  | Las Vegas | 2000 | 5974 | 2014-01-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 28000
2033EXT1 | EXTERIOR FINISHES | 2033 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 10/12/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | NDF/STATE PARKS OFFICE BUILDING | 9878 | CNR | Forestry |  | Las Vegas | 2000 | 5974 | 2014-01-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 28000
2033HVA1 | AIR CONDITIONER INSTALLATION | 2033 | The server room is not sufficiently cooled by the existing HVAC system. At the time of the survey, a ceiling tile was removed in the room to increase circulation. If the room is too warm, the computer equipment will prematurely age and may fail due to overheating. It is recommended to install an air conditioning system in the room to ensure that the temperature is properly regulated. This project would provide for the purchase and installation of an air conditioner including all required connections to existing utilities. | NDF/STATE PARKS OFFICE BUILDING | 9878 | CNR | Forestry |  | Las Vegas | 2000 | 5974 | 2014-01-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
2033EXT2 | RAIN GUTTER INSTALLATION | 2033 | The building does not have gutters or downspouts to control the runoff from the roof. The water currently sheet drains off the roof causing extensive erosion to the dirt planters around the foundation. This will eventually lead to failure of the foundation undermining the integrity of the entire structure. This project would provide funding for the installation of a seamless gutter and downspout system for the building. This project or a portion thereof was previously recommended in the FCA report dated 10/12/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | NDF/STATE PARKS OFFICE BUILDING | 9878 | CNR | Forestry |  | Las Vegas | 2000 | 5974 | 2014-01-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
1989EXT2 | ROOF REPLACEMENT | 1989 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2000. It is recommended that this building be re-roofed in the next 5-6 years to be consistent with the roofing program and the end of the warranty period. | WAREHOUSE/SHOP | 9878 | CNR | Forestry |  | Las Vegas | 2000 | 4500 | 2014-01-30 | Four to Ten Years | Long-Term Needs | 3 | 32400
1989EXT1 | EXTERIOR FINISHES | 1989 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 10/12/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | WAREHOUSE/SHOP | 9878 | CNR | Forestry |  | Las Vegas | 2000 | 4500 | 2014-01-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 13500
2033SFT2 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 2033 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 10/12/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | NDF/STATE PARKS OFFICE BUILDING | 9878 | CNR | Forestry |  | Las Vegas | 2000 | 5974 | 2014-01-30 | Immediate to Two Years | Currently Critical | 1 | 4000
2033PLM1 | FLOOR DRAIN REPAIRS | 2033 | The floor drain in the Women's restroom constantly emits a foul smell. It is not known whether there is a proper p-trap for the drain. The staff pours buckets of water into the drain to dissipate the smell. This project would provide for a licensed contractor to inspect and repair the drain to prevent any further odors coming from the drain. | NDF/STATE PARKS OFFICE BUILDING | 9878 | CNR | Forestry |  | Las Vegas | 2000 | 5974 | 2014-01-30 | Immediate to Two Years | Currently Critical | 1 | 1500
2494PLM1 | WATER SOFTENER INSTALLATION | 2494 | The existing water softening system in the building stopped working and was removed. Untreated water causes wear and tear on the domestic water supply lines, plumbing fixtures and HVAC equipment. This project would provide for the installation of a new water softening system. | JEAN CC NDF OFFICE | 9892 | CNR | Forestry |  | Jean | 1992 | 2400 | 2014-01-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
2517EXT1 | EXTERIOR FINISHES | 2517 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | NDF FUEL BUILDING | 9892 | CNR | Forestry |  | Jean | 0 | 96 | 2014-01-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 480
2517EXT2 | ROOF REPLACEMENT | 2517 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. There were several missing shingles and the plywood underlayment was exposed to the elements. It is recommended that this building be re-roofed immediately with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. | NDF FUEL BUILDING | 9892 | CNR | Forestry |  | Jean | 0 | 96 | 2014-01-30 | Immediate to Two Years | Currently Critical | 1 | 960
2517INT1 | INTERIOR FINISHES | 2517 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. | NDF FUEL BUILDING | 9892 | CNR | Forestry |  | Jean | 0 | 96 | 2014-01-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 480
2494PLM2 | WATER HEATER REPLACEMENT | 2494 | There is a 50 gallon electric water heater in the building. It does not have seismic straps or an expansion tank. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | JEAN CC NDF OFFICE | 9892 | CNR | Forestry |  | Jean | 1992 | 2400 | 2014-01-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
2198EXT4 | OVERHEAD DOOR REPLACEMENT | 2198 | There are two 10'x10' overhead doors which are damaged and do not function properly. Exposure and wind have caused the doors to bend, crack and lose their finish. They are original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead doors and replacement with new manually operated overhead doors. | CONSERVATION CAMP STORAGE | 9892 | CNR | Forestry |  | Jean | 2002 | 1500 | 2014-01-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
2198HVA1 | HVAC REPLACEMENT | 2198 | The existing HVAC system consists of a roof mounted evaporative cooler and does not have any heating equipment. The evaporative cooler is failing and should be replaced. There is a need for heating equipment as well to provide a comfortable work environment in the winter. This project would provide for replacing the existing evaporative cooler with an exterior ground mounted packaged unit that provides propane fired heating as well as air conditioning. | CONSERVATION CAMP STORAGE | 9892 | CNR | Forestry |  | Jean | 2002 | 1500 | 2014-01-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
2198EXT1 | EXTERIOR FINISHES | 2198 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | CONSERVATION CAMP STORAGE | 9892 | CNR | Forestry |  | Jean | 2002 | 1500 | 2014-01-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
2198EXT3 | EXTERIOR DOOR REPLACEMENT | 2198 | The 2 exterior wood man-doors appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement of the wood doors with new metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | CONSERVATION CAMP STORAGE | 9892 | CNR | Forestry |  | Jean | 2002 | 1500 | 2014-01-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
2198INT1 | INTERIOR FINISHES | 2198 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. | CONSERVATION CAMP STORAGE | 9892 | CNR | Forestry |  | Jean | 2002 | 1500 | 2014-01-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
2517EXT3 | EXTERIOR DOOR REPLACEMENT | 2517 | The exterior wood man-door appears to be original to the building. It is damaged from age and general wear and tear. This project would provide for the replacement of the wood door with a new metal door, frame and hardware. Removal and disposal of the existing door and painting of the new door is included in this estimate. | NDF FUEL BUILDING | 9892 | CNR | Forestry |  | Jean | 0 | 96 | 2014-01-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
2494EXT1 | EXTERIOR FINISHES | 2494 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | JEAN CC NDF OFFICE | 9892 | CNR | Forestry |  | Jean | 1992 | 2400 | 2014-01-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1296
2494INT1 | INTERIOR FINISHES | 2494 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 4-5 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | JEAN CC NDF OFFICE | 9892 | CNR | Forestry |  | Jean | 1992 | 2400 | 2014-01-30 | Four to Ten Years | Long-Term Needs | 3 | 6480
2494EXT2 | WINDOW REPLACEMENT | 2494 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 6 units. Removal and disposal of the existing windows is included in this estimate. | JEAN CC NDF OFFICE | 9892 | CNR | Forestry |  | Jean | 1992 | 2400 | 2014-01-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
2494ADA1 | ADA RESTROOM REMODEL | 2494 | The unisex restroom is original to the building and in overall poor condition. It does not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom. These items may include a new sink, toilet, shower, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | JEAN CC NDF OFFICE | 9892 | CNR | Forestry |  | Jean | 1992 | 2400 | 2014-01-30 | Immediate to Two Years | Currently Critical | 1 | 15000
2494SFT2 | FIRE ALARM SYSTEM INSTALLATION | 2494 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2009 Section 7 and the 2012 International Fire Code. | JEAN CC NDF OFFICE | 9892 | CNR | Forestry |  | Jean | 1992 | 2400 | 2014-01-30 | Immediate to Two Years | Currently Critical | 1 | 5184
2494SFT1 | FIRE SUPPRESSION SYSTEM INSTALLATION | 2494 | The building is a B occupancy per the 2012 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 or R-2 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. | JEAN CC NDF OFFICE | 9892 | CNR | Forestry |  | Jean | 1992 | 2400 | 2014-01-30 | Immediate to Two Years | Currently Critical | 1 | 18144
2494EXT3 | EXTERIOR DOOR REPLACEMENT | 2494 | The two exterior metal doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the door assemblies with new metal doors, frames and hardware. Removal and disposal of the existing doors is included in this estimate. | JEAN CC NDF OFFICE | 9892 | CNR | Forestry |  | Jean | 1992 | 2400 | 2014-01-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
2494EXT4 | ROOF DRAIN DOWNSPOUT MODIFICATIONS | 2494 | The roof drain downspouts currently terminate within inches of the building with no continuous drainage away from the foundation. This is causing the water to pool next to the foundation and damage the foundation and walls. This project would provide for the extension of the roof drains from the downspouts to approximately 5'-0" away from the perimeter of the building to prevent pooling and damage to the building. | JEAN CC NDF OFFICE | 9892 | CNR | Forestry |  | Jean | 1992 | 2400 | 2014-01-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
2494ENR1 | HVAC REPLACEMENT | 2494 | The HVAC roof top units were installed in 1992. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of a new HVAC packaged unit for the offices and a new evaporative cooler for the converted garage area. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | JEAN CC NDF OFFICE | 9892 | CNR | Forestry |  | Jean | 1992 | 2400 | 2014-01-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
2198EXT2 | ROOF REPLACEMENT | 2198 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 1-2 years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. | CONSERVATION CAMP STORAGE | 9892 | CNR | Forestry |  | Jean | 2002 | 1500 | 2014-01-30 | Immediate to Two Years | Currently Critical | 1 | 13500
9878SEC1 | SECURITY FENCE INSTALLATION | 9878 | The chain link perimeter fence is currently around the rear parking area only. For security purposes, the staff has requested to install a security fence around the rest of the property with card-controlled access gates at the street. This project recommends the installation of a 6 foot high 6 gauge wire perimeter chain link fence around the front perimeter with two 14' wide gates with hardware. | CNR / WILDLIFE OFFICES LAS VEGAS SITE | 9878 | CNR | Forestry |  | Las Vegas | 0 |  | 2014-01-30 | Immediate to Two Years | Currently Critical | 1 | 50000
9878SIT4 | SITE DRAINAGE IMPROVEMENTS | 9878 | There are many areas around the site where the grade does not properly slope away from the buildings. Rain accumulates adjacent to the buildings, creating a water problem which may infiltrate the interior during inclement weather. There is soil to wood contact and soil to metal contact which will cause premature deterioration to the building. This project would provide funding to re-grade these problem areas to create a positive slope away from the building and to eliminate any direct soil contact. This project or a portion thereof was previously recommended in the FCA report dated 02/25/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | CNR / WILDLIFE OFFICES LAS VEGAS SITE | 9878 | CNR | Forestry |  | Las Vegas | 0 |  | 2014-01-30 | Immediate to Two Years | Currently Critical | 1 | 3000
9878ENR1 | EXTERIOR SOLAR SITE LIGHTING INSTALLATION | 9878 | There is no site lighting for the access roads and parking areas which is a security and safety concern. This project would provide for the installation of 10 solar powered LED exterior light fixtures, 20 foot tall poles and 30" diameter raised concrete base. This installation will eliminate the need for trenching and electrical connections. This project or a portion thereof was previously recommended in the FCA report dated 02/25/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | CNR / WILDLIFE OFFICES LAS VEGAS SITE | 9878 | CNR | Forestry |  | Las Vegas | 0 |  | 2014-01-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 65000
9878SIT7 | CRACK FILL & SEAL ASPHALT PAVING | 9878 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the paving site wide including access roads and parking areas. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 25,000 square feet of asphalt area was used to generate this estimate. | CNR / WILDLIFE OFFICES LAS VEGAS SITE | 9878 | CNR | Forestry |  | Las Vegas | 0 |  | 2014-01-30 | Four to Ten Years | Long-Term Needs | 3 | 15000
2299EXT1 | EXTERIOR FINISHES | 2299 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/22/2014. | EAST FEE BOOTH | 9936 | CNR | Parks |  | South Fork SRA |  | 40 | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 200
2321ADA1 | ADA SIGNAGE & STRIPING | 2321 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The asphalt parking area and passenger loading area are missing proper signage and striping to comply with ADA requirements. This project would provide for striping, signage and any other necessary upgrades to the parking space. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | EAST BOAT RAMP CXT RESTROOM | 9936 | CNR | Parks |  | South Fork SRA | 0 | 250 | 2014-07-22 | Immediate to Two Years | Currently Critical | 1 | 1500
2299INT1 | INTERIOR FINISHES | 2299 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/22/2014. | EAST FEE BOOTH | 9936 | CNR | Parks |  | South Fork SRA |  | 40 | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 200
2300EXT1 | EXTERIOR FINISHES | 2300 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/22/2014. | WEST FEE BOOTH | 9936 | CNR | Parks |  | South Fork SRA |  | 100 | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
2300INT1 | INTERIOR FINISHES | 2300 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/22/2014. | WEST FEE BOOTH | 9936 | CNR | Parks |  | South Fork SRA |  | 100 | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
2737EXT1 | EXTERIOR/ INTERIOR FINISHES | 2737 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/22/2014. | FISHERMAN'S POINT CXT RESTROOM | 9936 | CNR | Parks |  | South Fork SRA | 2006 | 98 | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 245
2321EXT1 | EXTERIOR/ INTERIOR FINISHES | 2321 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/22/2014. | EAST BOAT RAMP CXT RESTROOM | 9936 | CNR | Parks |  | South Fork SRA | 0 | 250 | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 625
2301HVA1 | HEATER INSTALLATION | 2301 | The building is heated by several small wall mounted electric heaters. These units were not installed as part of the original building design and are insufficient for their application. This project provides for purchase and installation of propane fired heaters and associated connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/22/2014. | GARAGE/STORAGE BUILDING | 9936 | CNR | Parks |  | South Fork SRA |  | 1200 | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5200
2301EXT2 | EXTERIOR DOOR REPLACEMENT | 2301 | The exterior wood man door appears to be original to the building. It is damaged from age and general wear and tear. The frame has not held up over time and is causing the door to bind. This project would provide for the replacement of the wood door with a new metal door, frame and hardware. Removal and disposal of the existing door and painting of the new door is included in this estimate. | GARAGE/STORAGE BUILDING | 9936 | CNR | Parks |  | South Fork SRA |  | 1200 | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
2741EXT1 | EXTERIOR/ INTERIOR FINISHES | 2741 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/22/2014. | CXT RESTROOM #3 WEST | 9936 | CNR | Parks |  | South Fork SRA | 2006 | 196 | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 490
2301INT1 | INTERIOR FINISHES | 2301 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. | GARAGE/STORAGE BUILDING | 9936 | CNR | Parks |  | South Fork SRA |  | 1200 | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
2301EXT1 | EXTERIOR FINISHES | 2301 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing and staining the wood and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be stained and caulked in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/22/2014. | GARAGE/STORAGE BUILDING | 9936 | CNR | Parks |  | South Fork SRA |  | 1200 | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
2737ADA1 | ADA PARKING INSTALLATION | 2737 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. A concrete parking area and passenger loading area are necessary to comply with ADA requirements. This project would provide for a concrete van accessible ADA parking and loading space and walkway to the existing sidewalk. This will require regrading, installing P.C. concrete, striping, signage and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | FISHERMAN'S POINT CXT RESTROOM | 9936 | CNR | Parks |  | South Fork SRA | 2006 | 98 | 2014-07-22 | Immediate to Two Years | Currently Critical | 1 | 2500
2739EXT1 | EXTERIOR/ INTERIOR FINISHES | 2739 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 3-4 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/22/2014. | CXT RESTROOM #1 WEST | 9936 | CNR | Parks |  | South Fork SRA | 2006 | 98 | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 245
2741ADA1 | ADA PARKING INSTALLATION | 2741 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. A concrete parking area and passenger loading area are necessary to comply with ADA requirements. This project would provide for a concrete van accessible ADA parking and loading space and walkway to the existing sidewalk. This will require regrading, installing P.C. concrete, striping, signage and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/22/2014. | CXT RESTROOM #3 WEST | 9936 | CNR | Parks |  | South Fork SRA | 2006 | 196 | 2014-07-22 | Immediate to Two Years | Currently Critical | 1 | 2500
2740ADA1 | ADA PARKING INSTALLATION | 2740 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. A concrete parking area and passenger loading area are necessary to comply with ADA requirements. This project would provide for a concrete van accessible ADA parking and loading space and walkway to the existing sidewalk. This will require regrading, installing P.C. concrete, striping, signage and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/22/2014. | CXT RESTROOM #2 WEST | 9936 | CNR | Parks |  | South Fork SRA | 2006 | 196 | 2014-07-22 | Immediate to Two Years | Currently Critical | 1 | 2500
2753EXT1 | EXTERIOR FINISHES | 2753 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/22/2014. | IRRIGATION PUMP HOUSE | 9936 | CNR | Parks |  | South Fork SRA | 2006 | 144 | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 720
2740EXT1 | EXTERIOR/ INTERIOR FINISHES | 2740 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/22/2014. | CXT RESTROOM #2 WEST | 9936 | CNR | Parks |  | South Fork SRA | 2006 | 196 | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 490
3352EXT1 | EXTERIOR FINISHES | 3352 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | RESIDENCE 1 | 9936 | CNR | Parks |  | South Fork SRA | 2012 | 1500 | 2014-07-22 | Four to Ten Years | Long-Term Needs | 3 | 7500
9936SIT1 | ASPHALT PAVING INSTALLATION | 9936 | The campground loop and the individual campsite parking areas are not currently paved. This project would provide asphalt paving for a 10' wide access road around the campground and 10' wide parking spaces at each campsite. The estimate includes grading, compaction and installation of 4" thick asphalt cement. This project or a portion thereof was previously recommended in the FCA report dated 01/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/22/2014. | SOUTH FORK STATE RECREATION AREA SITE | 9936 | CNR | Parks |  | South Fork SRA |  |  | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 364000
3353EXT1 | EXTERIOR FINISHES | 3353 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | RESIDENCE 2 | 9936 | CNR | Parks |  | South Fork SRA | 2012 | 1500 | 2014-07-22 | Four to Ten Years | Long-Term Needs | 3 | 7500
9936ADA3 | ADA UPGRADES - PRESENTATION AREA | 9936 | The Presentation Area in the campground is used by the rangers for educational and interpretive talks to the public. There are benches provided but there is no accessible path of travel or accessible viewing area for the disabled. This project would provide for the purchase and installation of 300 SF of 4" thick concrete for an ADA compliant sidewalk and viewing area. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | SOUTH FORK STATE RECREATION AREA SITE | 9936 | CNR | Parks |  | South Fork SRA |  |  | 2014-07-22 | Immediate to Two Years | Currently Critical | 1 | 3500
9936SIT4 | FISH CLEANING STATION INSTALLATION | 9936 | There is no fish cleaning station installed at the site. This equipment is important to have on site because it reduces environmental hazards that would be prevalent without the equipment and also encourages people to visit the park for its convenient facilities. The estimate includes 2,500 feet of piping from the campground to the main water line. This project or a portion thereof was previously recommended in the FCA report dated 01/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/22/2014. | SOUTH FORK STATE RECREATION AREA SITE | 9936 | CNR | Parks |  | South Fork SRA |  |  | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
9936SIT2 | CRACK FILL & SEAL ASPHALT PAVING | 9936 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the paving site wide including access roads and parking areas. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 312,000 square feet of asphalt area was used to generate this estimate which includes the new paving in the campground. This project or a portion thereof was previously recommended in the FCA report dated 01/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/22/2014. | SOUTH FORK STATE RECREATION AREA SITE | 9936 | CNR | Parks |  | South Fork SRA |  |  | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 187200
3350ADA1 | ADA PARKING INSTALLATION | 3350 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. A concrete parking area and passenger loading area are necessary to comply with ADA requirements. This project would provide for a concrete van accessible ADA parking and loading space and walkway to the existing sidewalk. This will require regrading, installing P.C. concrete, striping, signage and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | SADDLE DAM CXT RESTROOM | 9936 | CNR | Parks |  | South Fork SRA | 2008 | 98 | 2014-07-22 | Immediate to Two Years | Currently Critical | 1 | 2500
9936EXT1 | EXTERIOR FINISHES, SHADE RAMADAS | 9936 | There are 59 steel shade ramadas in different locations throughout the site for a total of 8,864 square feet. It is important to maintain the finish, weather resistance and appearance of the structures. This project would provide for painting of the structures. This project should be done on a cyclical basis based on environmental conditions. This project or a portion thereof was previously recommended in the FCA report dated 01/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/22/2014. | SOUTH FORK STATE RECREATION AREA SITE | 9936 | CNR | Parks |  | South Fork SRA |  |  | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3456
3351EXT1 | EXTERIOR/ INTERIOR FINISHES | 3351 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | COYOTE COVE CXT RESTROOM | 9936 | CNR | Parks |  | South Fork SRA | 2014 | 196 | 2014-07-22 | Four to Ten Years | Long-Term Needs | 3 | 490
9936PLM2 | ISOLATION VALVE REPLACEMENT | 9936 | Two of the isolation valves for the site are no longer operating correctly. The main water line that serves each of the buildings on the site is in need of an isolation valve. This will allow the maintenance staff to do repairs to the plumbing without shutting down the whole site. More importantly, a leak in the building can be shut down quickly minimizing damage in an emergency. This estimate provides for a 2-1/2" gate valve to be installed at each building. | SOUTH FORK STATE RECREATION AREA SITE | 9936 | CNR | Parks |  | South Fork SRA |  |  | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
3353INT1 | INTERIOR FINISHES | 3353 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 5-6 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | RESIDENCE 2 | 9936 | CNR | Parks |  | South Fork SRA | 2012 | 1500 | 2014-07-22 | Four to Ten Years | Long-Term Needs | 3 | 7500
3354EXT1 | EXTERIOR FINISHES | 3354 | It is important to maintain the finish, weather resistance and appearance of the water tank. This project would provide for the painting of the water tank and caulking of the joints to maintain it in a good, weather tight condition. It is recommended that this project be implemented in the next 2-3 years and is recommended on a cyclical basis based on environmental conditions. | WATER TANK | 9936 | CNR | Parks |  | South Fork SRA | 0 |  | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
9936SIT3 | BOAT DOCK AND RAMP REPLACEMENT | 9936 | The boat dock and concrete ramp are approaching the end of their expected life due to extreme climatic conditions and heavy use. The existing ramp and dock should be scheduled for replacement. The concrete ramp is cracking and spalling. It is important for the concrete to be in good shape to insure proper traction for tow vehicles and to prevent accidents. This project would provide for purchase and installation of a new boat dock and concrete ramp. Removal and disposal of the existing concrete ramp and dock is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 01/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/22/2014. | SOUTH FORK STATE RECREATION AREA SITE | 9936 | CNR | Parks |  | South Fork SRA |  |  | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 150000
9936SIT5 | EXTERIOR SOLAR SITE LIGHTING INSTALLATION | 9936 | The visitors parking lot, maintenance yard and carport parking area have insufficient lighting. This project would provide for the installation of 10 solar powered LED exterior light fixtures, 20 foot tall poles and 30" diameter raised concrete bases. This installation will eliminate the need for trenching and electrical connections. This project or a portion thereof was previously recommended in the FCA report dated 01/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/22/2014. | SOUTH FORK STATE RECREATION AREA SITE | 9936 | CNR | Parks |  | South Fork SRA |  |  | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 65000
3352INT1 | INTERIOR FINISHES | 3352 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 5-6 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | RESIDENCE 1 | 9936 | CNR | Parks |  | South Fork SRA | 2012 | 1500 | 2014-07-22 | Four to Ten Years | Long-Term Needs | 3 | 7500
3350EXT1 | EXTERIOR/ INTERIOR FINISHES | 3350 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | SADDLE DAM CXT RESTROOM | 9936 | CNR | Parks |  | South Fork SRA | 2008 | 98 | 2014-07-22 | Four to Ten Years | Long-Term Needs | 3 | 245
0547EXT2 | EXTERIOR DOOR REPLACEMENT | 0547 | The exterior wood man door at the entrance appears to be original to the building. It is damaged from age and general wear and tear. This project would provide for the replacement of the wood door with a new metal door, frame and hardware. Removal and disposal of the existing door and painting of the new door is included in this estimate. | PARK OFFICE/SHOP | 9936 | CNR | Parks |  | South Fork SRA | 1994 | 3464 | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0547EXT1 | EXTERIOR FINISHES | 0547 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 01/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/22/2014. | PARK OFFICE/SHOP | 9936 | CNR | Parks |  | South Fork SRA | 1994 | 3464 | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 17320
0547INT4 | JANITORS CLOSET REPAIRS | 0547 | The mop sink in the Janitors Closet is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | PARK OFFICE/SHOP | 9936 | CNR | Parks |  | South Fork SRA | 1994 | 3464 | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
0580SFT1 | CHLORINE ALARM INSTALLATION | 0580 | The pump house has two rooms, one houses the water pump and the other houses the chlorination system. There is a monitoring and alarm system for the pump, but not for the chlorination system. This project would provide for a continuous area monitoring and alarm system to be installed to detect a chlorine leak in the chlorination system. The audible and visual alarm should be mounted on the exterior of the building. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/22/2014. | PUMP HOUSE | 9936 | CNR | Parks |  | South Fork SRA | 1992 | 104 | 2014-07-22 | Immediate to Two Years | Currently Critical | 1 | 2500
0547ADA3 | ADA SHOWER REMODEL | 0547 | The staff restroom is ADA compliant except for the shower. The existing shower does not fully comply with the ADA accessible guidelines. This project would provide for new ADA compliant plumbing fixtures and shower seat to be installed. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | PARK OFFICE/SHOP | 9936 | CNR | Parks |  | South Fork SRA | 1994 | 3464 | 2014-07-22 | Immediate to Two Years | Currently Critical | 1 | 5000
0547ENR1 | LIGHTING UPGRADE | 0547 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, conference rooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 01/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/22/2014. | PARK OFFICE/SHOP | 9936 | CNR | Parks |  | South Fork SRA | 1994 | 3464 | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5196
0547ELE1 | ELECTRICAL UPGRADE IN SHOP | 0547 | This building was constructed before the high demand for electrical services were needed for shop equipment and computers. As time has progressed, the shops electrical demand and equipment has changed and is now lacking sufficient electrical outlets. This project would provide for the purchase and installation of 10 additional duplex outlets. This project or a portion thereof was previously recommended in the FCA report dated 01/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/22/2014. | PARK OFFICE/SHOP | 9936 | CNR | Parks |  | South Fork SRA | 1994 | 3464 | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
0547SFT3 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0547 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 01/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/22/2014. | PARK OFFICE/SHOP | 9936 | CNR | Parks |  | South Fork SRA | 1994 | 3464 | 2014-07-22 | Immediate to Two Years | Currently Critical | 1 | 2500
0547ADA2 | ADA ACCESSIBLE COUNTER | 0547 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The lobby at the entrance of the building has a service counter for the public to approach which does not meet current requirements. Section 904.4 of the ADA Standards For Accessible Design states that a portion of the counter surface that is 36" long minimum and 36" high maximum above the finish floor shall be provided. This project will provide an accessible counter space in accordance with this requirement. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 01/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/22/2014. | PARK OFFICE/SHOP | 9936 | CNR | Parks |  | South Fork SRA | 1994 | 3464 | 2014-07-22 | Immediate to Two Years | Currently Critical | 1 | 1000
0547ENR2 | HEATER REPLACEMENT | 0547 | The ceiling mounted heaters in the garage are not energy efficient and have reached the end of their expected and useful life. They have undergone numerous repairs and should be scheduled for replacement. The new units shall be designed to significantly reduce electrical and propane gas usage in order to comply with the 2009 IECC and ASHRAE 90.1 and to reduce utility costs. This project would provide for replacing the existing heaters and all required connections to utilities. | PARK OFFICE/SHOP | 9936 | CNR | Parks |  | South Fork SRA | 1994 | 3464 | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
0547SFT1 | FIRE ALARM UPGRADE | 0547 | This building is equipped with an automatic fire detection and alarm system that no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 "If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure". When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. This project or a portion thereof was previously recommended in the FCA report dated 01/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/22/2014. | PARK OFFICE/SHOP | 9936 | CNR | Parks |  | South Fork SRA | 1994 | 3464 | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10392
0547ADA1 | ADA SIGNAGE | 0547 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 01/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/22/2014. | PARK OFFICE/SHOP | 9936 | CNR | Parks |  | South Fork SRA | 1994 | 3464 | 2014-07-22 | Immediate to Two Years | Currently Critical | 1 | 2500
0547SIT1 | CONCRETE PAVING INSTALLATION | 0547 | The building could use sidewalk upgrades and additional concrete around the exterior and under the carport. Some of the existing concrete is cracked and failing and is due for replacement. There are unpaved areas around the exterior of the building that staff walk on regularly. Areas around the building are walked on often and are not paved. The four-bay carport on the North side of the building is not paved and the dirt is insufficient for the heavy use and extreme climate. The drainage away from the building is also insufficient due to erosion of the dirt which also makes it difficult to remove snow from the perimeter of the building. This project would provide for 2,000 square feet of concrete to replace deteriorated concrete sidewalks, installation of new concrete sidewalks, installation of proper parking spaces under the carport and improved drainage. | PARK OFFICE/SHOP | 9936 | CNR | Parks |  | South Fork SRA | 1994 | 3464 | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0578EXT1 | EXTERIOR FINISHES | 0578 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/22/2014. | STORAGE BUILDING | 9936 | CNR | Parks |  | South Fork SRA | 1937 | 1064 | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5320
0580EXT2 | EXTERIOR DOOR REPLACEMENT | 0580 | The exterior metal doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the two exterior doors with new metal doors, frames and hardware. Removal and disposal of the existing doors is included in this estimate. | PUMP HOUSE | 9936 | CNR | Parks |  | South Fork SRA | 1992 | 104 | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0580HVA1 | HEATER REPLACEMENT | 0580 | There is an electric heater in the chlorinator room that is no longer operating. This project recommends replacing the electric heater. The estimate includes removal and disposal of the existing equipment. | PUMP HOUSE | 9936 | CNR | Parks |  | South Fork SRA | 1992 | 104 | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
0580EXT1 | EXTERIOR FINISHES | 0580 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units, painting the wood and metal trim and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/22/2014. | PUMP HOUSE | 9936 | CNR | Parks |  | South Fork SRA | 1992 | 104 | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 520
0581EXT1 | DEMOLISH STRUCTURE | 0581 | This building is not currently being used. It contains numerous code and safety issues including but not limited to rodent infestation, broken windows, broken or missing electrical fixtures, dry rot and possible structural damage due to the age. The building is dilapidated and deteriorating and has reached the end of its useful life. This project would provide funding for the demolition and disposal of the building. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/22/2014. | SHOP (VACANT) | 9936 | CNR | Parks |  | South Fork SRA | 1937 | 912 | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9120
0546INT1 | INTERIOR FINISHES | 0546 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 01/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/22/2014. | CAMPGROUND COMFORT STATION | 9936 | CNR | Parks |  | South Fork SRA | 1991 | 864 | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4320
0547STR1 | STRUCTURAL POST REPLACEMENT | 0547 | The wood posts supporting the roof overhang around the building are in various stages of deterioration and should be scheduled for replacement. The posts are drying out, twisting, splitting, pulling loose from the steel brackets and rotting at the bottom due to direct contact with dirt and moisture. To prevent the wood to ground contact from occurring in the future, the concrete footings will need to be widened and raised up. This project would provide for replacing 25 wood posts and concrete footings including all necessary hardware and painting or staining. | PARK OFFICE/SHOP | 9936 | CNR | Parks |  | South Fork SRA | 1994 | 3464 | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0580INT1 | INTERIOR FINISHES | 0580 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/22/2014. | PUMP HOUSE | 9936 | CNR | Parks |  | South Fork SRA | 1992 | 104 | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 520
0546HVA1 | HVAC REPLACEMENT | 0546 | The existing HVAC system consists of a propane-fired furnace and an air handler. The equipment is original to the building and does not provide sufficient heat in the colder months of the year. This project would provide for installation of a new HVAC system and cleaning of the existing duct work and grilles. The new system shall be designed to significantly reduce electrical and gas usage in order to comply with the 2009 IECC and ASHRAE 90.1 and to reduce utility costs. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | CAMPGROUND COMFORT STATION | 9936 | CNR | Parks |  | South Fork SRA | 1991 | 864 | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0546ADA2 | ADA SHOWER AND RESTROOM REMODEL | 0546 | The designated ADA restrooms and showers do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for construction of two unisex accessible restrooms and one accessible shower room. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | CAMPGROUND COMFORT STATION | 9936 | CNR | Parks |  | South Fork SRA | 1991 | 864 | 2014-07-22 | Immediate to Two Years | Currently Critical | 1 | 15000
0547INT3 | INTERIOR FINISHES | 0547 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 4 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | PARK OFFICE/SHOP | 9936 | CNR | Parks |  | South Fork SRA | 1994 | 3464 | 2014-07-22 | Four to Ten Years | Long-Term Needs | 3 | 17320
0546EXT2 | EXTERIOR FINISHES | 0546 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | CAMPGROUND COMFORT STATION | 9936 | CNR | Parks |  | South Fork SRA | 1991 | 864 | 2014-07-22 | Four to Ten Years | Long-Term Needs | 3 | 17280
1314EXT1 | EXTERIOR FINISHES | 1314 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, block sealing, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 2 to 3 years and is recommended on a cyclical basis based on environmental conditions. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/23/2014. | RESTROOM #2 | 9935 | CNR | Parks |  | Wild Horse SRA | 1982 | 507 | 2014-07-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2535
1315SFT1 | INSTALL FIRE SUPPRESSION SYSTEM | 1315 | This building does not have an automatic fire suppression system. Nevada State Fire Marshal NAC 477.915 (c) requires buildings having a floor area exceeding 12,000 s.f. on any floor or 24,000 s.f. on all floors, or which contain a B or R-1 occupancy, be scheduled for installation of an automatic fire suppression system during the next remodeling of, or addition to the building. Backflow prevention is included in this estimate. This building is partially classified as a B occupancy. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/23/2014. | PARK OFFICE/SHOP | 9935 | CNR | Parks |  | Wild Horse SRA | 1982 | 3400 | 2014-07-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 47600
1313INT1 | INTERIOR FINISHES | 1313 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 3 to 4 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/23/2014. | RESIDENCE #2 | 9935 | CNR | Parks |  | Wild Horse SRA | 1982 | 2304 | 2014-07-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11520
1312INT2 | REPLACE FLOORING | 1312 | The existing carpet and vinyl flooring has reached the end of it's useful life. This project would provide for the removal and disposal of the existing flooring and installation of new vinyl and carpet flooring throughout the residence. | RESIDENCE #1 | 9935 | CNR | Parks |  | Wild Horse SRA | 1982 | 2304 | 2014-07-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7200
1314INT1 | INTERIOR FINISHES | 1314 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/23/2014. | RESTROOM #2 | 9935 | CNR | Parks |  | Wild Horse SRA | 1982 | 507 | 2014-07-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2535
1313EXT2 | REPAIR VINYL SIDING | 1313 | The north side of the building had an attached carport that has since been removed. The vinyl siding was installed before the carport was removed and the siding does not extend up the entire wall. This project recommends removing the old wood siding at the gable end and installing vinyl siding to match the rest of the building. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/23/2014. | RESIDENCE #2 | 9935 | CNR | Parks |  | Wild Horse SRA | 1982 | 2304 | 2014-07-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2400
1313SFT2 | REMODEL FRONT ENTRY / STAIRWAY | 1313 | The existing front entry to the residence has a non conforming stairway and landing. The entry floor is cantilevered above grade and is supported by two posts sitting on an exposed concrete pier. This project would provide for a new concrete pier / foundation support for the floor and new landing and stairs, wood framed stairs with handrails and a concrete slab-on-grade landing at the bottom. The other entry is similar and is also recommended to be replaced. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/23/2014. | RESIDENCE #2 | 9935 | CNR | Parks |  | Wild Horse SRA | 1982 | 2304 | 2014-07-23 | Immediate to Two Years | Currently Critical | 1 | 4000
1313EXT1 | EXTERIOR FINISHES | 1313 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 3 to 4 years and is recommended on a cyclical basis based on environmental conditions. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/23/2014. | RESIDENCE #2 | 9935 | CNR | Parks |  | Wild Horse SRA | 1982 | 2304 | 2014-07-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11520
1313HVA1 | HVAC REPLACEMENT | 1313 | There is an existing propane fired furnace that is approaching 20 years old and is in need of replacement. This project would provide for the removal and disposal of the old unit and installation of a new propane gas fired furnace including all required connections to existing utilities. Cleaning of the existing ductwork is also included in this estimate. | RESIDENCE #2 | 9935 | CNR | Parks |  | Wild Horse SRA | 1982 | 2304 | 2014-07-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4800
1313INT3 | REPLACE FLOORING | 1313 | The existing carpet and vinyl flooring has reached the end of it's useful life. This project would provide for the removal and disposal of the existing flooring and installation of new vinyl and carpet flooring throughout the residence. | RESIDENCE #2 | 9935 | CNR | Parks |  | Wild Horse SRA | 1982 | 2304 | 2014-07-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7200
1315SFT2 | FIRE ALARM SYSTEM INSTALLATION | 1315 | This building is lacking a fire alarm and detection system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2009 Section 7 and the 2012 International Fire Code. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/23/2014. | PARK OFFICE/SHOP | 9935 | CNR | Parks |  | Wild Horse SRA | 1982 | 3400 | 2014-07-23 | Immediate to Two Years | Currently Critical | 1 | 17000
1312ENR1 | WINDOW REPLACEMENT | 1312 | The existing windows are old aluminum dual pane type and are in need of replacement. This project would provide for the removal and disposal of the existing windows and installation of new vinyl dual pane window units. A total of 9 window units was used for this estimate. | RESIDENCE #1 | 9935 | CNR | Parks |  | Wild Horse SRA | 1982 | 2304 | 2014-07-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
1313ENR1 | WINDOW REPLACEMENT | 1313 | The existing windows are old aluminum dual pane type and are in need of replacement. This project would provide for the removal and disposal of the existing windows and installation of new vinyl dual pane window units. A total of 9 window units was used for this estimate. | RESIDENCE #2 | 9935 | CNR | Parks |  | Wild Horse SRA | 1982 | 2304 | 2014-07-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
1312HVA1 | HVAC REPLACEMENT | 1312 | There is an existing propane fired furnace that is approaching 20 years old and is in need of replacement. This project would provide for the removal and disposal of the old unit and installation of a new propane gas fired furnace including all required connections to existing utilities. Cleaning of the existing ductwork is also included in this estimate. | RESIDENCE #1 | 9935 | CNR | Parks |  | Wild Horse SRA | 1982 | 2304 | 2014-07-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4800
1311EXT1 | EXTERIOR FINISHES | 1311 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 2 to 3 years and is recommended on a cyclical basis based on environmental conditions. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/23/2014. | UTILITY SHED | 9935 | CNR | Parks |  | Wild Horse SRA | 1982 | 200 | 2014-07-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 200
1312INT1 | INTERIOR FINISHES | 1312 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/23/2014. | RESIDENCE #1 | 9935 | CNR | Parks |  | Wild Horse SRA | 1982 | 2304 | 2014-07-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11520
1316ADA2 | ADA IMPROVEMENTS | 1316 | The existing restrooms and parking area are in need of some minor ADA accessibility upgrades. This project would provide for a no parking sign to be installed at the access isle, restroom signage, plumbing jackets on the sinks, and the installation of grab bars in the restroom containing the ADA accessible shower. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | RESTROOM #3 | 9935 | CNR | Parks |  | Wild Horse SRA | 1982 | 400 | 2014-07-23 | Immediate to Two Years | Currently Critical | 1 | 5000
1602INT1 | INTERIOR FINISHES | 1602 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 06/20/2003 and 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | RESTROOM #1 | 9935 | CNR | Parks |  | Wild Horse SRA | 1980 | 200 | 2014-07-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
1602EXT1 | EXTERIOR FINISHES | 1602 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, block sealing, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. This project or a portion thereof was previously recommended in the FCA report dated 06/20/2003 and 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | RESTROOM #1 | 9935 | CNR | Parks |  | Wild Horse SRA | 1980 | 200 | 2014-07-23 | Four to Ten Years | Long-Term Needs | 3 | 1000
1312EXT1 | EXTERIOR FINISHES | 1312 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 2 to 3 years and is recommended on a cyclical basis based on environmental conditions. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/23/2014. | RESIDENCE #1 | 9935 | CNR | Parks |  | Wild Horse SRA | 1982 | 2304 | 2014-07-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11520
1315EXT3 | REPLACE OVERHEAD COILING DOORS | 1315 | There are four 12'x10' overhead coiling doors which are damaged and do not function properly. They are original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead coiling doors and replacement with two motorized doors. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/23/2014. | PARK OFFICE/SHOP | 9935 | CNR | Parks |  | Wild Horse SRA | 1982 | 3400 | 2014-07-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24000
1315INT1 | INTERIOR FINISHES | 1315 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/23/2014. | PARK OFFICE/SHOP | 9935 | CNR | Parks |  | Wild Horse SRA | 1982 | 3400 | 2014-07-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 17000
1316EXT1 | EXTERIOR FINISHES | 1316 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, block sealing, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 2 to 3 years and is recommended on a cyclical basis based on environmental conditions. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/23/2014. | RESTROOM #3 | 9935 | CNR | Parks |  | Wild Horse SRA | 1982 | 400 | 2014-07-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4320
1316INT1 | INTERIOR FINISHES | 1316 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 2 to 3 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/23/2014. | RESTROOM #3 | 9935 | CNR | Parks |  | Wild Horse SRA | 1982 | 400 | 2014-07-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4320
1315SFT3 | INSTALL EXIT SIGNS AND EGRESS LIGHTING | 1315 | The building does not have any exit signs or emergency lighting. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency exit lighting to provide illumination along the egress route. IBC - 20012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/23/2014. | PARK OFFICE/SHOP | 9935 | CNR | Parks |  | Wild Horse SRA | 1982 | 3400 | 2014-07-23 | Immediate to Two Years | Currently Critical | 1 | 3500
1315ADA1 | ADA PARKING UPGRADE | 1315 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The main entrance to the building has an ADA parking stall which does not entirely meet the requirements of the code. This project provides funding to bring the existing ADA parking area up to code including a compliant path of travel from the parking space to the building entrance, updated signage and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/23/2014. | PARK OFFICE/SHOP | 9935 | CNR | Parks |  | Wild Horse SRA | 1982 | 3400 | 2014-07-23 | Immediate to Two Years | Currently Critical | 1 | 5000
1315EXT1 | EXTERIOR FINISHES | 1315 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 2 to 3 years and is recommended on a cyclical basis based on environmental conditions. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/23/2014. | PARK OFFICE/SHOP | 9935 | CNR | Parks |  | Wild Horse SRA | 1982 | 3400 | 2014-07-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 17000
1315EXT2 | WINDOW REPLACEMENT | 1315 | There are six windows in the building approximately 3'x7' with an exposed bottom edge less than 18" above the floor. IBC 2012 - Section 2406 requires these windows to have safety glass labeled due to their hazardous location. This project recommends replacing the windows with safety glazed windows. This estimate is for the replacement of 6 units. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/23/2014. | PARK OFFICE/SHOP | 9935 | CNR | Parks |  | Wild Horse SRA | 1982 | 3400 | 2014-07-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
1315HVA1 | HVAC UPGRADE | 1315 | The building is heated by a propane fired forced air unit installed in 1982. It is original to the building and has reached the end of its expected life. This project would provide for replacement of the heater and includes removal and disposal of the existing unit and all required connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/23/2014. | PARK OFFICE/SHOP | 9935 | CNR | Parks |  | Wild Horse SRA | 1982 | 3400 | 2014-07-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
2317EXT1 | EXTERIOR FINISHES | 2317 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 3 to 4 years and is recommended on a cyclical basis based on environmental conditions. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/23/2014. | RESIDENCE GARAGE #2 | 9935 | CNR | Parks |  | Wild Horse SRA | 2002 | 900 | 2014-07-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
2316EXT1 | EXTERIOR FINISHES | 2316 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 3 to 4 years and is recommended on a cyclical basis based on environmental conditions. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/23/2014. | RESIDENCE GARAGE #1 | 9935 | CNR | Parks |  | Wild Horse SRA | 1990 | 672 | 2014-07-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3360
2316INT1 | INTERIOR FINISHES | 2316 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 3 to 4 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/23/2014. | RESIDENCE GARAGE #1 | 9935 | CNR | Parks |  | Wild Horse SRA | 1990 | 672 | 2014-07-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3360
9935SIT6 | WELL SYSTEM TELEMETRY REPLACEMENT | 9935 | The existing well water telemetry system is no longer operational. Staff has to manually activate well pumps to fill tanks. This is not efficient. This project would provide for a new telemetry system including software to be installed. | WILD HORSE STATE RECREATION AREA SITE | 9935 | CNR | Parks |  | Wild Horse SRA |  |  | 2014-07-23 | Immediate to Two Years | Currently Critical | 1 | 10000
9935SIT5 | WATER STORAGE TANK REPLACEMENT | 9935 | There is a 10,000 gallon underground water storage tank that is leaking and no longer in use according to staff. This project would provide for the removal of the existing tank and installation of a new 10,000 gallon water storage tank including all required excavation and connections to existing water system. | WILD HORSE STATE RECREATION AREA SITE | 9935 | CNR | Parks |  | Wild Horse SRA |  |  | 2014-07-23 | Immediate to Two Years | Currently Critical | 1 | 27500
9935ADA1 | SITE ADA ISSUES | 9935 | The parking in the Day Use area and the route of travel from the parking space to the accessible picnic table are not fully ADA compliant. It is recommended that the parking area and route of travel be made accessible including updated signage. A concrete ADA parking space is included in this estimate. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 08/21/2002 and 11/7/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 7/23/2014 | WILD HORSE STATE RECREATION AREA SITE | 9935 | CNR | Parks |  | Wild Horse SRA |  |  | 2014-07-23 | Immediate to Two Years | Currently Critical | 1 | 10000
9935SIT3 | CRACK FILL / SLURRY SEAL ASPHALT PAVING | 9935 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site wide including access roads and parking areas. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 120,000 square feet of asphalt area was used to generate this estimate which includes the new paving in the campgrounds. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/23/2014. | WILD HORSE STATE RECREATION AREA SITE | 9935 | CNR | Parks |  | Wild Horse SRA |  |  | 2014-07-23 | Four to Ten Years | Long-Term Needs | 3 | 72000
9935SIT2 | AC PAVING INSTALLATION | 9935 | The AC paving behind the visitors center has failed and is in need of replacement. This project would provide for the removal of the damaged paving and installation of new 3" thick AC paving over a compacted base. It may be possible to grind in place the damaged paving and use for base which could reduce project cost. | WILD HORSE STATE RECREATION AREA SITE | 9935 | CNR | Parks |  | Wild Horse SRA |  |  | 2014-07-23 | Four to Ten Years | Long-Term Needs | 3 | 93750
9935EXT1 | EXTERIOR FINISHES, SHADE RAMADAS | 9935 | There are steel shade ramadas in different locations throughout the site which measure about 12'x12' each. It is important to maintain the finish, weather resistance and appearance of the structures. This project would provide for painting of the structures. This project should be done on a cyclical basis based on environmental conditions. This project or a portion thereof was previously recommended in the FCA report dated 11/7/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 7/23/2014 | WILD HORSE STATE RECREATION AREA SITE | 9935 | CNR | Parks |  | Wild Horse SRA |  |  | 2014-07-23 | Four to Ten Years | Long-Term Needs | 3 | 3400
1333EXT3 | ROOF REPLACEMENT | 1333 | The existing wood shingle roof is in poor condition. There are missing shingles and it is showing signs of failure. This project would provide for the installation of a new wood shingle roofing system including new underlayment and waterproofing. The shingles shall match the other wood shingle roofs at the park. Removal and disposal of the old roofing and underlayment is included in this estimate. | GROUP RAMADA | 9925 | CNR | Parks |  | Genoa | 1977 | 1268 | 2015-02-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19020
1334SEC1 | SECURITY SYSTEM INSTALLATION | 1334 | The Park Museum is lacking any type of a security system. It contains numerous artifacts and displays which are valuable. This project would provide for the installation of a security system complete with an alarm and motion detection devices and remote monitoring. | MORMON STATION PARK MUSEUM | 9925 | CNR | Parks |  | Genoa | 1947 | 450 | 2015-02-18 | Immediate to Two Years | Currently Critical | 1 | 15000
1334ENV1 | REPLACE ROOF | 1334 | The existing wood shingle roof is showing it's age. The wood shingles are deteriorating, there are signs of water damage and some shingles are missing. This project would provide for new wood shingles to be installed including rubberized asphalt sheet waterproofing and felt paper underlayment. Removal and disposal of the existing shingles and underlayment are included in this estimate. | MORMON STATION PARK MUSEUM | 9925 | CNR | Parks |  | Genoa | 1947 | 450 | 2015-02-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6750
1334EXT1 | EXTERIOR / INTERIOR FINISHES | 1334 | The cyclical treatment of the building interior and exterior is very important to help maintain the finish, weather proofing, integrity and appearance of the building. This treatment does not include the roofing material itself but it should include everything that has to do with weather proofing the building envelope including painting or staining, sealing, repairing the chinking and caulking where applicable. This project should be scheduled on a cyclical basis. Interior and exterior chinking maintenance is also part of this project. | MORMON STATION PARK MUSEUM | 9925 | CNR | Parks |  | Genoa | 1947 | 450 | 2015-02-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
1335EXT1 | EXTERIOR DOOR REPLACEMENT | 1335 | The exterior door to the pump house is in poor shape and is delaminating due to excess moisture and age. This project would provide for a new exterior door/frame assembly including door hardware. A paintable metal door system was used for this estimate and will help reduce maintenance costs related to wood. This door should be replaced in the next two years. This project or a portion there of was previously recommended in the FCA report dated 8/1/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 2/18/2015. | IRRIGATION PUMP HOUSE | 9925 | CNR | Parks |  | Genoa | 1977 | 160 | 2015-02-18 | Immediate to Two Years | Currently Critical | 1 | 2000
1335EXT2 | EXTERIOR FINISHES | 1335 | The cyclical treatment of the building exterior is very important to help maintain the finish, weather proofing, integrity and appearance of the building. This treatment does not include the roofing material itself but it should include everything that has to do with weather proofing the building envelope including painting or staining, sealing, repairing the chinking and caulking where applicable. This project should be scheduled on a cyclical basis. Interior and exterior chinking maintenance is also part of this project. | IRRIGATION PUMP HOUSE | 9925 | CNR | Parks |  | Genoa | 1977 | 160 | 2015-02-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1600
1333EXT2 | EXTERIOR FINISHES | 1333 | The cyclical treatment of the building exterior is very important to help maintain the finish, weather proofing, integrity and appearance of the building. This treatment does not include the roofing material itself but it should include everything that has to do with weather proofing the building envelope including painting or staining, sealing, repair, and caulking where applicable. This project should be scheduled on a cyclical basis. | GROUP RAMADA | 9925 | CNR | Parks |  | Genoa | 1977 | 1268 | 2015-02-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6340
2686EXT1 | CHICKEN COOP - NORTHEAST DEMOLITION | 2686 | The Chicken Coop - Northeast is an abandoned outbuilding on the newly acquired Campbell property. This structure is in poor condition and is not proposed to be used by the park staff. This project would provide for the demolition of this building. This project or a portion there of was previously recommended in the FCA report dated 8/1/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 2/18/2015. | CHICKEN COOP | 9925 | CNR | Parks |  | Genoa | 1945 | 350 | 2015-02-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3500
2680EXT1 | INTERIOR / EXTERIOR FINISHES | 2680 | The cyclical treatment of the building interior and exterior is very important to help maintain the finish, weather proofing, integrity and appearance of the building. This treatment does not include the roofing material itself but it should include everything that has to do with weather proofing the building envelope including painting or staining, sealing, repairing the chinking and caulking where applicable. This project should be scheduled on a cyclical basis. Exterior chinking maintenance and interior painting is also included in this estimate. | COMFORT STATION | 9925 | CNR | Parks |  | Genoa | 2006 | 783 | 2015-02-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3915
2682INT1 | INTERIOR FINISHES | 2682 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | CAMPBELL HOUSE-PARK OFFICE | 9925 | CNR | Parks |  | Genoa | 1945 | 1400 | 2015-02-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7000
2680PLM1 | WATER HEATER REPLACEMENT | 2680 | There is a 20 gallon electric water heater that is approaching 10 years old and should be scheduled for replacement. The average lifespan is 8-12 years for a water heater based on average use. This project would provide for a new 20 gallon electric water heater to be installed. Removal and disposal of the existing unit is included in this estimate. | COMFORT STATION | 9925 | CNR | Parks |  | Genoa | 2006 | 783 | 2015-02-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 850
2683EXT3 | EXTERIOR FINISHES | 2683 | It is important to maintain the finish, weather resistance and appearance of the building. The exterior finish on the building is starting to peel and blister. This project would provide funding to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. This building should be painted in the next two years. This project or a portion there of was previously recommended in the FCA report dated 8/1/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 2/18/2015. | PUMP HOUSE STORAGE | 9925 | CNR | Parks |  | Genoa | 1945 | 100 | 2015-02-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
2682PLM1 | REPLACE WATER HEATER | 2682 | The average life span of a typical gas/oil or electric water heater is eight to ten years. With the passage of time and constant use, this unit will be reaching the end of its useful life in approximately two to three years. It is recommended that a new natural gas water heater be installed for more efficient use of energy. This estimate includes 100 feet of gas pipe, fittings, couplers, and labor for installation. This project or a portion there of was previously recommended in the FCA report dated 8/1/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 2/18/2015. | CAMPBELL HOUSE-PARK OFFICE | 9925 | CNR | Parks |  | Genoa | 1945 | 1400 | 2015-02-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
2682ADA1 | ACCESSIBLE BUILDING ENTRANCE | 2682 | The existing exterior entry door and frame are original to the building. The entrance door system does not meet the requirements for ADA Accessibility. This project would provide for a new door, frame, lever action hardware, threshold and exterior landing to be installed. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 8/1/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 2/18/2015. | CAMPBELL HOUSE-PARK OFFICE | 9925 | CNR | Parks |  | Genoa | 1945 | 1400 | 2015-02-18 | Immediate to Two Years | Currently Critical | 1 | 5500
2682ELE1 | ELECTRICAL UPGRADE | 2682 | The building was originally a residence and now is being used as the park office. The electrical system is original and does not have the capacity for it's current use as a park office. This project would provide for a complete electrical upgrade including a new 200 amp service, rewire, and outlet installation. | CAMPBELL HOUSE-PARK OFFICE | 9925 | CNR | Parks |  | Genoa | 1945 | 1400 | 2015-02-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 21000
2682SFT1 | LIFE SAFETY UPGRADES | 2682 | The building's original occupancy and use was a residence. State park is currently using the facility as a park office which requires the addition of exit signs, a fire alarm and smoke detection system. This project would provide for the installation of new exit signs, a fire alarm and smoke detection system. | CAMPBELL HOUSE-PARK OFFICE | 9925 | CNR | Parks |  | Genoa | 1945 | 1400 | 2015-02-18 | Immediate to Two Years | Currently Critical | 1 | 9800
2682EXT3 | EXTERIOR FINISHES | 2682 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are sanding, priming and painting, and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CAMPBELL HOUSE-PARK OFFICE | 9925 | CNR | Parks |  | Genoa | 1945 | 1400 | 2015-02-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7000
2681EXT1 | EXTERIOR FINISHES | 2681 | The cyclical treatment of the kiosk exterior is very important to help maintain the finish, weather proofing, integrity and appearance of the structure. This treatment does not include the roofing material itself but it should include everything that has to do with weather proofing the kiosk including painting or staining, sealing, repair, and caulking where applicable. This project should be scheduled on a cyclical basis. | PARK KIOSK | 9925 | CNR | Parks |  | Genoa | 1998 | 36 | 2015-02-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 200
2684EXT2 | EXTERIOR FINISHES | 2684 | It is important to maintain the finish, weather resistance and appearance of the building. The exterior finish on the building is starting to peel and blister and some of the wood siding is damaged. This project would provide funding to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. Additional monies are included to replace damaged siding as needed and repair / stabilize the stairs. This building should be painted in the next two years. This project or a portion there of was previously recommended in the FCA report dated 8/1/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 2/18/2015. | BLACKSMITH SHOP | 9925 | CNR | Parks |  | Genoa | 1945 | 900 | 2015-02-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
2378EXT1 | EXTERIOR FINISHES | 2378 | The cyclical treatment of the building exterior is very important to help maintain the finish, weather proofing, integrity and appearance of the building. This treatment does not include the roofing material itself but it should include everything that has to do with water proofing the building envelope including painting or staining, sealing, repair, and caulking where applicable; for example, around all windows, flashing, fixtures, sills, etc. | WAGON SHED | 9925 | CNR | Parks |  | Genoa | 1995 | 800 | 2015-02-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
2680INT1 | INSTALL FIBERGLASS REINFORCED PANEL (FRP) | 2680 | There is a small mop sink in the janitor's storage room. The gypsum wall board behind the mop sink is damaged from exposure to water and should be repaired and protected. This project would provide for repairs to the wall board and installation of a fiberglass reinforced panel (FRP) on the walls adjacent to the sink. | COMFORT STATION | 9925 | CNR | Parks |  | Genoa | 2006 | 783 | 2015-02-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 400
2682ADA2 | ADA RESTROOM ADDITION | 2682 | The existing building was originally a residence and is now being used as a park office. Staff indicated that the public does use the park office on occasions. The existing restroom does not meet ADA accessibility requirements. This project would provide for the existing restroom to be remodeled into a unisex ADA compliant restroom including toilet, sink, door and hardware, signage and toilet accessories. Minor demolition and finishes including flooring and paint is included in this estimate. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | CAMPBELL HOUSE-PARK OFFICE | 9925 | CNR | Parks |  | Genoa | 1945 | 1400 | 2015-02-18 | Immediate to Two Years | Currently Critical | 1 | 15000
9925SIT6 | DRINKING FOUNTAIN REPLACEMENT | 9925 | There are 4 drinking fountains scattered around the park which are damaged from freeze thaw cycles. This project would provide for the replacement of these fountains with 4 new fountains. It is recommended that they be in a style compatible with the park's history and also be ADA compliant. | MORMON STATION STATE HISTORIC PARK SITE | 9925 | CNR | Parks |  | Genoa | 0 |  | 2015-02-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14000
9925SIT4 | PARKING LOT ADDITION | 9925 | The site currently has only a portion of the parking area paved. The area paved is where the ADA accessible parking is located. The rest of the parking area is loose compacted soil and gravel. This project would provide for 3" of asphalt concrete paving over 6" of compacted base. The length of the parking area used for this estimate is 300 feet and the width 25 feet. This project or a portion there of was previously recommended in the FCA report dated 8/1/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 2/18/2015. | MORMON STATION STATE HISTORIC PARK SITE | 9925 | CNR | Parks |  | Genoa | 0 |  | 2015-02-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 45000
9925PLM1 | GRINDER PUMP REPLACEMENT | 9925 | There are two grinder pumps which are problematic, failing and should be scheduled for replacement. This project would provide for the replacement of two grinder pumps including all required connections to existing utilities. Removal of the existing pumps is included in this estimate. | MORMON STATION STATE HISTORIC PARK SITE | 9925 | CNR | Parks |  | Genoa | 0 |  | 2015-02-18 | Immediate to Two Years | Currently Critical | 1 | 6000
9925SIT5 | STOCKADE GATE REPAIR | 9925 | The stockade gate on the south side of the stockade fence is in need of modifications to allow the gate to open properly. This project would provide for the modification of the gate including but not limited to adding sturdy wheels and hardware for ease of operation and stability. | MORMON STATION STATE HISTORIC PARK SITE | 9925 | CNR | Parks |  | Genoa | 0 |  | 2015-02-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
9925SIT7 | CRACK FILL / SEAL ASPHALT PAVING | 9925 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the paving at the ADA accessible parking spaces. Striping is included in this estimate. This project should be scheduled on a 4 year cyclical basis to maintain the integrity of the paving and prevent premature failure. If the new parking area project is completed, this project recommends the same level of maintenance. | MORMON STATION STATE HISTORIC PARK SITE | 9925 | CNR | Parks |  | Genoa | 0 |  | 2015-02-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 462
1374EXT1 | EXTERIOR/ INTERIOR FINISHES | 1374 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 10/03/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/27/2015. | TRT CXT TOILET - MARLETTE CAMPGROUND | 9928 | CNR | Parks |  | Lake Tahoe/Spooner | 2006 | 81 | 2015-10-27 | Four to Ten Years | Long-Term Needs | 3 | 810
1375EXT1 | EXTERIOR/ INTERIOR FINISHES | 1375 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 10/03/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/27/2015. | MARLETTE LAKE CXT TOILET | 9928 | CNR | Parks |  | Lake Tahoe/Spooner | 2000 | 81 | 2015-10-27 | Four to Ten Years | Long-Term Needs | 3 | 810
1376EXT1 | EXTERIOR/ INTERIOR FINISHES | 1376 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NORTH CANYON CXT TOILET | 9928 | CNR | Parks |  | Lake Tahoe/Spooner | 2000 | 81 | 2015-10-27 | Four to Ten Years | Long-Term Needs | 3 | 810
1371EXT2 | ROOF REPLACEMENT | 1371 | The wood shingle roof was installed in 1989. It is recommended that this building be re-roofed in the next 4-5 years with a new standing seam metal roof and new underlayments. This estimate includes removal and disposal of the old roofing. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. | SPENCER'S CABIN | 9928 | CNR | Parks |  | Lake Tahoe/Spooner | 1920 | 280 | 2015-10-27 | Immediate to Two Years | Currently Critical | 1 | 4760
1292EXT2 | EXTERIOR FINISHES | 1292 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | PARK CONCESSION | 9928 | CNR | Parks |  | Lake Tahoe/Spooner | 1977 | 1142 | 2015-10-27 | Four to Ten Years | Long-Term Needs | 3 | 11420
1292INT1 | INTERIOR FINISHES | 1292 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 10/03/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/27/2015. | PARK CONCESSION | 9928 | CNR | Parks |  | Lake Tahoe/Spooner | 1977 | 1142 | 2015-10-27 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11420
1291EXT1 | EXTERIOR FINISHES | 1291 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building, excluding the roof. Included in the cost is; sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 10/03/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/27/2015. | FEE STATION | 9928 | CNR | Parks |  | Lake Tahoe/Spooner | 1991 | 160 | 2015-10-27 | Four to Ten Years | Long-Term Needs | 3 | 1600
1291INT1 | INTERIOR FINISHES | 1291 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and adequately prepared to receive the coating. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 10/03/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/27/2015. | FEE STATION | 9928 | CNR | Parks |  | Lake Tahoe/Spooner | 1991 | 160 | 2015-10-27 | Four to Ten Years | Long-Term Needs | 3 | 1600
1290EXT2 | ROOF REPLACEMENT | 1290 | The asphalt roll roofing on this building was in poor condition at the time of the survey and had active leaks. It is recommended that this building be re-roofed in the next 1-2 years with a new single-ply roofing system which will be installed directly over the existing asphalt roll roofing. This will allow the roof to qualify for the statewide roofing program warranty and preventative maintenance agreement. | COMFORT STATION | 9928 | CNR | Parks |  | Lake Tahoe/Spooner | 1977 | 448 | 2015-10-27 | Immediate to Two Years | Currently Critical | 1 | 5376
1290INT1 | INTERIOR FINISHES | 1290 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and adequately prepared to receive the coating. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 10/03/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/27/2015. | COMFORT STATION | 9928 | CNR | Parks |  | Lake Tahoe/Spooner | 1977 | 448 | 2015-10-27 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4480
1323EXT1 | EXTERIOR FINISHES | 1323 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | WELL HOUSE | 9928 | CNR | Parks |  | Lake Tahoe/Spooner | 1977 | 1000 | 2015-10-27 | Immediate to Two Years | Currently Critical | 1 | 10000
1371EXT1 | EXTERIOR FINISHES | 1371 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing and staining the wood and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be stained and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. This project or a portion thereof was previously recommended in the FCA report dated 10/03/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/27/2015. | SPENCER'S CABIN | 9928 | CNR | Parks |  | Lake Tahoe/Spooner | 1920 | 280 | 2015-10-27 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2800
1323INT1 | INTERIOR FINISHES | 1323 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and adequately prepared to receive the coating. An epoxy-based paint should be utilized in wet areas for durability. | WELL HOUSE | 9928 | CNR | Parks |  | Lake Tahoe/Spooner | 1977 | 1000 | 2015-10-27 | Immediate to Two Years | Currently Critical | 1 | 10000
1372EXT1 | EXTERIOR FINISHES | 1372 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing and staining the wood and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be stained and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. This project or a portion thereof was previously recommended in the FCA report dated 10/03/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/27/2015. | RED HOUSE | 9928 | CNR | Parks |  | Lake Tahoe/Spooner | 1910 | 947 | 2015-10-27 | Four to Ten Years | Long-Term Needs | 3 | 9470
1372EXT2 | ROOF REPLACEMENT | 1372 | The wood shingle roof was installed in 1989. It is recommended that this building be re-roofed in the next 4-5 years with a new standing seam metal roof and new underlayments. This estimate includes removal and disposal of the old roofing. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. | RED HOUSE | 9928 | CNR | Parks |  | Lake Tahoe/Spooner | 1910 | 947 | 2015-10-27 | Four to Ten Years | Long-Term Needs | 3 | 16099
1325EXT1 | ROOF REPLACEMENT | 1325 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 1-2 years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. | PUMP HOUSE | 9928 | CNR | Parks |  | Lake Tahoe/Spooner | 1977 | 24 | 2015-10-27 | Immediate to Two Years | Currently Critical | 1 | 288
1325EXT2 | EXTERIOR FINISHES | 1325 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | PUMP HOUSE | 9928 | CNR | Parks |  | Lake Tahoe/Spooner | 1977 | 24 | 2015-10-27 | Immediate to Two Years | Currently Critical | 1 | 240
1323ELE1 | ELECTRICAL TRANSFORMER REPLACEMENT | 1323 | The electrical transformer that provides electrical services to the building was damaged at the time of inspection and does not function properly. This project recommends replacing the electrical transformer. | WELL HOUSE | 9928 | CNR | Parks |  | Lake Tahoe/Spooner | 1977 | 1000 | 2015-10-27 | Immediate to Two Years | Currently Critical | 1 | 5000
1323EXT2 | ROOF REPLACEMENT | 1323 | The roof is due for replacement. This project would provide funds for: the demolition of the tar and gravel roof; the demolition of the underlayment; the installation of a new single-ply membrane roof; and the installation of sheet metal over the rafter tails. Additionally, this project will provide funds to fabricate the drip edge over the rafter tails to prevent the collection of snow and moisture and to keep the moisture from running back into the building. | WELL HOUSE | 9928 | CNR | Parks |  | Lake Tahoe/Spooner | 1977 | 1000 | 2015-10-27 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
1290EXT1 | EXTERIOR FINISHES | 1290 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 10/03/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/27/2015. | COMFORT STATION | 9928 | CNR | Parks |  | Lake Tahoe/Spooner | 1977 | 448 | 2015-10-27 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4480
2696EXT1 | EXTERIOR FINISHES | 2696 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing and staining the wood and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be stained and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. This project or a portion thereof was previously recommended in the FCA report dated 10/03/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/27/2015. | BUNK HOUSE | 9928 | CNR | Parks |  | Lake Tahoe/Spooner | 1911 | 338 | 2015-10-27 | Four to Ten Years | Long-Term Needs | 3 | 3380
2696EXT2 | ROOF REPLACEMENT | 2696 | The wood shingle roof on this building was installed in 1989. It is recommended that this building be re-roofed in the next 4-5 years with a new standing seam metal roof and new underlayments. This estimate includes removal and disposal of the old roofing. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. | BUNK HOUSE | 9928 | CNR | Parks |  | Lake Tahoe/Spooner | 1911 | 338 | 2015-10-27 | Four to Ten Years | Long-Term Needs | 3 | 5746
2697EXT1 | EXTERIOR FINISHES | 2697 | It is important to maintain the finish, weather resistance and appearance of the kiosk. This project would provide funding to protect the exterior of the kiosk excluding the roof. Included in the cost is power washing and staining the wood. It is recommended that the building be stained in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 10/03/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/27/2015. | SPOONER SUMMIT TRT KIOSK | 9928 | CNR | Parks |  | Lake Tahoe/Spooner | 0 | 50 | 2015-10-27 | Four to Ten Years | Long-Term Needs | 3 | 500
2697EXT2 | ROOF REPLACEMENT | 2697 | The wood shingle roofing on the building is original and should be scheduled for replacement. This project would remove and dispose of the existing wood shingle roofing and install new pre-painted metal panels in the next 4-5 years. | SPOONER SUMMIT TRT KIOSK | 9928 | CNR | Parks |  | Lake Tahoe/Spooner | 0 | 50 | 2015-10-27 | Four to Ten Years | Long-Term Needs | 3 | 850
2698EXT1 | EXTERIOR FINISHES | 2698 | It is important to maintain the finish, weather resistance and appearance of the kiosk. This project would provide funding to protect the exterior of the kiosk excluding the roof. Included in the cost is power washing and staining the wood. It is recommended that the building be stained in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 10/03/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/27/2015. | BARK BEETLE KIOSK | 9928 | CNR | Parks |  | Lake Tahoe/Spooner | 0 | 36 | 2015-10-27 | Four to Ten Years | Long-Term Needs | 3 | 500
2699EXT1 | EXTERIOR/ INTERIOR FINISHES | 2699 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 10/03/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/27/2015. | HOBART CXT TOILET | 9928 | CNR | Parks |  | Lake Tahoe/Spooner | 2006 | 81 | 2015-10-27 | Two to Four Years | Necessary - Not Yet Critical | 2 | 810
2698EXT2 | ROOF REPLACEMENT | 2698 | The asphalt roll roofing covering the building is original and should be scheduled for replacement. This project would remove and dispose of the existing asphalt roll roofing and install new pre-painted metal panels in the next 2-3 years. | BARK BEETLE KIOSK | 9928 | CNR | Parks |  | Lake Tahoe/Spooner | 0 | 36 | 2015-10-27 | Two to Four Years | Necessary - Not Yet Critical | 2 | 612
3672EXT1 | CONSERVE AND PROTECT VACANT BUILDING | 3672 | The wood structure is over 80 years old and there are numerous areas where the wood is splitting, warping and deteriorating. This is also an exhibit for the park and requires maintenance time for presentation and displays. This project would provide for caulking the flashing, fixtures and windows, replacing metal roof panels as needed and maintaining the exhibit in a state of arrested decay. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HANNA'S HIDEAWAY | 9928 | CNR | Parks |  | Lake Tahoe/Spooner | 1929 | 168 | 2015-10-27 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5600
3756INT1 | INTERIOR FINISHES | 3756 | It is recommended to stain the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to staining, all surfaces should be repaired and adequately prepared to receive the coating. An epoxy-based stain should be utilized in wet areas for durability. | SPOONER CABIN | 9928 | CNR | Parks |  | Incline Village | 1998 | 340 | 2015-10-27 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3400
3756EXT1 | EXTERIOR FINISHES | 3756 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing and staining the wood and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be stained and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SPOONER CABIN | 9928 | CNR | Parks |  | Incline Village | 1998 | 340 | 2015-10-27 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3400
3757INT1 | INTERIOR FINISHES | 3757 | It is recommended to stain the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to staining, all surfaces should be repaired and adequately prepared to receive the coating. An epoxy-based stain should be utilized in wet areas for durability. | WILDCAT CABIN | 9928 | CNR | Parks |  | Incline Village | 1998 | 230 | 2015-10-27 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2300
3758INT1 | INTERIOR FINISHES | 3758 | It is recommended to stain the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to staining, all surfaces should be repaired and adequately prepared to receive the coating. | DEMONSTRATION CABIN | 9928 | CNR | Parks |  | Incline Village | 1998 | 80 | 2015-10-27 | Two to Four Years | Necessary - Not Yet Critical | 2 | 800
3758EXT1 | EXTERIOR FINISHES | 3758 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing and staining the wood and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be stained and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | DEMONSTRATION CABIN | 9928 | CNR | Parks |  | Incline Village | 1998 | 80 | 2015-10-27 | Two to Four Years | Necessary - Not Yet Critical | 2 | 800
9928SIT2 | CRACK FILL & SEAL ASPHALT PAVING | 9928 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the paving site wide including access roads, parking areas, and park pathways. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 279,875 square feet of asphalt area was used to generate this estimate. This project or a portion thereof was previously recommended in the FCA report dated 07/01/2003 and 10/03/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/27/2015. | LAKE TAHOE NV-SPOONER LAKE STATE PARK | 9928 | CNR | Parks |  | Lake Tahoe/Spooner | 0 |  | 2015-10-27 | Two to Four Years | Necessary - Not Yet Critical | 2 | 349844
9928ADA1 | ADA SIGNAGE | 9928 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed or upgraded at each accessible parking area and accessible paths of travel throughout the park. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | LAKE TAHOE NV-SPOONER LAKE STATE PARK | 9928 | CNR | Parks |  | Lake Tahoe/Spooner | 0 |  | 2015-10-27 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
9928ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 9928 | This site contains water fountains that are not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of six drinking fountains to meet the ADA requirements. | LAKE TAHOE NV-SPOONER LAKE STATE PARK | 9928 | CNR | Parks |  | Lake Tahoe/Spooner | 0 |  | 2015-10-27 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
3757EXT1 | EXTERIOR FINISHES | 3757 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing and staining the wood and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be stained and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | WILDCAT CABIN | 9928 | CNR | Parks |  | Incline Village | 1998 | 230 | 2015-10-27 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2300
1598HVA1 | ELECTRIC HEATER REPLACEMENT | 1598 | There is an electric heater in the building that has reached the end of its life expectancy. This project recommends replacing the electric heater. The estimate includes removal and disposal of the existing equipment. | WELL HOUSE | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 640 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
1603SIT1 | RELOCATE AND REMODEL | 1603 | The design of the building has proven to be inadequate in both size and location. The staff regularly sits outside of the building to collect fees stating that the building is too small and uncomfortable to stay inside. The building is also too close to the access road and has been hit by vehicles, trailers and boats on many occasions. This project would provide for moving the entire structure back from the road and adding 50 square feet of floor area. A new roof should be included for the entire structure. This project or a portion thereof was previously recommended in the FCA report dated 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | BOAT RAMP FEE STATION | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 48 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35000
1566ENR1 | LIGHTING UPGRADE | 1566 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in restrooms, conference rooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | MAIN OFFICE COMPLEX | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 1550 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5425
1603INT2 | INTERIOR FINISHES | 1603 | It is recommended to paint the interior walls and ceilings at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | BOAT RAMP FEE STATION | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 48 | 2015-10-28 | Four to Ten Years | Long-Term Needs | 3 | 480
1599EXT3 | ROOF REPLACEMENT | 1599 | The wood shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year metal roofing system and new underlayments. This estimate includes removal and disposal of the old roof. | MAIN FEE STATION | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 90 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1080
1599HVA1 | ELECTRIC HEATER REPLACEMENT | 1599 | There is an electric heater in the building that has reached the end of its life expectancy. This project recommends replacing the electric heater. The estimate includes removal and disposal of the existing equipment. | MAIN FEE STATION | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 90 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
1599INT2 | FLOORING REPLACEMENT | 1599 | The wood flooring in the Fee Station is damaged and reaching the end of its useful life. This project would provide for removal and disposal of the wood flooring and the installation of a new subfloor and 12x12 VCT with a 6" base. | MAIN FEE STATION | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 90 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1350
1599EXT1 | EXTERIOR FINISHES | 1599 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building, excluding the roof. Included in the cost is; sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | MAIN FEE STATION | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 90 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 900
1603EXT2 | EXTERIOR FINISHES | 1603 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building, excluding the roof. Included in the cost is; sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BOAT RAMP FEE STATION | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 48 | 2015-10-28 | Four to Ten Years | Long-Term Needs | 3 | 480
1599EXT2 | EXTERIOR DOOR REPLACEMENT | 1599 | The existing exterior wood door appears to be original to the building. It is damaged from age and general wear and tear. This project would provide for the replacement and installation of a new metal door, frame and hardware. Removal and disposal of the existing door and painting of the new door is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | MAIN FEE STATION | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 90 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
1593ENR1 | LIGHTING UPGRADE | 1593 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | WOOD SHOP | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 546 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4200
1598EXT1 | EXTERIOR FINISHES | 1598 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building, excluding the roof. Included in the cost is; sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | WELL HOUSE | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 640 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6400
1593INT1 | INTERIOR FINISHES | 1593 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and adequately prepared to receive the coating. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | WOOD SHOP | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 546 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5460
1593ENV1 | DUST COLLECTION SYSTEM INSTALLATION | 1593 | The building has a woodshop which does not have a complete dust collection system. In order to reduce the possibility of damage or injury, each piece of equipment should have complete collection capability. This project recommends installing a new dust collection system. | WOOD SHOP | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 546 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
1593SFT1 | EXTERIOR LANDING INSTALLATION | 1593 | There is an out-swinging exterior door from the building which swings out over a steep ramp and does not have a landing. This does not comply with 2012 IBC Section 1008: 1008.1.6 Landings at doors, which states, "Landings shall have a width not less than the width of the stairway or the door, whichever is greater. Doors in the fully open position shall not reduce a required dimension by more than 7 inches (178mm). When a landing serves an occupant load of 50 or more, doors in any position shall not reduce the landing to less than one-half its required width. Landings shall have a length measured in the direction of travel of not less than 44 inches (1118mm)." This project would provide for the installation of a compliant landing for the door. | WOOD SHOP | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 546 | 2015-10-28 | Immediate to Two Years | Currently Critical | 1 | 5000
1593SFT2 | EXIT SIGN AND EGRESS LIGHTING INSTALLATION | 1593 | The building does not have any emergency lighting and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. | WOOD SHOP | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 546 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1365
1593EXT2 | EXTERIOR FINISHES | 1593 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building, excluding the roof. Included in the cost is; sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | WOOD SHOP | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 546 | 2015-10-28 | Four to Ten Years | Long-Term Needs | 3 | 5460
1593HVA1 | ELECTRIC HEATER REPLACEMENT | 1593 | There is a ceiling mounted electric heater in the building that has reached the end of its life expectancy. This project recommends replacing the electric heater. The estimate includes removal and disposal of the existing equipment. | WOOD SHOP | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 546 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
1599INT1 | INTERIOR FINISHES | 1599 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. This project or a portion thereof was previously recommended in the FCA report dated and 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | MAIN FEE STATION | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 90 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 900
1548PLM2 | RESTROOM FIXTURES REPLACEMENT | 1548 | The existing restroom fixtures are original to the building. They are worn and damaged from many years of use and should be scheduled for replacement. This project recommends the replacement of the existing fixtures, to include: 3 water closets; 1 urinal; 2 sinks, and 2 faucets. | COMFORT STATION #6 | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 448 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
1566INT2 | FLOORING REPLACEMENT | 1566 | The VCT (vinyl composite tile) and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the next 2-3 years. This project or a portion thereof was previously recommended in the FCA report dated 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | MAIN OFFICE COMPLEX | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 1550 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3600
1559PLM1 | BACKFLOW PREVENTION | 1559 | State Health Law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of backsiphonage or backpressure. This project allows for the installation of double check valves or reduced pressure principle backflow preventers as appropriate to the hazard and in appropriate locations near the potential source of contamination. Costs include an above ground vault, and allowance for 200 feet of 1" conduit to provide power for freeze protection. | COMFORT STATION #8 | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 2016 | 378 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35000
1559PLM3 | RESTROOM FIXTURES REPLACEMENT | 1559 | The existing restroom fixtures are original to the building. They are worn and damaged from many years of use and should be scheduled for replacement. This project recommends the replacement of the existing fixtures, to include: 3 water closets; 1 urinal; 2 sinks, and 2 faucets. | COMFORT STATION #8 | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 2016 | 378 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
1549PLM2 | RESTROOM FIXTURES REPLACEMENT | 1549 | The existing restroom fixtures are original to the building. They are worn and damaged from many years of use and should be scheduled for replacement. This project recommends the replacement of the existing fixtures including 3 water closets, 1 urinal, 2 sinks and 2 faucets. | COMFORT STATION #7 | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 2016 | 378 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
1549PLM1 | BACKFLOW PREVENTION | 1549 | State Health Law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of backsiphonage or backpressure. This project allows for the installation of double check valves or reduced pressure principle backflow preventers as appropriate to the hazard and in appropriate locations near the potential source of contamination. Costs include an above ground vault, and allowance for 200 feet of 1" conduit to provide power for freeze protection. | COMFORT STATION #7 | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 2016 | 378 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35000
1549EXT2 | EXTERIOR FINISHES | 1549 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building, excluding the roof. Included in the cost is; sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | COMFORT STATION #7 | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 2016 | 378 | 2015-10-28 | Four to Ten Years | Long-Term Needs | 3 | 4480
1559PLM2 | EXTERIOR FINISHES | 1559 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building, excluding the roof. Included in the cost is; sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | COMFORT STATION #8 | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 2016 | 378 | 2015-10-28 | Four to Ten Years | Long-Term Needs | 3 | 4480
1548PLM1 | BACKFLOW PREVENTION | 1548 | State Health Law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of backsiphonage or backpressure. This project allows for the installation of double check valves or reduced pressure principle backflow preventers as appropriate to the hazard and in appropriate locations near the potential source of contamination. Costs include an above ground vault, and allowance for 200 feet of 1" conduit to provide power for freeze protection. | COMFORT STATION #6 | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 448 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35000
1566ELE1 | ELECTRICAL UPGRADE | 1566 | A portion of the building is used as office space by the staff. This space is required to be operational at all times, under all conditions. This project will provide for some additional capacity and hardware needed to operate the building's electrical system via the emergency generator. This project or a portion thereof was previously recommended in the FCA report dated 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | MAIN OFFICE COMPLEX | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 1550 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
15482 | EXTERIOR FINISHES | 1548 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building, excluding the roof. Included in the cost is; sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | COMFORT STATION #6 | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 448 | 2015-10-28 | Four to Ten Years | Long-Term Needs | 3 | 4480
1548INT2 | INTERIOR FINISHES | 1548 | It is recommended to paint the partitions and ceilings and re-caulk the Fiberglass Reinforced Panels (FRP) at least once in the next 4-5 years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project should be scheduled on a cyclical basis to maintain the integrity of the structure. | COMFORT STATION #6 | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 448 | 2015-10-28 | Four to Ten Years | Long-Term Needs | 3 | 4480
1538INT2 | INTERIOR FINISHES | 1538 | It is recommended to paint the partitions and ceilings and re-caulk the Fiberglass Reinforced Panels (FRP) at least once in the next 4-5 years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project should be scheduled on a cyclical basis to maintain the integrity of the structure. | COMFORT STATION #5 | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 448 | 2015-10-28 | Four to Ten Years | Long-Term Needs | 3 | 4480
1538PLM1 | RESTROOM FIXTURES REPLACEMENT | 1538 | The existing restroom fixtures are original to the building. They are worn and damaged from many years of use and should be scheduled for replacement. This project recommends the replacement of the existing fixtures, to include: 3 water closets; 1 urinal; 2 sinks, and 2 faucets. | COMFORT STATION #5 | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 448 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
1538PLM2 | BACKFLOW PREVENTION | 1538 | State Health Law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of backsiphonage or backpressure. This project allows for the installation of double check valves or reduced pressure principle backflow preventers as appropriate to the hazard and in appropriate locations near the potential source of contamination. Costs include an above ground vault, and allowance for 200 feet of 1" conduit to provide power for freeze protection. | COMFORT STATION #5 | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 448 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35000
1538EXT2 | EXTERIOR FINISHES | 1538 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building, excluding the roof. Included in the cost is; sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | COMFORT STATION #5 | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 448 | 2015-10-28 | Four to Ten Years | Long-Term Needs | 3 | 4480
15492 | INTERIOR FINISHES | 1549 | It is recommended to paint the partitions and ceilings and re-caulk the Fiberglass Reinforced Panels (FRP) at least once in the next 4-5 years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project should be scheduled on a cyclical basis to maintain the integrity of the structure. | COMFORT STATION #7 | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 2016 | 378 | 2015-10-28 | Four to Ten Years | Long-Term Needs | 3 | 4480
1567EXT2 | EXTERIOR FINISHES | 1567 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building, excluding the roof. Included in the cost is; sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SHOP | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 1620 | 2015-10-28 | Four to Ten Years | Long-Term Needs | 3 | 16200
1575EXT1 | EXTERIOR FINISHES | 1575 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building, excluding the roof. Included in the cost is sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | STORAGE/ MAINTENANCE OFFICE | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 400 | 2015-10-28 | Four to Ten Years | Long-Term Needs | 3 | 4000
1575INT1 | INTERIOR FINISHES | 1575 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | STORAGE/ MAINTENANCE OFFICE | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 400 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
1575SFT2 | EXTERIOR STAIR HANDRAIL REPLACEMENT | 1575 | The stair handrails and guardrails leading up to the second story of the Storage/ Maintenance Office do not meet code for safety. This project recommends the installation of handrails and guardrails in accordance with the 2012 IBC Section 1012 and Section 1013. Removal and disposal of the existing rails is included in the estimate. | STORAGE/ MAINTENANCE OFFICE | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 400 | 2015-10-28 | Immediate to Two Years | Currently Critical | 1 | 13200
1575SFT1 | SAFETY CABINETS | 1575 | The storage room is located on the ground floor and contains many different paints, stains and other hazardous products. This does not meet OSHA standards for hazardous materials containment. This project would provide two hazardous storage containers in the building and install placards on the building exterior in accordance with OSHA 1910.106 (d). This project or a portion thereof was previously recommended in the FCA report dated 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | STORAGE/ MAINTENANCE OFFICE | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 400 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
1568EXT2 | ROOF REPLACEMENT | 1568 | The asphalt roof on the building is in poor condition and had active leaks at the time of the survey. It is recommended that this building be re-roofed in the next 4-5 years with a new single-ply roofing system. This will allow the roof to qualify for the statewide roofing warranty and preventative maintenance agreement programs. | SEWER PLANT COVER | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1985 | 630 | 2015-10-28 | Four to Ten Years | Long-Term Needs | 3 | 7560
1568EXT1 | EXTERIOR FINISHES | 1568 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | SEWER PLANT COVER | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1985 | 630 | 2015-10-28 | Four to Ten Years | Long-Term Needs | 3 | 2520
1559INT2 | INTERIOR FINISHES | 1559 | It is recommended to paint the partitions and ceilings and re-caulk the Fiberglass Reinforced Panels (FRP) at least once in the next 4-5 years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project should be scheduled on a cyclical basis to maintain the integrity of the structure. | COMFORT STATION #8 | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 2016 | 378 | 2015-10-28 | Four to Ten Years | Long-Term Needs | 3 | 4480
1386EXT2 | EXTERIOR FINISHES | 1386 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building, excluding the roof. Included in the cost is; sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | COMFORT STATION #4 | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 1250 | 2015-10-28 | Four to Ten Years | Long-Term Needs | 3 | 12500
1575SFT3 | STORAGE REMOVAL | 1575 | Items in this building are stored too close to the ceiling. The 2012 IFC Section 315.3.1 states that, "Storage shall be maintained 2 feet or more below the ceiling in nonsprinklered areas of buildings or a minimum of 18 inches below sprinkler head deflectors in sprinklered areas of buildings." This project would provide for the removal of all items in conflict with code requirements to ensure that the fire suppression system operates correctly. | STORAGE/ MAINTENANCE OFFICE | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 400 | 2015-10-28 | Immediate to Two Years | Currently Critical | 1 | 1000
1567EXT3 | EXTERIOR DOOR REPLACEMENT | 1567 | The exterior wood man door appears to be original to the building. It is damaged from age and general wear and tear. This project would provide for the replacement of the wood door with new metal door, frame and hardware. Removal and disposal of the existing door and painting of the new door is included in this estimate. | SHOP | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 1620 | 2015-10-28 | Four to Ten Years | Long-Term Needs | 3 | 3000
1567PLM1 | WATER HEATER REPLACEMENT | 1567 | There is a 50 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 1-2 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | SHOP | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 1620 | 2015-10-28 | Immediate to Two Years | Currently Critical | 1 | 1500
1567INT2 | INTERIOR DOOR REPLACEMENT | 1567 | The interior doors in this building are hollow core units and most are damaged. This project would provide for the installation of new solid core interior doors including frames, lever action door handles, hardware and paint. Removal and disposal of the existing doors is included in this cost estimate. A total of 3 interior doors was used in this estimate. | SHOP | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 1620 | 2015-10-28 | Four to Ten Years | Long-Term Needs | 3 | 3000
1566INT1 | INTERIOR FINISHES | 1566 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | MAIN OFFICE COMPLEX | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 1550 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15500
1566SFT1 | EXIT SIGN AND EGRESS LIGHTING INSTALLATION | 1566 | The building does not have any emergency lighting and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. International Building Code 2012 Chapter 10 was referenced for this project. | MAIN OFFICE COMPLEX | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 1550 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3875
1566EXT2 | EXTERIOR FINISHES | 1566 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building, excluding the roof. Included in the cost is; sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MAIN OFFICE COMPLEX | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 1550 | 2015-10-28 | Four to Ten Years | Long-Term Needs | 3 | 15500
1567INT1 | INTERIOR FINISHES | 1567 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | SHOP | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 1620 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16200
1377SFT2 | INTERIOR STAIR HANDRAIL REPLACEMENT | 1377 | The stair handrails are older and do not meet code for safety or accessibility. The gripping surfaces are incorrect and they are not continuous from the top to bottom landings. This project recommends the installation of handrails with proper returns and supports per International Residential Code 2012 Section R311. This project or a portion thereof was previously recommended in the FCA reports dated 06/20/2003 and 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | RESIDENTIAL DUPLEX | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 3126 | 2015-10-28 | Immediate to Two Years | Currently Critical | 1 | 6000
1377SFT1 | SMOKE ALARM INSTALLATION | 1377 | International Residential Code (IRC) 2012 Section R314 and R315.3 explains the requirements for smoke alarms in dwelling units. This includes: installing and maintaining smoke alarms in each sleeping room; having a carbon monoxide and smoke detector on the ceiling or wall outside of each sleeping area; in the immediate vicinity of bedrooms when an alteration, repair or addition requiring a permit occurs. IRC 2012, requires that smoke detectors and carbon monoxide alarms be UL rated. State Fire Marshal NAC 477.915 (3) requires that smoke detectors be connected to the wiring in a building and include a battery for emergency backup power. This project would provide funding for the purchase and installation of smoke alarms and carbon monoxide alarms in accordance with IRC and NAC laws. This project or a portion thereof was previously recommended in the FCA reports dated 06/20/2003 and 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | RESIDENTIAL DUPLEX | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 3126 | 2015-10-28 | Immediate to Two Years | Currently Critical | 1 | 4000
1377ENR1 | ELECTRIC HEATER REPLACEMENT | 1377 | There are several electric heaters in the building that have reached the end of their expected life. This project recommends replacing the electric heaters. The estimate includes removal and disposal of the existing equipment. This project or a portion thereof was previously recommended in the FCA report dated 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | RESIDENTIAL DUPLEX | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 3126 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 40000
1377SIT1 | EXTERIOR LIGHTING | 1377 | This project recommends installing or replacing general security lighting fixtures around the parking area at the residential duplex to LED lighting. Cost includes light fixtures, wiring, trenching and installation. This project or a portion thereof was previously recommended in the FCA report dated 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | RESIDENTIAL DUPLEX | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 3126 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
1377INT4 | INTERIOR FINISHES | 1377 | It is recommended to paint the interior walls and ceilings at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | RESIDENTIAL DUPLEX | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 3126 | 2015-10-28 | Four to Ten Years | Long-Term Needs | 3 | 31260
1377EXT3 | EXTERIOR FINISHES | 1377 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building, excluding the roof. Included in the cost is sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | RESIDENTIAL DUPLEX | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 3126 | 2015-10-28 | Four to Ten Years | Long-Term Needs | 3 | 31260
1381INT2 | INTERIOR FINISHES | 1381 | It is recommended to paint the partitions and ceilings and re-caulk the Fiberglass Reinforced Panels (FRP) at least once in the next 4-5 years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project should be scheduled on a cyclical basis to maintain the integrity of the structure. | COMFORT STATION #1 | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 2015 | 499 | 2015-10-28 | Four to Ten Years | Long-Term Needs | 3 | 12500
1381PLM1 | BATHROOM FIXTURE REPLACEMENT | 1381 | The existing restroom fixtures are original to the building. They are worn and damaged from many years of use and should be scheduled for replacement. This project recommends the replacement of the existing fixtures, to include: 4 water closets; 2 urinals; 6 sinks, and 6 faucets. | COMFORT STATION #1 | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 2015 | 499 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
1381EXT2 | EXTERIOR FINISHES | 1381 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building, excluding the roof. Included in the cost is; sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | COMFORT STATION #1 | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 2015 | 499 | 2015-10-28 | Four to Ten Years | Long-Term Needs | 3 | 12500
1381ADA1 | ADA RESTROOM UPGRADE | 1381 | The building does not have an accessible restroom. The existing restroom does not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for remodeling the Men's and Women's restrooms into ADA compliant restrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | COMFORT STATION #1 | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 2015 | 499 | 2015-10-28 | Immediate to Two Years | Currently Critical | 1 | 40000
1382EXT2 | EXTERIOR FINISHES | 1382 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building, excluding the roof. Included in the cost is; sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | COMFORT STATION #2 | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 2016 | 654 | 2015-10-28 | Four to Ten Years | Long-Term Needs | 3 | 12500
1382INT2 | CONCRETE FLOOR REPLACEMENT | 1382 | The concrete flooring in the utility room is damaged and has reached the end of its useful life. It is recommended that the concrete flooring be replaced. This project would provide for removal and disposal of the existing concrete and installation of new concrete flooring. This project or a portion thereof was previously recommended in the FCA report dated 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | COMFORT STATION #2 | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 2016 | 654 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
1384INT2 | INTERIOR FINISHES | 1384 | It is recommended to paint the partitions and ceilings and re-caulk the Fiberglass Reinforced Panels (FRP) at least once in the next 4-5 years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project should be scheduled on a cyclical basis to maintain the integrity of the structure. | COMFORT STATION #3 | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 2016 | 654 | 2015-10-28 | Four to Ten Years | Long-Term Needs | 3 | 12500
1377EXT1 | ROOF REPLACEMENT | 1377 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. This project or a portion thereof was previously recommended in the FCA reports dated 06/20/2003 and 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | RESIDENTIAL DUPLEX | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 3126 | 2015-10-28 | Immediate to Two Years | Currently Critical | 1 | 37512
1382INT3 | INTERIOR FINISHES | 1382 | It is recommended to paint the partitions and ceilings and re-caulk the Fiberglass Reinforced Panels (FRP) at least once in the next 4-5 years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project should be scheduled on a cyclical basis to maintain the integrity of the structure. | COMFORT STATION #2 | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 2016 | 654 | 2015-10-28 | Four to Ten Years | Long-Term Needs | 3 | 12500
1386PLM2 | RESTROOM FIXTURES REPLACEMENT | 1386 | The existing restroom fixtures are original to the building. They are worn and damaged from many years of use and should be scheduled for replacement. This project recommends the replacement of the existing fixtures, to include: 4 water closets; 2 urinals; 6 sinks, and 6 faucets. | COMFORT STATION #4 | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 1250 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
1386PLM1 | BACKFLOW PREVENTION | 1386 | State Health Law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of backsiphonage or backpressure. This project allows for the installation of double check valves or reduced pressure principle backflow preventers as appropriate to the hazard and in appropriate locations near the potential source of contamination. Costs include an above ground vault, and allowance for 200 feet of 1" conduit to provide power for freeze protection. | COMFORT STATION #4 | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 1250 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35000
1384EXT2 | EXTERIOR FINISHES | 1384 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building, excluding the roof. Included in the cost is; sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | COMFORT STATION #3 | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 2016 | 654 | 2015-10-28 | Four to Ten Years | Long-Term Needs | 3 | 12500
1384PLM1 | BACKFLOW PREVENTION | 1384 | State Health Law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of backsiphonage or backpressure. This project allows for the installation of double check valves or reduced pressure principle backflow preventers as appropriate to the hazard and in appropriate locations near the potential source of contamination. Costs include an above ground vault, and allowance for 200 feet of 1" conduit to provide power for freeze protection. | COMFORT STATION #3 | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 2016 | 654 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35000
1384PLM2 | RESTROOM FIXTURE REPLACEMENT | 1384 | The existing restroom fixtures are original to the building. They are worn and damaged from many years of use and should be scheduled for replacement. This project recommends the replacement of the existing fixtures, to include: 4 water closets; 2 urinals; 6 sinks, and 6 faucets. | COMFORT STATION #3 | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 2016 | 654 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
1382ADA2 | ACCESSIBLE ENTRANCE RAMP | 1382 | This facility has an ADA accessible ramp located in front of the building. This ramp is on the accessible path of travel from the accessible parking space to the entrance of the building. The ramp does not have proper landings or handrails. This project would provide for an upgrade to the ramp to make it fully ADA compliant. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | COMFORT STATION #2 | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 2016 | 654 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35000
1382PLM2 | RESTROOM FIXTURE REPLACEMENT | 1382 | The existing restroom fixtures are original to the building. They are worn and damaged from many years of use and should be scheduled for replacement. This project recommends the replacement of the existing fixtures, to include: 4 water closets; 2 urinals; 6 sinks, and 6 faucets. | COMFORT STATION #2 | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 2016 | 654 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
1382PLM1 | BACKFLOW PREVENTION | 1382 | State Health Law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of backsiphonage or backpressure. This project allows for the installation of double check valves or reduced pressure principle backflow preventers as appropriate to the hazard and in appropriate locations near the potential source of contamination. Costs include an above ground vault, and allowance for 200 feet of 1" conduit to provide power for freeze protection. | COMFORT STATION #2 | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 2016 | 654 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35000
1386INT2 | INTERIOR FINISHES | 1386 | It is recommended to paint the partitions and ceilings and re-caulk the Fiberglass Reinforced Panels (FRP) at least once in the next 4-5 years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project should be scheduled on a cyclical basis to maintain the integrity of the structure. | COMFORT STATION #4 | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 1250 | 2015-10-28 | Four to Ten Years | Long-Term Needs | 3 | 12500
2904INT1 | INTERIOR FINISHES | 2904 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | FIRE PUMP HOUSE | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 2004 | 280 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2800
2905EXT1 | EXTERIOR FINISHES | 2905 | It is important to maintain the finish, weather resistance and appearance of the water tank. This project would provide for the painting of the water tank and the fence surrounding it to maintain it in a good, weather tight condition. It is recommended that this project be implemented in the next 2-3 years and is recommended on a cyclical basis based on environmental conditions. The square footage used is the area of the water tank walls (1,120 s.f.) plus the area of the top of the tank (700 s.f.) plus the area of the fence (1,120 s.f.). This project or a portion thereof was previously recommended in the FCA report dated 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | WATER TANK | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 2004 | 707 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 29400
2376ENR1 | LIGHTING UPGRADE | 2376 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures, ballasts and lighting to current standards, resulting in increased efficiency and reduced costs associated with illumination. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | GROUP USE RAMADA | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 1124 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3372
2376EXT2 | EXTERIOR FINISHES | 2376 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | GROUP USE RAMADA | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 1124 | 2015-10-28 | Four to Ten Years | Long-Term Needs | 3 | 4496
2906EXT2 | EXTERIOR/ INTERIOR FINISHES | 2906 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 2-3 years and for this project to be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | HIDDEN BEACH CXT RESTROOM | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 2000 | 81 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1620
2904EXT1 | EXTERIOR FINISHES | 2904 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building, excluding the roof. Included in the cost is; sanding, priming, painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | FIRE PUMP HOUSE | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 2004 | 280 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2800
2904PLM1 | VALVE REPLACEMENT | 2904 | The CLA-VAL pressure reducing valve is not operating and should be replaced. The valve is located on the 2" water line between the well and the storage tank. Staff noted that the valve is undersized and does not function properly requiring the flow to be manually operated. This project would provide for removal and disposal of the existing valve and replacement with a properly sized pressure reducing valve. This project or a portion thereof was previously recommended in the FCA report dated 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | FIRE PUMP HOUSE | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 2004 | 280 | 2015-10-28 | Immediate to Two Years | Currently Critical | 1 | 3000
2901INT2 | INTERIOR FINISHES | 2901 | It is recommended to paint the interior walls and ceilings at least once in the next 5-6 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | SHAKESPEARE STAGE | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1999 | 2590 | 2015-10-28 | Four to Ten Years | Long-Term Needs | 3 | 25900
2552EXT1 | EXTERIOR FINISHES | 2552 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building, excluding the roof. Included in the cost is; sanding, priming, painting, staining and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | VISITOR'S CENTER/ CONCESSION | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 2005 | 5580 | 2015-10-28 | Four to Ten Years | Long-Term Needs | 3 | 55800
2903EXT1 | EXTERIOR FINISHES | 2903 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 06/20/2003 and 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | BOAT RAMP KIOSK | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 0 | 60 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 600
2552PLM1 | WATER HEATER REPLACEMENT | 2552 | There is a 100 gallon electric water heater in the building. The average lifespan of a water heater is eight to ten years and the water heater was installed in 2007. It is recommended that a new electric water heater, straps, braided steel hose, expansion tank, ball valves, new flex gas line and pan be installed. Removal and disposal of the existing equipment is included in this estimate. | VISITOR'S CENTER/ CONCESSION | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 2005 | 5580 | 2015-10-28 | Immediate to Two Years | Currently Critical | 1 | 2200
2552INT1 | INTERIOR FINISHES | 2552 | It is recommended to paint the interior walls and ceilings at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | VISITOR'S CENTER/ CONCESSION | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 2005 | 5580 | 2015-10-28 | Four to Ten Years | Long-Term Needs | 3 | 55800
2902INT1 | INTERIOR FINISHES | 2902 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | SHAKESPEARE SOUND BOOTH | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1999 | 152 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1520
2902EXT1 | EXTERIOR FINISHES | 2902 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building, excluding the roof. Included in the cost is; sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | SHAKESPEARE SOUND BOOTH | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1999 | 152 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1520
2901EXT2 | EXTERIOR FINISHES | 2901 | It is important to maintain the finish, weather resistance and appearance of the stage. This project would provide funding to protect the exterior of the stage. Included in the cost are cleaning and sealing the masonry and to caulk and paint the stage and handrails. It is recommended that the stage and masonry be sealed and painted in the next 5-6 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | SHAKESPEARE STAGE | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1999 | 2590 | 2015-10-28 | Four to Ten Years | Long-Term Needs | 3 | 25900
2552SIT1 | PAVER REPAIR | 2552 | The concrete pavers on the front patio of the building are settling and sinking due to rodent holes. This project would provide for installing a rodent barrier around the perimeter of the pavers to prevent them from burrowing under the pavers. This project or a portion thereof was previously recommended in the FCA report dated 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | VISITOR'S CENTER/ CONCESSION | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 2005 | 5580 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
9927SIT5 | SIDEWALK REPLACEMENT, PHASE 3 | 9927 | The existing sidewalks serving the boat ramp and boat beach have deteriorated and are failing. In some areas, cracks wider than four inches have been identified, and there are potholes and settling in a number of locations. This project addresses removal and replacement of existing sidewalks as needed. The sidewalks should include flared curb cuts for site accessibility. This project or a portion thereof was previously recommended in the FCA report dated 06/20/2003 and 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | LAKE TAHOE NEVADA-SAND HARBOR STATE PARK | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 0 |  | 2015-10-28 | Four to Ten Years | Long-Term Needs | 3 | 100000
9927SIT10 | PEST CONTROL - COMFORT STATIONS | 9927 | The Comfort Stations have visible damage from carpenter ants which have infested the buildings. Carpenter ants may cause severe damage and could compromise the structural integrity of wood framed structures if left unchecked. This project would provide for a licensed pest control contractor to eradicate the ants from the Comfort Stations. This project or a portion thereof was previously recommended in the FCA report dated 06/20/2003 and 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | LAKE TAHOE NEVADA-SAND HARBOR STATE PARK | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 0 |  | 2015-10-28 | Immediate to Two Years | Currently Critical | 1 | 5000
9927SIT9 | SLURRY SEAL ASPHALT PAVING | 9927 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site wide including access roads, parking areas and the maintenance yard. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 400,000 square feet of asphalt area was used to generate this estimate. This project or a portion thereof was previously recommended in the FCA report dated 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | LAKE TAHOE NEVADA-SAND HARBOR STATE PARK | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 0 |  | 2015-10-28 | Four to Ten Years | Long-Term Needs | 3 | 300000
9927SFT5 | EXTERIOR STAIR HANDRAIL INSTALLATION | 9927 | Exterior stairs have been installed behind the Memorial Point Comfort Station. They start at the parking lot and extend down to the nature trails and do not have handrails or guardrails. This project recommends the installation of handrails and guardrails from the parking area to the trails. Chapter 10 Section's 1012 and 1013 of the 2012 IBC were referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 06/20/2003 and 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | LAKE TAHOE NEVADA-SAND HARBOR STATE PARK | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 0 |  | 2015-10-28 | Immediate to Two Years | Currently Critical | 1 | 18000
0651EXT2 | EXTERIOR/ INTERIOR FINISHES | 0651 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 2-3 years and for this project to be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | MEMORIAL POINT COMFORT STATION | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1998 | 1200 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24000
1655ADA4 | ADA ACCESSIBLE COUNTER | 1655 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. This building contains a counter which does not meet current codes. Section 7.2 of the Americans with Disabilities Act Accessible Guidelines (ADAAG) states that the counter must have a portion which is at least 36" in length with a maximum height of 36" above the finish floor. This project will provide an accessible counter space in accordance with this requirement. International Building Code (IBC) - 2012, ICC/ANSI A117.1 - 2009 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2009 were referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 03/04/2003 and 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | WESTERN AREA HEADQUARTERS | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 12330 | 2015-12-16 | Immediate to Two Years | Currently Critical | 1 | 4000
1655INT1 | INTERIOR FINISHES | 1655 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to three years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 03/04/2003 and 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | WESTERN AREA HEADQUARTERS | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 12330 | 2015-12-16 | Two to Four Years | Necessary - Not Yet Critical | 2 | 115300
1655SIT1 | SITE BOLLARDS | 1655 | The Headquarters building has seven sectional overhead doors. These areas are in need of bollards to protect the building. This project would provide funding for 15 eight inch diameter bollards to be located on each side of the garage sectional overhead doors. This project or a portion thereof was previously recommended in the FCA report dated and 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | WESTERN AREA HEADQUARTERS | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 12330 | 2015-12-16 | Immediate to Two Years | Currently Critical | 1 | 9750
1655EXT4 | OVERHEAD DOOR REPLACEMENT | 1655 | There are two 12'x14' overhead coiling doors in the repair shop which are damaged and do not function properly. They are original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the power-operated overhead coiling doors and replacement with new power-operated doors. This project or a portion thereof was previously recommended in the FCA report dated 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | WESTERN AREA HEADQUARTERS | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 12330 | 2015-12-16 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16000
1655ELE1 | EXTERIOR OUTLET REPLACEMENT | 1655 | The building has an exterior electrical outlet that does not meet code. The outlet is not a GFCI type outlet which is required according to the 2011 NEC. This project would provide for the purchase and installation of one GFCI duplex outlet. This project or a portion thereof was previously recommended in the FCA report dated 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | WESTERN AREA HEADQUARTERS | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 12330 | 2015-12-16 | Immediate to Two Years | Currently Critical | 1 | 400
1655ADA5 | ADA SHOWER UPGRADE | 1655 | The shower in the office area is not accessible. If a shower is provided, then at least one accessible shower stall shall be provided. This project would provide for one ADA compliant shower stall to be installed to provide shower facilities for the disabled. Included in this estimate is removal of the existing shower stall and installation of an ADA compliant shower stall complete with accessible plumbing fixtures, seat, etc. International Building Code (IBC) - 2012, ICC/ANSI A117.1 - 2009 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2009 were referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | WESTERN AREA HEADQUARTERS | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 12330 | 2015-12-16 | Immediate to Two Years | Currently Critical | 1 | 7500
1655EXT3 | ROOF REPLACEMENT | 1655 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 15 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2004. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | WESTERN AREA HEADQUARTERS | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 12330 | 2015-12-16 | Two to Four Years | Necessary - Not Yet Critical | 2 | 172950
1655SFT4 | STORAGE REMOVAL | 1655 | The storage areas in the parts room and the apparatus room mezzanine have items stored too close to the fire sprinkler heads. The 2012 IFC Section 315.3.1 states that, "Storage shall be maintained a minimum of 18 inches below sprinkler head deflectors in sprinklered areas of buildings." This project would provide for the removal of all items in conflict with this code requirement to insure that the fire suppression system operates correctly. This project or a portion thereof was previously recommended in the FCA report dated 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | WESTERN AREA HEADQUARTERS | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 12330 | 2015-12-16 | Immediate to Two Years | Currently Critical | 1 | 500
1655ENV1 | SPILL CONTAINMENT | 1655 | The vehicle garage does not have a method for containing spills or leakage from oil drums and other containers. This does not meet OSHA standards for hazardous materials containment. This project would add secondary containment pallets for all containers in the building and install placards on the building exterior in accordance with OSHA 1910.106 (d). This project or a portion thereof was previously recommended in the FCA report dated 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | WESTERN AREA HEADQUARTERS | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 12330 | 2015-12-16 | Immediate to Two Years | Currently Critical | 1 | 6500
1655SFT2 | GENERATOR MODIFICATIONS | 1655 | The emergency generator is not currently connected to the overhead garage doors in the fire response garage. The doors should be connected to the generator so that the emergency vehicles can be deployed at any time. It is not unlikely that a power outage would coincide with other types of emergencies where the vehicles would be needed. This project recommends connecting the overhead doors to the emergency generator and includes purchase and installation of wiring and electrical hardware. This project or a portion thereof was previously recommended in the FCA report dated 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | WESTERN AREA HEADQUARTERS | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 12330 | 2015-12-16 | Immediate to Two Years | Currently Critical | 1 | 6000
1655INT2 | SHEET VINYL FLOORING REPLACEMENT | 1655 | The sheet vinyl flooring in the shop restroom is damaged and reaching the end of its useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the flooring and installation of new sheet vinyl with a 6" cove base. This project or a portion thereof was previously recommended in the FCA report dated 03/04/2003 and 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | WESTERN AREA HEADQUARTERS | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 12330 | 2015-12-16 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1350
1655SFT5 | MEZZANINE STAIR HANDRAIL REPLACEMENT | 1655 | The stair handrails and guardrails leading up to the mezzanine in the apparatus room do not meet code for safety. This project recommends the installation of handrails on both sides of the stairs and guardrails at the top landing in accordance with the 2012 IBC Section 1012 and Section 1013. Removal and disposal of the existing rails is included in the estimate. This project or a portion thereof was previously recommended in the FCA report dated 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | WESTERN AREA HEADQUARTERS | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 12330 | 2015-12-16 | Immediate to Two Years | Currently Critical | 1 | 3600
1655STR1 | STRUCTURAL REPAIRS | 1655 | A storage area has been constructed in the apparatus room, accessed via stairs in the garage. There is no record of a CIP project for this work or of any structural evaluations having been conducted. This project recommends adding structural members to the existing framing to ensure proper load bearing capacity. This will require a structural design from a licensed engineer, inspections and permitting which are not included in the estimate. This project or a portion thereof was previously recommended in the FCA report dated 03/04/2003 and 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | WESTERN AREA HEADQUARTERS | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 12330 | 2015-12-16 | Immediate to Two Years | Currently Critical | 1 | 15000
1655SFT3 | STAIR HANDRAIL REPLACEMENT | 1655 | There are three sets of stair handrails in the building that are older and do not meet code for safety. The rails do not extend at the top and bottom of the stairs in accordance with the 2012 International Building Code (IBC) Section 1012.6. This project applies to the stairs between the offices and the shop, the stairs in the vehicle garage and the exterior stairs off of the Ready Room. Each of these flights of stairs has 4 risers. This project recommends the installation of handrails on both sides of the stairs at each of these locations in accordance with the 2012 International Building Code (IBC) Section 1012. This project or a portion thereof was previously recommended in the FCA report dated 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | WESTERN AREA HEADQUARTERS | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 12330 | 2015-12-16 | Immediate to Two Years | Currently Critical | 1 | 3000
1655PLM1 | WATER HEATER REPLACEMENT | 1655 | The average life span of a water heater is eight to ten years. The 40 gallon electric water heater in the generator room was installed in 2004. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 1-2 years. It is recommended that a new gas-fired water heater be installed for more efficient use of energy. This estimate includes: 100 feet of gas pipe, fittings, couplers, and labor for installation. This project or a portion thereof was previously recommended in the FCA report dated 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | WESTERN AREA HEADQUARTERS | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 12330 | 2015-12-16 | Immediate to Two Years | Currently Critical | 1 | 3000
1655EXT2 | EXTERIOR LIGHTING UPGRADE | 1655 | The exterior wall-mounted light fixtures appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the purchase and installation of six energy efficient light fixtures. Removal and disposal of the existing fixtures is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 03/04/2003 and 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | WESTERN AREA HEADQUARTERS | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 12330 | 2015-12-16 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
1655ADA3 | POWER DOOR ACTUATOR REPAIRS | 1655 | The building has an existing ADA entry with a power assisted door opener. The opener is currently not operational and should be scheduled for replacement. This project recommends replacing the ADA actuator and includes removal and disposal of the existing equipment. This project or a portion thereof was previously recommended in the FCA report dated and 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | WESTERN AREA HEADQUARTERS | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 12330 | 2015-12-16 | Immediate to Two Years | Currently Critical | 1 | 1500
1655HVA2 | HEAT PUMP REPLACEMENT | 1655 | There is one roof top heat pump (Goodman) system that was installed in 1995. It is not energy efficient and has reached the end of its useful life. This project would provide for installation of the heat pump system and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing heat pump system and all required connections to utilities. | WESTERN AREA HEADQUARTERS | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 12330 | 2015-12-16 | Immediate to Two Years | Currently Critical | 1 | 12000
1655ELE2 | ELECTRICAL UPGRADE | 1655 | This building was constructed before the high demand for electrical services were needed for computers and other electrical devices. As time has progressed, the buildings electrical demand and system has changed. It is utilized to its current maximum potential. The electrical panels and receptacles are at their limit. It is recommended the entire system be upgraded to meet the evolving needs of the building including three-phase power. | WESTERN AREA HEADQUARTERS | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 12330 | 2015-12-16 | Two to Four Years | Necessary - Not Yet Critical | 2 | 308250
1655HVA3 | HVAC EQUIPMENT REPLACEMENT | 1655 | There are several HVAC packaged units and swamp coolers on the roof that were installed in 2004. This project would provide for installation of the new HVAC packaged units, swamp coolers and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC equipment and all required connections to utilities. | WESTERN AREA HEADQUARTERS | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 12330 | 2015-12-16 | Four to Ten Years | Long-Term Needs | 3 | 308250
1655SFT1 | FIRE ALARM ANNUNCIATOR PANEL REPLACEMENT | 1655 | There is a fire alarm annunciator panel mounted on the exterior of the building near the main entrance. The panel is not rated for exterior applications and was not operating during the survey of 2009. It was most likely damaged from exposure and should be scheduled for replacement. This project recommends replacing the panel with an exterior rated panel and includes connections to the fire alarm system and any other utilities. This project or a portion thereof was previously recommended in the FCA report dated 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | WESTERN AREA HEADQUARTERS | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 12330 | 2015-12-16 | Immediate to Two Years | Currently Critical | 1 | 6500
1655ADA1 | ADA DOOR HARDWARE REPLACEMENT | 1655 | The 2010 ADA Standards for Accessible Design states that handles, pulls, latches, locks and other operable parts on doors and gates shall be operable with one hand and shall not require tight grasping, pinching, or twisting of the wrist. The force to activate operable parts shall be 5 pounds maximum. It is recommended that proper lever hardware be installed on all of the interior and exterior doors in this building to meet these requirements. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and sections 309.4 and 404.2.7 of the 2010 ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 03/04/2003 and 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | WESTERN AREA HEADQUARTERS | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 12330 | 2015-12-16 | Immediate to Two Years | Currently Critical | 1 | 20000
1655EXT1 | EXTERIOR FINISHES | 1655 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is painting the masonry and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted, sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 03/04/2003 and 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | WESTERN AREA HEADQUARTERS | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 12330 | 2015-12-16 | Two to Four Years | Necessary - Not Yet Critical | 2 | 115300
1655ADA6 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 1655 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. This project or a portion thereof was previously recommended in the FCA report dated 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | WESTERN AREA HEADQUARTERS | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 12330 | 2015-12-16 | Immediate to Two Years | Currently Critical | 1 | 4000
2348INT1 | INTERIOR FINISHES | 2348 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to three years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 03/04/2003 and 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | HQ GARDEN EQUIPMENT STORAGE | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 320 | 2015-12-16 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3200
2348PLM1 | FLOOR DRAIN REPAIR | 2348 | The floor drain in the building is clogged and water has pooled around it. The standing water will prematurely deteriorate the building components as well as create a slipping hazard. This project would provide for a licensed contractor to clear the drain and provide any necessary repairs to prevent future problems. This project or a portion thereof was previously recommended in the FCA report dated 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | HQ GARDEN EQUIPMENT STORAGE | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 320 | 2015-12-16 | Immediate to Two Years | Currently Critical | 1 | 2000
2348ELE5 | ELECTRICAL UPGRADE | 2348 | This building was constructed before the high demand for electrical services were needed. As time has progressed, the building’s electrical demand and system has changed. The electrical panel has been altered and added to improperly. There are open circuits missing cover plates and wires attached to the panel incorrectly. The electrical panels and receptacles do not comply with NEC 2011. It is recommended to have the entire system upgraded to meet the current standards including three-phase power. | HQ GARDEN EQUIPMENT STORAGE | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 320 | 2015-12-16 | Immediate to Two Years | Currently Critical | 1 | 16000
2339EXT1 | EXTERIOR FINISHES | 2339 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding for the maintenance of the exterior of the building. Included in the cost is the painting, sealing and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted, caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 03/04/2003 and 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | HQ WELDING SHOP | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 1250 | 2015-12-16 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12500
2348EXT0 | EXTERIOR DOOR REPLACEMENT | 2348 | The existing exterior metal door and frame appear to be original to the building. It is damaged from age and general wear and tear. This project would provide for the replacement and installation of a new metal door, frame and hardware. Removal and disposal of the existing door and painting of the new door is included in this estimate. | HQ GARDEN EQUIPMENT STORAGE | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 320 | 2015-12-16 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
2348ENR1 | LIGHTING UPGRADE | 2348 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade T-12 lamps to T-8 lamps with electronic ballasts and upgrade the HID (high intensity discharge) lamps to current standards, resulting in increased efficiency and reduced costs associated with illumination. An occupancy sensor will be installed in the Garden Equipment Storage room for additional savings. Any electrical wiring upgrades are not included in this estimate. | HQ GARDEN EQUIPMENT STORAGE | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 320 | 2015-12-16 | Two to Four Years | Necessary - Not Yet Critical | 2 | 480
2348EXT1 | EXTERIOR FINISHES | 2348 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding for the maintenance of the exterior of the building. Included in the cost is the painting, sealing and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted, caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 03/04/2003 and 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | HQ GARDEN EQUIPMENT STORAGE | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 320 | 2015-12-16 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3200
2347EXT1 | EXTERIOR FINISHES | 2347 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are sealing and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 03/04/2003 and 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | HQ RADIO EQUIPMENT STORAGE | 9957 | CNR | Forestry |  | Washoe Valley | 1990 | 50 | 2015-12-16 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
2339ENR0 | INSULATE BUILDING | 2339 | The building is not insulated and is not energy efficient. Due to this, the heater continuously runs. This project would provide for the installation of blanket insulation with impermeable vinyl interior surface batt insulation in the walls (R19) and ceilings (R38) to help moderate temperature fluctuations. | HQ WELDING SHOP | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 1250 | 2015-12-16 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
2966EXT1 | EXTERIOR FINISHES | 2966 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding for the maintenance of the exterior of the building. Included in the cost is the sealing and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | PUMP HOUSE | 9957 | CNR | Forestry |  | Washoe Valley | 2008 | 150 | 2015-12-16 | Four to Ten Years | Long-Term Needs | 3 | 1500
9957SIT2 | EXTERIOR SITE LIGHTING INSTALLATION | 9957 | The site has minimal lighting in the parking lot and between the buildings which is a security and safety concern. This project would provide funding for the purchase and installation of five 20'-0" high light poles including 30" diameter raised concrete bases, electrical trenching, conduit, wiring and connections to existing utilities. This estimate includes removal and disposal of the three existing pole lights in the parking lot. This project or a portion thereof was previously recommended in the FCA report dated 03/04/2003 and 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | NDF WESTERN AREA HEADQUARTERS SITE | 9957 | CNR | Forestry |  | Washoe Valley | 0 |  | 2015-12-16 | Four to Ten Years | Long-Term Needs | 3 | 60000
9957SFT8 | MOTORIZED GATE INSTALLATION | 9957 | The site has a perimeter fence that has a sliding vehicle access gate. It is manually operated, has no track system and is difficult to open and close. Several employees have sustained injuries operating the gate. This project recommends the gate be upgraded to a motorized track system that can handle heavy equipment traffic. The gates will be required to meet UL Standard 325, per NRS 405.270. This project or a portion thereof was previously recommended in the FCA report dated 03/04/2003 and 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | NDF WESTERN AREA HEADQUARTERS SITE | 9957 | CNR | Forestry |  | Washoe Valley | 0 |  | 2015-12-16 | Immediate to Two Years | Currently Critical | 1 | 45000
9957ENV3 | 4" BACKFLOW ASSEMBLY, VAULT, AND POWER | 9957 | State Health Law (NAC 445A.67185) and the Uniform Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of back siphonage or backpressure. This project allows for the installation of double check valves or reduced pressure principle backflow preventers as appropriate to the hazard and in appropriate locations near the potential source of contamination. Costs include an above ground vault, and allowance for 200 feet of 1" conduit to provide power for freeze protection. This project or a portion thereof was previously recommended in the FCA report dated 03/04/2003 and 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | NDF WESTERN AREA HEADQUARTERS SITE | 9957 | CNR | Forestry |  | Washoe Valley | 0 |  | 2015-12-16 | Immediate to Two Years | Currently Critical | 1 | 35000
9957SIT8 | SLURRY SEAL ASPHALT PAVING | 9957 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site wide including access roads, parking areas and the maintenance yard. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 50,000 square feet of asphalt area was used to generate this estimate. This project or a portion thereof was previously recommended in the FCA report dated 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | NDF WESTERN AREA HEADQUARTERS SITE | 9957 | CNR | Forestry |  | Washoe Valley | 0 |  | 2015-12-16 | Four to Ten Years | Long-Term Needs | 3 | 62500
9957ELE1 | BUILDING DISCONNECTS | 9957 | Power for the smaller buildings around the HQ building is pulled off the main panel in the HQ apparatus garage. There is no way to shut off power to the individual buildings, or shut off power for the HQ without de-energizing all of the buildings. This project will provide six separate building disconnects as well as disconnects in the HQ building, for the garage and shop. The 2011 NEC 250.32 (D) was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 03/04/2003 and 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | NDF WESTERN AREA HEADQUARTERS SITE | 9957 | CNR | Forestry |  | Washoe Valley | 0 |  | 2015-12-16 | Immediate to Two Years | Currently Critical | 1 | 24000
9957SIT4 | SITE BOLLARDS | 9957 | There are two above ground fuel tanks on the site, one for diesel and one for unleaded gasoline. The unleaded gasoline tank does not have adequate protection from vehicles. Per International Fire Code 2012 Section 312 Vehicle Impact Protection, steel posts need to be installed, not less than 4 inches in diameter and filled with concrete. The spacing shall be not more than 4 feet between posts on center and located not less than 3 feet from each gas tank. This project would provide funding for two new bollards to be located in front of the unleaded gasoline tank. | NDF WESTERN AREA HEADQUARTERS SITE | 9957 | CNR | Forestry |  | Washoe Valley | 0 |  | 2015-12-16 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
9957SIT5 | INSTALL WHEEL STOPS | 9957 | The Headquarters building has four parking spaces next to the building. These spaces are missing wheel stops which could cause damage to the building. This project would provide for the purchase and installation of four 72"x6"x4" rubber composite wheel stops. This project or a portion thereof was previously recommended in the FCA report dated 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | NDF WESTERN AREA HEADQUARTERS SITE | 9957 | CNR | Forestry |  | Washoe Valley | 0 |  | 2015-12-16 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
9957SIT7 | SIDEWALK AND LANDING INSTALLATIONS | 9957 | A number of buildings at the site do not have proper landings at exit doors as required by the 2012 IBC 1008.1.5. This project addresses new sidewalks and landings as needed including the rear door from the parts room in the Headquarters building and the entrance to the HQ Welding Shop. This estimate is for 2,000 square feet of 4" thick concrete. This project or a portion thereof was previously recommended in the FCA report dated 03/04/2003 and 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | NDF WESTERN AREA HEADQUARTERS SITE | 9957 | CNR | Forestry |  | Washoe Valley | 0 |  | 2015-12-16 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0895HVA1 | HEATER REPLACEMENT | 0895 | The existing heating system consists of a ceiling mounted heater and does not have cooling equipment. The heater is inefficient and was installed in 2004. The heater should be replaced within 8-10 years with a 80% AFUE or higher unit. This project would replace the existing heater. | HQ PAINT SHOP | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 3200 | 2015-12-16 | Four to Ten Years | Long-Term Needs | 3 | 3500
0895EXT3 | WINDOW REPLACEMENT | 0895 | The windows are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 2 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | HQ PAINT SHOP | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 3200 | 2015-12-16 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0895EXT1 | EXTERIOR FINISHES | 0895 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding for the maintenance of the exterior of the building. Included in the cost is the sealing and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 03/04/2003 and 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | HQ PAINT SHOP | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 3200 | 2015-12-16 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6400
0895INT2 | INTERIOR DOOR REPLACEMENT | 0895 | The interior doors in this building are hollow core units and are damaged from general wear and tear. This project would provide for the installation of new solid core interior doors including frames, lever action door handles, hardware and paint. Removal and disposal of the existing doors is included in this cost estimate. A total of 3 interior doors was used in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | HQ PAINT SHOP | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 3200 | 2015-12-16 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0895EXT2 | EXTERIOR DOOR REPLACEMENT | 0895 | The exterior metal vestibule door is damaged from age and general wear and tear and has reached the end of its expected life. This project would provide for the replacement of the door assembly with a new metal door, frame and hardware. Removal and disposal of the existing door and painting of the new door is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | HQ PAINT SHOP | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 3200 | 2015-12-16 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0895INT1 | INTERIOR FINISHES | 0895 | The interior walls are insulated and sheet rocked in the front half of the building only. The sheet rock in the office room is severely damaged and should be removed, replaced and painted. It is recommended that these interior walls be painted at least once in the next two to three years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 03/04/2003 and 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | HQ PAINT SHOP | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 3200 | 2015-12-16 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16000
2935EXT2 | EXTERIOR FINISHES | 2935 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | ENTRANCE KIOSK | 9944 | CNR | Parks |  | Kershaw-Ryan | 1996 | 32 | 2016-04-12 | Four to Ten Years | Long-Term Needs | 3 | 175
2934INT1 | INTERIOR FINISHES | 2934 | It is recommended to repair and seal the interior concrete block walls in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. This project or a portion thereof was previously recommended in the FCA report dated 09/16/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/12/2016. | COMFORT STATION #2 - LOWER | 9944 | CNR | Parks |  | Kershaw-Ryan | 2003 | 1024 | 2016-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10240
2934EXT1 | EXTERIOR FINISHES | 2934 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/16/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/12/2016. | COMFORT STATION #2 - LOWER | 9944 | CNR | Parks |  | Kershaw-Ryan | 2003 | 1024 | 2016-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10240
2252HVA1 | HVAC EQUIPMENT REPLACEMENT | 2252 | The building is heated by a propane-fired heater and cooled with an air conditioner (split system). It is original to the building and is reaching the end of its useful life. This project provides for the disposal of the existing split system and the replacement with a new split system, and includes all connections to the utilities. | PARK RESIDENCE | 9944 | CNR | Parks |  | Kershaw-Ryan | 1998 | 1585 | 2016-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
2933EXT2 | EXTERIOR FINISHES | 2933 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | FEE KIOSK | 9944 | CNR | Parks |  | Kershaw-Ryan | 1996 | 18 | 2016-04-12 | Four to Ten Years | Long-Term Needs | 3 | 175
2932EXT1 | EXTERIOR FINISHES | 2932 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is caulking and sealing the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/16/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/12/2016. | PARK RESIDENCE GARAGE | 9944 | CNR | Parks |  | Kershaw-Ryan | 2006 | 290 | 2016-04-12 | Four to Ten Years | Long-Term Needs | 3 | 580
2252INT3 | KITCHEN REMODEL | 2252 | The kitchen is in fair to poor condition. The cabinets and equipment are showing signs of general wear and tear and are approaching the end of their expected life. This project recommends the replacement of the existing kitchen cabinets, countertops, fixtures and equipment with mid range, high quality components. | PARK RESIDENCE | 9944 | CNR | Parks |  | Kershaw-Ryan | 1998 | 1585 | 2016-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35000
2930EXT3 | OVERHEAD DOOR REPLACEMENT | 2930 | There is an overhead coiling door which is damaged and does not function properly. It is original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead coiling door and replacement with a motorized door. | PARK MAINTENANCE BUILDING | 9944 | CNR | Parks |  | Kershaw-Ryan | 2006 | 355 | 2016-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7000
2252EXT3 | EXTERIOR FINISHES | 2252 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | PARK RESIDENCE | 9944 | CNR | Parks |  | Kershaw-Ryan | 1998 | 1585 | 2016-04-12 | Four to Ten Years | Long-Term Needs | 3 | 15850
2252INT2 | CARPET REPLACEMENT | 2252 | The carpet in the building is showing signs of extreme wear and should be scheduled for replacement. It is recommended that the carpet be replaced with heavy duty commercial grade carpet in the next 2-3 years. | PARK RESIDENCE | 9944 | CNR | Parks |  | Kershaw-Ryan | 1998 | 1585 | 2016-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8820
2928EXT1 | EXTERIOR FINISHES | 2928 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4-5 years and it is also recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/16/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/12/2016. | PARK MAINTENANCE OFFICE | 9944 | CNR | Parks |  | Kershaw-Ryan | 1998 | 200 | 2016-04-12 | Four to Ten Years | Long-Term Needs | 3 | 2000
2537EXT2 | HISTORIC STRUCTURES REPORT | 2537 | The building was constructed in 1921 and is currently operating as a living museum. It may be eligible to be on the National Register of Historic Places. A historic structure report would provide documentary, graphic, and physical information about a property's history and existing condition. It also provides guidelines for maintenance of the building. This project recommends obtaining the report in accordance with the U.S. Department of Interior Recommended Guidelines in Preservation Brief 43. This property may be eligible for federal grants or special funding if this project is implemented. This project or a portion thereof was previously recommended in the FCA report dated 09/16/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/12/2016. | ELGIN SCHOOLHOUSE | 9944 | CNR | Parks |  | Kershaw-Ryan | 1921 | 1500 | 2016-04-12 | Immediate to Two Years | Currently Critical | 1 | 15000
2537EXT3 | HISTORIC BUILDING MAINTENANCE | 2537 | The Elgin Schoolhouse is over 95 years old and there are numerous areas where the wood siding is missing and not painted or sealed properly. This is an exhibit for the park and requires maintenance and signage. This project would provide for the cleaning, repair and re-siding where needed and maintaining the exhibit. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | ELGIN SCHOOLHOUSE | 9944 | CNR | Parks |  | Kershaw-Ryan | 1921 | 1500 | 2016-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 22500
2537EXT4 | CONCRETE FOUNDATION | 2537 | The addition to the backside of the Elgin Schoolhouse has wood to earth contact. This can lead to wood rot and insect infestation. Per 2012 International Building Code (IBC) Section 2304 wood siding, clearance between wood siding and earth on the exterior of the building shall not be less than 6 inches; wood shall be protected from decay and termites. This project will remove the addition on the backside of the Elgin Schoolhouse. A concrete foundation will be poured and the addition will be installed on top of the new concrete foundation. | ELGIN SCHOOLHOUSE | 9944 | CNR | Parks |  | Kershaw-Ryan | 1921 | 1500 | 2016-04-12 | Immediate to Two Years | Currently Critical | 1 | 50000
2252INT1 | INTERIOR FINISHES | 2252 | It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and every 5-7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/16/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/12/2016. | PARK RESIDENCE | 9944 | CNR | Parks |  | Kershaw-Ryan | 1998 | 1585 | 2016-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15850
2252PLM2 | WATER HEATER REPLACEMENT | 2252 | There is a 40 gallon propane fired water heater in the building. The average life span of a water heater is 8-10 years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new propane fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | PARK RESIDENCE | 9944 | CNR | Parks |  | Kershaw-Ryan | 1998 | 1585 | 2016-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2200
2931HVA1 | HEATER REPLACEMENT | 2931 | The building is heated by two wall mounted propane-fired heating units. One of the two heaters is original to the building and is reaching the end of its useful life. This project provides for the disposal of the existing unit and the replacement with a new propane-fired unit and includes all connections to utilities. | GREENHOUSE | 9944 | CNR | Parks |  | Kershaw-Ryan | 2006 | 495 | 2016-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
2252EXT2 | HANDRAIL & CONCRETE LANDING INSTALLATION | 2252 | The entry deck and stairs/ landing do not meet current code. This project would provide for a guardrail around the deck, guardrail and handrail at the stairs and a 4" thick concrete landing at the bottom of the stairs. The 2012 International Building Code (IBC) Chapter 10, Section's 1009.4, 1012 and 1013 were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/16/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/12/2016. | PARK RESIDENCE | 9944 | CNR | Parks |  | Kershaw-Ryan | 1998 | 1585 | 2016-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
2931EXT1 | EXTERIOR FINISHES | 2931 | It is important to maintain the finish, weather resistance and appearance of the structure. This project recommends work to protect the exterior building envelope including repairs to the exterior membrane and caulking around the flashing, fixtures, and other penetrations to maintain the building in good weather tight condition. It is recommended that this project be implemented in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/16/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/12/2016. | GREENHOUSE | 9944 | CNR | Parks |  | Kershaw-Ryan | 2006 | 495 | 2016-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 990
2929EXT120 | EXTERIOR FINISHES | 2929 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | GARDEN SHED | 9944 | CNR | Parks |  | Kershaw-Ryan | 1996 | 120 | 2016-04-12 | Four to Ten Years | Long-Term Needs | 3 | 1200
2930INT1 | INTERIOR FINISHES | 2930 | It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and every 5-7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/16/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/12/2016. | PARK MAINTENANCE BUILDING | 9944 | CNR | Parks |  | Kershaw-Ryan | 2006 | 355 | 2016-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3550
2930EXT1 | EXTERIOR FINISHES | 2930 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/16/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/12/2016. | PARK MAINTENANCE BUILDING | 9944 | CNR | Parks |  | Kershaw-Ryan | 2006 | 355 | 2016-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 710
2930SFT2 | SAFETY CABINETS | 2930 | The building contains many different paints, stains, and other hazardous products located on open shelves and on the floor. This does not meet Occupational Safety and Health Administration (OSHA) standards or International Fire Code (IFC) for hazardous materials containment. This project would provide for a self-closing hazardous storage container in the building and installing placards on the building’s exterior in accordance with OSHA 1910.106 (d) and IFC Chapter 57 Section 5704.3.2.1.3. | PARK MAINTENANCE BUILDING | 9944 | CNR | Parks |  | Kershaw-Ryan | 2006 | 355 | 2016-04-12 | Immediate to Two Years | Currently Critical | 1 | 5000
2930ENR2 | LIGHTING UPGRADE | 2930 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | PARK MAINTENANCE BUILDING | 9944 | CNR | Parks |  | Kershaw-Ryan | 2006 | 355 | 2016-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2840
2928INT1 | INTERIOR FINISHES | 2928 | It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and every 5-7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/16/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/12/2016. | PARK MAINTENANCE OFFICE | 9944 | CNR | Parks |  | Kershaw-Ryan | 1998 | 200 | 2016-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
9944ADA3 | INSTALL HANDRAILS | 9944 | The existing stone and concrete stairs which connect the access road to Ramada #1 - Upper are missing handrails. The 2012 International Building Code (IBC) Chapter 1009.15 states that stairways shall have handrails on each side. This project would provide for 1-1/2 inch diameter steel handrails, one on each side of the stairway to meet the 2012 IBC code requirements. Painting of the handrails is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/11/2002 and 09/16/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/12/2016. | KERSHAW-RYAN STATE PARK SITE | 9944 | CNR | Parks |  | Kershaw-Ryan |  |  | 2016-04-12 | Immediate to Two Years | Currently Critical | 1 | 10000
9944EXT2 | EXTERIOR FINISHES | 9944 | There are 17 wood and steel shade ramadas in different locations throughout the site which are either 144 s.f., 108 s.f. or 612 s.f. for a total of 2,880 square feet. It is important to maintain the finish, weather resistance and appearance of the structures. This project would provide for painting of the structures and it is recommended that this project is scheduled on a cyclical basis to maintain the integrity of the structures. | KERSHAW-RYAN STATE PARK SITE | 9944 | CNR | Parks |  | Kershaw-Ryan |  |  | 2016-04-12 | Four to Ten Years | Long-Term Needs | 3 | 5760
9944SIT2 | TREE REMOVAL | 9944 | There are five large cottonwood trees that pose a hazard to several buildings on the site. The trees drop large branches on the buildings as well as leaves and sap which contribute to the deterioration of the exterior of the building. The trees are dying and pose a threat to fall on the buildings. The trees should be removed before damage occurs. This project would provide funding to remove the trees and debris. This project or a portion thereof was previously recommended in the FCA report dated 09/16/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/12/2016. | KERSHAW-RYAN STATE PARK SITE | 9944 | CNR | Parks |  | Kershaw-Ryan |  |  | 2016-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6500
9944SIT3 | CRACK FILL & SEAL ASPHALT PAVING | 9944 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the pavement site wide including the access roads and parking areas. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 200,000 square feet of asphalt was used to generate this estimate. It is recommended for this project to coincide with the ADA Parking Space project. | KERSHAW-RYAN STATE PARK SITE | 9944 | CNR | Parks |  | Kershaw-Ryan |  |  | 2016-04-12 | Four to Ten Years | Long-Term Needs | 3 | 250000
9944ADA1 | ADA UPGRADES | 9944 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The upper area of the park including the Ramada #1 - Upper, wading pool and children's playground should be accessible to comply with ADA regulations. A hard-surfaced parking area with an adjacent passenger loading zone should be installed near Ramada #1 - Upper, including compliant signage and striping. A compliant path of travel should be provided from the ADA parking space to the ramada, wading pool and playground. The path will likely include several accessible ramps. IBC 2012, ICC/ANSI A117.1 - 2009 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2010 were referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/11/2002 and 09/16/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/12/2016. | KERSHAW-RYAN STATE PARK SITE | 9944 | CNR | Parks |  | Kershaw-Ryan |  |  | 2016-04-12 | Immediate to Two Years | Currently Critical | 1 | 260000
3716HVA1 | ELECTRIC HEATER REPLACEMENT | 3716 | There is an electric heater in the building that has reached the end of its expected life. This project recommends replacing the electric heater. The estimate includes removal and disposal of the existing equipment. | PUMP HOUSE | 9944 | CNR | Parks |  | Kershaw-Ryan | 2009 | 120 | 2016-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
3715INT2 | INTERIOR FINISHES | 3715 | It is recommended to paint the interior walls and ceilings at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | ENTRANCE FEE STATION | 9944 | CNR | Parks |  | Kershaw-Ryan | 2010 | 420 | 2016-04-12 | Four to Ten Years | Long-Term Needs | 3 | 2500
3702INT1 | INTERIOR FINISHES | 3702 | It is recommended to paint the interior walls and ceilings at least once in the next 9-10 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | STORAGE BUILDING | 9944 | CNR | Parks |  | Kershaw-Ryan | 2014 | 900 | 2016-04-12 | Four to Ten Years | Long-Term Needs | 3 | 9000
3716EXT0 | EXTERIOR FINISHES | 3716 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking the flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | PUMP HOUSE | 9944 | CNR | Parks |  | Kershaw-Ryan | 2009 | 120 | 2016-04-12 | Four to Ten Years | Long-Term Needs | 3 | 1080
3715EXT0 | EXTERIOR FINISHES | 3715 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | ENTRANCE FEE STATION | 9944 | CNR | Parks |  | Kershaw-Ryan | 2010 | 420 | 2016-04-12 | Four to Ten Years | Long-Term Needs | 3 | 2500
3686EXT2 | EXTERIOR DOOR REPLACEMENT | 3686 | The exterior door was missing at the time of the survey. This project would provide for the replacement and installation of a new metal door, frame and hardware. Removal and disposal of the existing door frame and painting of the new door is included in this estimate. | ELGIN OUTHOUSE | 9944 | CNR | Parks |  | Kershaw-Ryan | 1924 | 25 | 2016-04-12 | Immediate to Two Years | Currently Critical | 1 | 2000
3716ENR1 | LIGHTING UPGRADE | 3716 | The interior light in the building has an old light fixture and is not energy efficient. This project would provide for the replacement of the interior light fixture and bulb with a new light fixture and LED bulb. An occupancy sensor will be installed for additional savings. Electrical wiring upgrades have not been included in this estimate. | PUMP HOUSE | 9944 | CNR | Parks |  | Kershaw-Ryan | 2009 | 120 | 2016-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 350
3686INT1 | INTERIOR FINISHES | 3686 | It is recommended to paint the interior walls and ceilings at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. | ELGIN OUTHOUSE | 9944 | CNR | Parks |  | Kershaw-Ryan | 1924 | 25 | 2016-04-12 | Four to Ten Years | Long-Term Needs | 3 | 300
3686EXT1 | EXTERIOR FINISHES | 3686 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. | ELGIN OUTHOUSE | 9944 | CNR | Parks |  | Kershaw-Ryan | 1924 | 25 | 2016-04-12 | Immediate to Two Years | Currently Critical | 1 | 300
3685SFT1 | BATTERY STORAGE IMPROVEMENTS | 3685 | Section 608 of the 2012 International Fire Code (IFC) explains the requirements for stationary storage of battery systems. This project will provide funding to properly store, charge and/or use batteries indoors. IFC Section 608 states batteries shall have safety caps, spill control and neutralization, mechanical ventilation and/or cabinet ventilation, supervision over the mechanical ventilation, building or cabinet signage, seismically braced, and a smoke alarm. This project would provide funding for the requirements of Section 608 of the 2012 IFC. | ELGIN GENERATOR BUILDING | 9944 | CNR | Parks |  | Kershaw-Ryan | 2009 | 64 | 2016-04-12 | Immediate to Two Years | Currently Critical | 1 | 25000
3716INT1 | INTERIOR FINISHES | 3716 | It is recommended to repair and seal the interior concrete block walls at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to sealing, all surfaces should be repaired and prepped. | PUMP HOUSE | 9944 | CNR | Parks |  | Kershaw-Ryan | 2009 | 120 | 2016-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1080
3685EXT1 | EXTERIOR FINISHES | 3685 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the doors, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | ELGIN GENERATOR BUILDING | 9944 | CNR | Parks |  | Kershaw-Ryan | 2009 | 64 | 2016-04-12 | Four to Ten Years | Long-Term Needs | 3 | 120
3702EXT1 | EXTERIOR FINISHES | 3702 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 9-10 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | STORAGE BUILDING | 9944 | CNR | Parks |  | Kershaw-Ryan | 2014 | 900 | 2016-04-12 | Four to Ten Years | Long-Term Needs | 3 | 9000
0552PLM3 | WATER HEATER REPLACEMENT | 0552 | There is a 12 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new on-demand electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/16/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/12/2016. | COMFORT STATION #1 - UPPER | 9944 | CNR | Parks |  | Kershaw-Ryan | 1996 | 452 | 2016-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0552INT2 | DOOR HARDWARE REPLACEMENT | 0552 | The exterior metal doors are in good shape, but staff has had continuous problems with the hardware. The handles and locks are damaged from age and general wear and tear and have reached the end of their useful life. This project would provide for the replacement of the hardware on seven doors. Removal and disposal of the existing hardware is included in this estimate. | COMFORT STATION #1 - UPPER | 9944 | CNR | Parks |  | Kershaw-Ryan | 1996 | 452 | 2016-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3500
0552ENR1 | LIGHTING UPGRADE | 0552 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade the fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/16/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/12/2016. | COMFORT STATION #1 - UPPER | 9944 | CNR | Parks |  | Kershaw-Ryan | 1996 | 452 | 2016-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3616
0553EXT1 | HISTORIC BUILDING MAINTENANCE | 0553 | The structure is made of unreinforced stone masonry. It is over 82 years old and there are numerous areas where the mortar is failing, missing and not sealed properly. This is also an exhibit for the park and requires maintenance and requires signage. This project would provide for the cleaning, repair and re-pointing of the stone work and maintaining the exhibit. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CCC RESTROOM | 9944 | CNR | Parks |  | Kershaw-Ryan | 1934 | 78 | 2016-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1170
0553EXT2 | HISTORIC STRUCTURE REPORT | 0553 | The building was constructed in 1934. It may be eligible to be on the National Register of Historic Places. A historic structure report would provide documentary, graphic, and physical information about a property's history and existing condition. It also provides guidelines for maintenance of the building. This project recommends obtaining the report in accordance with the U.S. Department of Interior Recommended Guidelines in Preservation Brief 43. This property may be eligible for federal grants or special funding if this project is implemented. | CCC RESTROOM | 9944 | CNR | Parks |  | Kershaw-Ryan | 1934 | 78 | 2016-04-12 | Four to Ten Years | Long-Term Needs | 3 | 8000
0552ADA1 | ADA PARKING UPGRADE | 0552 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. There is a designated ADA parking space which does not meet the intent of the code. This project provides funding to bring the existing ADA parking space up to code including a concrete parking stall and loading zone, updated signage, striping and any other necessary upgrades. International Building Code (IBC) 2012, ICC/ANSI A117.1 - 2009 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2009 were referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/16/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/12/2016. | COMFORT STATION #1 - UPPER | 9944 | CNR | Parks |  | Kershaw-Ryan | 1996 | 452 | 2016-04-12 | Immediate to Two Years | Currently Critical | 1 | 6400
0552EXT1 | EXTERIOR FINISHES | 0552 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/16/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/12/2016. | COMFORT STATION #1 - UPPER | 9944 | CNR | Parks |  | Kershaw-Ryan | 1996 | 452 | 2016-04-12 | Four to Ten Years | Long-Term Needs | 3 | 4520
0529INT1 | INTERIOR FINISHES | 0529 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | BRICK PUMP HOUSE | 9944 | CNR | Parks |  | Kershaw-Ryan | 2008 | 100 | 2016-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
0529EXT1 | EXTERIOR FINISHES | 0529 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/16/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/12/2016. | BRICK PUMP HOUSE | 9944 | CNR | Parks |  | Kershaw-Ryan | 2008 | 100 | 2016-04-12 | Four to Ten Years | Long-Term Needs | 3 | 1000
0552INT1 | INTERIOR FINISHES | 0552 | It is recommended that the interior walls and ceilings be painted or sealed at least once in the next 2-3 years and every 5-6 years thereafter to maintain the integrity of the interior of the building. Prior to painting or sealing, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/16/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/12/2016. | COMFORT STATION #1 - UPPER | 9944 | CNR | Parks |  | Kershaw-Ryan | 1996 | 452 | 2016-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4520
0549EXT1 | EXTERIOR FINISHES | 0549 | It is important to maintain the finish, weather resistance and appearance of the structure. This project recommends work to protect the exterior of the structure, other than the roof, including sealing, painting or other applied finishes, and caulking around, flashing, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | GROUP USE RAMADA - UPPER | 9944 | CNR | Parks |  | Kershaw-Ryan | 1996 | 612 | 2016-04-12 | Four to Ten Years | Long-Term Needs | 3 | 6120
0527ADA1 | ADA UPGRADES | 0527 | The Americans with Disabilities Act (ADA) provides for accessibility to Ramada #1 – Lower and services for people with physical limitations. There is a designated ADA parking space which does not meet the intent of the code. This project provides funding to bring the existing ADA parking space up to code including a concrete parking stall and loading zone, updated signage, striping and an ADA accessible pathway, picnic table and barbeque. International Building Code (IBC) 2012, ICC/ANSI A117.1 - 2009 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2009 were referenced for this project. | GROUP USE RAMADA - LOWER | 9944 | CNR | Parks |  | Kershaw-Ryan | 1996 | 612 | 2016-04-12 | Immediate to Two Years | Currently Critical | 1 | 30000
0527EXT1 | EXTERIOR FINISHES | 0527 | It is important to maintain the finish, weather resistance and appearance of the structure. This project recommends work to protect the exterior of the structure, other than the roof, including sealing, painting or other applied finishes, and caulking around, flashing, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/16/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/12/2016. | GROUP USE RAMADA - LOWER | 9944 | CNR | Parks |  | Kershaw-Ryan | 1996 | 612 | 2016-04-12 | Four to Ten Years | Long-Term Needs | 3 | 6120
1178ADA3 | ADA ACCESSIBLE PATH OF TRAVEL | 1178 | The ADA provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to Comfort Station #2 are necessary to comply with ADA accessibility requirements. This project would provide for the removal and replacement of the concrete van accessible ADA parking and loading space and the concrete walkway to the existing sidewalk. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. 750 square feet of concrete was used for this estimate. | COMFORT STATION #2 | 9943 | CNR | Parks |  | Spring Valley | 1975 | 380 | 2016-04-13 | Immediate to Two Years | Currently Critical | 1 | 30000
1175EXT1 | HISTORIC BUILDING MAINTENANCE | 1175 | The wood structure is over 75 years old and there are numerous areas where the wood is splitting, warping and deteriorating. This is also an exhibit for the park and requires maintenance. This project would provide for sealing the wood and repairing the roof as needed. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements, which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | MILLET RANCH CHICKEN COOP | 9943 | CNR | Parks |  | Spring Valley | 1930 | 208 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3120
1218SFT1 | FIRE EXTINGUISHER INSTALLATION | 1218 | The building does not have a portable fire extinguisher available. 2012 International Fire Code (IFC) Section 906 requires that portable fire extinguishers shall be installed in S occupancies. This project would provide funding for the purchase and installation of 2 fire extinguishers, cabinets and the hardware necessary to install them per IFC. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | PARK HEADQUARTERS SHOP/ GARAGE | 9943 | CNR | Parks |  | Spring Valley | 1941 | 827 | 2016-04-13 | Immediate to Two Years | Currently Critical | 1 | 1000
1218EXT1 | EXTERIOR FINISHES | 1218 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | PARK HEADQUARTERS SHOP/ GARAGE | 9943 | CNR | Parks |  | Spring Valley | 1941 | 827 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8270
1218HVA1 | ELECTRIC HEATER REPLACEMENT | 1218 | There is an electric heater in the Park Headquarters Shop/ Garage that has reached the end of its expected life. This project recommends replacing the electric heater. The estimate includes removal and disposal of the existing equipment. | PARK HEADQUARTERS SHOP/ GARAGE | 9943 | CNR | Parks |  | Spring Valley | 1941 | 827 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
1180EXT1 | HISTORIC BUILDING MAINTENANCE | 1180 | The wood structure is over 75 years old and there are numerous areas where the wood is splitting, warping and deteriorating. This project would provide for sealing the wood, replacing metal roof panels as needed, and to replace the wood siding as needed. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements, which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | TIMBER HORSE BARN | 9943 | CNR | Parks |  | Spring Valley | 1940 | 480 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7200
1178PLM1 | FUEL GAS SEDIMENT TRAP INSTALLATION | 1178 | The gas line serving the appliances in the Comfort Station #2 does not have sediment traps. Per International Fuel Gas Code (IFGC) 2012, Section 408, "where a sediment trap is not incorporated as part of the appliance, a sediment trap shall be installed downstream of the appliance shutoff valve as close to the inlet of the appliance as practical. The sediment trap shall be either; a tee fitting, having a capped nipple, of any length, installed vertically in the bottommost opening of the tee, or other device approved as an effective sediment trap." This project would provide for all labor and materials to have sediment traps installed near all gas appliances. | COMFORT STATION #2 | 9943 | CNR | Parks |  | Spring Valley | 1975 | 380 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
1178EXT3 | ROOF REPLACEMENT | 1178 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayment. This estimate includes removal and disposal of the old underlayment and roof. | COMFORT STATION #2 | 9943 | CNR | Parks |  | Spring Valley | 1975 | 380 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4560
1178ADA2 | ADA SIDEWALK REPLACEMENT | 1178 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The concrete sidewalk around the building does not meet ADA requirements and is in need of replacement. Settling, spalling and cracking have created a non-ADA compliant path of travel to the restrooms. This project would provide for the removal and replacement of the concrete sidewalk. 500 SF of 4" thick P.C. concrete sidewalk was used for this estimate. The 2012 International Building Code (IBC), ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | COMFORT STATION #2 | 9943 | CNR | Parks |  | Spring Valley | 1975 | 380 | 2016-04-13 | Immediate to Two Years | Currently Critical | 1 | 7500
1178ADA4 | ADA SIGNAGE | 1178 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria include: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with these criteria. It is recommended that applicable signage be installed where required. The 2012 International Building Code (IBC), ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | COMFORT STATION #2 | 9943 | CNR | Parks |  | Spring Valley | 1975 | 380 | 2016-04-13 | Immediate to Two Years | Currently Critical | 1 | 750
1218ENR1 | LIGHTING UPGRADE | 1218 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | PARK HEADQUARTERS SHOP/ GARAGE | 9943 | CNR | Parks |  | Spring Valley | 1941 | 827 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6616
1178ADA1 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 1178 | The building contains a water fountain that is not Americans with Disabilities Act (ADA) compliant. The 2012 International Building Code (IBC) Section 1109.5 states "where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons." This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | COMFORT STATION #2 | 9943 | CNR | Parks |  | Spring Valley | 1975 | 380 | 2016-04-13 | Immediate to Two Years | Currently Critical | 1 | 4000
1218EXT2 | WINDOW REPLACEMENT | 1218 | The window is original, single pane construction and has a metal frame. This older window is drafty and not energy efficient. This project recommends replacing the window with a dual pane, higher efficiency unit. This estimate is for the replacement of one window. Removal and disposal of the existing window is included in this estimate. | PARK HEADQUARTERS SHOP/ GARAGE | 9943 | CNR | Parks |  | Spring Valley | 1941 | 827 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
1177INT1 | INTERIOR FINISHES | 1177 | It is recommended to paint the partitions and ceilings and re-caulk the Fiberglass Reinforced Panels (FRP) at least once in the next 2-3 years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project should be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | COMFORT STATION #1 | 9943 | CNR | Parks |  | Spring Valley | 1975 | 334 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3340
1177EXT1 | EXTERIOR FINISHES | 1177 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 2-3 years and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | COMFORT STATION #1 | 9943 | CNR | Parks |  | Spring Valley | 1975 | 334 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3340
1177HVA1 | ELECTRIC HEATER REPLACEMENT | 1177 | There are two electric heaters in the building that have reached the end of their expected life. This project recommends replacing the electric heaters. The estimate includes removal and disposal of the existing equipment. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | COMFORT STATION #1 | 9943 | CNR | Parks |  | Spring Valley | 1975 | 334 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
1177ADA1 | ADA PARKING UPGRADE | 1177 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The ADA parking space next to the building is deteriorating and no longer meets the requirements of ADA. The concrete for the parking space, adjacent passenger loading zone and path of travel to the building is spalling and should be removed and replaced. The parking space and path of travel will also require updated signage and striping. 2012 International Building Code (IBC), ICC/ANSI A117.1 - 2009, Nevada Revised Statutes (NRS) 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | COMFORT STATION #1 | 9943 | CNR | Parks |  | Spring Valley | 1975 | 334 | 2016-04-13 | Immediate to Two Years | Currently Critical | 1 | 30000
1177ADA2 | ADA RESTROOM UPGRADE | 1177 | The Men's and Women's designated ADA restrooms do not meet the Americans with Disabilities Act (ADA) regulations. A retrofit is necessary to comply with 2012 International Building Code (IBC) Chapter 11, ICC/ANSI A117.1-2009 Sections 603 - 604 and the Americans with Disabilities Act Accessibility Guidelines (ADAAG). Given the current configuration of the restrooms, the work will include the installation of a new toilet, sink, grab bars, faucets, mirrors, dispensers and hardware. Some minor design work will be required and may impact the final cost estimate. This estimate is for one ADA Unisex restroom facility, the other restroom will be assigned as Unisex as well. The removal and disposal of the old restroom fixtures is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | COMFORT STATION #1 | 9943 | CNR | Parks |  | Spring Valley | 1975 | 334 | 2016-04-13 | Immediate to Two Years | Currently Critical | 1 | 25000
1177EXT2 | ROOF REPLACEMENT | 1177 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayment. This estimate includes removal and disposal of the old underlayment and roof. | COMFORT STATION #1 | 9943 | CNR | Parks |  | Spring Valley | 1975 | 334 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4560
1176ELE1 | GENERATOR REPLACEMENT | 1176 | There is a propane-fired generator on site that has reached the end of its expected life and was not working at the time of the survey. It does not have automatic switch gear and the room that it is stored in does not have proper ventilation. The generator provides backup power for the buildings. It is recommended that a new 12 kW propane-fired generator be installed. This estimate includes removal and disposal of the old generator. | PARK HEADQUARTERS GENERATOR BUILDING | 9943 | CNR | Parks |  | Spring Valley | 1979 | 184 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
1176SFT1 | EXTERIOR LANDING INSTALLATION | 1176 | Section 1008.1, of the 2012 International Building Code (IBC), describes requirements for doors and landings; floors or landings shall be at the same elevation on each side of the door; exterior landings shall not exceed a 2% slope and shall have a length measured in the direction of travel of not less than 44 inches. There is no compliant landing located at the outside of the door of the building. This is out of compliance and poses a safety hazard. This project would provide for the installation of a compliant landing for the door. | PARK HEADQUARTERS GENERATOR BUILDING | 9943 | CNR | Parks |  | Spring Valley | 1979 | 184 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
1176EXT1 | EXTERIOR FINISHES | 1176 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting the wood finishes, re-pointing the stone where needed and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | PARK HEADQUARTERS GENERATOR BUILDING | 9943 | CNR | Parks |  | Spring Valley | 1979 | 184 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1840
1176INT1 | INTERIOR FINISHES | 1176 | This project would provide funding to maintain the interior of the building. Included in the cost is painting the walls and ceilings, sealing the exposed masonry, repairing cracks in the masonry and replacing grout and caulk as needed. An epoxy-based paint should be utilized in wet areas for durability. It is recommended that the interior of the building be painted, sealed and repaired in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | PARK HEADQUARTERS GENERATOR BUILDING | 9943 | CNR | Parks |  | Spring Valley | 1979 | 184 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1840
1178EXT1 | EXTERIOR FINISHES | 1178 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | COMFORT STATION #2 | 9943 | CNR | Parks |  | Spring Valley | 1975 | 380 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3800
1067EXT1 | REBUILD STRUCTURE | 1067 | The ramada is structurally failing and should be scheduled for replacement. This project would provide for demolishing the existing structure and rebuilding a new one. The new structure will have new concrete footings, steel framing and a metal standing seam roof. The design plans and permitting fees are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | ADA RAMADA - GROUP AREA | 9945 | CNR | Parks |  | Echo Canyon | 1990 | 493 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
1063INT1 | INTERIOR FINISHES | 1063 | It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | COMFORT STATION #2 - GROUP AREA | 9945 | CNR | Parks |  | Echo Canyon | 1990 | 437 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4370
1063ADA1 | ADA ACCESSIBLE PATH OF TRAVEL | 1063 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the restrooms are necessary to comply with ADA accessibility requirements. This project would provide for a concrete, van accessible, ADA parking and loading space, and a concrete ADA walkway to the existing sidewalk. This will require re-grading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2012 International Building Code (IBC), ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | COMFORT STATION #2 - GROUP AREA | 9945 | CNR | Parks |  | Echo Canyon | 1990 | 437 | 2016-04-13 | Immediate to Two Years | Currently Critical | 1 | 30000
1063ADA3 | ADA SIGNAGE | 1063 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with these criteria. It is recommended that applicable signage be installed where required. The 2012 International Building Code (IBC), ICC/ANSI A117.1 - 2009, Nevada Revised Statutes (NRS) 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | COMFORT STATION #2 - GROUP AREA | 9945 | CNR | Parks |  | Echo Canyon | 1990 | 437 | 2016-04-13 | Immediate to Two Years | Currently Critical | 1 | 2500
1063ADA2 | ADA RESTROOM UPGRADE | 1063 | The Men's and Women's restrooms do not comply with the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding remodel one Men's and one Women's accessible restroom in the building. Items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. Nevada Revised Statutes (NRS) 338.180, International Building Code (IBC) 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | COMFORT STATION #2 - GROUP AREA | 9945 | CNR | Parks |  | Echo Canyon | 1990 | 437 | 2016-04-13 | Immediate to Two Years | Currently Critical | 1 | 40000
1063EXT2 | EXTERIOR FINISHES | 1063 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | COMFORT STATION #2 - GROUP AREA | 9945 | CNR | Parks |  | Echo Canyon | 1990 | 437 | 2016-04-13 | Four to Ten Years | Long-Term Needs | 3 | 4370
1064INT1 | INTERIOR FINISHES | 1064 | It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | COMFORT STATION #1 - NORTH CAMPGROUND | 9945 | CNR | Parks |  | Echo Canyon | 1990 | 433 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4330
1064ADA3 | ADA SIGNAGE | 1064 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with these criteria. It is recommended that applicable signage be installed where required. Nevada Revised Statutes (NRS) 338.180, International Building Code (IBC) 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | COMFORT STATION #1 - NORTH CAMPGROUND | 9945 | CNR | Parks |  | Echo Canyon | 1990 | 433 | 2016-04-13 | Immediate to Two Years | Currently Critical | 1 | 2500
1064ADA2 | ADA RESTROOM UPGRADE | 1064 | The Men's and Women's restrooms do not comply with the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding to remodel one Men's and one Women's accessible restroom in the building. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. Nevada Revised Statutes (NRS) 338.180, International Building Code (IBC) 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | COMFORT STATION #1 - NORTH CAMPGROUND | 9945 | CNR | Parks |  | Echo Canyon | 1990 | 433 | 2016-04-13 | Immediate to Two Years | Currently Critical | 1 | 40000
1064ADA1 | ADA PARKING AND PATH OF TRAVEL | 1064 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the restroom are necessary to comply with ADA accessibility requirements. This project would provide for a concrete van accessible ADA parking and loading space and concrete walkway to the existing sidewalk. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2012 International Building Code (IBC), ICC/ANSI A117.1 - 2009 and the most current version of the Americans With Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | COMFORT STATION #1 - NORTH CAMPGROUND | 9945 | CNR | Parks |  | Echo Canyon | 1990 | 433 | 2016-04-13 | Immediate to Two Years | Currently Critical | 1 | 30000
1064EXT2 | EXTERIOR FINISHES | 1064 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | COMFORT STATION #1 - NORTH CAMPGROUND | 9945 | CNR | Parks |  | Echo Canyon | 1990 | 433 | 2016-04-13 | Four to Ten Years | Long-Term Needs | 3 | 4330
1218INT1 | INTERIOR FINISHES | 1218 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | PARK HEADQUARTERS SHOP/ GARAGE | 9943 | CNR | Parks |  | Spring Valley | 1941 | 827 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8270
1065EXT2 | CONCRETE PATCH/ ROOFING | 1065 | It is important to maintain the water proofing and structural integrity of the concrete roof deck on the building. This project would provide funding to repair the spalling concrete using an epoxy patch (to repair and seal) and then painting with an epoxy-based paint on the concrete roof decking. Included in the cost is the preparation of the concrete roof decking by cleaning, sanding, and removing all paint, loose concrete and aggregate from the roof decking. Per 2012 International Energy Conservation Code (IECC), the minimum insulation in a zone 5 entirely above the deck per Table C402.2 is R- 25. After the concrete roof decking is completely repaired, an R-25 insulation is to be fastened to the concrete roof decking, and a fully adhered single ply membrane should be installed over the insulation. The current roof decking was installed in 1970 and it is recommended that the work be performed in the next year. | PARK WELL HOUSE | 9945 | CNR | Parks |  | Echo Canyon | 1970 | 48 | 2016-04-13 | Immediate to Two Years | Currently Critical | 1 | 5280
1178INT1 | INTERIOR FINISHES | 1178 | It is recommended to maintain the Fiberglass Reinforced Plastic (FRP) at least once in the next 2-3 years. This will include cleaning all surfaces, if needed, adding additional adhesive or fasteners to the FRP, caulking and to make necessary repairs to expansion joints and moldings. This project should be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | COMFORT STATION #2 | 9943 | CNR | Parks |  | Spring Valley | 1975 | 380 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3800
1221EXT1 | EXTERIOR FINISHES | 1221 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking, sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | PARK HEADQUARTERS STORAGE SHED | 9943 | CNR | Parks |  | Spring Valley | 1998 | 1078 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2156
1220ELE1 | WIRING CLEANUP | 1220 | The wiring in the Park Headquarters Supply Room is disorganized and not in proper electrical boxes. This creates a safety issue. This project would provide for proper labeling, organization and for the wiring to be placed in electrical boxes per NEC 2011. | PARK HEADQUARTERS SUPPLY ROOM | 9943 | CNR | Parks |  | Spring Valley | 1940 | 333 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
1220EXT2 | WINDOW REPLACEMENT | 1220 | The windows are original, single pane construction in an aluminum frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 2 windows and the removal and disposal of the old windows. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | PARK HEADQUARTERS SUPPLY ROOM | 9943 | CNR | Parks |  | Spring Valley | 1940 | 333 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
1220INT1 | INTERIOR FINISHES | 1220 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | PARK HEADQUARTERS SUPPLY ROOM | 9943 | CNR | Parks |  | Spring Valley | 1940 | 333 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3330
1220EXT3 | EXTERIOR DOOR REPLACEMENT | 1220 | The existing exterior wood door appears to be original to the building. It is damaged from age and general wear and tear. This project would provide for the replacement of the wood door with a new metal door, frame and hardware. Removal and disposal of the existing door and painting of the new door is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | PARK HEADQUARTERS SUPPLY ROOM | 9943 | CNR | Parks |  | Spring Valley | 1940 | 333 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
1220HVA1 | ELECTRIC HEATER REPLACEMENT | 1220 | This building is heated by an electric heater that has reached the end of its expected life. This project recommends replacing the electric heater. The estimate includes removal and disposal of the existing equipment. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | PARK HEADQUARTERS SUPPLY ROOM | 9943 | CNR | Parks |  | Spring Valley | 1940 | 333 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
1220EXT1 | EXTERIOR FINISHES | 1220 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | PARK HEADQUARTERS SUPPLY ROOM | 9943 | CNR | Parks |  | Spring Valley | 1940 | 333 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3330
1219EXT1 | EXTERIOR FINISHES | 1219 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | MILLET RANCH TACK SHED | 9943 | CNR | Parks |  | Spring Valley | 1941 | 135 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1350
1218SFT2 | EXTERIOR LANDING INSTALLATION | 1218 | The concrete stairs that access the building are deteriorating. Spalling and cracking have occurred. Exposure to the elements is a contributing factor. It appears that the stairs are original to the building. The stairs do not comply with 2012 International Building Code (IBC) Section 1008.1, which requires a proper landing and for the landing to not be more than 1/2" below the threshold. This project would provide for the installation of compliant landings and stairs. | PARK HEADQUARTERS SHOP/ GARAGE | 9943 | CNR | Parks |  | Spring Valley | 1941 | 827 | 2016-04-13 | Immediate to Two Years | Currently Critical | 1 | 10000
1218ELE1 | WIRING CLEANUP | 1218 | The wiring at the Park Headquarters Shop/ Garage does not have a dead panel or cover for the electrical panel. This creates a safety issue and is a code violation. This project would provide for a new dead panel, proper labeling and for the cover to be reinstalled over the electrical panel per NEC 2011. | PARK HEADQUARTERS SHOP/ GARAGE | 9943 | CNR | Parks |  | Spring Valley | 1941 | 827 | 2016-04-13 | Immediate to Two Years | Currently Critical | 1 | 2000
1065EXT1 | EXTERIOR/ INTERIOR FINISHES | 1065 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost is repairing cracked concrete, painting the precast concrete and caulking of any exterior penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended for this work to be performed in the next 2-3 years and for this project to be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | PARK WELL HOUSE | 9945 | CNR | Parks |  | Echo Canyon | 1970 | 48 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 960
1101EXT1 | EXTERIOR FINISHES | 1101 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is caulking and sealing the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | PARK OFFICE STORAGE SHED #3 | 9945 | CNR | Parks |  | Echo Canyon | 1990 | 198 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 396
1068EXT1 | REBUILD STRUCTURE | 1068 | The ramada is structurally failing and should be scheduled for replacement. This project would provide for demolishing the existing structure and rebuilding a new one. The new structure will have new concrete footings, steel framing and a metal standing seam roof. The design plans and permitting fees are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | RAMADA - GROUP AREA | 9945 | CNR | Parks |  | Echo Canyon | 1990 | 493 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
1178EXT2 | EXTERIOR DOOR REPLACEMENT | 1178 | The exterior metal doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the seven door assemblies with new metal doors, frames and hardware. Removal and disposal of the existing doors is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | COMFORT STATION #2 | 9943 | CNR | Parks |  | Spring Valley | 1975 | 380 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 21000
2266INT1 | INTERIOR FINISHES | 2266 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | HISTORIC STONE CABIN | 9943 | CNR | Parks |  | Spring Valley | 1870 | 423 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4230
2266EXT1 | HISTORIC BUILDING MAINTENANCE | 2266 | The structure is made of unreinforced stone masonry. It is over 100 years old and there are numerous areas where the mortar is failing, missing and not sealed properly. This is also an exhibit for the park and requires maintenance time to display the artifacts and maintain the signage. This project would provide for the cleaning, repair and re-pointing of the stone work and maintaining the exhibit. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | HISTORIC STONE CABIN | 9943 | CNR | Parks |  | Spring Valley | 1870 | 423 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6345
2266EXT2 | HISTORIC STRUCTURE REPORT | 2266 | The building was constructed in 1870 and is currently operating as a living museum. It may be eligible to be on the National Register of Historic Places. A historic structure report would provide documentary, graphic, and physical information about a property's history and existing condition. It also provides guidelines for maintenance of the building. This project recommends obtaining the report in accordance with the U.S. Department of Interior Recommended Guidelines in Preservation Brief 43. This property may be eligible for federal grants or special funding if this project is implemented. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | HISTORIC STONE CABIN | 9943 | CNR | Parks |  | Spring Valley | 1870 | 423 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
2266SIT1 | DRAINAGE IMPROVEMENTS | 2266 | The site has a drainage problem around the Historic Stone Cabin where the grade does not properly slope away from the building. The rain accumulates in several areas adjacent to the building creating a water problem which may infiltrate the interior during inclement weather. This standing water also causes premature deterioration of the landscape improvements. This project would provide for a site survey and drainage report to be completed by a licensed professional and for that work to be performed by a licensed contractor. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | HISTORIC STONE CABIN | 9943 | CNR | Parks |  | Spring Valley | 1870 | 423 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
2265EXT1 | EXTERIOR FINISHES | 2265 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | HORSETHIEF GULCH STORAGE BUILDING | 9943 | CNR | Parks |  | Spring Valley | 1977 | 25 | 2016-04-13 | Four to Ten Years | Long-Term Needs | 3 | 250
2265INT1 | INTERIOR FINISHES | 2265 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | HORSETHIEF GULCH STORAGE BUILDING | 9943 | CNR | Parks |  | Spring Valley | 1977 | 25 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 250
2265EXT2 | ROOF REPLACEMENT | 2265 | The wood shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle or a standing seam metal roof system and new underlayment. This estimate includes removal and disposal of the old underlayment and roof. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | HORSETHIEF GULCH STORAGE BUILDING | 9943 | CNR | Parks |  | Spring Valley | 1977 | 25 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
2262EXT2 | EXTERIOR/ INTERIOR FINISHES | 2262 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 4-5 years and for this project to be scheduled on a cyclical basis to maintain the integrity of the structure. | NEW WELL/ PUMP HOUSE | 9943 | CNR | Parks |  | Spring Valley | 1998 | 60 | 2016-04-13 | Four to Ten Years | Long-Term Needs | 3 | 1200
2267EXT3 | HISTORIC STRUCTURES REPORT | 2267 | The building was constructed in 1870 and is currently not in use. It may be eligible to be on the National Register of Historic Places. A historic structure report would provide documentary, graphic, and physical information about a property's history and existing condition. It also provides guidelines for maintenance of the building. This project recommends obtaining the report in accordance with the U.S. Department of Interior Recommended Guidelines in Preservation Brief 43. This property may be eligible for federal grants or special funding if this project is implemented. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | HAMMOND CABIN | 9943 | CNR | Parks |  | Spring Valley | 1870 | 880 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
2920EXT1 | EXTERIOR FINISHES | 2920 | It is important to maintain the finish, weather resistance and appearance of the structure. This project recommends work to protect the exterior building envelope, other than the roof including sealing and caulking around penetrations to maintain the building in good, weather tight condition. It is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | PARK HEADQUARTERS CARPORT | 9943 | CNR | Parks |  | Spring Valley | 2008 | 468 | 2016-04-13 | Four to Ten Years | Long-Term Needs | 3 | 1872
2927EXT1 | EXTERIOR FINISHES | 2927 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | CAMPGROUND TRELLIS #2 | 9943 | CNR | Parks |  | Spring Valley | 2008 | 180 | 2016-04-13 | Four to Ten Years | Long-Term Needs | 3 | 720
2926EXT1 | EXTERIOR FINISHES | 2926 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | CAMPGROUND TRELLIS #1 | 9943 | CNR | Parks |  | Spring Valley | 2008 | 180 | 2016-04-13 | Four to Ten Years | Long-Term Needs | 3 | 720
2925EXT1 | EXTERIOR FINISHES | 2925 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | INFORMATION KIOSK | 9943 | CNR | Parks |  | Spring Valley | 2008 | 18 | 2016-04-13 | Four to Ten Years | Long-Term Needs | 3 | 175
2925EXT2 | ROOF REPLACEMENT | 2925 | The wood shingle roof on this kiosk was in poor condition at the time of the survey. It is recommended that this kiosk be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayment. This estimate includes removal and disposal of the old roofing. | INFORMATION KIOSK | 9943 | CNR | Parks |  | Spring Valley | 2008 | 18 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 216
2924EXT2 | ROOF REPLACEMENT | 2924 | The asphalt composition shingle roof on this Campground Kiosk was in poor condition at the time of the survey. It is recommended that this Campground Kiosk be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayment. This estimate includes removal and disposal of the old underlayment and roof. | CAMPGROUND KIOSK | 9943 | CNR | Parks |  | Spring Valley | 2008 | 18 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 216
2924EXT1 | EXTERIOR FINISHES | 2924 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | CAMPGROUND KIOSK | 9943 | CNR | Parks |  | Spring Valley | 2008 | 18 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 175
2922EXT2 | HISTORIC BUILDING MAINTENANCE | 2922 | The wood structure is over 76 years old and there are numerous areas where the wood is splitting, warping and deteriorating. This is also an exhibit for the park and requires maintenance time to display the artifacts and maintain the signage. This project would provide for sealing the wood, caulking the flashing and fixtures, replacing metal roof panels as needed, replacing wood siding as needed and maintaining the exhibit in a state of arrested decay. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | PARK HEADQUARTERS OUTHOUSE | 9943 | CNR | Parks |  | Spring Valley | 1941 | 25 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 375
2921EXT1 | EXTERIOR FINISHES | 2921 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | LIFE JACKET KIOSK | 9943 | CNR | Parks |  | Spring Valley | 2008 | 18 | 2016-04-13 | Four to Ten Years | Long-Term Needs | 3 | 175
2267EXT1 | HISTORIC BUILDING MAINTENANCE | 2267 | The structure is made of unreinforced stone masonry. It is over 100 years old and there are numerous areas where the mortar is failing, missing and not sealed properly. This is also an exhibit for the park and requires maintenance time to display the artifacts and maintain the signage. This project would provide for the cleaning, repair and re-pointing of the stone work and maintaining the exhibit. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | HAMMOND CABIN | 9943 | CNR | Parks |  | Spring Valley | 1870 | 880 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 13200
9945ADA3 | ADA HANDRAIL INSTALLATION | 9945 | The Americans with Disabilities Act (ADA) ramp leading up to the amphitheater is missing handrails. This project recommends the installation of handrails on both sides of the ramp and compliant returns and supports. Nevada Revised Statutes (NRS) 338.180, 2012 International Building Code (IBC) Chapter 10, Section 1012, ICC/ANSI A117.1 - 2009, and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | ECHO CANYON STATE PARK SITE | 9945 | CNR | Parks |  | Echo Canyon | 1970 |  | 2016-04-13 | Immediate to Two Years | Currently Critical | 1 | 15000
9945EXT1 | EXTERIOR FINISHES | 9945 | There are 63 wood and steel shade ramadas in different locations throughout the site which are either 144 s.f., 224 s.f., 234 s.f., 256 s.f., or 493 s.f. for a total of 14,010 square feet. It is important to maintain the finish, weather resistance and appearance of the structures. This project would provide for the painting of the structures. It is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structures. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | ECHO CANYON STATE PARK SITE | 9945 | CNR | Parks |  | Echo Canyon | 1970 |  | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 71924
9945ADA6 | ADA ACCESSIBLE PATH OF TRAVEL | 9945 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the Park Office are necessary to comply with ADA accessibility requirements. This project would provide for a concrete, van accessible, ADA parking and loading space, and a concrete ADA walkway to the existing sidewalk. This will require re-grading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2012 International Building Code (IBC), ICC/ANSI A117.1 - 2009, Nevada Revised Statutes (NRS) 338.180, and the most current version of the ADA Standards for Accessible Design were used as references for this project. 750 square feet of concrete was used for this estimate. It is recommended that this project coincide with the ADA parking and ADA signage projects. | ECHO CANYON STATE PARK SITE | 9945 | CNR | Parks |  | Echo Canyon | 1970 |  | 2016-04-13 | Immediate to Two Years | Currently Critical | 1 | 30000
9945ADA7 | ADA SIGNAGE | 9945 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage at the Park Office does not comply with these criteria. This project would provide funding for the purchase and installation of ADA signage, including directional signage from parking to accessible building entrances. The 2012 International Building Code (IBC), ICC/ANSI A117.1 - 2009, Nevada Revised Statutes (NRS) 338.180 and the most current version of the ADA Standards For Accessible Design were used as references for this project. | ECHO CANYON STATE PARK SITE | 9945 | CNR | Parks |  | Echo Canyon | 1970 |  | 2016-04-13 | Immediate to Two Years | Currently Critical | 1 | 2500
9945ADA5 | ADA PARKING SPACE | 9945 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. At the Park Office a concrete parking area and passenger loading area are necessary to comply with ADA requirements. This project would provide for a concrete, van accessible, ADA parking and loading space and walkway to the existing sidewalk. This will require regrading, installing P.C. concrete, striping, signage and any other necessary upgrades. The 2012 International Building Code (IBC), ICC/ANSI A117.1 - 2009, Nevada Revised Statutes (NRS) 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | ECHO CANYON STATE PARK SITE | 9945 | CNR | Parks |  | Echo Canyon | 1970 |  | 2016-04-13 | Immediate to Two Years | Currently Critical | 1 | 2500
3750EXT1 | EXTERIOR FINISHES | 3750 | It is important to maintain the finish, weather resistance and appearance of the ramada. This project would provide funding to protect the exterior of the ramada excluding the roof. Included in the cost is power washing and staining the wood. It is recommended that the ramada be stained in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | PARK OFFICE SHADE STRUCTURE | 9945 | CNR | Parks |  | Echo Canyon | 1990 | 232 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 464
3729EXT1 | EXTERIOR/ INTERIOR FINISHES | 3729 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | RV ADA COMFORT STATION #1 | 9945 | CNR | Parks |  | Echo Canyon | 2014 | 432 | 2016-04-13 | Four to Ten Years | Long-Term Needs | 3 | 8640
3728EXT1 | EXTERIOR FINISHES | 3728 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | PARK RESIDENCE METAL SHED #2 | 9945 | CNR | Parks |  | Echo Canyon | 0 | 450 | 2016-04-13 | Four to Ten Years | Long-Term Needs | 3 | 900
3727SFT1 | SAFETY CABINETS | 3727 | The building contains many different paints, stains, and other hazardous products located on open shelves and on the floor. This does not meet Occupational Safety and Health Administration (OSHA) standards or International Fire Code (IFC) for hazardous materials containment. This project would provide for a self-closing hazardous storage container in the building and the installation of placards on the building’s exterior in accordance with OSHA 1910.106 (d) and IFC Chapter 57 Section 5704.3.2.1.3. | PARK RESIDENCE METAL SHED #1 | 9945 | CNR | Parks |  | Echo Canyon | 1990 | 90 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
3727EXT1 | EXTERIOR FINISHES | 3727 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | PARK RESIDENCE METAL SHED #1 | 9945 | CNR | Parks |  | Echo Canyon | 1990 | 90 | 2016-04-13 | Four to Ten Years | Long-Term Needs | 3 | 180
3725EXT1 | EXTERIOR/ INTERIOR FINISHES | 3725 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 4-5 years and for this project to be scheduled on a cyclical basis to maintain the integrity of the structure. | CXT COMFORT STATION #1 | 9943 | CNR | Parks |  | Spring Valley | 2010 | 98 | 2016-04-13 | Four to Ten Years | Long-Term Needs | 3 | 1960
3081EXT1 | EXTERIOR FINISHES | 3081 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | PARK OFFICE STORAGE SHED #1 | 9945 | CNR | Parks |  | Echo Canyon | 2008 | 288 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2880
3081EXT2 | ROOF REPLACEMENT | 3081 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 4-5 years with a new 50 year asphalt composition roofing shingle and new underlayment. This estimate includes the installation of a new roof and the removal and disposal of the old roofing. | PARK OFFICE STORAGE SHED #1 | 9945 | CNR | Parks |  | Echo Canyon | 2008 | 288 | 2016-04-13 | Four to Ten Years | Long-Term Needs | 3 | 3456
3082EXT2 | ROOF REPLACEMENT | 3082 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayment. This estimate includes the installation of a new roof and the removal and disposal of the old roofing. | PARK OFFICE STORAGE SHED #2 | 9945 | CNR | Parks |  | Echo Canyon | 2004 | 288 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3456
3726EXT1 | EXTERIOR/ INTERIOR FINISHES | 3726 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 4-5 years and for this project to be scheduled on a cyclical basis to maintain the integrity of the structure. | CXT COMFORT STATION #2 | 9943 | CNR | Parks |  | Spring Valley | 2010 | 98 | 2016-04-13 | Four to Ten Years | Long-Term Needs | 3 | 1960
3674EXT1 | HISTORIC BUILDING MAINTENANCE | 3674 | The underground structure is over 100 years old and is at rick of caving in. This is also an exhibit for the park and requires maintenance time to display the artifacts and maintain the signage. This project would provide for replacing any deteriorated wood poles or beams, replacing any stones that have become dislodged and patching the roof assembly to prevent water intrusion. This project would create a 5% slope away from the structure. Additional drainage swales shall be installed, as needed. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HAMMOND CABIN OUTBUILDING 2 | 9943 | CNR | Parks |  | Spring Valley | 1870 | 256 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6400
3673EXT1 | HISTORIC BUILDING MAINTENANCE | 3673 | The underground structure is over 100 years old and is at rick of caving in. This is also an exhibit for the park and requires maintenance time to display the artifacts and maintain the signage. This project would provide for replacing any deteriorated wood poles or beams, replacing any stones that have become dislodged and patching the roof assembly to prevent water intrusion. This project would create a 5% slope away from the structure. Additional drainage swales shall be installed, as needed. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HAMMOND CABIN OUTBUILDING 1 | 9943 | CNR | Parks |  | Spring Valley | 1870 | 300 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
3082EXT1 | EXTERIOR FINISHES | 3082 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | PARK OFFICE STORAGE SHED #2 | 9945 | CNR | Parks |  | Echo Canyon | 2004 | 288 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2880
9943EXT1 | EXTERIOR FINISHES, SHADE RAMADAS | 9943 | There are 44 wood and steel shade ramadas in different locations throughout the site which are either 168 s.f., 256 s.f., 300 s.f. or 240 s.f. for a total of 9,088 square feet. It is important to maintain the finish, weather resistance and appearance of the structures. This project would provide for painting of the structures and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structures. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | SPRING VALLEY STATE PARK SITE | 9943 | CNR | Parks |  | Spring Valley |  |  | 2016-04-13 | Four to Ten Years | Long-Term Needs | 3 | 36352
9943ADA1 | CONCRETE STAIR REPLACEMENT | 9943 | There are two sets of stairs at the site constructed of landscaping blocks which do not meet construction, safety, or accessibility requirements, according to the 2012 International Building Code (IBC) Chapter 1009. One set of stairs near the restroom has four risers and the other rises up the face of the earthen dam with approximately 16 risers. This project recommends the installation of concrete landings, stairs and risers, with guard rails and handrails having proper height, spacing, and extensions according to the code requirements. Because of the critical construction dimensions and potential liability to the state, a licensed professional should be contracted to design the new stairs. IBC 2012, ICC/ANSI A117.1 - 2009 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2010 were referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/11/2002 and 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | SPRING VALLEY STATE PARK SITE | 9943 | CNR | Parks |  | Spring Valley |  |  | 2016-04-13 | Immediate to Two Years | Currently Critical | 1 | 25000
0508ADA2 | ADA PARKING SPACE | 0508 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. A concrete parking area and passenger loading area are necessary to comply with ADA requirements. This project would provide for a concrete, van accessible, ADA parking and loading space and a walkway. This will require regrading, installing P.C. concrete, striping, signage and any other necessary upgrades. The 2012 International Building Code (IBC), ICC/ANSI A117.1 - 2009, Nevada Revised Statutes (NRS) 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | PARK OFFICE | 9945 | CNR | Parks |  | Echo Canyon | 1986 | 147 | 2016-04-13 | Immediate to Two Years | Currently Critical | 1 | 2500
0508EXT2 | WINDOW REPLACEMENT | 0508 | The windows are original, double pane construction with metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. Removal and disposal of the existing windows is included in this estimate. | PARK OFFICE | 9945 | CNR | Parks |  | Echo Canyon | 1986 | 147 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0508ADA3 | ADA UPGRADES | 0508 | Section 4.13.9 of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) states that handles, pulls, latches, locks and other operating devices on accessible doors shall have a shape that is easy to grasp with one hand and does not require tight grasping, tight pinching, or twisting of the wrist to operate. Lever-operated mechanisms, push-type mechanisms, and U-shaped handles are acceptable designs. It is recommended that proper lever hardware be installed in this building to meet these requirements. | PARK OFFICE | 9945 | CNR | Parks |  | Echo Canyon | 1986 | 147 | 2016-04-13 | Immediate to Two Years | Currently Critical | 1 | 500
0509ENR1 | PHOTOVOLTAIC SYSTEM INSTALLATION | 0509 | There is a propane-fired furnace and a propane-fired water heater in the building that are not connected to power. The existing photovoltaic system only has enough power for the lighting and it is recommended to install a second photovoltaic system to provide additional power. This project would provide for the purchase and installation of a photovoltaic system including solar panels, deep cycle solar batteries and all associated electrical boxes and hardware to connect it to the furnace and water heater. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | COMFORT STATION #3 - BOAT RAMP | 9945 | CNR | Parks |  | Echo Canyon | 1994 | 250 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
0507PLM1 | WATER HEATER REPLACEMENT | 0507 | There is a 74 gallon propane water heater in the building. The average lifespan of a water heater is eight to ten years. This unit was installed in 2004. It is recommended that a new propane water heater, seismic straps, braided steel hose, expansion tank, ball valves, new flex gas line and a pan be installed. The removal and disposal of the existing equipment is included in this estimate. | PARK RESIDENCE | 9945 | CNR | Parks |  | Echo Canyon | 1991 | 1580 | 2016-04-13 | Immediate to Two Years | Currently Critical | 1 | 2500
0509INT1 | INTERIOR FINISHES | 0509 | It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | COMFORT STATION #3 - BOAT RAMP | 9945 | CNR | Parks |  | Echo Canyon | 1994 | 250 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0509ADA2 | ADA SIGNAGE | 0509 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with these criteria. It is recommended that applicable signage be installed where required. The 2012 International Building Code (IBC), ICC/ANSI A117.1 - 2009, Nevada Revised Statutes (NRS) 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | COMFORT STATION #3 - BOAT RAMP | 9945 | CNR | Parks |  | Echo Canyon | 1994 | 250 | 2016-04-13 | Immediate to Two Years | Currently Critical | 1 | 2500
0509ADA1 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0509 | There is a water fountain mounted on the exterior of this building. The 2012 International Building Code (IBC) Section 1109.5 states where a water fountain is provided, at least half should be accessible for people who use a wheelchair. This project would provide funding for the purchase and installation of a ADA new accessible fixed high/ low drinking fountain. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | COMFORT STATION #3 - BOAT RAMP | 9945 | CNR | Parks |  | Echo Canyon | 1994 | 250 | 2016-04-13 | Immediate to Two Years | Currently Critical | 1 | 4000
0509EXT1 | EXTERIOR FINISHES | 0509 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | COMFORT STATION #3 - BOAT RAMP | 9945 | CNR | Parks |  | Echo Canyon | 1994 | 250 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0508ADA1 | ADA DOOR & THRESHOLD REPLACEMENT | 0508 | The existing exterior entrance door and threshold to the Park Office is not accessible. This project would provide for a new accessible door and threshold assembly including removal of the existing door assembly and installation of the new accessible door assembly. ADA compliant signage is also included in this project. The 2012 International Building Code (IBC), ICC/ANSI A117.1 - 2009, Nevada Revised Statutes (NRS) 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/29/2016. | PARK OFFICE | 9945 | CNR | Parks |  | Echo Canyon | 1986 | 147 | 2016-04-13 | Immediate to Two Years | Currently Critical | 1 | 30000
0525EXT2 | EXTERIOR FINISHES | 0525 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | PARK RANGER RESIDENCE | 9943 | CNR | Parks |  | Spring Valley | 1941 | 2280 | 2016-04-13 | Four to Ten Years | Long-Term Needs | 3 | 22800
0508INT1 | INTERIOR FINISHES | 0508 | It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. This project or a portion there of was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | PARK OFFICE | 9945 | CNR | Parks |  | Echo Canyon | 1986 | 147 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1470
0510EXT1 | EXTERIOR FINISHES | 0510 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | FISH CLEANING STATION - BOAT RAMP | 9945 | CNR | Parks |  | Echo Canyon | 1990 | 93 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 930
0528INT1 | INTERIOR FINISHES | 0528 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | CAMPGROUND STORAGE #1 | 9943 | CNR | Parks |  | Spring Valley | 1970 | 140 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
0528EXT2 | ROOF REPLACEMENT | 0528 | The wood shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayment. This estimate includes removal and disposal of the old underlayment and roof. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | CAMPGROUND STORAGE #1 | 9943 | CNR | Parks |  | Spring Valley | 1970 | 140 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1680
0528EXT1 | EXTERIOR FINISHES | 0528 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | CAMPGROUND STORAGE #1 | 9943 | CNR | Parks |  | Spring Valley | 1970 | 140 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
0525INT1 | INTERIOR FINISHES | 0525 | It is recommended to paint the interior walls and ceilings at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | PARK RANGER RESIDENCE | 9943 | CNR | Parks |  | Spring Valley | 1941 | 2280 | 2016-04-13 | Four to Ten Years | Long-Term Needs | 3 | 22800
0507INT1 | INTERIOR FINISHES | 0507 | It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | PARK RESIDENCE | 9945 | CNR | Parks |  | Echo Canyon | 1991 | 1580 | 2016-04-13 | Four to Ten Years | Long-Term Needs | 3 | 15800
0507EXT1 | EXTERIOR FINISHES | 0507 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | PARK RESIDENCE | 9945 | CNR | Parks |  | Echo Canyon | 1991 | 1580 | 2016-04-13 | Four to Ten Years | Long-Term Needs | 3 | 15800
0508EXT1 | EXTERIOR FINISHES | 0508 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding and painting the wood trim and caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion there of was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | PARK OFFICE | 9945 | CNR | Parks |  | Echo Canyon | 1986 | 147 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1470
0513INT3 | JANITORS CLOSET REPAIRS | 0513 | The mop sinks in the plumbing chase are mounted adjacent to CMU and are showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | COMFORT STATION #3 | 9943 | CNR | Parks |  | Spring Valley | 2000 | 299 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
0524EXT1 | EXTERIOR FINISHES | 0524 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | OLD WELL/ PUMP HOUSE - CAMPGROUND | 9943 | CNR | Parks |  | Spring Valley | 1970 | 96 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9600
0524EXT2 | ROOF REPLACEMENT | 0524 | The wood shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle or standing seam metal roofing system and new underlayment. This estimate includes removal and disposal of the old underlayment and roof. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | OLD WELL/ PUMP HOUSE - CAMPGROUND | 9943 | CNR | Parks |  | Spring Valley | 1970 | 96 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1152
0524EXT3 | EXTERIOR LANDING INSTALLATION | 0524 | Section 1008.1 of the 2012 IBC describes the requirements for doors including floor elevations and landings. The floor or landing shall be at the same elevation on each side of the door, the exterior landing shall not exceed a 2-percent slope and shall have a length measured in the direction of travel of not less than 44 inches. The landing at the door on the building does not comply with this code and poses a safety hazard. This project would provide for the installation of a compliant landing for the door. | OLD WELL/ PUMP HOUSE - CAMPGROUND | 9943 | CNR | Parks |  | Spring Valley | 1970 | 96 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0523INT1 | INTERIOR FINISHES | 0523 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. | PARK OFFICE | 9943 | CNR | Parks |  | Spring Valley | 1940 | 216 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2160
0523ADA1 | ADA DOOR HARDWARE | 0523 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The exterior entrance door is on an accessible path of travel, but the door hardware and threshold are not compliant. This project would provide for ADA compliant door hardware and threshold on the exterior door. ADA compliant signage is also included in this project. The 2012 International Building Code (IBC), ICC/ANSI A117.1 - 2009, Nevada Revised Statutes (NRS) 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | PARK OFFICE | 9943 | CNR | Parks |  | Spring Valley | 1940 | 216 | 2016-04-13 | Immediate to Two Years | Currently Critical | 1 | 1000
0523SFT2 | FIRE EXTINGUISHER INSTALLATION | 0523 | The building does not have a portable fire extinguisher available. International Fire Code 2012 (IFC) Section 906 requires that portable fire extinguishers shall be installed in B occupancies. This project would provide funding for the purchase and installation of 1 fire extinguisher, cabinet, and the hardware necessary to install it. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | PARK OFFICE | 9943 | CNR | Parks |  | Spring Valley | 1940 | 216 | 2016-04-13 | Immediate to Two Years | Currently Critical | 1 | 500
0523EXT1 | EXTERIOR FINISHES | 0523 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming, painting the metal panels and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended to paint the building in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | PARK OFFICE | 9943 | CNR | Parks |  | Spring Valley | 1940 | 216 | 2016-04-13 | Four to Ten Years | Long-Term Needs | 3 | 2160
0523EXT2 | WINDOW REPLACEMENT | 0523 | The windows are older, double pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 2 windows. Removal and disposal of the existing windows is included in this estimate. | PARK OFFICE | 9943 | CNR | Parks |  | Spring Valley | 1940 | 216 | 2016-04-13 | Four to Ten Years | Long-Term Needs | 3 | 3000
0523SFT1 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0523 | The building is a B occupancy per the 2012 International Building Code (IBC). Pursuant to the Nevada State Fire Marshal (NSFM), Nevada Administrative Code (NAC) 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | PARK OFFICE | 9943 | CNR | Parks |  | Spring Valley | 1940 | 216 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6480
0510ADA1 | ADA SIGNAGE | 0510 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with these criteria. It is recommended that applicable signage be installed where required. The 2012 International Building Code (IBC), ICC/ANSI A117.1 - 2009, Nevada Revised Statutes (NRS) 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | FISH CLEANING STATION - BOAT RAMP | 9945 | CNR | Parks |  | Echo Canyon | 1990 | 93 | 2016-04-13 | Immediate to Two Years | Currently Critical | 1 | 2500
0522EXT2 | HISTORIC BUILDING MAINTENANCE | 0522 | The wood structure is over 77 years old and there are numerous areas where the wood is splitting, warping and deteriorating. This is also an exhibit for the park and requires maintenance time to display the artifacts and maintain the signage. This project would provide for sealing the wood, caulking the flashing, fixtures and windows, replacing metal roof panels as needed, replacing wood siding as needed and maintaining the exhibit in a state of arrested decay. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MILLET RANCH LEAN-TO BARN | 9943 | CNR | Parks |  | Spring Valley | 1940 | 736 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11040
0509ELE2 | WIRING CLEANUP | 0509 | The wiring inside the Comfort Station #3 - Boat Ramp is disorganized and not in proper electrical boxes, particularly the old main service wires. This creates a safety issue during repairs or upgrades. This project would provide for organization, proper labeling and for the wiring to be placed in electrical boxes per National Electrical Code (NEC) 2011. | COMFORT STATION #3 - BOAT RAMP | 9945 | CNR | Parks |  | Echo Canyon | 1994 | 250 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
0513ADA1 | ADA ACCESSIBLE PATH OF TRAVEL | 0513 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the Comfort Station are necessary to comply with ADA accessibility requirements. This project would provide for a concrete van accessible ADA parking and loading space and concrete walkway to the existing sidewalk. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. 750 square feet of concrete was used for this estimate. It is recommended that this project coincide with the paving project. | COMFORT STATION #3 | 9943 | CNR | Parks |  | Spring Valley | 2000 | 299 | 2016-04-13 | Immediate to Two Years | Currently Critical | 1 | 30000
0525PLM2 | WATER HEATER REPLACEMENT | 0525 | There is a 50 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater, seismic straps, braided steel hose, expansion tank, ball valves and a pan be installed. Removal and disposal of the existing equipment is included in this estimate. | PARK RANGER RESIDENCE | 9943 | CNR | Parks |  | Spring Valley | 1941 | 2280 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0525HVA1 | HEATER REPLACEMENT | 0525 | The building is heated by three wall mounted propane-fired and electric heating units. They have reached the end of their useful life. This project provides for disposal of the existing units and replacement with new propane-fired and electric units, and includes connections to utilities. | PARK RANGER RESIDENCE | 9943 | CNR | Parks |  | Spring Valley | 1941 | 2280 | 2016-04-13 | Four to Ten Years | Long-Term Needs | 3 | 4500
0525SFT1 | INSTALL SMOKE DETECTORS | 0525 | International Residential Code (IRC) 2012 Section R314 and R315.3 explains the requirements for smoke alarms in dwelling units. This includes: installing and maintaining smoke alarms in each sleeping room; having a carbon monoxide and smoke detector on the ceiling or wall outside of each sleeping area, and in the immediate vicinity of bedrooms when an alteration, repair or addition requiring a permit occurs. IRC 2012, requires that smoke detectors and carbon monoxide alarms be UL rated. Nevada Administrative Code (NAC) 477.915 (3) requires that smoke detectors be connected to the wiring in a building and include a battery for emergency backup power. This project would provide funding for the purchase and installation of smoke alarms and carbon monoxide alarms in accordance with IRC and NAC. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | PARK RANGER RESIDENCE | 9943 | CNR | Parks |  | Spring Valley | 1941 | 2280 | 2016-04-13 | Immediate to Two Years | Currently Critical | 1 | 2500
0513EXT2 | EXTERIOR FINISHES | 0513 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | COMFORT STATION #3 | 9943 | CNR | Parks |  | Spring Valley | 2000 | 299 | 2016-04-13 | Four to Ten Years | Long-Term Needs | 3 | 2990
0513PLM1 | WATER HEATER REPLACEMENT | 0513 | There is an 80 gallon electric water heater in the building. The bottom of the water heater is rusted, due to leaking water from the inner tank, the water heater should be replaced immediately. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | COMFORT STATION #3 | 9943 | CNR | Parks |  | Spring Valley | 2000 | 299 | 2016-04-13 | Immediate to Two Years | Currently Critical | 1 | 2200
0510ADA2 | FISH CLEANING STATION REPLACEMENT | 0510 | The Fish Cleaning Station is original to the building, has reached the end of its expected life and does not meet the Americans with Disabilities Act (ADA) requirements. A complete replacement of the fish cleaning equipment is necessary. This project would provide for removal and disposal of the existing equipment and the replacement with a new accessible fish cleaning station equipped with a grinder and sprayer. Nevada Revised Statutes (NRS) 338.180, International Building Code (IBC) 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | FISH CLEANING STATION - BOAT RAMP | 9945 | CNR | Parks |  | Echo Canyon | 1990 | 93 | 2016-04-13 | Immediate to Two Years | Currently Critical | 1 | 10000
0513INT2 | INTERIOR FINISHES | 0513 | It is recommended to repair and seal the interior concrete block walls at least once in 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. | COMFORT STATION #3 | 9943 | CNR | Parks |  | Spring Valley | 2000 | 299 | 2016-04-13 | Four to Ten Years | Long-Term Needs | 3 | 2990
0510INT1 | INTERIOR FINISHES | 0510 | It is recommended that the Fiberglass Reinforced Panels be power washed and re-caulked as needed. This project should be done at least once in the next 2-3 years and scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | FISH CLEANING STATION - BOAT RAMP | 9945 | CNR | Parks |  | Echo Canyon | 1990 | 93 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 930
0509PLM1 | WATER HEATER REPLACEMENT | 0509 | There is an on-demand propane-fired water heater in the building. The average life span of a water heater is 8-10 years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 4-5 years. It is recommended that a new on-demand propane-fired water heater be installed. Removal and disposal of the existing equipment is included in the estimate. | COMFORT STATION #3 - BOAT RAMP | 9945 | CNR | Parks |  | Echo Canyon | 1994 | 250 | 2016-04-13 | Four to Ten Years | Long-Term Needs | 3 | 2500
0523ENR1 | EXTERIOR LIGHTING REPLACEMENT | 0523 | The building has perimeter lighting on the exterior of the building, but the light fixtures are old, failing and not energy efficient. This project would provide for the replacement of the exterior lighting fixtures with new LED light fixtures, utilizing the existing wiring. | PARK OFFICE | 9943 | CNR | Parks |  | Spring Valley | 1940 | 216 | 2016-04-13 | Four to Ten Years | Long-Term Needs | 3 | 800
0525PLM1 | FUEL GAS SEDIMENT TRAP INSTALLATION | 0525 | The gas line serving the appliances in the residence does not have sediment traps. Per International Fuel Gas Code (IFGC) 2012, Section 408, where a sediment trap is not incorporated as part of the appliance, a sediment trap shall be installed downstream of the appliance shutoff valve as close to the inlet of the appliance as practical. The sediment trap shall be either; a tee fitting, having a capped nipple, of any length, installed vertically in the bottommost opening of the tee, or other device approved as an effective sediment trap. This project would provide for all labor and materials to have sediment traps installed near two gas heaters. | PARK RANGER RESIDENCE | 9943 | CNR | Parks |  | Spring Valley | 1941 | 2280 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
2196EXT1 | REBUILD STRUCTURE | 2196 | The structure is over 30 years old and houses brand new equipment including the well pump and expansion tanks. There is no solid floor and the walls and roof are damaged and severely deteriorated. There is evidence of water damage on the interior walls indicating a failed building envelope. As such, the equipment is basically exposed to the elements and will deteriorate prematurely. This project would provide for demolishing the existing structure and rebuilding a new one around the equipment. The new structure will have a poured concrete foundation, wood framing and an asphalt composition roof. Design fees are not included in this estimate. | NURSERY PUMP HOUSE | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 | 48 | 2016-05-10 | Immediate to Two Years | Currently Critical | 1 | 10000
2701EXT1 | ROOF REPLACEMENT | 2701 | The Custom Shade Cloth roof on the Nursery Shade Structure was in poor condition at the time of the survey. It is recommended that the Nursery Shade Structure be re-roofed in the next 4-5 years with a new Custom Shade Cloth. This estimate includes removal and disposal of the old Custom Shade Cloth roofing. | NURSERY SHADE STRUCTURE | 9966 | CNR | Forestry |  | Floyd Lamb | 2006 | 20000 | 2016-05-10 | Four to Ten Years | Long-Term Needs | 3 | 30000
2195EXT1 | PANEL REPLACEMENT | 2195 | The corrugated fiberglass panels covering the building are original to the building and should be scheduled for replacement. Many of the panels are damaged from general wear and tear and have needed maintenance often. This project would provide for removal and disposal of the existing panels and replacement with polycarbonate panels. The estimate is based on 1,200 linear feet of 4'-0" wide panels at $17 per linear foot. This project or a portion thereof was previously recommended in the FCA reports dated 01/30/2002 and 05/12/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/10/2016. | NURSERY GREENHOUSE #3 | 9966 | CNR | Forestry |  | Floyd Lamb | 1983 | 2480 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20400
2195HVA1 | HVAC EQUIPMENT REPLACEMENT | 2195 | The greenhouse is currently cooled via a modified evaporative cooling system and is heated by a propane heater. These units are not energy efficient and have reached the end of their expected and useful life. This project recommends replacing the equipment in the next 2-3 years. The estimate includes removal and disposal of the existing HVAC units and all required connections to utilities. This project or a portion thereof was previously recommended in the FCA reports dated 01/30/2002 and 05/12/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/10/2016. | NURSERY GREENHOUSE #3 | 9966 | CNR | Forestry |  | Floyd Lamb | 1983 | 2480 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
3046ENR1 | WINDOW REPLACEMENT | 3046 | The windows are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 7 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 05/12/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/10/2016. | NURSERY RESIDENCE (VACANT) | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 | 1600 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10500
3046ENV1 | PEST CONTROL | 3046 | There are numerous rodent droppings throughout this building and a dead rabbit is located at the crawl space entrance. Due to the potential risk of disease, this project would provide for the treatment and cleanup of all rodent droppings, removal of the dead rabbit, and sealing the home so no other animals can crawl under the house. This work should be conducted by a licensed pest control business. | NURSERY RESIDENCE (VACANT) | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 | 1600 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
3046PLM1 | WATER HEATER REPLACEMENT | 3046 | There is a 40 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | NURSERY RESIDENCE (VACANT) | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 | 1600 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
3753EXT4 | SITE DRAINAGE UPGRADES | 3753 | The grade does not slope away effectively from the building. Water has pooled against the foundation and over time, this can cause damage to the foundation and siding. It is recommended per IBC 1804.3 Site Grading the ground immediately adjacent to the foundation shall be sloped away from the building at a slope of not less than one vertical in 20 units horizontal (5-percent slope) for a minimum distance of 10 feet (3048 mm) measured perpendicular to the face of the wall. This project would create a 5% slope away from the building. Additional drainage swales should be installed, as needed. | NURSERY RESIDENCE SHED | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 | 196 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
3046EXT2 | EXTERIOR DOOR REPLACEMENT | 3046 | The two exterior wood doors appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement of the doors with new wood doors, storm doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 05/12/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/10/2016. | NURSERY RESIDENCE (VACANT) | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 | 1600 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
3046HVA1 | HVAC EQUIPMENT REPLACEMENT | 3046 | The HVAC system is original to the building and should be scheduled for replacement. It is not energy efficient and has reached the end of its expected and useful life. The R-22 refrigerant in the cooling system is no longer EPA compliant and its production is mandated to be phased out completely by January 1, 2020. This project would provide for installation of a new HVAC system and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC system and all required connections to utilities. | NURSERY RESIDENCE (VACANT) | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 | 1600 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
3046INT4 | FLOORING REPLACEMENT | 3046 | The plywood subfloor under the furnace and water heater is damaged and reaching the end of its useful life. This project would provide for a licensed contractor to evaluate the floor joists, and determine if they are structurally sound. The costs will cover repair or replacement (if necessary) and the installation of new plywood. Removal and disposal of materials has been included in the estimate. | NURSERY RESIDENCE (VACANT) | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 | 1600 | 2016-05-10 | Immediate to Two Years | Currently Critical | 1 | 10000
3046EXT1 | EXTERIOR FINISHES | 3046 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the masonry, painting the wood siding and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/12/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/10/2016. | NURSERY RESIDENCE (VACANT) | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 | 1600 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16000
3046ELE1 | GFCI OUTLETS | 3046 | The existing receptacles in the kitchen, bathroom and on the outside of the structure, are standard duplex receptacles. The 2011 National Electrical Code (NEC) 210.8 requires these locations to have Ground Fault Circuit Interrupters (GFCI) for protection. This project would provide for removing the standard receptacles and installing GFCI receptacles. | NURSERY RESIDENCE (VACANT) | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 | 1600 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1600
3046SFT2 | SMOKE ALARM INSTALLATION | 3046 | International Residential Code (IRC) 2012 Section R314 and R315.3 explains the requirements for smoke alarms in dwelling units. This includes: installing and maintaining smoke alarms in each sleeping room; having a carbon monoxide and smoke detector on the ceiling or wall outside of each sleeping area and in the immediate vicinity of bedrooms when an alteration, repair or addition requiring a permit occurs. IRC 2012, requires that smoke detectors and carbon monoxide alarms be UL rated. State Fire Marshal NAC 477.915 (3) requires that smoke detectors be connected to the wiring in a building and include a battery for emergency backup power. This project would provide funding for the purchase and installation of smoke alarms and carbon monoxide alarms in accordance with IRC and NAC laws. | NURSERY RESIDENCE (VACANT) | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 | 1600 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
3753EXT2 | ROOF REPLACEMENT | 3753 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next year with a new 50 year asphalt composition roofing shingle and new underlayment. This estimate includes removal and disposal of the old roofing. | NURSERY RESIDENCE SHED | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 | 196 | 2016-05-10 | Immediate to Two Years | Currently Critical | 1 | 2352
3753ELE1 | WIRING CLEANUP | 3753 | The wiring in the residence shed is disorganized and not in proper electrical boxes. This creates a safety issue when conducting repairs or upgrades. This project would provide for cleanup and labeling of the wiring. | NURSERY RESIDENCE SHED | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 | 196 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
3753EXT3 | REPAIR/ REPLACE FASCIA AND SOFFITS | 3753 | The fascia and the soffits surrounding the building are weather beaten, peeling, and are showing signs of considerable wear. This project would provide funding to repair and/or replace the fascia and soffits. Repairs include: replacing sections or entirely where needed, sanding, scraping, priming and paint. This project should coincide with the Roof Replacement project. | NURSERY RESIDENCE SHED | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 | 196 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4900
3753EXT1 | EXTERIOR FINISHES | 3753 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NURSERY RESIDENCE SHED | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 | 196 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1960
9966SIT1 | SITE BOLLARDS | 9966 | There is an above ground propane tank on the site that does not have bollards in place for protection. Per International Fire Code 2012 Section 312 Vehicle Impact Protection, there needs to be steel posts installed, not less than 4 inches in diameter and filled with concrete around the propane tank. The spacing shall not be more than 4 feet between posts on center and located not less than 3 feet from the propane tank. This project would provide funding for eight new bollards to be located around the propane tank. | LAS VEGAS STATE TREE NURSERY SITE | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 |  | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
9966PLM1 | BACKFLOW PREVENTION | 9966 | State Health Law (NAC 445A.67185) and the Uniform Plumbing Code (UPC Section 603) require backflow prevention on water service connections. This is to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of back siphonage or backpressure. This project allows for the installation of double check valves or reduced pressure principle backflow preventers as appropriate to the hazard and in appropriate locations near the potential source of contamination. Costs also include an above ground vault, and allowance for 200 feet of 1" conduit to provide power for freeze protection. This project or a portion thereof was previously recommended in the FCA report dated 05/12/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/10/2016. | LAS VEGAS STATE TREE NURSERY SITE | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 |  | 2016-05-10 | Immediate to Two Years | Currently Critical | 1 | 35000
3046INT2 | INTERIOR FINISHES | 3046 | It is recommended to paint the interior walls and ceilings at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | NURSERY RESIDENCE (VACANT) | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 | 1600 | 2016-05-10 | Four to Ten Years | Long-Term Needs | 3 | 16000
3045PLM1 | FERTILIZER INJECTOR REPLACEMENT | 3045 | The building has fertilizer injectors on the domestic water system. The fertilizer injectors have built-up water calcium deposits, are problematic and intermittently work. This project recommends the removal and disposal of the current fertilizer injectors and the installation of new fertilizer injectors and provides for all necessary connections to the existing utilities. | NURSERY FERTILIZATION SHED | 9966 | CNR | Forestry |  | Floyd Lamb | 1981 | 40 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
3045EXT2 | ROOF REPLACEMENT | 3045 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 4-5 years with a new 50 year asphalt composition roofing shingle and new underlayment. This estimate includes removal and disposal of the old roofing. | NURSERY FERTILIZATION SHED | 9966 | CNR | Forestry |  | Floyd Lamb | 1981 | 40 | 2016-05-10 | Four to Ten Years | Long-Term Needs | 3 | 600
3045ENR1 | LIGHTING UPGRADE | 3045 | The interior light in the building has an old light fixture and is not energy efficient. This project would provide for the replacement of the interior light fixture and bulb with a new light fixture and LED bulb. An occupancy sensor will be installed for additional savings. Electrical wiring upgrades have not been included in this estimate. | NURSERY FERTILIZATION SHED | 9966 | CNR | Forestry |  | Floyd Lamb | 1981 | 40 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 350
3044HVA1 | EVAPORATIVE COOLER REPLACEMENT | 3044 | A wet wall evaporative cooler system is installed on the side of this building. It is severely scaled and the damper and motor are not functioning properly. The system has reached the end of its useful and expected life. This project would provide for a new wet wall evaporative cooler system to be installed, and includes all required connections to utilities. The estimate includes removal and disposal of the old cooler. | NURSERY GREENHOUSE #4 | 9966 | CNR | Forestry |  | Floyd Lamb | 2006 | 2480 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
9966ADA3 | ADA ACCESSIBLE PATH OF TRAVEL | 9966 | The ADA provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the office are necessary to comply with ADA accessibility requirements. This project would provide for a new concrete van accessible ADA parking and loading space and concrete walkway to the existing sidewalk. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. 750 square feet of concrete was used for this estimate. | LAS VEGAS STATE TREE NURSERY SITE | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 |  | 2016-05-10 | Immediate to Two Years | Currently Critical | 1 | 30000
3045EXT1 | EXTERIOR FINISHES | 3045 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/12/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/10/2016. | NURSERY FERTILIZATION SHED | 9966 | CNR | Forestry |  | Floyd Lamb | 1981 | 40 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 400
3046INT3 | INTERIOR REMODEL | 3046 | The interior fixtures and finishes are in general disrepair and the building is due for a complete remodel. This project would provide for removal and replacement of the flooring, doors and frames, cabinetry, trim and baseboards and any other interior finishes and fixtures in need of replacement at the time. | NURSERY RESIDENCE (VACANT) | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 | 1600 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 80000
9966ADA4 | ADA SIDEWALK REPLACEMENT | 9966 | The concrete sidewalks around the site are in need of replacement. The sidewalks have cracks and are spalling. This project would provide for the removal and replacement of the concrete sidewalks. 4,000 SF of 4" thick concrete was used for this estimate. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | LAS VEGAS STATE TREE NURSERY SITE | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 |  | 2016-05-10 | Immediate to Two Years | Currently Critical | 1 | 60000
0283EXT6 | ROOF REPLACEMENT | 0283 | The corrugated metal roof on this building is in poor condition. It is over 40 years old and signs of leaking were observed at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a standing seam metal roofing system. This estimate includes removal and disposal of the old roofing. | NURSERY OFFICE | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 | 2250 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 33750
0283EXT2 | EXTERIOR DOOR REPLACEMENT | 0283 | The three exterior metal doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the existing doors, frames and hardware with new metal doors, frames and hardware. Removal and disposal of the existing doors is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 05/12/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/10/2016. | NURSERY OFFICE | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 | 2250 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
0283HVA3 | HVAC UPGRADE | 0283 | There is not a central HVAC system in the building. The office areas are cooled by window mounted AC units and have no heat. These units are problematic and require frequent replacement. The lack of heat has resulted in frozen pipes and drainage problems. There is a ceiling mounted heater in the garage that is not operational. This project would provide for the purchase and installation of a packaged HVAC unit, ducting and associated controls for the office areas and a ceiling mounted heater and evaporative cooler for the Shop Area. This project includes removal and disposal of the existing units and all required connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 01/30/2002 and 05/12/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/10/2016. | NURSERY OFFICE | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 | 2250 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 56250
0283SIT1 | SITE DRAINAGE UPGRADES | 0283 | The grade does not slope away effectively from the building. Water has pooled against the foundation and over time, this can cause damage to the foundation and siding. It is recommended per IBC 1804.3 Site Grading the ground immediately adjacent to the foundation shall be sloped away from the building at a slope of not less than one vertical in 20 units horizontal (5-percent slope) for a minimum distance of 10 feet (3048 mm) measured perpendicular to the face of the wall. This project would create a 5% slope away from the building. Additional drainage swales should be installed, as needed. It is recommended that the grading be completed within 2-3 years. | NURSERY OFFICE | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 | 2250 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
0283EXT7 | GUTTER REPLACEMENT | 0283 | The existing rain gutters and down spouts on the Nursery Office have numerous joints that have multiple leaks. The leaks have been repaired multiple times, but continue to leak. The leaking rain gutters and down spouts will cause premature deterioration to the building finishes and the site hardscape. This project would replace the existing segmented rain gutters and down spouts with seamless rain gutters and new down spouts. | NURSERY OFFICE | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 | 2250 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6500
0283SFT3 | FIRE ALARM SYSTEM INSTALLATION | 0283 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2012 Section 7 and the 2012 International Fire Code. This project or a portion thereof was previously recommended in the FCA report dated 05/12/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/10/2016. | NURSERY OFFICE | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 | 2250 | 2016-05-10 | Immediate to Two Years | Currently Critical | 1 | 18000
0283SFT2 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0283 | The Nursery Office does not have a fire sprinkler system. The building is a B occupancy per the 2012 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. This project or a portion thereof was previously recommended in the FCA report dated 05/12/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/10/2016. | NURSERY OFFICE | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 | 2250 | 2016-05-10 | Immediate to Two Years | Currently Critical | 1 | 31500
0283ADA2 | ADA UPGRADES | 0283 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. There are several areas pertaining to building access and restrooms that need to be altered to ensure that the facility is compliant. ADA regulations pertaining to building access, route of travel and restrooms has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms and sign contrast and finish. This project would provide funding for the purchase and installation of ADA signage, including directional signage from the parking to the accessible building entrances, route of travel inside the building and restrooms. Section 4.13.9 of the Americans with Disabilities Act Accessible Guidelines (ADAAG) states that handles, pulls, latches, locks and other operating devices on accessible doors shall have a shape that is easy to grasp with one hand and does not require tight grasping, tight pinching, or twisting of the wrist to operate. Lever-operated mechanisms, push-type mechanisms, and U-shaped handles are acceptable designs. It is recommended that proper lever hardware be installed on the entry door and ADA restroom door to meet these requirements. This building contains a counter which does not meet current code. Section 7.2 of the Americans with Disabilities Act Accessible Guidelines (ADAAG) states the counter must have a portion which is at least 36" in length with a maximum height of 36" above the finish floor. This project will provide an accessible counter space in accordance with this requirement. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2009 were referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 05/12/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/10/2016. | NURSERY OFFICE | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 | 2250 | 2016-05-10 | Immediate to Two Years | Currently Critical | 1 | 15000
0283PLM2 | PLUMBING REPLACEMENT | 0283 | The plumbing and waste system is older and in poor condition. There is a floor drain in the Work Room that is backed up and is no longer functional. Most of the system is original to the building and should be scheduled for replacement. This project recommends replacing all of the water and sewer lines in the building to a point 5 feet outside of the building. This estimate includes removal and disposal of the existing system as required. This project or a portion thereof was previously recommended in the FCA report dated 05/12/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/10/2016. | NURSERY OFFICE | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 | 2250 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 56250
0283EXT3 | OVERHEAD DOOR REPLACEMENT | 0283 | There are two 10'x12' overhead coiling doors which are damaged and do not function properly. Exposure and wind have caused the doors to bend, crack and lose their finish. They are original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead coiling doors and replacement with new manually operated overhead coiling doors. This project or a portion thereof was previously recommended in the FCA report dated 01/30/2002 and 05/12/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/10/2016. | NURSERY OFFICE | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 | 2250 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14000
0283EXT5 | CONCRETE APRON REPLACEMENT | 0283 | Outside of the Shop Area, the exterior concrete apron has extensive cracking and is due for replacement. This project would provide for the installation of a new 120 square foot 4" thick concrete slab-on-grade apron. Removal and disposal of the existing concrete is included in this estimate. | NURSERY OFFICE | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 | 2250 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1200
0283INT2 | FLOORING REPLACEMENT | 0283 | The Vinyl Composite Tile (VCT) in the building is damaged and reaching the end of its useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" cove base in the next 2-3 years. This project or a portion thereof was previously recommended in the FCA report dated 01/30/2002 and 05/12/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/10/2016. | NURSERY OFFICE | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 | 2250 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18000
0283PLM1 | WATER HEATER REPLACEMENT | 0283 | There is a 40 gallon electric water heater in the building. The average lifespan of a water heater is eight to ten years. This unit was installed in 2004. It is recommended that a new water heater, seismic straps, braided steel hose, expansion tank, ball valves, new flex gas line and pan be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 05/12/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/10/2016. | NURSERY OFFICE | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 | 2250 | 2016-05-10 | Immediate to Two Years | Currently Critical | 1 | 1500
0283EXT1 | EXTERIOR FINISHES | 0283 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming, painting the metal panels and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended to paint the building in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/12/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/10/2016. | NURSERY OFFICE | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 | 2250 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 22500
0283INT3 | INTERIOR FINISHES | 0283 | It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project does not cover the garage in the rear of the building, it will be addressed in the Shop Area Remodel project. This project or a portion thereof was previously recommended in the FCA report dated 05/12/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/10/2016. | NURSERY OFFICE | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 | 2250 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14400
0283ADA3 | BREAK ROOM REMODEL | 0283 | The kitchenette and associated cabinets in the employee break room are original to the building. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and countertops are delaminating and failing. This project recommends the replacement of the existing kitchen countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish to cover the door, frame and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards for Accessible Design should be incorporated into the design such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. | NURSERY OFFICE | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 | 2250 | 2016-05-10 | Immediate to Two Years | Currently Critical | 1 | 15000
0283ENR2 | WINDOW REPLACEMENT | 0283 | The windows are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 8 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 05/12/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/10/2016. | NURSERY OFFICE | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 | 2250 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
0283EXT4 | TRIM OR REMOVE TREES | 0283 | The building has several trees which are growing up against the structure. The trees move in windy conditions and rub the roof, which can cause premature failure of the roof system and void roof warranties. The root systems are causing shifting and heaving of sidewalks, creating unsafe conditions. There are also several large trees in need of trimming. Lack of maintenance can become a safety issue. This project recommends that these issues be addressed before additional damage is done. | NURSERY OFFICE | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 | 2250 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0283INT4 | SHOP AREA REMODEL | 0283 | The Shop Area at the rear of the building has gypsum board covering the walls. This is not an appropriate wall covering for the garage because it does not hold up to the heavy water usage. Buckets, hand tools and plant containers are washed here daily and water makes contact with the walls. The existing gypsum board is severely damaged and in some places has been removed and covered with plywood. This project would remove and dispose of the gypsum board and replace it with a type X gypsum board and FRP. The damaged ceiling gypsum board is also included in this project. It is recommended that the roof leaks be repaired prior to implementing this project. This project or a portion thereof was previously recommended in the FCA report dated 05/12/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/10/2016. | NURSERY OFFICE | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 | 2250 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12150
0637ELE1 | WIRING CLEANUP | 0637 | The wiring is disorganized and not in proper electrical boxes. This creates a safety issue when making repairs or upgrades and is not up to National Electrical Code (NEC) 2011. This project would provide for cleanup and labeling of the wiring. | NURSERY SHOP/ STORAGE #1 | 9966 | CNR | Forestry |  | Floyd Lamb | 1985 | 1440 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
0637SFT1 | EXTERIOR LANDING INSTALLATION | 0637 | Section 1008.1 of the 2012 International Building Code (IBC) describes the requirements for doors including floor elevations and landings. The floor or landing shall be at the same elevation on each side of the door, the exterior landing shall not exceed a 2-percent slope and shall have a length measured in the direction of travel of not less than 44 inches. The landing at the door on the building does not comply with code and poses a safety hazard. This project would provide for the installation of a compliant landing for the door. | NURSERY SHOP/ STORAGE #1 | 9966 | CNR | Forestry |  | Floyd Lamb | 1985 | 1440 | 2016-05-10 | Immediate to Two Years | Currently Critical | 1 | 2500
0637ENR1 | INSULATE BUILDING | 0637 | The building is not insulated and is not energy efficient. Due to this, the building has extreme temperature fluctuations and is not a comfortable work environment. This project will install (R19) batt insulation in the walls and (R38) batt insulation in the ceiling with an impermeable vinyl surface to help moderate temperature fluctuations. It is recommended that this project coincide with the HVAC Installation project. | NURSERY SHOP/ STORAGE #1 | 9966 | CNR | Forestry |  | Floyd Lamb | 1985 | 1440 | 2016-05-10 | Four to Ten Years | Long-Term Needs | 3 | 21600
0637EXT3 | ROOF REPLACEMENT | 0637 | The corrugated metal roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 4-5 years with a standing seam metal roofing system. This estimate includes removal and disposal of the old roofing. | NURSERY SHOP/ STORAGE #1 | 9966 | CNR | Forestry |  | Floyd Lamb | 1985 | 1440 | 2016-05-10 | Four to Ten Years | Long-Term Needs | 3 | 21600
0637EXT1 | EXTERIOR FINISHES | 0637 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming, painting the metal panels and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended to paint the building in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/12/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/10/2016. | NURSERY SHOP/ STORAGE #1 | 9966 | CNR | Forestry |  | Floyd Lamb | 1985 | 1440 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14400
0637EXT4 | SITE DRAINAGE UPGRADES | 0637 | The grade does not slope away effectively from the building. Water has pooled against the foundation and over time, this can cause damage to the foundation and siding. It is recommended per IBC 1804.3 Site Grading the ground immediately adjacent to the foundation shall be sloped away from the building at a slope of not less than one vertical in 20 units horizontal (5-percent slope) for a minimum distance of 10 feet (3048 mm) measured perpendicular to the face of the wall. This project would create a 5% slope away from the building. Additional drainage swales should be installed, as needed. It is recommended that the grading be completed within 2-3 years. | NURSERY SHOP/ STORAGE #1 | 9966 | CNR | Forestry |  | Floyd Lamb | 1985 | 1440 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
0637SIT1 | CONCRETE APRON INSTALLATION | 0637 | The vehicle garage door does not have a concrete apron in front of it. There are some pavers in place, but these will not last very long with the large vehicles and tractors that drive over them daily. This project would provide for the installation of a 10'x20', 4" thick concrete slab-on-grade apron at the vehicle garage door. This project or a portion thereof was previously recommended in the FCA report dated 05/12/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/10/2016. | NURSERY SHOP/ STORAGE #1 | 9966 | CNR | Forestry |  | Floyd Lamb | 1985 | 1440 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
0637EXT2 | OVERHEAD DOOR REPLACEMENT | 0637 | There is an 8'x8' manually operated overhead coiling door on the building which is damaged and does not function properly. It is original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead coiling door and the replacement with a new manually operated overhead coiling door. This project or a portion thereof was previously recommended in the FCA report dated 05/12/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/10/2016. | NURSERY SHOP/ STORAGE #1 | 9966 | CNR | Forestry |  | Floyd Lamb | 1985 | 1440 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7000
0638EXT3 | ROOF REPLACEMENT | 0638 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayment. This estimate includes the removal and disposal of the old roofing. | NURSERY STORAGE #2 | 9966 | CNR | Forestry |  | Floyd Lamb | 1980 | 875 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 13125
0638EXT1 | EXTERIOR FINISHES | 0638 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units, staining the wood siding and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/12/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/10/2016. | NURSERY STORAGE #2 | 9966 | CNR | Forestry |  | Floyd Lamb | 1980 | 875 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8750
0638INT2 | WINDOW REPLACEMENT | 0638 | The windows are original, single pane construction in metal frames. These older windows are drafty and damaged. This project recommends replacing the windows with new dual pane, vinyl framed units. This estimate is for the replacement of 3 units. Removal and disposal of the existing windows is included in this estimate. | NURSERY STORAGE #2 | 9966 | CNR | Forestry |  | Floyd Lamb | 1980 | 875 | 2016-05-10 | Four to Ten Years | Long-Term Needs | 3 | 4500
0638EXT2 | OVERHEAD DOOR INSTALLATION | 0638 | The building has an exterior opening large enough for vehicles to enter through. Since the seed refrigerator is housed here, vehicles come in and out often and are also stored here. It is recommended to install an overhead door at the opening to protect the vehicles and other equipment inside. This project would provide for the purchase and installation of the door including the door frame and hardware. This project or a portion thereof was previously recommended in the FCA report dated 05/12/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/10/2016. | NURSERY STORAGE #2 | 9966 | CNR | Forestry |  | Floyd Lamb | 1980 | 875 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7000
0638ENR1 | LIGHTING UPGRADE | 0638 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project would upgrade the lighting fixtures to the higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested and the addition of new tombstones, if needed. Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | NURSERY STORAGE #2 | 9966 | CNR | Forestry |  | Floyd Lamb | 1980 | 875 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7000
0616EXT2 | ROOF REPLACEMENT | 0616 | The Custom Shade Cloth roof on the Nursery Lath House was in poor condition at the time of the survey. It is recommended that the Nursery Lath House be re-roofed in the next 3-4 years with a new Custom Shade Cloth. This estimate includes removal and disposal of the old Custom Shade Cloth roofing. | NURSERY LATH HOUSE | 9966 | CNR | Forestry |  | Floyd Lamb | 2008 | 15000 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 22500
0637HVA1 | HVAC INSTALLATION | 0637 | The building does not have a central cooling or heating system and is uncomfortably warm in the summer and cold in the winter. It is recommended to install an evaporative cooler and propane fired heater in the building to ensure a comfortable work environment. This project would provide for the purchase and installation of new equipment, including all required connections to existing utilities. It is recommended that this project coincide with the Insulate Building project. This project or a portion thereof was previously recommended in the FCA report dated 05/12/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/10/2016. | NURSERY SHOP/ STORAGE #1 | 9966 | CNR | Forestry |  | Floyd Lamb | 1985 | 1440 | 2016-05-10 | Four to Ten Years | Long-Term Needs | 3 | 10000
1620SIT1 | PROVIDE CLEARANCE AT ELECTRICAL PANELS | 1620 | There are electrical panels in the building which do not have proper clear floor space around them. The 2012 IFC Section 605.3 states a working space of not less than 30 inches in width, 36 inches in depth and 78 inches in height shall be provided in front of electrical service equipment. Where the electrical service equipment is wider than 30 inches, the working space shall not be less than the width of the equipment. No storage of any materials shall be located within the designated working space. This project would provide funds to relocate the chair, shelf and other items currently blocking the working space. | NDF ADMINISTRATION BUILDING | 9975 | CNR | Forestry |  | Tonopah | 1990 | 2452 | 2016-06-07 | Immediate to Two Years | Currently Critical | 1 | 250
1620ENR1 | LIGHTING UPGRADE | 1620 | The existing lighting fixtures are the older fluorescent type and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/11/2000 and 07/12/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2016. | NDF ADMINISTRATION BUILDING | 9975 | CNR | Forestry |  | Tonopah | 1990 | 2452 | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19616
1620ADA2 | ADA SIGNAGE | 1620 | ADA regulations pertaining to building access has established building signage criteria for permanent spaces for buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with these criteria. This project would provide for accessible signage which is required under ADA. All signage shall conform to ICC/ANSI A117.1-2009 Chapter 7 requirements. This project or a portion thereof was previously recommended in the FCA report dated 09/11/2000 and 07/12/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2016. | NDF ADMINISTRATION BUILDING | 9975 | CNR | Forestry |  | Tonopah | 1990 | 2452 | 2016-06-07 | Immediate to Two Years | Currently Critical | 1 | 3000
1620EXT3 | OVERHEAD DOOR REPLACEMENT | 1620 | The existing 8' x 10' metal overhead coiling door does not function properly due to age and abuse and repair parts are difficult to find. This project would provide for the removal and disposal of the existing door and the purchase and installation of a new manually operated overhead coiling door. This project or a portion thereof was previously recommended in the FCA report dated 07/12/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2016. | NDF ADMINISTRATION BUILDING | 9975 | CNR | Forestry |  | Tonopah | 1990 | 2452 | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
1620ADA5 | ADA SHOWER UPGRADE | 1620 | This project would provide for an ADA compliant stainless steel shower cabinet to be installed to provide shower facilities for the disabled. Included in this estimate is the installation of a stainless steel ADA compliant shower cabinet unit complete with accessible plumbing fixtures, seat, etc. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | NDF ADMINISTRATION BUILDING | 9975 | CNR | Forestry |  | Tonopah | 1990 | 2452 | 2016-06-07 | Immediate to Two Years | Currently Critical | 1 | 25000
1620HVA1 | HVAC EQUIPMENT REPLACEMENT | 1620 | The HVAC split system was installed in 1990. It is not energy efficient and has reached the end of its expected and useful life. This project would provide for the installation of a new HVAC split system and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing equipment and all required connections to utilities. | NDF ADMINISTRATION BUILDING | 9975 | CNR | Forestry |  | Tonopah | 1990 | 2452 | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
1620SFT3 | FIRE RATED CEILING REPAIRS | 1620 | The fire rated ceiling in the equipment closet is damaged and should be scheduled for immediate repair. A square hole has been cut in the one hour fire rated assembly which compromises the fire protection design of the building. This project would provide for repair of the gypsum board ceiling with a 5/8" type X fire rated gypsum board to include tape, mud, texture and paint. | NDF ADMINISTRATION BUILDING | 9975 | CNR | Forestry |  | Tonopah | 1990 | 2452 | 2016-06-07 | Immediate to Two Years | Currently Critical | 1 | 2500
1620ADA3 | ADA DOOR HARDWARE REPLACEMENT | 1620 | The 2010 ADA Standards for Accessible Design states that handles, pulls, latches, locks and other operable parts on doors and gates shall be operable with one hand and shall not require tight grasping, pinching, or twisting of the wrist. The force to activate operable parts shall be 5 pounds maximum. It is recommended that proper lever hardware be installed on all of the interior and exterior doors in this building to meet these requirements. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and Sections 309.4 and 404.2.7 of the 2010 ADA Standards for Accessible Design were used as references for this project. | NDF ADMINISTRATION BUILDING | 9975 | CNR | Forestry |  | Tonopah | 1990 | 2452 | 2016-06-07 | Immediate to Two Years | Currently Critical | 1 | 10000
1620ADA4 | ADA PARKING SPACE | 1620 | The ADA provides for accessibility to sites and services for people with physical limitations. A concrete parking area and passenger loading area are necessary to comply with ADA requirements. This project would provide for a concrete van accessible ADA parking and loading space and walkway to the existing sidewalk. This will require regrading, installing P.C. concrete, striping, signage and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | NDF ADMINISTRATION BUILDING | 9975 | CNR | Forestry |  | Tonopah | 1990 | 2452 | 2016-06-07 | Immediate to Two Years | Currently Critical | 1 | 2500
1620INT3 | JANITORS CLOSET REPAIRS | 1620 | The mop sink in the Janitors Closet is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide fiberglass reinforced plastic (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | NDF ADMINISTRATION BUILDING | 9975 | CNR | Forestry |  | Tonopah | 1990 | 2452 | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
1620EXT7 | EXTERIOR FINISHES | 1620 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting, and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NDF ADMINISTRATION BUILDING | 9975 | CNR | Forestry |  | Tonopah | 1990 | 2452 | 2016-06-07 | Four to Ten Years | Long-Term Needs | 3 | 24520
1620ADA6 | ADA ACCESSIBLE COUNTER | 1620 | ADA provides for accessibility to sites and services for people with physical limitations. The lobby at the entrance of the building has a service counter for the public to approach which does not meet current requirements. Section 904.4 of the ADA Standards for Accessible Design states that a portion of the counter surface that is 36" long minimum and 36" high maximum above the finish floor shall be provided. This project would provide an accessible counter space in accordance with this requirement. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | NDF ADMINISTRATION BUILDING | 9975 | CNR | Forestry |  | Tonopah | 1990 | 2452 | 2016-06-07 | Immediate to Two Years | Currently Critical | 1 | 4000
1620INT5 | FLOORING REPLACEMENT | 1620 | The VCT flooring in the NDF Administration Building is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. | NDF ADMINISTRATION BUILDING | 9975 | CNR | Forestry |  | Tonopah | 1990 | 2452 | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 22068
1620EXT2 | EXTERIOR DOOR REPLACEMENT | 1620 | The existing hollow metal doors and frames are original to the building and are showing signs of age and are damaged. This project would provide for the removal of the existing door assemblies and installation of new metal door assemblies including all required hardware and painting. ADA door hardware is included for the main entrance. This project or a portion thereof was previously recommended in the FCA report dated 07/12/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2016. | NDF ADMINISTRATION BUILDING | 9975 | CNR | Forestry |  | Tonopah | 1990 | 2452 | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
1620INT1 | INTERIOR FINISHES | 1620 | It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and every 5-7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/11/2000 and 07/12/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2016. | NDF ADMINISTRATION BUILDING | 9975 | CNR | Forestry |  | Tonopah | 1990 | 2452 | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24520
1620PLM4 | WATER HEATER REPLACEMENT | 1620 | There is a 30 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 4-5 years. It is recommended that a new on-demand electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | NDF ADMINISTRATION BUILDING | 9975 | CNR | Forestry |  | Tonopah | 1990 | 2452 | 2016-06-07 | Four to Ten Years | Long-Term Needs | 3 | 2500
2493EXT1 | WINDOW REPLACEMENT | 2493 | The building has two dual pane windows. Both windows are broken. This project would provide funding for the purchase and installation of two dual pane windows as well as disposal of the existing windows. This project or a portion thereof was previously recommended in the FCA report dated 09/01/2005 and 07/12/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2016. | NDF INDUSTRY BUILDING | 9975 | CNR | Forestry |  | Tonopah | 2004 | 1296 | 2016-06-07 | Immediate to Two Years | Currently Critical | 1 | 4800
2493INT1 | INTERIOR FINISHES | 2493 | It is recommended that the interior walls be painted at least once in the next 2-3 years and every 5-7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 07/12/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2016. | NDF INDUSTRY BUILDING | 9975 | CNR | Forestry |  | Tonopah | 2004 | 1296 | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12960
2493ENV1 | PROVIDE HAZARDOUS MATERIALS CONTAINMENT | 2493 | This project will provide for the purchase of 4 OSHA approved drum spill pallets capable of storing 4 drums each, and the purchase of 1 OSHA approved storage cabinet for miscellaneous items, such as gas cans, etc. According to OSHA 1910.106 (d), a proper storage container shall be provided for flammable or combustible liquids in drums or other containers (including flammable aerosols) not exceeding 60 gallons individual capacity and those portable tanks not exceeding 660 gallons individual capacity. This project or a portion thereof was previously recommended in the FCA report dated 07/12/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2016. | NDF INDUSTRY BUILDING | 9975 | CNR | Forestry |  | Tonopah | 2004 | 1296 | 2016-06-07 | Immediate to Two Years | Currently Critical | 1 | 25000
2493EXT3 | EXTERIOR FINISHES | 2493 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 2-3 years. It is recommended on a cyclical basis based on environmental conditions. This project or a portion thereof was previously recommended in the FCA report dated 07/12/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2016. | NDF INDUSTRY BUILDING | 9975 | CNR | Forestry |  | Tonopah | 2004 | 1296 | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12960
2493SFT8 | FLUE REPLACEMENT | 2493 | There is a heater flue in the building, which does not comply with UMC 2012 Chapter 8, Chimneys and Vents. The flue was installed with an improper flue and per Section 804 Direct-Vent Terminations, vent terminals for direct-vented appliances shall be installed in accordance with the manufacturer’s installation instructions. The flue is disconnected, and some of the flue is aluminum flex duct and per 803.8 Vent Connector Construction, vent connectors shall be constructed of metal. The minimum thickness of the connector shall be (No. 28 gage) for galvanized steel. Per 801.18.2, flue passageways, the flue liner, chimney inner wall or vent inner wall shall be continuous and shall be free of cracks, gaps, perforations or other damage or deteriorations, which would allow the escape of combustion products, including gases, moisture and creosote. It is recommended that the flue be replaced. Replacements shall meet the manufacture’s specifications and UMC 2012. The flue should be installed by a licensed contractor. This project would provide funds to replace and install 1 new flue to the existing heater. | NDF INDUSTRY BUILDING | 9975 | CNR | Forestry |  | Tonopah | 2004 | 1296 | 2016-06-07 | Immediate to Two Years | Currently Critical | 1 | 2000
24936 | COMPRESSED AIR SYSTEM LEAKS | 2493 | The air compressor is leaking. This is causing the compressor to cycle frequently and is inefficient. This project will provide for repairs, and/or removal of the lines to stop the leaks. | NDF INDUSTRY BUILDING | 9975 | CNR | Forestry |  | Tonopah | 2004 | 1296 | 2016-06-07 | Four to Ten Years | Long-Term Needs | 3 | 500
2493EXT4 | OVERHEAD DOOR REPLACEMENT | 2493 | There is an overhead coiling door which is damaged and does not function properly. It is original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead coiling door and the replacement with a motorized door. | NDF INDUSTRY BUILDING | 9975 | CNR | Forestry |  | Tonopah | 2004 | 1296 | 2016-06-07 | Four to Ten Years | Long-Term Needs | 3 | 8000
2493EXT0 | EXTERIOR DOOR REPLACEMENT | 2493 | The existing exterior doors to the Industry Building are original. They are showing signs of wear and deterioration from constant use and inmate abuse. Due to security concerns and the condition of the door, replacement is recommended. This project would provide for the removal and disposal of the existing doors and frames and replacement with new exterior security doors including door frames, hardware, security glazing, painting and connections to the security system as required. A total of 2 doors were used to generate this estimate. | NDF INDUSTRY BUILDING | 9975 | CNR | Forestry |  | Tonopah | 2004 | 1296 | 2016-06-07 | Four to Ten Years | Long-Term Needs | 3 | 9000
2493SIT1 | REPLACE CONCRETE APRON | 2493 | The NDF Industry Building has a 20' x 50' concrete apron leading up to the overhead doors. The concrete is damaged and should be scheduled for replacement in the next 2-3 years. This project or a portion thereof was previously recommended in the FCA report dated 07/12/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2016. | NDF INDUSTRY BUILDING | 9975 | CNR | Forestry |  | Tonopah | 2004 | 1296 | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
1399EXT3 | OVERHEAD DOOR REPLACEMENT | 1399 | There is a 16'x14' overhead coiling door which is damaged and does not function properly. It is original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead coiling door and replacement with a motorized door. | NDF MAINTENANCE SHOP | 9972 | CNR | Forestry |  | Winnemucca | 1987 | 960 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
1399STR6 | STRUCTURAL REPAIRS | 1399 | A storage area has been constructed in the Maintenance Shop, accessed via stairs. There is no record of a Capital Improvement Project (CIP) for this work or of any structural evaluations having been conducted. This project recommends adding structural members to the existing framing to ensure proper load bearing capacity. This will require a structural design from a licensed engineer, inspections and permitting which are not included in the estimate. | NDF MAINTENANCE SHOP | 9972 | CNR | Forestry |  | Winnemucca | 1987 | 960 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 8000
1399SFT4 | DOOR HARDWARE REPLACEMENT | 1399 | The doors have manually operated flush bolts with a padlock on the outside of each door. International Building Code (IBC) 2012 chapter 10 Means of Egress, section 1008, manually operated flush bolts or surface bolts are not permitted. This project is to install new Schlage grade 1 or approved equal keyed ADA approved dead bolts and levers. | NDF MAINTENANCE SHOP | 9972 | CNR | Forestry |  | Winnemucca | 1987 | 960 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 2000
1399HVA8 | HEATER REPLACEMENT | 1399 | The existing heating system consists of a ceiling mounted propane heater (30,000 - 50,000 BTU) and does not have cooling equipment. The heater is inefficient and should be replaced with a propane fired heater 80% AFUE or higher unit. This project would provide for disposal of the existing unit and replacement with a new propane fired unit including connections to utilities. | NDF MAINTENANCE SHOP | 9972 | CNR | Forestry |  | Winnemucca | 1987 | 960 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3600
1399SFT2 | EMERGENCY EYE WASH STATION | 1399 | The building has outdated containers of eye wash solution. Where the eyes or body of any person may be exposed to injurious corrosive materials, suitable facilities for quick drenching or flushing of the eyes and body shall be provided within the work area for immediate emergency use, Occupational Safety and Health Administration (OSHA) 1910.151(c). This project would provide funding for the purchase and the installation of an emergency eye and body wash station. This project or a portion thereof was previously recommended in the FCA report dated 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | NDF MAINTENANCE SHOP | 9972 | CNR | Forestry |  | Winnemucca | 1987 | 960 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 3500
1399INT1 | INTERIOR FINISHES | 1399 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | NDF MAINTENANCE SHOP | 9972 | CNR | Forestry |  | Winnemucca | 1987 | 960 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9600
1399PLM1 | WATER HEATER REPLACEMENT | 1399 | There is an electric water heater in the building. The average lifespan of a water heater is eight to ten years. This unit was not working at the time of the survey. It is recommended that a new electric water heater, seismic straps, braided steel hoses, expansion tank, ball valve, new flex gas line and pan be installed. Removal and disposal of the existing equipment is included in this estimate. | NDF MAINTENANCE SHOP | 9972 | CNR | Forestry |  | Winnemucca | 1987 | 960 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 2200
1605ADA1 | ADA RESTROOM UPGRADE | 1605 | The building does not have an accessible restroom. The existing restroom does not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom. Items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 International Building Code (IBC), ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. The project should be implemented concurrently with the Shower Installation project. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2000 and 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | NDF ADMINISTRATION OFFICE | 9972 | CNR | Forestry |  | Winnemucca | 1986 | 1800 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 14000
1605EXT1 | EXTERIOR FINISHES | 1605 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking, sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NDF ADMINISTRATION OFFICE | 9972 | CNR | Forestry |  | Winnemucca | 1986 | 1800 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3600
1605SFT4 | EXIT SIGN UPGRADE | 1605 | The existing exit signs in this building are outdated and should be replaced with new self-illuminated or LED style signs with battery-backed internal systems. International Building Code (IBC) 2012 chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2000 and 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | NDF ADMINISTRATION OFFICE | 9972 | CNR | Forestry |  | Winnemucca | 1986 | 1800 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 1800
1605SFT5 | DOOR HARDWARE REPLACEMENT | 1605 | The doors have manually operated flush bolts with a padlock on the outside of each door. International Building Code (IBC) 2012 chapter 10 Means of Egress, section 1008, manually operated flush bolts or surface bolts are not permitted. This project is to install new Schlage grade 1 or approved equal keyed ADA approved dead bolts and levers. | NDF ADMINISTRATION OFFICE | 9972 | CNR | Forestry |  | Winnemucca | 1986 | 1800 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 2000
1605PLM4 | WATER HEATER REPLACEMENT | 1605 | There is a 40 gallon electric water heater in the building that was installed in 2011. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 3-4 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | NDF ADMINISTRATION OFFICE | 9972 | CNR | Forestry |  | Winnemucca | 1986 | 1800 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
1605HVA2 | HEATER REPLACEMENT | 1605 | The garage part of the building is heated by two ceiling mounted propane-fired heating units. They are original to the building and one of the units was not working at the time of the survey. They have both reached the end of their useful life. This project provides for the disposal of the existing units and replacement with two new propane-fired units including connections to utilities. | NDF ADMINISTRATION OFFICE | 9972 | CNR | Forestry |  | Winnemucca | 1986 | 1800 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 4000
1605INT3 | INTERIOR FINISHES | 1605 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and adequately prepared to receive the coating. An epoxy-based paint should be utilized in wet areas for durability. | NDF ADMINISTRATION OFFICE | 9972 | CNR | Forestry |  | Winnemucca | 1986 | 1800 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18000
1605ADA2 | ADA SIGNAGE | 1605 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with these criteria. It is recommended that applicable signage be installed where required. The 2012 International Building Code (IBC), ICC/ANSI A117.1 - 2009, Nevada Revised Statutes (NRS) 338.180 and the most current version of the ADA Standards For Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2000 and 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | NDF ADMINISTRATION OFFICE | 9972 | CNR | Forestry |  | Winnemucca | 1986 | 1800 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 3000
1605ADA4 | ADA UPGRADES | 1605 | Section 4.13.9 of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) states that handles, pulls, latches, locks and other operating devices on accessible doors shall have a shape that is easy to grasp with one hand and does not require tight grasping, tight pinching, or twisting of the wrist to operate. Lever-operated mechanisms, push-type mechanisms, and U-shaped handles are acceptable designs. It is recommended that proper lever hardware be installed in this building to meet these requirements. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2000 and 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | NDF ADMINISTRATION OFFICE | 9972 | CNR | Forestry |  | Winnemucca | 1986 | 1800 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 7000
1605ADA5 | ADA ACCESSIBLE COUNTER | 1605 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The lobby at the entrance of the building has a service counter for the public to approach which does not meet current requirements. Section 904.4 of the ADA Standards For Accessible Design states that a portion of the counter surface that is 36" long minimum and 36" high maximum above the finish floor shall be provided. This project will provide an accessible counter space in accordance with this requirement. The 2012 International Building Code (IBC), ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | NDF ADMINISTRATION OFFICE | 9972 | CNR | Forestry |  | Winnemucca | 1986 | 1800 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 4000
1605SFT0 | FIRE SUPPRESSION SYSTEM INSTALLATION | 1605 | The building is a B occupancy per the 2012 International Building Code (IBC). Pursuant to the Nevada State Fire Marshal Regulation, Nevada Administrative Code (NAC) 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 or R-2 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. This project also includes an allowance for 100 lineal feet of 4" water line, excavation and backfill, all fittings and an above ground backflow prevention device. This project or a portion thereof was previously recommended in the FCA report dated 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | NDF ADMINISTRATION OFFICE | 9972 | CNR | Forestry |  | Winnemucca | 1986 | 1800 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 50000
1399ADA1 | INTERIOR STAIR HANDRAIL REPLACEMENT | 1399 | The stairs and handrails between the first floor and the mezzanine do not meet the requirements in the 2012 International Building Code (IBC) sections 1009 and 1012. This project would provide funding to remove and replace the stairway and handrail and replace with new stairs and handrails. This project or a portion thereof was previously recommended in the FCA report dated 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | NDF MAINTENANCE SHOP | 9972 | CNR | Forestry |  | Winnemucca | 1987 | 960 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 9000
1605ELE1 | LIGHTING UPGRADE | 1605 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2000 and 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | NDF ADMINISTRATION OFFICE | 9972 | CNR | Forestry |  | Winnemucca | 1986 | 1800 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14400
1399SFT3 | OSHA COMPLIANT LADDER | 1399 | The ladder in the mezzanine was constructed in-house and does not comply with OSHA guidelines. This project recommends an Occupational Safety and Health Administration (OSHA) compliant ladder per OSHA 1926.1053 for the interior mezzanine storage area of the building. | NDF MAINTENANCE SHOP | 9972 | CNR | Forestry |  | Winnemucca | 1987 | 960 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 800
1399SFT8 | EXIT SIGN AND EGRESS LIGHTING INSTALLATION | 1399 | The building does not have emergency lighting and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. International Building Code (IBC) 2012 chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | NDF MAINTENANCE SHOP | 9972 | CNR | Forestry |  | Winnemucca | 1987 | 960 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 2400
1399ELE8 | ELECTRICAL OUTLET REPAIR | 1399 | The building has several interior and exterior electrical outlets which are damaged. Some outlets appear to have shorted out or have arced, leaving burn marks on them. Others are missing safety covers. These problems pose the risk of fire and injury. This project would provide for repair and/or replacement of the damaged electrical outlets. | NDF MAINTENANCE SHOP | 9972 | CNR | Forestry |  | Winnemucca | 1987 | 960 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 600
1399ADA7 | ADA RESTROOM UPGRADE | 1399 | The building does not have an accessible restroom. The existing restroom does not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for remodeling the restroom into an ADA compliant restroom. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 International Building Code (IBC), ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | NDF MAINTENANCE SHOP | 9972 | CNR | Forestry |  | Winnemucca | 1987 | 960 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 40000
1399EXT1 | EXTERIOR FINISHES | 1399 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | NDF MAINTENANCE SHOP | 9972 | CNR | Forestry |  | Winnemucca | 1987 | 960 | 2016-07-07 | Four to Ten Years | Long-Term Needs | 3 | 1920
1605INT1 | ADA SHOWER INSTALLATION | 1605 | The Nevada Division of Forestry (NDF) uses large quantities of herbicides, chemicals and also provides fire fighting services. After spraying chemicals, there is no shower for NDF employees to wash off these chemicals and no place to clean up after fighting a fire. This project would provide funding for the installation of an accessible unisex shower. Cost includes plumbing, fiberglass shower stall, exhaust fan, gypsum board, and needed electrical. The final design may impact these costs and are not included in this estimate. This project should coincide with the ADA Restroom Upgrade project. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2000 and 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | NDF ADMINISTRATION OFFICE | 9972 | CNR | Forestry |  | Winnemucca | 1986 | 1800 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 7500
2143EXT1 | EXTERIOR FINISHES | 2143 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting the metal siding and caulking the flashing, fixtures and all other penetrations. It is recommended to paint the building within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HAZARDOUS MATERIAL STORAGE BUILDING | 9972 | CNR | Forestry |  | Winnemucca | 1986 | 96 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 960
2139EXT2 | CONCRETE FOUNDATION | 2139 | The Metal Storage Shed floor is made of plywood and was in poor condition at the time of the survey. This project would provide for the removal of the plywood flooring, metal shed walls, and roofing, and additionally for the installation of a stem wall, 4" thick concrete floor and an apron in front of the building. The Metal Storage Shed walls and roof would need to be anchored to the stem wall per the engineer’s or architect’s design. Additionally, this project would require a plan review and permit from State Public Works Division. | METAL STORAGE SHED | 9972 | CNR | Forestry |  | Winnemucca | 1986 | 192 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19200
2142EXT2 | EXTERIOR FINISHES | 2142 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | FUEL ISLAND BUILDING | 9972 | CNR | Forestry |  | Winnemucca | 1988 | 98 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 980
2143SFT4 | HAZARDOUS MATERIALS STORAGE | 2143 | The Hazardous Material Storage Building contains hazardous materials (i.e. gasoline, herbicides and pesticides). Per International Fire Code (IFC) 2012 Hazardous Materials, and in accordance with National Fire Protection Association (NFPA); where hazardous materials are stored, dispensed or used, section 5003 states the proper use and application is to have mechanical exhaust and ventilation, and hazard identification signs shall be installed. Refer to section 5004 and 5005 for the proper use and setup. It is important to comply with all applicable codes. This project would provide for all requirements in IFC 2012, to include section 105 permits and inspections through the State Fire Marshal’s Office and the State Public Works Division. | HAZARDOUS MATERIAL STORAGE BUILDING | 9972 | CNR | Forestry |  | Winnemucca | 1986 | 96 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 30000
2143HVA1 | EXHAUST FAN INSTALLATION | 2143 | The mechanical room within the housing unit has plumbing fixtures and drains. Due to moisture in this room, the humidity is very high and there is an increase probability for indoor air quality concern. This project would provide for the purchase and installation of a new commercial grade exhaust fan and the assemblies and will include the connections to utilities. | HAZARDOUS MATERIAL STORAGE BUILDING | 9972 | CNR | Forestry |  | Winnemucca | 1986 | 96 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
2138EXT1 | EXTERIOR FINISHES | 2138 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting the metal panels and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended to paint the building in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SAW SHOP | 9972 | CNR | Forestry |  | Winnemucca | 1986 | 480 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4800
2143INT3 | INTERIOR FINISHES | 2143 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 4-5 years and that this project scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. | HAZARDOUS MATERIAL STORAGE BUILDING | 9972 | CNR | Forestry |  | Winnemucca | 1986 | 96 | 2016-07-07 | Four to Ten Years | Long-Term Needs | 3 | 960
2140INT2 | DOOR HARDWARE REPLACEMENT | 2140 | The doors have manually operated flush bolts with a padlock on the outside of each door. International Building Code (IBC) 2012 chapter 10 Means of Egress, section 1008, manually operated flush bolts or surface bolts are not permitted. This project is to install new Schlage grade 1 or approved equal keyed ADA approved dead bolts and levers. | OFFICE TRAILER | 9972 | CNR | Forestry |  | Winnemucca | 1986 | 261 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 2000
2143ENR1 | EXPLOSION PROOF INTERIOR LED LIGHTING | 2143 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient or explosion proof. This project will upgrade fixtures to higher efficiency units with longer life cycles and will be explosion proof. 4' LEDs in class 1 explosion proof fixtures are suggested. Occupancy sensors will be installed for additional savings. Electrical wiring upgrades have not been included in this estimate. | HAZARDOUS MATERIAL STORAGE BUILDING | 9972 | CNR | Forestry |  | Winnemucca | 1986 | 96 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 2000
2140EXT1 | EXTERIOR FINISHES | 2140 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting the metal and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended to paint the building in the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | OFFICE TRAILER | 9972 | CNR | Forestry |  | Winnemucca | 1986 | 261 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 2610
2147ELE1 | GFCI OUTLETS | 2147 | The existing receptacles in the compressor room and outside are standard duplex receptacles. The 2011 National Electrical Code (NEC) 210.8 requires these locations to have Ground Fault Circuit Interrupter (GFCI) protection. This project would provide for removing the standard receptacles and installing GFCI receptacles. This project or a portion there of was previously recommended in the FCA report dated 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | NDF COMPRESSOR BUILDING | 9972 | CNR | Forestry |  | Winnemucca | 1988 | 112 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 800
2147EXT1 | EXTERIOR FINISHES | 2147 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NDF COMPRESSOR BUILDING | 9972 | CNR | Forestry |  | Winnemucca | 1988 | 112 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1120
2138EXT4 | EXTERIOR DOOR REPLACEMENT | 2138 | The 2 exterior wood man doors appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement of the wood doors with new metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | SAW SHOP | 9972 | CNR | Forestry |  | Winnemucca | 1986 | 480 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
2139INT1 | INTERIOR FINISHES | 2139 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | METAL STORAGE SHED | 9972 | CNR | Forestry |  | Winnemucca | 1986 | 192 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1920
2142INT1 | INTERIOR FINISHES | 2142 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | FUEL ISLAND BUILDING | 9972 | CNR | Forestry |  | Winnemucca | 1988 | 98 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 980
2138EXT3 | WOOD SKIRTING REPLACEMENT | 2138 | The skirting on the modular building is made of T1-11 and was in poor condition at the time of the survey. International Building Code (IBC) 2012, section 2304.11.2.6, wood siding clearance between wood siding and earth on the exterior of a building shall not be less than 6 inches (152 mm) or less than 2 inches (51mm) vertical from concrete steps, porch slabs, patio slabs and similar horizontal surfaces exposed to the weather except where siding, sheathing and wall framing are of naturally durable or preservative-treated wood. This project would provide for the removal of the T1-11 skirting and the installation of new vinyl skirting. | SAW SHOP | 9972 | CNR | Forestry |  | Winnemucca | 1986 | 480 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
2141EXT0 | EXTERIOR FINISHES | 2141 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MECHANICAL SHOP | 9972 | CNR | Forestry |  | Winnemucca | 1988 | 960 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9600
2142EXT3 | ROOF REPLACEMENT | 2142 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition shingle roof and new underlayments. This estimate includes removal and disposal of the old asphalt composition shingle roof. | FUEL ISLAND BUILDING | 9972 | CNR | Forestry |  | Winnemucca | 1988 | 98 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1176
2138INT2 | DOOR HARDWARE REPLACEMENT | 2138 | The doors have manually operated flush bolts with a padlock on the outside of each door. International Building Code (IBC) 2012 chapter 10 Means of Egress, section 1008, manually operated flush bolts or surface bolts are not permitted. This project is to install new Schlage grade 1 or approved equal keyed ADA approved dead bolts and levers. | SAW SHOP | 9972 | CNR | Forestry |  | Winnemucca | 1986 | 480 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 2000
2138INT0 | LIGHTING UPGRADE | 2138 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | SAW SHOP | 9972 | CNR | Forestry |  | Winnemucca | 1986 | 480 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2100
2138INT3 | INTERIOR REMODEL | 2138 | The interior fixtures and finishes are in general disrepair and the building is due for a complete remodel. This project would provide for removal and replacement of the flooring, doors and frames, cabinetry, trim and baseboards and any other interior finishes and fixtures in need of replacement. | SAW SHOP | 9972 | CNR | Forestry |  | Winnemucca | 1986 | 480 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24000
2139EXT1 | EXTERIOR FINISHES | 2139 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is caulking and sealing the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | METAL STORAGE SHED | 9972 | CNR | Forestry |  | Winnemucca | 1986 | 192 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 384
2142SFT2 | HAZARDOUS MATERIALS STORAGE | 2142 | The Fuel Island Building contains hazardous materials (i.e. gasoline, herbicides and pesticides). Per International Fire Code (IFC) 2012 Hazardous Materials, and in accordance with National Fire Protection Association (NFPA); where hazardous materials are stored, dispensed or used, section 5003 states the proper use and application is to have mechanical exhaust and ventilation, and hazard identification signs shall be installed. Refer to section 5004 and 5005 for the proper use and setup. It is important to comply with all applicable codes. This project would provide for all requirements in IFC 2012, to include section 105 permits and inspections through the State Fire Marshal’s Office and the State Public Works Division. | FUEL ISLAND BUILDING | 9972 | CNR | Forestry |  | Winnemucca | 1988 | 98 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 30000
2138SIT1 | STAIRWAY REPAIRS | 2138 | The 2012 International Building Code (IBC) section 1009.11 requires handrails to be installed on stairs with two or more risers. There are two stairways that provide access to the saw shop. They do not have any handrails. This project would provide for the repair of the existing stairs and installation of handrails on each side of the stairways. This project or a portion thereof was previously recommended in the FCA report dated 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | SAW SHOP | 9972 | CNR | Forestry |  | Winnemucca | 1986 | 480 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
2142EXT1 | EXTERIOR SIDING REPLACEMENT | 2142 | The wood siding has some areas that are damaged from exposure to the elements and should be replaced. This project would provide for the removal and replacement of damaged siding and trim including caulking and painting to match existing conditions. | FUEL ISLAND BUILDING | 9972 | CNR | Forestry |  | Winnemucca | 1988 | 98 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2450
2138EXT2 | ROOF REPLACEMENT | 2138 | The metal roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a standing seam metal roofing system. This estimate includes removal and disposal of the old roofing. | SAW SHOP | 9972 | CNR | Forestry |  | Winnemucca | 1986 | 480 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5760
2141INT2 | DOOR HARDWARE REPLACEMENT | 2141 | The doors have manually operated flush bolts with a padlock on the outside of each door. International Building Code (IBC) 2012 chapter 10 Means of Egress, section 1008, manually operated flush bolts or surface bolts are not permitted. This project is to install new Schlage grade 1 or approved equal keyed ADA approved dead bolts and levers. | MECHANICAL SHOP | 9972 | CNR | Forestry |  | Winnemucca | 1988 | 960 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 2000
2141INT1 | INTERIOR FINISHES | 2141 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | MECHANICAL SHOP | 9972 | CNR | Forestry |  | Winnemucca | 1988 | 960 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9600
2141SFT1 | SAFETY CABINETS | 2141 | The building contains many different paints, stains, and other hazardous products located on open shelves and on the floor. This does not meet OSHA standards or International Fire Code (IFC) for hazardous materials containment. This project would provide a self-closing hazardous storage container in the building and install placards on the building exterior in accordance with Occupational Safety and Health Administration (OSHA) 1910.106 (d) and IFC chapter 57 section 5704.3.2.1.3. This project or a portion thereof was previously recommended in the FCA report dated 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | MECHANICAL SHOP | 9972 | CNR | Forestry |  | Winnemucca | 1988 | 960 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 10000
2138HVA1 | HEATER REPLACEMENT | 2138 | The existing heating system consists of a wall mounted electric/propane heater and it does not have cooling equipment. The heater is inefficient and should be replaced with a propane fired heater 80% AFUE or higher unit. This project would replace the existing heater. | SAW SHOP | 9972 | CNR | Forestry |  | Winnemucca | 1986 | 480 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7200
2140INT1 | INTERIOR FINISHES | 2140 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and adequately prepared to receive the coating. An epoxy-based paint should be utilized in wet areas for durability. | OFFICE TRAILER | 9972 | CNR | Forestry |  | Winnemucca | 1986 | 261 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2610
2140ENR2 | EXPLOSION PROOF INTERIOR LED LIGHTING | 2140 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient or explosion proof. This project will upgrade fixtures to higher efficiency units with a longer life cycle and will be explosion proof. 4' LEDs with a class 1 explosion proof are suggested. Occupancy sensors will be installed for additional savings. Electrical wiring upgrades have not been included in this estimate. | OFFICE TRAILER | 9972 | CNR | Forestry |  | Winnemucca | 1986 | 261 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 2000
2140SFT3 | HAZARDOUS MATERIALS STORAGE | 2140 | The Hazardous Material Storage Building contains hazardous materials (i.e. gasoline, herbicides and pesticides). Per International Fire Code (IFC) 2012 Hazardous Materials, and in accordance with National Fire Protection Association (NFPA); where hazardous materials are stored, dispensed or used, section 5003 states the proper use and application is to have mechanical exhaust and ventilation, and hazard identification signs shall be installed. Refer to section 5004 and 5005 for the proper use and setup. It is important to comply with all applicable codes. This project would provide for all requirements in IFC 2012, to include section 105 permits and inspections through the State Fire Marshal’s Office and the State Public Works Division. | OFFICE TRAILER | 9972 | CNR | Forestry |  | Winnemucca | 1986 | 261 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 30000
2140EXT3 | WOOD SKIRTING REPLACEMENT | 2140 | The skirting on the modular building is made of T1-11 and was in poor condition at the time of the survey. International Building Code (IBC) 2012, section 2304.11.2.6, wood siding clearance between wood siding and earth on the exterior of a building shall not be less than 6 inches (152 mm) or less than 2 inches (51mm) vertical from concrete steps, porch slabs, patio slabs and similar horizontal surfaces exposed to the weather except where siding, sheathing and wall framing are of naturally durable or preservative-treated wood. This project would provide for the removal of the T1-11 skirting and the installation of new vinyl skirting. | OFFICE TRAILER | 9972 | CNR | Forestry |  | Winnemucca | 1986 | 261 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
2165INT1 | DOOR HARDWARE REPLACEMENT | 2165 | The door has a manually operated flush bolt with a padlock on the outside of each door. Per IBC 2012 Chapter 10 Means of Egress, Section 1008, manually operated flush bolts or surface bolts are not permitted. This project is to install new Schlage grade 1 or approved equal keyed ADA approved lever. | NDF STORAGE SHED #1 | 9974 | CNR | Forestry |  | Wells | 1985 | 160 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 1000
2165EXT1 | EXTERIOR FINISHES | 2165 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | NDF STORAGE SHED #1 | 9974 | CNR | Forestry |  | Wells | 1985 | 160 | 2016-08-24 | Four to Ten Years | Long-Term Needs | 3 | 320
2165EXT2 | CONCRETE FOUNDATION | 2165 | The metal storage shed’s floor and landing is dirt. This project would provide for the removal of the metal shed and would provide for the installation of a stem wall, 4” thick concrete floor and a landing in front of the building. The metal shed would need to be anchored to the stem wall per the engineer’s or architect’s design. Additionally, this project would require a plan review and permit from State Public Works Division. | NDF STORAGE SHED #1 | 9974 | CNR | Forestry |  | Wells | 1985 | 160 | 2016-08-24 | Four to Ten Years | Long-Term Needs | 3 | 16000
0621SFT3 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0621 | This building does not have an automatic fire suppression system. It should be retrofitted with fire sprinklers during the next remodel or addition. This project would provide funding for the installation of fire sprinklers including backflow prevention devices. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | NDF ADMINISTRATION OFFICE | 9974 | CNR | Forestry |  | Wells | 1985 | 1200 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 16800
0622EXT3 | ROOF REPLACEMENT | 0622 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition shingle roof and new underlayment. This estimate includes removal and disposal of the old roof. | NDF GARAGE/ SAW SHOP | 9974 | CNR | Forestry |  | Wells | 1986 | 960 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11520
0622SFT2 | SAFETY CABINETS | 0622 | The building contains many different paints, stains, gas and other hazardous products located on open shelves and on the floor. This does not meet OSHA standards or IFC for hazardous materials containment. This project would provide a self-closing hazardous storage container in the building and install placards on the building exterior in accordance with OSHA 1910.106 (d) and IFC Chapter 57 Section 5704.3.2.1.3. | NDF GARAGE/ SAW SHOP | 9974 | CNR | Forestry |  | Wells | 1986 | 960 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 5000
0621ENR4 | WINDOW REPLACEMENT | 0621 | The windows are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 6 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | NDF ADMINISTRATION OFFICE | 9974 | CNR | Forestry |  | Wells | 1985 | 1200 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
0622SFT1 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0622 | The building does not have emergency lighting and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | NDF GARAGE/ SAW SHOP | 9974 | CNR | Forestry |  | Wells | 1986 | 960 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 4800
0622ENV1 | SPILL CONTAINMENT | 0622 | The shop does not have a method for containing spills or leakage from hazardous materials. According to OSHA 1910.106 (d), a proper storage container shall be provided for flammable or combustible liquids in drums or other containers (including flammable aerosols) not exceeding 60 gallons individual capacity and those portable tanks not exceeding 660 gallons individual capacity. This project would provide proper storage containers and secondary containment pallets as needed and install placards on the building exterior. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | NDF GARAGE/ SAW SHOP | 9974 | CNR | Forestry |  | Wells | 1986 | 960 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 6500
0622EXT4 | CONCRETE APRON REPAIRS | 0622 | The exterior concrete aprons have extensive cracking and are due for replacement. This project would provide for the installation of two new 4" thick concrete slab-on-grade aprons at the vehicle garage doors. Removal and disposal of the existing concrete is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | NDF GARAGE/ SAW SHOP | 9974 | CNR | Forestry |  | Wells | 1986 | 960 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0622EXT2 | OVERHEAD DOOR REPLACEMENT | 0622 | There is a 10'x14' overhead door which is damaged and does not function properly. It is original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead door and replacement with a motorized door. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | NDF GARAGE/ SAW SHOP | 9974 | CNR | Forestry |  | Wells | 1986 | 960 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7000
0622INT1 | INTERIOR FINISHES | 0622 | It is recommended to paint the interior walls and ceilings at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | NDF GARAGE/ SAW SHOP | 9974 | CNR | Forestry |  | Wells | 1986 | 960 | 2016-08-24 | Four to Ten Years | Long-Term Needs | 3 | 9600
0622EXT1 | EXTERIOR FINISHES | 0622 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | NDF GARAGE/ SAW SHOP | 9974 | CNR | Forestry |  | Wells | 1986 | 960 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9600
0622ENR2 | LIGHTING UPGRADE | 0622 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | NDF GARAGE/ SAW SHOP | 9974 | CNR | Forestry |  | Wells | 1986 | 960 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7680
0621SFT4 | WATER HEATER SEISMIC BRACING | 0621 | The water heater is not seismically anchored to the structure. This project would provide funding for seismic bracing of the water heater to the structure. | NDF ADMINISTRATION OFFICE | 9974 | CNR | Forestry |  | Wells | 1985 | 1200 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 500
0621ADA3 | INSTALL LEVER ACTION HARDWARE | 0621 | Section 4.13.9 of the ADAAG states that handles, pulls, latches, locks and other operating devices on accessible doors shall have a shape that is easy to grasp with one hand and does not require tight grasping, tight pinching, or twisting of the wrist to operate. Lever-operated mechanisms, push-type mechanisms, and U-shaped handles are acceptable designs. It is recommended that proper lever hardware be installed in this building to meet these requirements. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | NDF ADMINISTRATION OFFICE | 9974 | CNR | Forestry |  | Wells | 1985 | 1200 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 5000
0621ADA4 | EXTERIOR DOOR REPLACEMENT | 0621 | The exterior entrance door is on an accessible path of travel, but the door hardware and threshold are not compliant. The door and frame are also damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for replacement of the door and frame including ADA compliant door hardware and a compliant threshold. ADA compliant signage is also included in this project. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and ADAAG - 2010 were referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | NDF ADMINISTRATION OFFICE | 9974 | CNR | Forestry |  | Wells | 1985 | 1200 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 6000
0621ADA5 | ADA ACCESSIBLE COUNTER | 0621 | The ADA provides for accessibility to sites and services for people with physical limitations. The lobby at the entrance of the building has a service counter for the public to approach which does not meet current requirements. Section 904.4 of the ADA Standards for Accessible Design states that a portion of the counter surface that is 36" long minimum and 36" high maximum above the finish floor shall be provided. This project will provide an accessible counter space in accordance with this requirement. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | NDF ADMINISTRATION OFFICE | 9974 | CNR | Forestry |  | Wells | 1985 | 1200 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 4000
0621INT3 | VCT FLOORING REPLACEMENT | 0621 | The VCT flooring in the building is worn and damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | NDF ADMINISTRATION OFFICE | 9974 | CNR | Forestry |  | Wells | 1985 | 1200 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
0621ENR2 | HVAC UPGRADE | 0621 | The propane heaters and window mounted air conditioners were installed in 1985. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of a new HVAC system which will result in energy savings and efficiency. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2000 and 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | NDF ADMINISTRATION OFFICE | 9974 | CNR | Forestry |  | Wells | 1985 | 1200 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18000
0621EXT1 | EXTERIOR FINISHES | 0621 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking, sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | NDF ADMINISTRATION OFFICE | 9974 | CNR | Forestry |  | Wells | 1985 | 1200 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2400
0622HVA1 | HEATER REPLACEMENT | 0622 | The existing HVAC system consists of a ceiling mounted propane heater and does not have cooling equipment. The heater is inefficient and should be replaced with a propane fired heater 80% AFUE or higher unit. This project would provide for disposal of the existing unit and replacement with a new propane fired unit including connections to utilities. | NDF GARAGE/ SAW SHOP | 9974 | CNR | Forestry |  | Wells | 1986 | 960 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3600
0621ENR5 | LIGHTING UPGRADE | 0621 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | NDF ADMINISTRATION OFFICE | 9974 | CNR | Forestry |  | Wells | 1985 | 1200 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9600
0621ADA2 | ADA SIGNAGE | 0621 | ADA regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with these criteria. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2000 and 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | NDF ADMINISTRATION OFFICE | 9974 | CNR | Forestry |  | Wells | 1985 | 1200 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 1500
0621SIT1 | IRRIGATION UPGRADE | 0621 | The existing irrigation system for the building was not working at the time of the survey. The irrigation system should be scheduled for repair. This project would provide for the repairs of the existing irrigation lines. | NDF ADMINISTRATION OFFICE | 9974 | CNR | Forestry |  | Wells | 1985 | 1200 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
0621INT1 | INTERIOR FINISHES | 0621 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2000 and 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | NDF ADMINISTRATION OFFICE | 9974 | CNR | Forestry |  | Wells | 1985 | 1200 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
0621ELE1 | WIRING CLEANUP | 0621 | The wiring in the Administration Office is disorganized and not in proper electrical boxes with covers. This creates a safety issue when making repairs or upgrades. This project would provide for cleanup and labeling of the wiring. | NDF ADMINISTRATION OFFICE | 9974 | CNR | Forestry |  | Wells | 1985 | 1200 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 2000
0621ADA1 | ADA RESTROOM REMODEL | 0621 | The building does not have an accessible restroom. The existing restroom does not meet the ADA requirements. A complete retrofit is necessary. This project would provide funding for construction of one unisex accessible restroom. Items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2000 and 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | NDF ADMINISTRATION OFFICE | 9974 | CNR | Forestry |  | Wells | 1985 | 1200 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 15000
0621ADA6 | BREAK ROOM REMODEL | 0621 | The kitchenette and associated cabinets in the employee break room are original to the building. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and countertops are delaminating and failing. This project recommends the replacement of the existing kitchen countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards for Accessible Design should be incorporated into the design such as providing an accessible sink. This estimate includes the removal and the disposal of the existing materials. | NDF ADMINISTRATION OFFICE | 9974 | CNR | Forestry |  | Wells | 1985 | 1200 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 15000
0621EXT2 | GUTTER REPLACEMENT | 0621 | The existing gutter on the Administration Office eave has numerous joints that have proven impossible to seal against leaks. The leaking gutters will cause premature deterioration to the building finishes and the site hardscape. This project would replace the existing segmented gutter with a seamless gutter. | NDF ADMINISTRATION OFFICE | 9974 | CNR | Forestry |  | Wells | 1985 | 1200 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0621ENR3 | REPLACE WATER HEATER | 0621 | There is a 19 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new on-demand electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2000 and 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | NDF ADMINISTRATION OFFICE | 9974 | CNR | Forestry |  | Wells | 1985 | 1200 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0622INT2 | DOOR HARDWARE REPLACEMENT | 0622 | The doors have manually operated flush bolts with a padlock on the outside of each door. Per IBC 2012 Chapter 10 Means of Egress, Section 1008, manually operated flush bolts or surface bolts are not permitted. This project is to install new Schlage grade 1 or approved equal keyed ADA approved dead bolts and levers. | NDF GARAGE/ SAW SHOP | 9974 | CNR | Forestry |  | Wells | 1986 | 960 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 2000
0622ELE1 | WIRING CLEANUP | 0622 | The wiring in the building is disorganized and not in proper electrical boxes and doesn’t have covers on the boxes. This creates a safety issue when making repairs or upgrades. This project would provide for cleanup and labeling of the wiring. | NDF GARAGE/ SAW SHOP | 9974 | CNR | Forestry |  | Wells | 1986 | 960 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
0622ELE2 | ELECTRICAL PANEL UPGRADES | 0622 | The electrical subpanel in the building does not have a cover that properly protects individuals from touching the breakers. This does not comply with NEC 2011 or OSHA 1910. This project would provide funds to fabricate and install a new cover in accordance with NEC 2011 and OSHA 1910. | NDF GARAGE/ SAW SHOP | 9974 | CNR | Forestry |  | Wells | 1986 | 960 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
0622SFT3 | STORAGE REMOVAL | 0622 | Items in this building are stored too close to the ceiling. The 2012 IFC Section 315.3.1 states that, Storage shall be maintained 2 feet or more below the ceiling in nonsprinklered areas of buildings or a minimum of 18 inches below sprinkler head deflectors in sprinklered areas of buildings. This project would provide for the removal of all items in conflict with code requirements to ensure that the fire suppression system operates correctly. | NDF GARAGE/ SAW SHOP | 9974 | CNR | Forestry |  | Wells | 1986 | 960 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 1000
1156ADA1 | ADA TABLE UPGRADE | 1156 | Per the United States Access Board and ICC ANSI-A117.1-2009, at least 5 percent of the seating spaces shall be, if fixed seating is provided, a loose seat or open space for a wheelchair. This project would provide funding to remove 2 of the fixed seats, which will allow access for wheel chairs. | GROUP USE SHELTER | 9930 | CNR | Parks |  | Spring Mountain | 1983 | 2592 | 2016-12-15 | Immediate to Two Years | Currently Critical | 1 | 2000
1159EXT2 | ROOF REPLACEMENT | 1159 | The wood shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new wood shingle roof and new underlayment. This estimate includes removal and disposal of the old roof. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. | CATTLE FEEDER SHED | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 389 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5835
1155SFT3 | FIRE ALARM SYSTEM INSTALLATION | 1155 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2009 Section 7 and the 2018 IFC. | WORK SHOP | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 1962 | 2016-12-15 | Immediate to Two Years | Currently Critical | 1 | 7848
1155EXT3 | GUTTER AND DOWNSPOUT INSTALLATION | 1155 | The building does not have gutters or downspouts to control the runoff from the roof. The water currently sheet drains off the roof causing extensive erosion to the grade around the foundation and contributes to the drainage problems at the rear of the building. This will eventually lead to failure of the foundation undermining the integrity of the entire structure. This project would provide funding for the installation of a seamless gutter and downspout system for the building. This project should coincide with the Drainage Improvements project. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | WORK SHOP | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 1962 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
1155SIT1 | DRAINAGE IMPROVEMENTS | 1155 | The rear of the building has poor drainage in the corner near the office entrance. The grade does not properly slope away from the building causing water to accumulate next to the structure. This project provides for installing a French drain along the entire length of the wall and regrading to ensure a positive slope away from the structure. This project should coincide with the GUTTER and DOWNSPOUT INSTALLATION project. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | WORK SHOP | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 1962 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
1156EXT1 | EXTERIOR FINISHES | 1156 | It is important to maintain the finish, weather resistance and appearance of the structure excluding the roof. This project would provide for cleaning and sealing the wood and the concrete masonry and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | GROUP USE SHELTER | 9930 | CNR | Parks |  | Spring Mountain | 1983 | 2592 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10368
1156ENR1 | EXTERIOR LIGHTING REPLACEMENT | 1156 | The building has perimeter lighting on the exterior of the building, but the light fixtures are old, failing and not energy efficient. This project would provide for the replacement of the exterior lighting fixtures with new LED light fixtures, using existing wiring. | GROUP USE SHELTER | 9930 | CNR | Parks |  | Spring Mountain | 1983 | 2592 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
1157SFT4 | EXTERIOR DOOR LANDING INSTALLATION | 1157 | There are two out-swinging exterior doors on the building, which swing out over a step that does not have a landing. This does not comply with 2018 IBC Section 1008.1, which requires a proper landing and for the landing to not be more than 1/2" below the threshold. This project would provide for the installation of compliant landings. | HAY & HORSE BARN/ CORRAL/ SHOP | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 2112 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
1158EXT1 | EXTERIOR FINISHES | 1158 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | VERA'S STABLES | 9930 | CNR | Parks |  | Spring Mountain | 1930 | 500 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
1158ELE1 | WIRING CLEANUP | 1158 | The wiring in the northwest electrical room is disorganized and not in proper electrical boxes, particularly around the irrigation controls. This creates a safety issue when making repairs or upgrades. This project would provide for cleanup and labeling of the wiring. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. | VERA'S STABLES | 9930 | CNR | Parks |  | Spring Mountain | 1930 | 500 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
1158EXT2 | ROOF REPLACEMENT | 1158 | The building’s roof system has major structural problems and the asphalt composition shingles are due for replacement. The wood shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new wood roofing shingle and new underlayment. This estimate includes removal and disposal of the old roof. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | VERA'S STABLES | 9930 | CNR | Parks |  | Spring Mountain | 1930 | 500 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
1158ENV1 | PEST CONTROL | 1158 | There are numerous rodent droppings throughout this building. Due to the potential risk of disease, this project provides for treatment and cleanup of the rodent droppings by a licensed pest control business. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. | VERA'S STABLES | 9930 | CNR | Parks |  | Spring Mountain | 1930 | 500 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
1157SFT2 | SAFETY CABINETS | 1157 | The shop contains many different paints, stains, pesticides and other hazardous products on open shelves and on the floor. This does not meet OSHA standards for hazardous materials containment. This project would provide two hazardous storage containers in the building and install placards on the building is exterior in accordance with OSHA 1910.106 (d). This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | HAY & HORSE BARN/ CORRAL/ SHOP | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 2112 | 2016-12-15 | Immediate to Two Years | Currently Critical | 1 | 10000
1157ENV1 | DUST COLLECTION SYSTEM INSTALLATION | 1157 | The existing wood working equipment has only partial dust collection capacity. In order to reduce the possibility of damage or injury, each piece of equipment should have full collection capability. This project will provide for the replacement of the existing system and installation of additional capacity to minimize explosion hazard and disruption to production. | HAY & HORSE BARN/ CORRAL/ SHOP | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 2112 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
1156EXT3 | ROOF AND RAFTER REPLACEMENT | 1156 | The rafters are cracked, broken, missing bolts and were in need of replacement at the time of the survey. It is recommended that new rafters, sheathing, underlayment, and a new 50 year asphalt composition roofing system be installed within the next 2-3 years. This estimate includes removal and disposal of the old rafters, sheathing, roofing system and underlayment, and installation of the new roof. | GROUP USE SHELTER | 9930 | CNR | Parks |  | Spring Mountain | 1983 | 2592 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 129600
1157HVA1 | ELECTRIC HEATER REPLACEMENT | 1157 | There are two electric heaters in the building that have reached the end of their expected life. This project recommends replacing the electric heaters. The estimate includes removal and disposal of the existing equipment. | HAY & HORSE BARN/ CORRAL/ SHOP | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 2112 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
1156ADA2 | ADA BARBEQUE UPGRADE | 1156 | Per the United States Access Board and ICC ANSI-A117.1-2009, at least 5 percent of the barbeques shall be ADA compliant. This project would provide funding to remove 3 of the barbeques, and install ADA complaint barbeques which will allow access for wheel chairs. | GROUP USE SHELTER | 9930 | CNR | Parks |  | Spring Mountain | 1983 | 2592 | 2016-12-15 | Immediate to Two Years | Currently Critical | 1 | 4500
1157EXT1 | EXTERIOR FINISHES | 1157 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, doors, flashing, fixtures and all other penetrations and mitigating the earth to wood contact. It is recommended that the building be painted within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | HAY & HORSE BARN/ CORRAL/ SHOP | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 2112 | 2016-12-15 | Immediate to Two Years | Currently Critical | 1 | 21120
1157INT1 | INTERIOR FINISHES | 1157 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | HAY & HORSE BARN/ CORRAL/ SHOP | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 2112 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 21120
1157ENR1 | LIGHTING UPGRADE | 1157 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | HAY & HORSE BARN/ CORRAL/ SHOP | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 2112 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16896
1157SFT1 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 1157 | The exit signs do not meet current standards and there is no emergency egress lighting. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2018 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | HAY & HORSE BARN/ CORRAL/ SHOP | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 2112 | 2016-12-15 | Immediate to Two Years | Currently Critical | 1 | 1000
1156SIT1 | SITE DRAINAGE UPGRADES | 1156 | The grade does not slope away effectively from the structure. Water has pooled against the foundation. In the winter months, as the water freezes against the foundation, over time, this can cause damage to the foundation. It is recommended per IBC 1804.3 Site Grading the ground immediately adjacent to the foundation shall be sloped away from the building at a slope of not less than one vertical in 20 units horizontal (5-percent slope) for a minimum distance of 10 feet (3048 mm) measured perpendicular to the face of the wall. This project would create a 5% slope away from the buildings. Additional drainage swales shall be installed, as needed. It is recommended that the grading be completed within 2-3 years. | GROUP USE SHELTER | 9930 | CNR | Parks |  | Spring Mountain | 1983 | 2592 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
1155ENR1 | LIGHTING UPGRADE | 1155 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | WORK SHOP | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 1962 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15696
1157SFT3 | STAIR HANDRAIL & LANDING INSTALLATION | 1157 | There is an exit door which has a stairway down into the shop area of the building. There are no handrails nor proper landings at this exit. This project would provide for a concrete exterior landing and a new wood framed stairway, landing and handrails on the interior. The ICC 2018 Chapter 10, Section's 1008, 1009 and 1012 were referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | HAY & HORSE BARN/ CORRAL/ SHOP | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 2112 | 2016-12-15 | Immediate to Two Years | Currently Critical | 1 | 1200
1149STR1 | STRUCTURAL REPAIRS | 1149 | The Chinchilla Shed has a major crack in the masonry wall. It is recommended that a structural assessment and repairs be done by licensed professionals to correct this problem. A structural assessment, design and repairs are included in this estimate. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. | CHINCHILLA SHED | 9930 | CNR | Parks |  | Spring Mountain | 1940 | 1296 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
1155HVA1 | EXHAUST FAN INSTALLATION | 1155 | The welding shop area does not have adequate ventilation. This project would provide for the purchase and installation of an exhaust fan assembly for the welding shop including connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | WORK SHOP | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 1962 | 2016-12-15 | Immediate to Two Years | Currently Critical | 1 | 10000
1151HVA1 | ELECTRIC HEATER REPLACEMENT | 1151 | There is an electric heater in the pipe chase/ janitor area of the building that has reached the end of its life expectancy. This project recommends replacing the electric heater. The estimate includes removal and disposal of the existing equipment. | COMFORT STATION #2 - GROUP USE | 9930 | CNR | Parks |  | Spring Mountain | 1981 | 402 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
1151EXT1 | EXTERIOR FINISHES | 1151 | It is important to maintain the finish, weather resistance and appearance of the building. The caulked control joints in the CMU of the exterior surface of this building are uniformly deteriorated and should be removed and the joints re-caulked. The metal doors and window frames should be sanded and painted on a cyclical basis. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | COMFORT STATION #2 - GROUP USE | 9930 | CNR | Parks |  | Spring Mountain | 1981 | 402 | 2016-12-15 | Four to Ten Years | Long-Term Needs | 3 | 4020
1150ELE1 | GFCI OUTLETS | 1150 | The existing receptacles in the Comfort Station #1 are standard duplex receptacles. The 2011 (NEC) National Electrical Code 210.8 requires these locations to have Ground Fault Circuit Interrupter (GFCI) protection. This project would provide for removing the standard receptacles and installing GFCI receptacles. | COMFORT STATION #1 | 9930 | CNR | Parks |  | Spring Mountain | 1981 | 402 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2400
1150ADA1 | ADA RESTROOM UPGRADE | 1150 | The designated ADA accessible restrooms do not fully meet the ADA requirements. This project would provide for remodeling two of the restrooms into ADA compliant restrooms including but not limited to proper signage, sink, toilet, grab bars, tissue dispensers, mirror, electric hand dryers and door hardware. NRS 338.180, IBC - 2018, ICC/ANSI A117.1 - 2009 and ADAAG - 2010 were referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | COMFORT STATION #1 | 9930 | CNR | Parks |  | Spring Mountain | 1981 | 402 | 2016-12-15 | Immediate to Two Years | Currently Critical | 1 | 4000
1150HVA1 | ELECTRIC HEATER REPLACEMENT | 1150 | There is an electric heater in the pipe chase/ janitor area of the building that has reached the end of its life expectancy. This project recommends replacing the electric heater. The estimate includes removal and disposal of the existing equipment. | COMFORT STATION #1 | 9930 | CNR | Parks |  | Spring Mountain | 1981 | 402 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
1151EXT2 | DOOR HARDWARE REPLACEMENT | 1151 | The exterior metal doors are in good shape, but staff has had continuous problems with the hardware. The handles and locks are damaged from age and general wear and tear and have reached the end of their useful life. This project would provide for the replacement of the hardware on six doors. Removal and disposal of the existing hardware is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | COMFORT STATION #2 - GROUP USE | 9930 | CNR | Parks |  | Spring Mountain | 1981 | 402 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
1150EXT1 | EXTERIOR FINISHES | 1150 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry and caulking of the windows, doors, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | COMFORT STATION #1 | 9930 | CNR | Parks |  | Spring Mountain | 1981 | 402 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4020
1151INT1 | INTERIOR FINISHES | 1151 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | COMFORT STATION #2 - GROUP USE | 9930 | CNR | Parks |  | Spring Mountain | 1981 | 402 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4020
1149EXT2 | GUTTER AND DOWNSPOUT INSTALLATION | 1149 | The building does not have gutters or downspouts to control the runoff from the roof. The water currently sheet drains off the roof causing extensive erosion to the grade around the building and allowing water to penetrate into the walls. There are already major cracks in the west wall due to poor water control. This will eventually lead to failure of the foundation and walls undermining the integrity of the entire structure. This project would provide funding for the installation of a seamless gutter and downspout system for the buildings. This project should coincide with the DRAINAGE IMPROVEMENTS project. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | CHINCHILLA SHED | 9930 | CNR | Parks |  | Spring Mountain | 1940 | 1296 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
1149SIT1 | DRAINAGE IMPROVEMENTS | 1149 | The west wall is largely below grade and experiences water weeping through it during inclement weather. The water erodes the mortar and is causing major cracks in the wall. This project provides for waterproofing the exterior wall below grade and installing a French drain. The work will include excavation to expose the entire wall, applying a 100% polymer waterproof membrane to the wall, backfilling and installing a French drain along the length of the wall. This project should coincide with the Gutter and Downspout Installation project. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | CHINCHILLA SHED | 9930 | CNR | Parks |  | Spring Mountain | 1940 | 1296 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
1149EXT3 | ROOF REPLACEMENT | 1149 | The wood shake roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2 - 3 years with a new 50 year asphalt composition shingle roof and new underlayment. This estimate includes removal and disposal of the old roof. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. This project should coincide with the GUTTER AND DOWNSPOUT INSTALLATION project. | CHINCHILLA SHED | 9930 | CNR | Parks |  | Spring Mountain | 1940 | 1296 | 2016-12-15 | Four to Ten Years | Long-Term Needs | 3 | 19440
1149EXT1 | EXTERIOR FINISHES | 1149 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding for the sealing and painting of the exterior of the building. Included in the cost is sealing the stone, repairing the cracks and caulking the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and repaired in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | CHINCHILLA SHED | 9930 | CNR | Parks |  | Spring Mountain | 1940 | 1296 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12960
1149SFT1 | SAFETY CABINET | 1149 | The building contains many different paints, stains, and other hazardous products located on open shelves and on the floor. This does not meet OSHA standards or IFC for hazardous materials containment. This project would provide a self-closing hazardous storage container in the building and install placards on the building exterior in accordance with OSHA 1910.106 (d) and IFC Chapter 57 Section 5704.3.2.1.3. | CHINCHILLA SHED | 9930 | CNR | Parks |  | Spring Mountain | 1940 | 1296 | 2016-12-15 | Immediate to Two Years | Currently Critical | 1 | 10000
1148EXT1 | HISTORIC BUILDING MAINTENANCE | 1148 | The wood structure is over 100 years old and there are numerous areas where the wood is splitting, warping and deteriorating. This is also an exhibit for the park and requires maintenance time to display the artifacts and maintain the signage. This project would provide for sealing the wood, caulking the flashing, fixtures and windows, replacing metal roof panels as needed, replacing wood siding as needed and maintaining the exhibit pieces. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | HISTORIC BUNKHOUSE | 9930 | CNR | Parks |  | Spring Mountain | 1870 | 322 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4830
1150INT1 | INTERIOR FINISHES | 1150 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | COMFORT STATION #1 | 9930 | CNR | Parks |  | Spring Mountain | 1981 | 402 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4020
1153SFT1 | EXTERIOR LANDING INSTALLATION | 1153 | Section 1008.1 of the 2018 IBC describes the requirements for doors including floor elevations and landings. The floor or landing shall be at the same elevation on each side of the door, the exterior landing shall not exceed a 2-percent slope and shall have a length measured in the direction of travel of not less than 44 inches. The landing at the door on the building does not comply with this code and poses a safety hazard. This project would provide for the installation of a compliant landing for the door. | DOG KENNEL | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 123 | 2016-12-15 | Immediate to Two Years | Currently Critical | 1 | 5000
1162SFT1 | EXTERIOR LANDING INSTALLATION | 1162 | There are two out-swinging exterior doors on the building, which swing out over a step that does not have a landing. This does not comply with 2018 IBC Section 1008.1, which requires a proper landing and for the landing to not be more than 1/2" below the threshold. This project would provide for the installation of compliant landings. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. | CHICKEN COOP | 9930 | CNR | Parks |  | Spring Mountain | 1930 | 589 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
1155EXT2 | OVERHEAD DOOR REPLACEMENT | 1155 | There are two 10'x12' overhead coiling doors which are damaged and do not function properly. Exposure and wind have caused the doors to bend, crack and lose their finish. They have reached the end of their useful life and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead coiling doors and replacement with new manually operated overhead coiling doors. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | WORK SHOP | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 1962 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14000
1155EXT1 | EXTERIOR FINISHES | 1155 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, doors, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | WORK SHOP | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 1962 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19620
1155INT1 | INTERIOR FINISHES | 1155 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | WORK SHOP | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 1962 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19620
1154EXT2 | EXTERIOR FINISHES | 1154 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | THEATRE FEE BOOTH | 9930 | CNR | Parks |  | Spring Mountain | 1988 | 64 | 2016-12-15 | Four to Ten Years | Long-Term Needs | 3 | 640
1154INT1 | INTERIOR FINISHES | 1154 | It is recommended to paint the interior walls and ceilings at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | THEATRE FEE BOOTH | 9930 | CNR | Parks |  | Spring Mountain | 1988 | 64 | 2016-12-15 | Four to Ten Years | Long-Term Needs | 3 | 640
1151ADA1 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 1151 | This building contains a water fountain that is not ADA compliant. The 2018 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | COMFORT STATION #2 - GROUP USE | 9930 | CNR | Parks |  | Spring Mountain | 1981 | 402 | 2016-12-15 | Immediate to Two Years | Currently Critical | 1 | 4000
1153EXT1 | EXTERIOR FINISHES | 1153 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | DOG KENNEL | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 123 | 2016-12-15 | Four to Ten Years | Long-Term Needs | 3 | 1230
1155SFT1 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 1155 | The exit signs do not meet current standards and there is no emergency egress lighting. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2018 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | WORK SHOP | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 1962 | 2016-12-15 | Immediate to Two Years | Currently Critical | 1 | 1962
1153EXT3 | EXTERIOR SIDING REPLACEMENT | 1153 | The storage shed has painted T1-11 siding that is damaged, in poor condition, and due for replacement. This project recommends removing the damaged T1-11 siding and replacing it with new T1-11 siding finished with an oil-based stain or paint. | DOG KENNEL | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 123 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 300
1152INT1 | INTERIOR FINISHES | 1152 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and adequately prepared to receive the coating. An epoxy-based paint should be utilized in wet areas for durability. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. | MILKING BARN | 9930 | CNR | Parks |  | Spring Mountain | 1930 | 421 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4210
1152ELE1 | WIRING CLEANUP | 1152 | The wiring in the Milk Barn is disorganized and not in proper electrical boxes. This creates a safety issue when making repairs or upgrades. This project would provide for cleanup and labeling of the wiring. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. | MILKING BARN | 9930 | CNR | Parks |  | Spring Mountain | 1930 | 421 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
1152EXT1 | EXTERIOR FINISHES | 1152 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting the wood siding, re-pointing the stone masonry as needed and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | MILKING BARN | 9930 | CNR | Parks |  | Spring Mountain | 1930 | 421 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4210
1152EXT2 | WINDOW REPLACEMENT | 1152 | The windows are original, single pane construction in a wooden frame. These older windows are drafty, not energy efficient and the wooden frames have deteriorated significantly. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 2 units including wooden frames. Removal and disposal of the existing windows is included in this estimate. | MILKING BARN | 9930 | CNR | Parks |  | Spring Mountain | 1930 | 421 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
1151ADA2 | ADA RESTROOM UPGRADE | 1151 | The designated ADA accessible restrooms do not fully meet the ADA requirements. This project would provide for remodeling two of the restrooms into ADA compliant restrooms including but not limited to proper signage, sink, toilet, grab bars, tissue dispensers, mirror, electric hand dryers and door hardware. NRS 338.180, IBC - 2018, ICC/ANSI A117.1 - 2009 and ADAAG - 2010 were referenced for this project. | COMFORT STATION #2 - GROUP USE | 9930 | CNR | Parks |  | Spring Mountain | 1981 | 402 | 2016-12-15 | Immediate to Two Years | Currently Critical | 1 | 15000
1153EXT2 | ROOF REPLACEMENT | 1153 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition shingle roof and new underlayments. This estimate includes removal and disposal of the old roof. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | DOG KENNEL | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 123 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1845
1172ENR1 | WINDOW REPLACEMENT | 1172 | Most of the windows have been upgraded, but there are two older units left to replace. These older windows are drafty, not energy efficient and the wooden frames have deteriorated significantly. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 2 units including vinyl frames. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | VISITOR'S CENTER | 9930 | CNR | Parks |  | Spring Mountain | 1948 | 4228 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
1160EXT1 | EXTERIOR FINISHES | 1160 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | CALVING SHED | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 569 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5690
1168ELE3 | EXTERIOR OUTLET REPLACEMENT | 1168 | The building has exterior electrical outlets that do not meet current building codes. These outlets should be changed to GFCI type outlets with covers per the 2011 NEC. This project would provide for the purchase and installation of 4 GFCI duplex outlets. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | RESIDENCE #4 - OLD BUNKHOUSE/ DUPLEX | 9930 | CNR | Parks |  | Spring Mountain | 1957 | 2440 | 2016-12-15 | Immediate to Two Years | Currently Critical | 1 | 1600
1169EXT1 | EXTERIOR FINISHES | 1169 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, doors, flashing, fixtures and all other penetrations and mitigating the earth to wood contact. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | RESIDENCE #5 - SPRING HOUSE | 9930 | CNR | Parks |  | Spring Mountain | 1930 | 620 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6200
1169INT1 | INTERIOR REMODEL | 1169 | The interior fixtures and finishes are in general disrepair and the building is due for a complete remodel. This project would provide for removal and replacement of the flooring, doors and frames, cabinetry, trim and baseboards and any other interior finishes and fixtures in need of replacement. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. | RESIDENCE #5 - SPRING HOUSE | 9930 | CNR | Parks |  | Spring Mountain | 1930 | 620 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 31000
1169EXT2 | WINDOW REPLACEMENT | 1169 | The windows are original, single pane construction in a wooden frame. These older windows are drafty, not energy efficient and the wooden frames have deteriorated significantly. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 5 units including wooden frames. Removal and disposal of the existing windows is included in this estimate. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. | RESIDENCE #5 - SPRING HOUSE | 9930 | CNR | Parks |  | Spring Mountain | 1930 | 620 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
1170INT2 | INTERIOR FINISHES | 1170 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and adequately prepared to receive the coating. An epoxy-based paint should be utilized in wet areas for durability. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. | RESIDENCE #6 - COWHAND HOUSE | 9930 | CNR | Parks |  | Spring Mountain | 1930 | 432 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4320
1170EXT1 | EXTERIOR FINISHES | 1170 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, doors, flashing, fixtures and all other penetrations and mitigating the earth to wood contact. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | RESIDENCE #6 - COWHAND HOUSE | 9930 | CNR | Parks |  | Spring Mountain | 1930 | 432 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4320
1170EXT2 | WINDOW REPLACEMENT | 1170 | The windows are original, single pane construction in a wooden frame. These older windows are drafty, not energy efficient and the wooden frames have deteriorated significantly. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 5 units including wooden frames. Removal and disposal of the existing windows is included in this estimate. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. | RESIDENCE #6 - COWHAND HOUSE | 9930 | CNR | Parks |  | Spring Mountain | 1930 | 432 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
1171SIT1 | SITE DRAINAGE UPGRADES | 1171 | The grade does not slope away effectively from the buildings. Water has pooled against the foundation. In the winter months, as the water freezes against the foundation, over time, this can cause damage to the foundation. It is recommended per IBC 1804.3 Site Grading the ground immediately adjacent to the foundation shall be sloped away from the building at a slope of not less than one vertical in 20 units horizontal (5-percent slope) for a minimum distance of 10 feet (3048 mm) measured perpendicular to the face of the wall. This project would create a 5% slope away from the buildings. Additional drainage swales shall be installed, as needed. It is recommended that the grading be completed within 2-3 years. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. | HISTORIC STORAGE SHED | 9930 | CNR | Parks |  | Spring Mountain | 1870 | 120 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
1171EXT1 | HISTORIC BUILDING MAINTENANCE | 1171 | The metal clad wood structure is over 100 years old. It is important to maintain the finish, weather resistance and appearance of the building. This is also an exhibit for the park and requires maintenance time to display the artifacts and maintain the signage. This project would provide for caulking the metal panels, sealing the wood door, replacing the metal roof and wall panels as needed and maintaining the exhibit. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | HISTORIC STORAGE SHED | 9930 | CNR | Parks |  | Spring Mountain | 1870 | 120 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1800
1172ENR2 | HVAC EQUIPMENT REPLACEMENT | 1172 | The existing HVAC system consists of window mounted HVAC systems and a split system. This project would provide for replacing the existing equipment with exterior ground mounted packaged units that provide heating and air conditioning. Ducting and vents will need to be installed in the attic. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | VISITOR'S CENTER | 9930 | CNR | Parks |  | Spring Mountain | 1948 | 4228 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 63420
1172SFT1 | SMOKE CARBON MONOXIDE ALARM | 1172 | IRC 2018 Section R314 and R315.3 explains the requirements for smoke alarms in dwelling units. This includes: installing and maintaining smoke alarms in each sleeping room; having a carbon monoxide and smoke detector on the ceiling or wall outside of each sleeping area and in the immediate vicinity of bedrooms when an alteration, repair or addition requiring a permit occurs. IRC 2018, requires that smoke detectors and carbon monoxide alarms be UL rated. State Fire Marshal NAC 477.915 (3) requires that smoke detectors be connected to the wiring in a building and include a battery for emergency backup power. This project would provide funding for the purchase and installation of smoke alarms and carbon monoxide alarms in accordance with IRC and NAC laws. | VISITOR'S CENTER | 9930 | CNR | Parks |  | Spring Mountain | 1948 | 4228 | 2016-12-15 | Immediate to Two Years | Currently Critical | 1 | 5000
1168INT2 | INTERIOR FINISHES | 1168 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | RESIDENCE #4 - OLD BUNKHOUSE/ DUPLEX | 9930 | CNR | Parks |  | Spring Mountain | 1957 | 2440 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24400
1172PLM1 | PLUMBING REPLACEMENT | 1172 | The plumbing and waste system is older and in poor condition. Most of the system appears to be original to the building and should be scheduled for replacement. This project recommends replacing all of the water and sewer lines in the building. This estimate includes removal and disposal of the existing system as required. | VISITOR'S CENTER | 9930 | CNR | Parks |  | Spring Mountain | 1948 | 4228 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 105700
1168INT3 | FLOORING REPLACEMENT | 1168 | The sheet vinyl and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new sheet vinyl with a 6" base and heavy duty commercial grade carpet in the next 2-3 years. | RESIDENCE #4 - OLD BUNKHOUSE/ DUPLEX | 9930 | CNR | Parks |  | Spring Mountain | 1957 | 2440 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19520
1172INT1 | INTERIOR FINISHES | 1172 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | VISITOR'S CENTER | 9930 | CNR | Parks |  | Spring Mountain | 1948 | 4228 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 42280
1173PLM1 | WATER HEATER REPLACEMENT | 1173 | There is a 6 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 6-7 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | RANGER'S OFFICE/ GUEST HOUSE | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 912 | 2016-12-15 | Four to Ten Years | Long-Term Needs | 3 | 1000
1173EXT1 | EXTERIOR FINISHES | 1173 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | RANGER'S OFFICE/ GUEST HOUSE | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 912 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9120
1173ADA1 | ADA SIGNAGE | 1173 | ADA regulations pertaining to building access, route of travel and restrooms has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances, route of travel inside the building and restrooms. It is recommended that applicable signage be installed where required. The 2018 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | RANGER'S OFFICE/ GUEST HOUSE | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 912 | 2016-12-15 | Immediate to Two Years | Currently Critical | 1 | 900
1173EXT2 | ROOF REPLACEMENT | 1173 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 4-5 years with a new 50 year asphalt composition shingle roof and new underlayment. This estimate includes removal and disposal of the old roof. | RANGER'S OFFICE/ GUEST HOUSE | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 912 | 2016-12-15 | Four to Ten Years | Long-Term Needs | 3 | 13680
1173ADA2 | ADA ACCESSIBLE PATH OF TRAVEL | 1173 | The ADA provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the office are necessary to comply with ADA accessibility requirements and need to be updated. This project would provide for an updated concrete van accessible ADA parking and loading space and concrete walkway to the existing sidewalk. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2018 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. 750 square feet of concrete was used for this estimate. | RANGER'S OFFICE/ GUEST HOUSE | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 912 | 2016-12-15 | Immediate to Two Years | Currently Critical | 1 | 30000
1173ENR1 | WINDOW REPLACEMENT | 1173 | The windows are original, dual pane construction in a metal frame and have reached the end of their useful life. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 10 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | RANGER'S OFFICE/ GUEST HOUSE | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 912 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
1173SFT2 | FIRE ALARM SYSTEM INSTALLATION | 1173 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2009 Section 7 and the 2018 International Fire Code. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | RANGER'S OFFICE/ GUEST HOUSE | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 912 | 2016-12-15 | Immediate to Two Years | Currently Critical | 1 | 3648
1173INT2 | INTERIOR FINISHES | 1173 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and adequately prepared to receive the coating. An epoxy-based paint should be utilized in wet areas for durability. | RANGER'S OFFICE/ GUEST HOUSE | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 912 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9120
1173ENR2 | LIGHTING UPGRADE | 1173 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | RANGER'S OFFICE/ GUEST HOUSE | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 912 | 2016-12-15 | Four to Ten Years | Long-Term Needs | 3 | 7296
1173ADA3 | BREAK ROOM REMODEL | 1173 | The kitchenette and associated cabinets in the employee break room are original to the building. This project recommends the replacement of the existing kitchen countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2018, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards for Accessible Design should be incorporated into the design such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. | RANGER'S OFFICE/ GUEST HOUSE | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 912 | 2016-12-15 | Immediate to Two Years | Currently Critical | 1 | 15000
1174EXT1 | HISTORIC BUILDING MAINTENANCE | 1174 | The structure is made of unreinforced stone masonry. It is over 100 years old and there are numerous areas where the mortar is failing, missing and not sealed properly. This is also an exhibit for the park and requires maintenance time to display the artifacts and maintain the signage. This project would provide for the cleaning, repair and re-pointing of the stone work and maintaining the exhibit. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | WILSON RESIDENCE/ SANDSTONE CABIN | 9930 | CNR | Parks |  | Spring Mountain | 1870 | 681 | 2016-12-15 | Immediate to Two Years | Currently Critical | 1 | 10215
1172EXT1 | EXTERIOR FINISHES | 1172 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, doors, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | VISITOR'S CENTER | 9930 | CNR | Parks |  | Spring Mountain | 1948 | 4228 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 42280
1167ENV1 | PEST CONTROL | 1167 | There are numerous signs throughout this building of insect infestation including ants. Due to the potential risk of disease and damage to the building, this project provides for treatment and cleanup of the insects by a licensed pest control business. It is recommended that the building be treated in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain control of the pests. | RESIDENCE #3 - FOREMAN'S HOUSE | 9930 | CNR | Parks |  | Spring Mountain | 1957 | 925 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
1159INT1 | INTERIOR FINISHES | 1159 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. | CATTLE FEEDER SHED | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 389 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3890
1160EXT2 | ROOF REPLACEMENT | 1160 | The wood shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition shingle roof and new underlayment. This estimate includes removal and disposal of the old roof. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. | CALVING SHED | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 569 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8535
1147EXT1 | HISTORIC BUILDING MAINTENANCE | 1147 | The structure is made of unreinforced stone masonry. It is over 100 years old and there are numerous areas where the mortar is failing, missing and not sealed properly. This is also an exhibit for the park and requires time to display the artifacts and maintain the signage. This project would provide for the cleaning, repair and re-pointing of the stone work and maintaining the exhibit. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | HISTORIC BLACKSMITH SHOP | 9930 | CNR | Parks |  | Spring Mountain | 1870 | 437 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6555
1162EXT2 | ROOF REPLACEMENT | 1162 | The wood shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new wood shingle roof and new underlayment. This estimate includes removal and disposal of the old roof. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. | CHICKEN COOP | 9930 | CNR | Parks |  | Spring Mountain | 1930 | 589 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8835
1163HVA1 | EVAPORATIVE COOLER REPLACEMENT | 1163 | A window air conditioning unit is installed on the side of this building. It was not working at the time of the survey and has reached the end of its useful and expected life. This project would provide for a new air conditioning unit to be installed including all required connections to utilities. The estimate includes removal and disposal of the old air conditioning unit. | POWER CONTROL SHED | 9930 | CNR | Parks |  | Spring Mountain | 1940 | 125 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
1162EXT1 | EXTERIOR FINISHES | 1162 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | CHICKEN COOP | 9930 | CNR | Parks |  | Spring Mountain | 1930 | 589 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5890
1162EXT3 | WINDOW REPLACEMENT | 1162 | The windows are original, single pane construction in a wooden frame. These older windows are drafty, not energy efficient and the wooden frames have deteriorated significantly. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 4 units including wooden frames. Removal and disposal of the existing windows is included in this estimate. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. | CHICKEN COOP | 9930 | CNR | Parks |  | Spring Mountain | 1930 | 589 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
1163EXT1 | EXTERIOR FINISHES | 1163 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | POWER CONTROL SHED | 9930 | CNR | Parks |  | Spring Mountain | 1940 | 125 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1250
1163SFT1 | EXTERIOR DOOR LANDING INSTALLATION | 1163 | There are two out-swinging exterior doors on the building, which swing out over a step that does not have a landing. This does not comply with 2018 IBC Section 1008.1, which requires a proper landing and for the landing to not be more than 1/2" below the threshold. This project would provide for the installation of compliant landings. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. | POWER CONTROL SHED | 9930 | CNR | Parks |  | Spring Mountain | 1940 | 125 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
1163INT1 | REPLACE INSULATION | 1163 | The building has a layer of insulation installed on the interior walls that has reached the end of its useful life. It is falling off the walls and ceiling and should be scheduled for replacement in the next 1-2 years. This project recommends replacement with a foil-backed R-30 insulation. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. | POWER CONTROL SHED | 9930 | CNR | Parks |  | Spring Mountain | 1940 | 125 | 2016-12-15 | Immediate to Two Years | Currently Critical | 1 | 250
1164EXT1 | EXTERIOR FINISHES | 1164 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | PUMP CONTROL/ SEASONAL SHED | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 237 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2370
1164EXT2 | ROOF REPLACEMENT | 1164 | The wood shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new wood shingle roofing system and new underlayment. This estimate includes removal and disposal of the old roof. | PUMP CONTROL/ SEASONAL SHED | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 237 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3555
1168EXT2 | EXTERIOR FINISHES | 1168 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations and mitigating the earth to wood contact.. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | RESIDENCE #4 - OLD BUNKHOUSE/ DUPLEX | 9930 | CNR | Parks |  | Spring Mountain | 1957 | 2440 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24400
1167PLM1 | WATER SOFTENER INSTALLATION | 1167 | The domestic water supply is a gravity fed water system and the water is full of minerals. This project recommends the installation of a water softening system to extend the life of the plumbing system, fixtures and appliances. This project or a portion thereof was previously recommended in the FCA report dated 05/05/2003 and 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | RESIDENCE #3 - FOREMAN'S HOUSE | 9930 | CNR | Parks |  | Spring Mountain | 1957 | 925 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
1159EXT1 | EXTERIOR FINISHES | 1159 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | CATTLE FEEDER SHED | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 389 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3890
1167PLM2 | WATER HEATER REPLACEMENT | 1167 | There is a 50 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | RESIDENCE #3 - FOREMAN'S HOUSE | 9930 | CNR | Parks |  | Spring Mountain | 1957 | 925 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
1167ENR3 | HVAC UPGRADE | 1167 | The building is heated and cooled by an electric roof mounted packaged unit. It is reaching the end of its service life and should be scheduled for replacement in the next three to four years. This project provides for disposal of the existing unit and replacement with a new electric unit including connections to existing utilities. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | RESIDENCE #3 - FOREMAN'S HOUSE | 9930 | CNR | Parks |  | Spring Mountain | 1957 | 925 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
1167EXT2 | EXTERIOR FINISHES | 1167 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, doors, flashing, fixtures and all other penetrations and mitigating the earth to wood contact. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | RESIDENCE #3 - FOREMAN'S HOUSE | 9930 | CNR | Parks |  | Spring Mountain | 1957 | 925 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9250
1167ENR1 | WINDOW REPLACEMENT | 1167 | The windows are original, dual pane construction in a metal frame and have reached the end of their expected life. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 8 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | RESIDENCE #3 - FOREMAN'S HOUSE | 9930 | CNR | Parks |  | Spring Mountain | 1957 | 925 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
1167INT2 | INTERIOR FINISHES | 1167 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | RESIDENCE #3 - FOREMAN'S HOUSE | 9930 | CNR | Parks |  | Spring Mountain | 1957 | 925 | 2016-12-15 | Four to Ten Years | Long-Term Needs | 3 | 9250
1167ENR2 | LIGHTING UPGRADE | 1167 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | RESIDENCE #3 - FOREMAN'S HOUSE | 9930 | CNR | Parks |  | Spring Mountain | 1957 | 925 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7400
1168INT1 | KITCHEN CABINET REPLACEMENT | 1168 | The kitchens in both duplexes were in fair to poor condition at the time of the survey. The cabinets and equipment are showing signs of general wear and tear and are approaching the end of their expected life. This project recommends the replacement of the existing kitchen cabinets, countertops, fixtures and equipment with mid range, high quality components. This project or a portion thereof was previously recommended in the FCA report dated 05/05/2003 and 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | RESIDENCE #4 - OLD BUNKHOUSE/ DUPLEX | 9930 | CNR | Parks |  | Spring Mountain | 1957 | 2440 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 70000
1168PLM1 | WATER SOFTENER INSTALLATION | 1168 | The domestic water supply is a gravity fed water system and the water is full of minerals. This project recommends the installation of a water softening system to extend the life of the plumbing system, fixtures and appliances. This project or a portion thereof was previously recommended in the FCA report dated 05/05/2003 and 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | RESIDENCE #4 - OLD BUNKHOUSE/ DUPLEX | 9930 | CNR | Parks |  | Spring Mountain | 1957 | 2440 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
1168ENR1 | HVAC EQUIPMENT REPLACEMENT | 1168 | The building is heated and cooled by two electric roof mounted packaged units. They are reaching the end of their serviceable life and should be scheduled for replacement. This project provides for disposal of the existing units and replacement with two new roof mounted packaged units including connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | RESIDENCE #4 - OLD BUNKHOUSE/ DUPLEX | 9930 | CNR | Parks |  | Spring Mountain | 1957 | 2440 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
1168ENR2 | LIGHTING UPGRADE | 1168 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | RESIDENCE #4 - OLD BUNKHOUSE/ DUPLEX | 9930 | CNR | Parks |  | Spring Mountain | 1957 | 2440 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19520
1168ENR3 | WINDOW REPLACEMENT | 1168 | The windows are original, dual pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 12 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | RESIDENCE #4 - OLD BUNKHOUSE/ DUPLEX | 9930 | CNR | Parks |  | Spring Mountain | 1957 | 2440 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18000
1168EXT3 | ROOF REPLACEMENT | 1168 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 8-9 years with a new 50 year asphalt composition shingle roof and new underlayment. This estimate includes removal and disposal of the old roofing system. | RESIDENCE #4 - OLD BUNKHOUSE/ DUPLEX | 9930 | CNR | Parks |  | Spring Mountain | 1957 | 2440 | 2016-12-15 | Four to Ten Years | Long-Term Needs | 3 | 29280
1164SFT1 | EXTERIOR DOOR LANDING INSTALLATION | 1164 | There are two out-swinging exterior doors on the building, which swing out over a step that does not have a landing. This does not comply with 2018 IBC Section 1008.1, which requires a proper landing and for the landing to not be more than 1/2" below the threshold. This project would provide for the installation of compliant landings. | PUMP CONTROL/ SEASONAL SHED | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 237 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
1634EXT2 | EXTERIOR FINISHES | 1634 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, staining the wood and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be stained and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | THEATRE/ PAVILION | 9930 | CNR | Parks |  | Spring Mountain | 1988 | 6230 | 2016-12-15 | Four to Ten Years | Long-Term Needs | 3 | 62300
1163EXT2 | ROOF REPLACEMENT | 1163 | The wood shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new wood shingle roof and new underlayment. This estimate includes removal and disposal of the old roof. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. | POWER CONTROL SHED | 9930 | CNR | Parks |  | Spring Mountain | 1940 | 125 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1875
1633EXT2 | EXTERIOR FINISHES | 1633 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, staining the wood and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be stained and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | THEATRE CONCESSION | 9930 | CNR | Parks |  | Spring Mountain | 1988 | 400 | 2016-12-15 | Four to Ten Years | Long-Term Needs | 3 | 4000
1633INT2 | INTERIOR FINISHES | 1633 | It is recommended to paint the interior walls and ceilings at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and adequately prepared to receive the coating. An epoxy-based paint should be utilized in wet areas for durability. | THEATRE CONCESSION | 9930 | CNR | Parks |  | Spring Mountain | 1988 | 400 | 2016-12-15 | Four to Ten Years | Long-Term Needs | 3 | 4000
1634ADA1 | ACCESSIBLE ENTRANCE RAMP | 1634 | The Theatre/ Pavilion is in need of an accessible entrance into the basement. This building is required to have an accessible entrance to the basement per the ADA regulations. This project would provide for an accessible ramp to access the basement of the building. The 2018 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | THEATRE/ PAVILION | 9930 | CNR | Parks |  | Spring Mountain | 1988 | 6230 | 2016-12-15 | Immediate to Two Years | Currently Critical | 1 | 35000
1634INT1 | INTERIOR FINISHES | 1634 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | THEATRE/ PAVILION | 9930 | CNR | Parks |  | Spring Mountain | 1988 | 6230 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 62300
1635PLM1 | WATER HEATER REPLACEMENT | 1635 | There is an on-demand propane-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new on-demand propane-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | ENTRANCE STATION | 9930 | CNR | Parks |  | Spring Mountain | 1992 | 225 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
1635EXT1 | EXTERIOR FINISHES | 1635 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting, cleaning and sealing the stone and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | ENTRANCE STATION | 9930 | CNR | Parks |  | Spring Mountain | 1992 | 225 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2250
1635INT1 | INTERIOR FINISHES | 1635 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | ENTRANCE STATION | 9930 | CNR | Parks |  | Spring Mountain | 1992 | 225 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2250
1635ADA1 | ADA ACCESSIBLE PATH OF TRAVEL | 1635 | The ADA provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the office are necessary to comply with ADA accessibility requirements. This project would provide for a concrete van accessible ADA parking and loading space and concrete walkway to the existing sidewalk. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2018 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. 750 square feet of concrete was used for this estimate. It is recommended that this project coincide with the paving project. | ENTRANCE STATION | 9930 | CNR | Parks |  | Spring Mountain | 1992 | 225 | 2016-12-15 | Immediate to Two Years | Currently Critical | 1 | 30000
1636EXT1 | EXTERIOR FINISHES | 1636 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | IRRIGATION PUMP HOUSE | 9930 | CNR | Parks |  | Spring Mountain | 1997 | 117 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1170
1636PLM1 | PUMP REPLACEMENT | 1636 | The pump in the Irrigation Pump House was problematic at the time of the survey. The irrigation pump reached the end of its expected life and is due for replacement. It is recommended to replace the pump with a 10 H.P. Pump. This project includes removal and disposal of the existing pump and all required connections to utilities. | IRRIGATION PUMP HOUSE | 9930 | CNR | Parks |  | Spring Mountain | 1997 | 117 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
1636INT1 | INTERIOR FINISHES | 1636 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | IRRIGATION PUMP HOUSE | 9930 | CNR | Parks |  | Spring Mountain | 1997 | 117 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1170
1636ENR1 | AIR CONDITIONER REPLACEMENT | 1636 | The wall-mounted air conditioner was installed in 1997. It is not energy efficient and has reached the end of its expected and useful life. This project would provide for the purchase and installation of a new wall-mounted air conditioner. This project includes removal and disposal of the existing unit and all required connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | IRRIGATION PUMP HOUSE | 9930 | CNR | Parks |  | Spring Mountain | 1997 | 117 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
1633HVA1 | EVAPORATIVE COOLER REPLACEMENT | 1633 | An evaporative cooler is installed on the side of this building. It is severely scaled and has reached the end of its useful and expected life. This project would provide for a new evaporative cooler to be installed including all required connections to utilities. The estimate includes removal and disposal of the old cooler. | THEATRE CONCESSION | 9930 | CNR | Parks |  | Spring Mountain | 1988 | 400 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
2410EXT2 | EXTERIOR FINISHES | 2410 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | THEATRE STORAGE | 9930 | CNR | Parks |  | Spring Mountain | 1988 | 196 | 2016-12-15 | Four to Ten Years | Long-Term Needs | 3 | 1960
9930ADA2 | ADA PARKING SPACE UPGRADE | 9930 | The ADA provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the Ranger’s Office, Theatre area and Visitors Center are necessary to comply with ADA accessibility requirements. This project would provide for a concrete van accessible ADA parking and loading space and concrete walkway to the existing sidewalk. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2018 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. 750 square feet of concrete was used for this estimate for each location. It is recommended that this project coincide with the paving projects. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | SPRING MOUNTAIN RANCH STATE PARK SITE | 9930 | CNR | Parks |  | Spring Mountain | 0 |  | 2016-12-15 | Immediate to Two Years | Currently Critical | 1 | 90000
9930SFT3 | WOOD ROOF FIRE RETARDANT TREATMENT | 9930 | There are 13 structures throughout the site that have wood shingle roofs. Altogether the square footage adds up to about 12,124 square feet of wood roof area. Due to the historic nature of the site and structures, these wood roofs should not be replaced with another roofing material. It is recommended to develop an annual roof maintenance program to address the fire resistance of the shingles. This project would provide for the purchase and application of a fire retardant coating for the wood roofs. This project should be scheduled on an annual basis to ensure that the structures are thoroughly protected. The structures included are: 1147 Historic Blacksmith Shop, 1149 Chinchilla Shed, 1152 Milking Barn, 1157 Hay & Horse barn/ Corral/ Shop, 1159 Cattle Feeder Shed, 1160 Calving Shed, 1162 Chicken Coop, 1163 Power Control Shed, 1169 Residence #5 - Spring House, 1170 Residence #6 - Cowhand House, 1172 Visitor's Center, 1174 Wilson Residence/ Sandstone Cabin, and 1635 Entrance Station. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | SPRING MOUNTAIN RANCH STATE PARK SITE | 9930 | CNR | Parks |  | Spring Mountain | 0 |  | 2016-12-15 | Immediate to Two Years | Currently Critical | 1 | 6062
3043EXT1 | EXTERIOR FINISHES | 3043 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting, and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | DOMESTIC WELL/ PUMP HOUSE | 9930 | CNR | Parks |  | Spring Mountain | 2005 | 96 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 960
9930ADA3 | ADA PROGRAM ACCESSIBILITY | 9930 | The site has historic structures and other ranch features that are open to the public for viewing. There are also guided tours of the site offered at various times throughout the week. There is no designated ADA access to most of these areas across the ranch. This project would provide for an ADA accessible location inside of the Visitor's center for an audio/ visual (A/V) presentation of the historic structures and other inaccessible features of the site. This project includes funds for an audio/ visual consultant to outline and document the inaccessible areas and purchase and installation of all required A/V equipment including signage, TDD equipment and minor remodeling of the public area of the building as required to accommodate this program. The 2018 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | SPRING MOUNTAIN RANCH STATE PARK SITE | 9930 | CNR | Parks |  | Spring Mountain | 0 |  | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
9930SIT1 | SLURRY SEAL ASPHALT PAVING | 9930 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving at the main parking lot near the Picnic Area. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 50,000 square feet of asphalt area was used to generate this estimate. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | SPRING MOUNTAIN RANCH STATE PARK SITE | 9930 | CNR | Parks |  | Spring Mountain | 0 |  | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 62500
0863PLM1 | WATER HEATER REPLACEMENT | 0863 | There is a 20 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended to replace water heater with an on-demand propane-fired water heater. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/11/2002 and 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | PIOCHE CONSERVATION CAMP NDF OFFICE | 9949 | CNR | Forestry |  | Pioche | 1987 | 2400 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0863ENR1 | WINDOW REPLACEMENT | 0863 | The windows are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 8 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | PIOCHE CONSERVATION CAMP NDF OFFICE | 9949 | CNR | Forestry |  | Pioche | 1987 | 2400 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16000
0863ENV1 | BREAK ROOM REMODEL | 0863 | The kitchenette and associated cabinets in the employee break room are original to the building. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and counter tops are delaminating and failing. This project recommends the replacement of the existing kitchen counters, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. This estimate includes disposal of the existing materials. This project or a portion thereof was previously recommended in the FCA report dated 04/11/2002 and 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | PIOCHE CONSERVATION CAMP NDF OFFICE | 9949 | CNR | Forestry |  | Pioche | 1987 | 2400 | 2017-03-02 | Immediate to Two Years | Currently Critical | 1 | 15000
0863ADA2 | ADA SIGNAGE | 0863 | ADA regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with these criteria. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | PIOCHE CONSERVATION CAMP NDF OFFICE | 9949 | CNR | Forestry |  | Pioche | 1987 | 2400 | 2017-03-02 | Immediate to Two Years | Currently Critical | 1 | 2500
0863EXT1 | EXTERIOR FINISHES | 0863 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | PIOCHE CONSERVATION CAMP NDF OFFICE | 9949 | CNR | Forestry |  | Pioche | 1987 | 2400 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24000
0863ADA1 | ADA RESTROOM UPGRADE | 0863 | The building does not have an accessible restroom. The existing restroom does not meet the ADA requirements. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom. Items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | PIOCHE CONSERVATION CAMP NDF OFFICE | 9949 | CNR | Forestry |  | Pioche | 1987 | 2400 | 2017-03-02 | Immediate to Two Years | Currently Critical | 1 | 15000
0863ENR2 | HVAC EQUIPMENT REPLACEMENT | 0863 | The existing HVAC equipment consists of isolated evaporative coolers and space heaters. They do not condition the spaces adequately, are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of a gas-fired packaged unit and ducting to upgrade the existing system. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 04/11/2002 and 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | PIOCHE CONSERVATION CAMP NDF OFFICE | 9949 | CNR | Forestry |  | Pioche | 1987 | 2400 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0863INT2 | INTERIOR FINISHES | 0863 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 04/11/2002 and 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | PIOCHE CONSERVATION CAMP NDF OFFICE | 9949 | CNR | Forestry |  | Pioche | 1987 | 2400 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24000
0863ENR3 | LIGHTING UPGRADE | 0863 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | PIOCHE CONSERVATION CAMP NDF OFFICE | 9949 | CNR | Forestry |  | Pioche | 1987 | 2400 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19200
0863ADA3 | ADA PARKING AND PATH OF TRAVEL | 0863 | The ADA provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the office are necessary to comply with ADA accessibility requirements. This project would provide for a concrete van accessible ADA parking and loading space and concrete walkway to the existing sidewalk. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. 750 square feet of concrete was used for this estimate. It is recommended that this project coincide with the paving project. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | PIOCHE CONSERVATION CAMP NDF OFFICE | 9949 | CNR | Forestry |  | Pioche | 1987 | 2400 | 2017-03-02 | Immediate to Two Years | Currently Critical | 1 | 15000
0863EXT2 | ROOF REPLACEMENT | 0863 | The corrugated metal roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a standing seam metal roofing system. This estimate includes the removal and the disposal of the old roof. | PIOCHE CONSERVATION CAMP NDF OFFICE | 9949 | CNR | Forestry |  | Pioche | 1987 | 2400 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 36000
0863SFT4 | EXTERIOR LANDING UPGRADE | 0863 | There are two out-swinging exterior doors which swing out over a step and do not have a landing that comply with IBC 2012. IBC Section 1008 requires that landings not be more than 1/2" below the threshold. This project would provide for the installation of two compliant landings for the doors. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | PIOCHE CONSERVATION CAMP NDF OFFICE | 9949 | CNR | Forestry |  | Pioche | 1987 | 2400 | 2017-03-02 | Immediate to Two Years | Currently Critical | 1 | 10000
0863EXT4 | OVERHEAD DOOR REPLACEMENT | 0863 | There is a 10'x12' overhead coiling door which is damaged and does not function properly. It is original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead coiling door and replacement with a motorized door. | PIOCHE CONSERVATION CAMP NDF OFFICE | 9949 | CNR | Forestry |  | Pioche | 1987 | 2400 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7000
1036EXT2 | HISTORIC BUILDING MAINTENANCE | 1036 | The wood structure is over 82 years old and there are numerous areas where the wood is splitting, warping and deteriorating. This is also an exhibit for the park and requires maintenance time to display the artifacts and maintain the signage. This project would provide for sealing the wood, replacing wood roof shingles as needed and maintaining the exhibit in a state of arrested decay. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | COMFORT STATION #1 - CCC | 9947 | CNR | Parks |  | Cathedral Gorge | 1934 | 180 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8925
0997ENR1 | WINDOW REPLACEMENT | 0997 | Some of the windows are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 2 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/23/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | BDSP PARK RESIDENCE | 9948 | CNR | Parks |  | Beaver Dam | 1964 | 588 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0997PLM1 | WATER HEATER REPLACEMENT | 0997 | There is a 40 gallon propane-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement immediately. It is recommended that a new propane-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | BDSP PARK RESIDENCE | 9948 | CNR | Parks |  | Beaver Dam | 1964 | 588 | 2017-04-05 | Immediate to Two Years | Currently Critical | 1 | 1750
1037EXT1 | EXTERIOR FINISHES | 1037 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4-5 years and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CAMPGROUND STORAGE | 9947 | CNR | Parks |  | Cathedral Gorge | 1962 | 117 | 2017-04-05 | Four to Ten Years | Long-Term Needs | 3 | 1170
0997ENR2 | LIGHTING UPGRADE | 0997 | The existing lighting fixtures are the older fluorescent type and are not energy efficient. This project will upgrade the fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/23/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | BDSP PARK RESIDENCE | 9948 | CNR | Parks |  | Beaver Dam | 1964 | 588 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4704
1037INT1 | INTERIOR FINISHES | 1037 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and every 5-6 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | CAMPGROUND STORAGE | 9947 | CNR | Parks |  | Cathedral Gorge | 1962 | 117 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1170
1036STR1 | STRUCTURAL RETROFIT | 1036 | The timber framing supporting the roof is beginning to fail. The timbers have dried out, cracked, and broken in some areas. The roof material is already falling through in some areas. This project would provide for removing and replacing the timber construction. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | COMFORT STATION #1 - CCC | 9947 | CNR | Parks |  | Cathedral Gorge | 1934 | 180 | 2017-04-05 | Immediate to Two Years | Currently Critical | 1 | 18000
0997INT1 | INTERIOR FINISHES | 0997 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/23/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | BDSP PARK RESIDENCE | 9948 | CNR | Parks |  | Beaver Dam | 1964 | 588 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5880
0997CUL1 | KITCHEN REMODEL | 0997 | At the time of the survey, the kitchen was in fair to poor condition. The cabinets and equipment are showing signs of general wear and tear and are approaching the end of their expected life. This project recommends the replacement of the existing kitchen cabinets, countertops, fixtures and equipment with mid-range, high quality components. This project or a portion thereof was previously recommended in the FCA report dated 09/23/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | BDSP PARK RESIDENCE | 9948 | CNR | Parks |  | Beaver Dam | 1964 | 588 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35000
0997EXT1 | EXTERIOR FINISHES | 0997 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting, and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BDSP PARK RESIDENCE | 9948 | CNR | Parks |  | Beaver Dam | 1964 | 588 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5880
0997SFT1 | SMOKE ALARM INSTALLATION | 0997 | IRC 2018 Section R314 and R315.3 explains the requirements for smoke alarms in dwelling units. This includes: installing and maintaining smoke alarms in each sleeping room; having a carbon monoxide and smoke detector on the ceiling or wall outside of each sleeping area; in the immediate vicinity of bedrooms when an alteration, repair or addition requiring a permit occurs. IRC 2018 requires that smoke detectors and carbon monoxide alarms be UL rated. State Fire Marshal NAC 477.915 (3) requires that smoke detectors be connected to the wiring in a building and include a battery for emergency backup power. This project would provide funding for the purchase and installation of smoke alarms and carbon monoxide alarms in accordance with IRC and NAC laws. This project or a portion thereof was previously recommended in the FCA report dated 09/23/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | BDSP PARK RESIDENCE | 9948 | CNR | Parks |  | Beaver Dam | 1964 | 588 | 2017-04-05 | Immediate to Two Years | Currently Critical | 1 | 500
1060EXT1 | EXTERIOR FINISHES | 1060 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof. This shall include sealing or other applied finishes, caulking around flashing, fixtures, and other penetrations to keep the building in a weather tight condition. It is recommended that this project be implemented in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | CCC WATER TOWER | 9947 | CNR | Parks |  | Cathedral Gorge | 1934 | 59 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
0997ENV1 | PEST CONTROL | 0997 | There are numerous rodent droppings throughout this building. Due to the potential risk of disease, this project provides for treatment and cleanup of the rodent droppings by a licensed pest control business. | BDSP PARK RESIDENCE | 9948 | CNR | Parks |  | Beaver Dam | 1964 | 588 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
1039EXT2 | ROOF REPLACEMENT | 1039 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. | COMFORT STATION #4 - CAMPGROUND | 9947 | CNR | Parks |  | Cathedral Gorge | 1971 | 308 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4520
1038INT1 | INTERIOR FINISHES | 1038 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and every 5-6 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | MILLER'S POINT COMFORT STATION #3 | 9947 | CNR | Parks |  | Cathedral Gorge | 1996 | 120 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1200
1060EXT2 | ROOF REPLACEMENT | 1060 | The standing seam metal roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new single-ply roofing system which will be installed directly over the existing metal roof. This will allow the roof to qualify for the statewide roofing program warranty and preventative maintenance agreement. | CCC WATER TOWER | 9947 | CNR | Parks |  | Cathedral Gorge | 1934 | 59 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 13650
0997SFT2 | FLUE DISTANCES | 0997 | There is a water heater flue in the building that does not comply with UMC 2018 chapter 8, chimneys and vents. The flue is close to combustibles and does not have the proper clearances per UMC 2018. This is a fire hazard. It is recommended that the flue in the building meet the proper clearances per UMC 2018 and the manufacture’s specifications. The flue should be installed by a licensed contractor. | BDSP PARK RESIDENCE | 9948 | CNR | Parks |  | Beaver Dam | 1964 | 588 | 2017-04-05 | Immediate to Two Years | Currently Critical | 1 | 2000
0997ELE1 | WIRING CLEANUP | 0997 | The wiring in the residence is disorganized and not in proper electrical boxes and cover plates. This creates a safety issue. This project would provide for electrical wiring to be placed in the proper boxes and for cover plates to be installed per NEC 2011. | BDSP PARK RESIDENCE | 9948 | CNR | Parks |  | Beaver Dam | 1964 | 588 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
1053EXT2 | HISTORIC BUILDING MAINTENANCE | 1053 | The wood structure is over 82 years old and there are numerous areas where the wood is splitting, warping and deteriorating. This is also an exhibit for the park and requires maintenance time to display the artifacts and maintain the signage. This project would provide for sealing the wood, replacing wood roof shingles as needed and maintaining the exhibit in a state of arrested decay. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MILLER'S POINT CCC RAMADA | 9947 | CNR | Parks |  | Cathedral Gorge | 1934 | 306 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4590
1040EXT3 | WINDOW REPLACEMENT | 1040 | The windows are original, double pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 6 units. Removal and disposal of the existing windows is included in this estimate. | MAINTENANCE OFFICE/ SHOP | 9947 | CNR | Parks |  | Cathedral Gorge | 1976 | 4400 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
1038EXT1 | EXTERIOR FINISHES | 1038 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof. This shall include sealing or other applied finishes, caulking around flashing, fixtures, and other penetrations to keep the building in a weather tight condition. It is recommended that this project be implemented in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | MILLER'S POINT COMFORT STATION #3 | 9947 | CNR | Parks |  | Cathedral Gorge | 1996 | 120 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1200
1040ADA3 | ADA PARKING SPACE | 1040 | The ADA provides for accessibility to sites and services for people with physical limitations. A concrete parking area and passenger loading area are necessary to comply with ADA requirements. This project would provide for a concrete van accessible ADA parking and loading space and walkway to the existing sidewalk. This will require regrading, installing P.C. concrete, striping, signage and any other necessary upgrades. The 2018 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | MAINTENANCE OFFICE/ SHOP | 9947 | CNR | Parks |  | Cathedral Gorge | 1976 | 4400 | 2017-04-05 | Immediate to Two Years | Currently Critical | 1 | 30000
1039INT2 | JANITORS CLOSET REPAIRS | 1039 | The mop sink in the Janitors Closet has several cracks in the concrete and is leaking. This could lead to mold growth if not addressed. This project would provide for a new fiberglass mop sink and FRP to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | COMFORT STATION #4 - CAMPGROUND | 9947 | CNR | Parks |  | Cathedral Gorge | 1971 | 308 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2800
1042EXT2 | HISTORIC BUILDING MAINTENANCE | 1042 | The wood structure is over 82 years old and there are numerous areas where the wood is splitting, warping and deteriorating. This is also an exhibit for the park and requires maintenance time to display the artifacts and maintain the signage. This project would provide for sealing the wood, replacing wood roof shingles as needed and maintaining the exhibit in a state of arrested decay. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CCC RAMADA | 9947 | CNR | Parks |  | Cathedral Gorge | 1934 | 595 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8925
1043EXT1 | EXTERIOR FINISHES | 1043 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting or staining of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | GROUP RAMADA #1 | 9947 | CNR | Parks |  | Cathedral Gorge | 1962 | 680 | 2017-04-05 | Four to Ten Years | Long-Term Needs | 3 | 6800
1043ADA1 | GROUP USE AREA IMPROVEMENTS | 1043 | The group use area is not ADA compliant. This area should be scheduled for improvements. Currently, the picnic tables under the Group Ramada #1 are not ADA complaint. 5% of the picnic tables are required to be in compliance per IBC 2018 and ICC ANSI-A117.1-2009. This project would provide for the purchase and installation of 1 new ADA accessible picnic table. | GROUP RAMADA #1 | 9947 | CNR | Parks |  | Cathedral Gorge | 1962 | 680 | 2017-04-05 | Immediate to Two Years | Currently Critical | 1 | 1000
1040SFT2 | EXIT SIGN AND EGRESS LIGHTING | 1040 | The building does not have emergency lighting and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC 2018 Chapter 10 was referenced for this project. | MAINTENANCE OFFICE/ SHOP | 9947 | CNR | Parks |  | Cathedral Gorge | 1976 | 4400 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 22000
1044SIT1 | CONCRETE SLAB-ON-GRADE INSTALLATION | 1044 | Group Ramada #2 has a dirt floor area underneath the structure. This project would provide for the installation of a concrete slab-on-grade, 3-1/2 inches thick, underneath the structure. Included in this estimate is a 3-1/2 inches thick concrete walkway from the parking area to the Ramada. 800 square feet of concrete was used to generate this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | GROUP RAMADA #2 | 9947 | CNR | Parks |  | Cathedral Gorge | 1962 | 680 | 2017-04-05 | Four to Ten Years | Long-Term Needs | 3 | 6400
1040PLM1 | WATER HEATER REPLACEMENT | 1040 | There is a 40 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | MAINTENANCE OFFICE/ SHOP | 9947 | CNR | Parks |  | Cathedral Gorge | 1976 | 4400 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2200
1054EXT1 | EXTERIOR FINISHES | 1054 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including sealing and caulking around, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 2-3 years and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | METAL STORAGE SHED #1 | 9947 | CNR | Parks |  | Cathedral Gorge | 1982 | 266 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2660
1055EXT1 | EXTERIOR FINISHES | 1055 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof. This shall include sealing or other applied finishes, caulking around flashing, fixtures, and other penetrations to keep the building in a weather tight condition. It is recommended that this project be implemented in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | WOOD STORAGE SHED #2 | 9947 | CNR | Parks |  | Cathedral Gorge | 1983 | 102 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5100
1056EXT2 | ROOF REPLACEMENT | 1056 | The wood shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayment. This estimate includes removal and disposal of the old roofing. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | WOOD STORAGE SHED #3 | 9947 | CNR | Parks |  | Cathedral Gorge | 1964 | 147 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2205
1056EXT1 | EXTERIOR FINISHES | 1056 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. Due to the current condition of the exterior, it is recommended that this project be implemented immediately and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | WOOD STORAGE SHED #3 | 9947 | CNR | Parks |  | Cathedral Gorge | 1964 | 147 | 2017-04-05 | Immediate to Two Years | Currently Critical | 1 | 1470
1057EXT1 | DEMOLISH BUILDING | 1057 | The metal storage shed is in extremely poor condition and the roof is damaged. This project would provide for the demolition of the structure including debris removal. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | METAL STORAGE SHED #4 | 9947 | CNR | Parks |  | Cathedral Gorge | 1980 | 261 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
1059EXT1 | EXTERIOR FINISHES | 1059 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof. This shall include sealing, painting, staining or other applied finishes, caulking around flashing, fixtures, and other penetrations to keep the building in a weather tight condition. It is recommended that this project be implemented in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | PARK RESIDENCE | 9947 | CNR | Parks |  | Cathedral Gorge | 1990 | 910 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9100
1059INT1 | INTERIOR FINISHES | 1059 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and every 5-6 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | PARK RESIDENCE | 9947 | CNR | Parks |  | Cathedral Gorge | 1990 | 910 | 2017-04-05 | Four to Ten Years | Long-Term Needs | 3 | 9910
1059EXT2 | HANDRAIL & CONCRETE LANDING INSTALLATION | 1059 | The entry deck and stairs/ landing do not meet current code. This project would provide for a guardrail around the deck, guardrail and handrail at the stairs and a 4" thick concrete landing at the bottom of the stairs. The 2018 IBC Chapter 10, Section's 1009.4, 1012 and 1013 were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | PARK RESIDENCE | 9947 | CNR | Parks |  | Cathedral Gorge | 1990 | 910 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
1044EXT1 | EXTERIOR FINISHES | 1044 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting or staining of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | GROUP RAMADA #2 | 9947 | CNR | Parks |  | Cathedral Gorge | 1962 | 680 | 2017-04-05 | Four to Ten Years | Long-Term Needs | 3 | 6800
1039ADA2 | ADA SIGNAGE | 1039 | ADA regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with these criteria. It is recommended that applicable signage be installed where required. The 2018 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | COMFORT STATION #4 - CAMPGROUND | 9947 | CNR | Parks |  | Cathedral Gorge | 1971 | 308 | 2017-04-05 | Immediate to Two Years | Currently Critical | 1 | 900
1039HVA1 | ELECTRIC HEATER REPLACEMENT | 1039 | There are two electric heaters in the building that have reached the end of their expected life. This project recommends replacing the electric heaters. The estimate includes removal and disposal of the existing equipment. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | COMFORT STATION #4 - CAMPGROUND | 9947 | CNR | Parks |  | Cathedral Gorge | 1971 | 308 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4400
1039ADA3 | ADA SIDEWALK REPAIR | 1039 | The ADA provides for accessibility to sites and services for people with physical limitations. The concrete sidewalk around the building does not meet ADA requirements and is in need of replacement. Settling, spalling and cracking have created a non-ADA compliant path of travel to the restrooms. This project would provide for the removal and replacement of the concrete sidewalk. 500 SF of 4" thick P.C. concrete sidewalk was used for this estimate. IBC 2018, ICC/ANSI A117.1- 2009 and ADAAG - 2010 were referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | COMFORT STATION #4 - CAMPGROUND | 9947 | CNR | Parks |  | Cathedral Gorge | 1971 | 308 | 2017-04-05 | Immediate to Two Years | Currently Critical | 1 | 7500
1039ADA1 | ADA RESTROOM UPGRADE | 1039 | The building does not have an accessible restroom. The existing restroom does not meet the ADA requirements. A complete retrofit is necessary. This project would provide funding for remodeling the Men's and Women's restrooms per ADA regulations. Items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2018 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | COMFORT STATION #4 - CAMPGROUND | 9947 | CNR | Parks |  | Cathedral Gorge | 1971 | 308 | 2017-04-05 | Immediate to Two Years | Currently Critical | 1 | 40000
1039INT1 | INTERIOR FINISHES | 1039 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and every 5-6 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | COMFORT STATION #4 - CAMPGROUND | 9947 | CNR | Parks |  | Cathedral Gorge | 1971 | 308 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3080
1040ENR1 | LIGHTING UPGRADE | 1040 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | MAINTENANCE OFFICE/ SHOP | 9947 | CNR | Parks |  | Cathedral Gorge | 1976 | 4400 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35200
1039ENR1 | LIGHTING UPGRADE | 1039 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | COMFORT STATION #4 - CAMPGROUND | 9947 | CNR | Parks |  | Cathedral Gorge | 1971 | 308 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2464
1040ADA4 | BREAK ROOM REMODEL | 1040 | The kitchenette and associated cabinets in the employee break room are original to the building. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and countertops are delaminating and failing. This project recommends the replacement of the existing kitchen countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2018, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards for Accessible Design should be incorporated into the design such as providing an accessible sink. This estimate includes the removal and the disposal of the existing materials. | MAINTENANCE OFFICE/ SHOP | 9947 | CNR | Parks |  | Cathedral Gorge | 1976 | 4400 | 2017-04-05 | Immediate to Two Years | Currently Critical | 1 | 15000
1060SIT2 | SITE DRAINAGE UPGRADES | 1060 | The grade does not slope away effectively from the buildings. This allows water to pool against the skirting. In the winter months, as the water freezes against the skirting, and over time, this can cause damage. It is recommended per IBC 1804.3 Site Grading that the ground immediately adjacent to the foundation shall be sloped away from the building at a slope of not less than one vertical in 20 units horizontal (5-percent slope) for a minimum distance of 10 feet (3048 mm) measured perpendicular to the face of the wall. This project would create a 5% slope away from the buildings. Additional drainage swales shall be installed, as needed. It is recommended that the grading be completed within 2-3 years. | CCC WATER TOWER | 9947 | CNR | Parks |  | Cathedral Gorge | 1934 | 59 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
1060INT1 | FLOORING REPLACEMENT | 1060 | The linoleum and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for the removal and the disposal of the existing flooring and the installation of new linoleum with a 6"cove base and a heavy duty commercial grade carpet. | CCC WATER TOWER | 9947 | CNR | Parks |  | Cathedral Gorge | 1934 | 59 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7280
1040EXT2 | OVERHEAD DOOR REPLACEMENT | 1040 | There are two 10'x12' overhead coiling doors which are damaged and do not function properly. Exposure and wind have caused the doors to bend, crack and lose their finish. They are original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead coiling doors and replacement with new manually operated overhead coiling doors. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | MAINTENANCE OFFICE/ SHOP | 9947 | CNR | Parks |  | Cathedral Gorge | 1976 | 4400 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
1039EXT1 | EXTERIOR FINISHES | 1039 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 2- 3 years and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | COMFORT STATION #4 - CAMPGROUND | 9947 | CNR | Parks |  | Cathedral Gorge | 1971 | 308 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3080
1040SFT3 | SAFETY CABINETS | 1040 | The building contains many different paints, stains, and other hazardous products located on open shelves and on the floor. This does not meet OSHA standards or IFC for hazardous materials containment. This project would provide for two self-closing hazardous storage containers in the building and install placards on the building exterior in accordance with OSHA 1910.106 (d) and IFC Chapter 57 Section 5704.3.2.1.3. | MAINTENANCE OFFICE/ SHOP | 9947 | CNR | Parks |  | Cathedral Gorge | 1976 | 4400 | 2017-04-05 | Immediate to Two Years | Currently Critical | 1 | 10000
1040SFT4 | BATTERY STORAGE | 1040 | Section 608 of the 2018 IFC explains the requirements for stationary storage of battery systems. This project will provide funding for the proper way to store, charge and/or use batteries indoors. IFC Section 608 states batteries shall have safety caps, spill control and neutralization, mechanical ventilation and/or cabinet ventilation, supervision over the mechanical ventilation, building or cabinet signage, seismically braced, and a smoke alarm. This project would provide funding for the requirement of Section 608 of the 2018 IFC. | MAINTENANCE OFFICE/ SHOP | 9947 | CNR | Parks |  | Cathedral Gorge | 1976 | 4400 | 2017-04-05 | Immediate to Two Years | Currently Critical | 1 | 25000
1040HVA1 | HVAC EQUIPMENT REPLACEMENT | 1040 | The HVAC systems are original to the building and should be scheduled for replacement. They are not energy efficient and have reached the end of their expected and useful life. The R-22 refrigerant in the cooling systems are no longer EPA complaint and its production is mandated to be phased out completely by January 1, 2020. This project would provide for installation of a new HVAC systems and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC systems and all required connections to utilities. | MAINTENANCE OFFICE/ SHOP | 9947 | CNR | Parks |  | Cathedral Gorge | 1976 | 4400 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 60000
1040EXT1 | EXTERIOR FINISHES | 1040 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof. This shall include sealing or other applied finishes, caulking around flashing, fixtures, and other penetrations to keep the building in a weather tight condition. It is recommended that this project be implemented in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | MAINTENANCE OFFICE/ SHOP | 9947 | CNR | Parks |  | Cathedral Gorge | 1976 | 4400 | 2017-04-05 | Four to Ten Years | Long-Term Needs | 3 | 44000
1040INT1 | INTERIOR FINISHES | 1040 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and every 5-6 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | MAINTENANCE OFFICE/ SHOP | 9947 | CNR | Parks |  | Cathedral Gorge | 1976 | 4400 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 44000
1040ADA1 | ADA RESTROOM UPGRADE | 1040 | The building does not have an accessible restroom. The existing restroom does not meet the ADA requirements. A complete retrofit is necessary. This project would provide funding for remodeling the Men's and Women's restrooms per ADA regulations. Items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2018 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | MAINTENANCE OFFICE/ SHOP | 9947 | CNR | Parks |  | Cathedral Gorge | 1976 | 4400 | 2017-04-05 | Immediate to Two Years | Currently Critical | 1 | 40000
1060SIT1 | SITE BOLLARDS | 1060 | The Park Residence utilizes a propane tank for the home. The above ground propane tank requires bollards for protection from vehicle impact per IFC 2018. This project would provide for the purchase and installation of 6 - 8" concrete filled steel bollards to protect the propane tank. | CCC WATER TOWER | 9947 | CNR | Parks |  | Cathedral Gorge | 1934 | 59 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
2939INT1 | INTERIOR FINISHES | 2939 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and every 5-6 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | WOOD SHOP | 9947 | CNR | Parks |  | Cathedral Gorge | 2002 | 1200 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
2936ENR1 | LIGHTING UPGRADE | 2936 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | COMFORT STATION #5 - GROUP USE | 9947 | CNR | Parks |  | Cathedral Gorge | 2003 | 1024 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8192
2939EXT1 | EXTERIOR FINISHES | 2939 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof. This shall include sealing or other applied finishes, caulking around flashing, fixtures, and other penetrations to keep the building in a weather tight condition. It is recommended that this project be implemented in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | WOOD SHOP | 9947 | CNR | Parks |  | Cathedral Gorge | 2002 | 1200 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
2256EXT1 | EXTERIOR/ INTERIOR FINISHES | 2256 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. Epoxy paint is recommended on the interior precast concrete. It is recommended to seal and caulk the building in the next 2-3 years. This project should be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | CCC DAY USE CXT COMFORT STATION | 9947 | CNR | Parks |  | Cathedral Gorge | 2002 | 100 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
2255SIT1 | PARKING LOT STRIPING | 2255 | It is important to maintain the striping on the pavement at the site. This project would provide for the necessary striping and painting of the curbs and parking spaces. An ADA parking and loading space emblem will be painted on the concrete that is designated for ADA parking. This project should be scheduled on a 2 year cyclical basis to maintain the integrity of the striping, painting, and ADA designation. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180, and the most current version of the ADA Standards for Accessible Design were used as references for this project. | BDSP ADA CXT TOILET #3 - LOOP B | 9948 | CNR | Parks |  | Beaver Dam | 2002 | 95 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
2255EXT2 | EXTERIOR/ INTERIOR FINISHES | 2255 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing of the precast concrete, and caulking of the windows, flashing, fixtures and all other penetrations. Epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 4-5 years and for this project to be scheduled on a cyclical basis to maintain the integrity of the structure. | BDSP ADA CXT TOILET #3 - LOOP B | 9948 | CNR | Parks |  | Beaver Dam | 2002 | 95 | 2017-04-05 | Four to Ten Years | Long-Term Needs | 3 | 1900
2254EXT2 | EXTERIOR/ INTERIOR FINISHES | 2254 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing of the precast concrete, and caulking of the windows, flashing, fixtures and all other penetrations. Epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 4-5 years and for this project to be scheduled on a cyclical basis to maintain the integrity of the structure. | BDSP CXT TOILET #2 - LOOP B | 9948 | CNR | Parks |  | Beaver Dam | 2002 | 95 | 2017-04-05 | Four to Ten Years | Long-Term Needs | 3 | 1900
2254ADA1 | ADA ACCESSIBLE PATH OF TRAVEL | 2254 | The ADA provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area, and path of travel to the office are necessary to comply with ADA accessibility requirements. This project would provide for a concrete van accessible ADA parking, loading space, and concrete walkway to the existing sidewalk. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. 750 square feet of concrete was used for this estimate. | BDSP CXT TOILET #2 - LOOP B | 9948 | CNR | Parks |  | Beaver Dam | 2002 | 95 | 2017-04-05 | Immediate to Two Years | Currently Critical | 1 | 30000
2936INT2 | JANITORS CLOSET REPAIRS | 2936 | The mop sink in the plumbing chase is mounted adjacent to CMU walls and is showing signs of water damage. This project would provide FRP to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | COMFORT STATION #5 - GROUP USE | 9947 | CNR | Parks |  | Cathedral Gorge | 2003 | 1024 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
2936PLM1 | WATER HEATER REPLACEMENT | 2936 | There is a 50 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. The removal and disposal of the existing equipment is included in this estimate. | COMFORT STATION #5 - GROUP USE | 9947 | CNR | Parks |  | Cathedral Gorge | 2003 | 1024 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
2939ENV1 | DUST COLLECTION SYSTEM REPLACEMENT | 2939 | The building has a woodshop which has an inoperative dust collection system. The existing exhaust fan is undersized for the equipment being used. This project recommends the replacement of the dust collection system with a higher capacity system, including the fan, motor and ducting to each piece of equipment. | WOOD SHOP | 9947 | CNR | Parks |  | Cathedral Gorge | 2002 | 1200 | 2017-04-05 | Immediate to Two Years | Currently Critical | 1 | 20000
2939SIT1 | SITE DRAINAGE UPGRADES | 2939 | The grade does not slope away effectively from the buildings. This allows water to pool against the foundation. In the winter months, the water freezes against the foundation, and over time, this can cause damage to the foundation. It is recommended per IBC 1804.3 Site Grading that the ground immediately adjacent to the foundation shall be sloped away from the building at a slope of not less than one vertical in 20 units horizontal (5-percent slope) for a minimum distance of 10 feet (3048 mm) measured perpendicular to the face of the wall. This project would create a 5% slope away from the buildings. Additional drainage swales shall be installed, as needed. It is recommended that the grading be completed within 2-3 years. | WOOD SHOP | 9947 | CNR | Parks |  | Cathedral Gorge | 2002 | 1200 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
2939EXT2 | EXTERIOR DOOR REPLACEMENT | 2939 | The exterior metal doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the south double door assembly and the north single door assembly with new metal doors, frames and hardware. The removal and disposal of the existing doors is included in this estimate. | WOOD SHOP | 9947 | CNR | Parks |  | Cathedral Gorge | 2002 | 1200 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
2939ADA1 | ADA RESTROOM UPGRADE | 2939 | The building does not have an accessible restroom. The existing restroom does not meet the ADA requirements. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom. Items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2018 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | WOOD SHOP | 9947 | CNR | Parks |  | Cathedral Gorge | 2002 | 1200 | 2017-04-05 | Immediate to Two Years | Currently Critical | 1 | 15000
2939ENR1 | LIGHTING UPGRADE | 2939 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | WOOD SHOP | 9947 | CNR | Parks |  | Cathedral Gorge | 2002 | 1200 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9600
2936INT1 | INTERIOR FINISHES | 2936 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and every 5-6 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | COMFORT STATION #5 - GROUP USE | 9947 | CNR | Parks |  | Cathedral Gorge | 2003 | 1024 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10240
2253EXT2 | EXTERIOR/ INTERIOR FINISHES | 2253 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing of the precast concrete, and caulking of the windows, flashing, fixtures and all other penetrations. Epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 4-5 years and for this project to be scheduled on a cyclical basis to maintain the integrity of the structure. | BDSP ADA CXT TOILET #1 - LOOP A | 9948 | CNR | Parks |  | Beaver Dam | 2002 | 95 | 2017-04-05 | Four to Ten Years | Long-Term Needs | 3 | 1900
2941ENR1 | LIGHTING UPGRADE | 2941 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | RESIDENCE SHED #5 | 9947 | CNR | Parks |  | Cathedral Gorge | 2004 | 280 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3360
2936EXT1 | EXTERIOR FINISHES | 2936 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof. This shall include sealing or other applied finishes, caulking around flashing, fixtures, and other penetrations to keep the building in a weather tight condition. It is recommended that this project be implemented in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | COMFORT STATION #5 - GROUP USE | 9947 | CNR | Parks |  | Cathedral Gorge | 2003 | 1024 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10240
2941EXT1 | EXTERIOR FINISHES | 2941 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof. This shall include sealing or other applied finishes, caulking around flashing, fixtures, and other penetrations to keep the building in a weather tight condition. It is recommended that this project be implemented in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | RESIDENCE SHED #5 | 9947 | CNR | Parks |  | Cathedral Gorge | 2004 | 280 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2800
9947SIT1 | SLURRY SEAL ASPHALT PAVING | 9947 | It is important to maintain the asphalt cement paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site wide including access roads, parking areas and the maintenance yard. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 172,500 square feet of asphalt area was used to generate this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | CATHEDRAL GORGE STATE PARK SITE | 9947 | CNR | Parks |  | Cathedral Gorge |  |  | 2017-04-05 | Four to Ten Years | Long-Term Needs | 3 | 129375
9947EXT3 | EXTERIOR HANDRAIL INSTALLATION | 9947 | At the Miller Point Overlook, there are no sidewalks or handrails. This is creating a safety hazard due to erosion. This project recommends for the installation of erosion control, new handrails, sidewalks, ramps and for the proper returns and supports to be installed. The 2018 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | CATHEDRAL GORGE STATE PARK SITE | 9947 | CNR | Parks |  | Cathedral Gorge |  |  | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500000
3085EXT1 | EXTERIOR FINISHES | 3085 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing of the brick masonry, and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BDSP SPRING HOUSE | 9948 | CNR | Parks |  | Beaver Dam | 1996 | 72 | 2017-04-05 | Four to Ten Years | Long-Term Needs | 3 | 360
9948SFT1 | BRIDGE GUARDRAIL REPLACEMENT | 9948 | The park has an interpretive trail that crosses over the creek by a bridge. The guardrail for the bridge does not meet current code. Section 1013.3 of the 2018 IBC states that open guardrails shall have balusters or ornamental patterns such that a 4-inch-diameter (102 mm) sphere cannot pass through any opening up to a height of 34 inches (864 mm). This project would provide for the installation of a compliant guardrail for the bridge from a height of 34 inches (864 mm) to 42 inches (1067 mm) above the adjacent walking surfaces. This project or a portion thereof was previously recommended in the FCA report dated 04/11/2002 and 09/23/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | BEAVER DAM STATE PARK SITE | 9948 | CNR | Parks |  | Beaver Dam |  |  | 2017-04-05 | Immediate to Two Years | Currently Critical | 1 | 1000
9947EXT1 | EXTERIOR FINISHES, SHADE RAMADAS | 9947 | There are 28 steel shade ramadas in different locations throughout the site which are 151 s.f. each for a total of 4,228 square feet. It is important to maintain the finish, weather resistance and appearance of the structures. This project would provide for painting of the structures and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structures. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | CATHEDRAL GORGE STATE PARK SITE | 9947 | CNR | Parks |  | Cathedral Gorge |  |  | 2017-04-05 | Four to Ten Years | Long-Term Needs | 3 | 8456
0273PLM1 | WATER HEATER REPLACEMENT | 0273 | The average life span of a water heater is eight to ten years. The two existing 10 gallon propane fired water heaters in the building have reached the end of their expected life and are not energy efficient. This project would provide for the removal and disposal of the old water heaters and installation of two new 10 gallon propane fired water heaters. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | REGIONAL INFORMATION CENTER | 9947 | CNR | Parks |  | Cathedral Gorge | 1996 | 1200 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
0273HVA2 | HVAC EQUIPMENT REPLACEMENT | 0273 | The HVAC system is original to the building and should be scheduled for replacement. It is not energy efficient and has reached the end of its expected and useful life. The R-22 refrigerant in the cooling system is no longer EPA complaint and its production is mandated to be phased out completely by January 1, 2020. This project would provide for installation of a new HVAC system and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC system and all required connections to utilities. | REGIONAL INFORMATION CENTER | 9947 | CNR | Parks |  | Cathedral Gorge | 1996 | 1200 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0273SFT1 | EXIT SIGN UPGRADE | 0273 | The existing exit signs in this building are older types and should be replaced with new self-illuminated or LED style signs with battery-backed internal systems. IBC - 2018 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | REGIONAL INFORMATION CENTER | 9947 | CNR | Parks |  | Cathedral Gorge | 1996 | 1200 | 2017-04-05 | Immediate to Two Years | Currently Critical | 1 | 900
0273EXT1 | EXTERIOR FINISHES | 0273 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof. This shall include sealing or other applied finishes, caulking around flashing, fixtures, and other penetrations to keep the building in a weather tight condition. It is recommended that this project be implemented in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | REGIONAL INFORMATION CENTER | 9947 | CNR | Parks |  | Cathedral Gorge | 1996 | 1200 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
0273HVA3 | AIR CONDITIONER INSTALLATION | 0273 | The theater room is not sufficiently cooled by the existing HVAC system. It is recommended to install an air conditioning system in the theater room to ensure that the temperature is properly regulated. This project would provide for the purchase and installation of an air conditioner including all required connections to existing utilities. | REGIONAL INFORMATION CENTER | 9947 | CNR | Parks |  | Cathedral Gorge | 1996 | 1200 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0273SIT1 | CONCRETE REPLACEMENT | 0273 | The concrete patio at the entrance to the building does not drain properly and is showing signs of failure. It is important to maintain positive drainage away from the building to protect it from moisture penetration. The existing concrete is also settling and cracking and should be scheduled for replacement. This project would provide for replacing approximately 1,500 square feet of concrete including removal and disposal of the existing concrete. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | REGIONAL INFORMATION CENTER | 9947 | CNR | Parks |  | Cathedral Gorge | 1996 | 1200 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0273HVA4 | EXHAUST FAN REPLACEMENT | 0273 | Many of the exhaust fans in the restrooms and shower areas were inoperative and/or damaged at the time of the survey. Due to building code requirements and excessive humidity concerns, this project would provide funding for the purchase and installation of high volume commercial exhaust fans. | REGIONAL INFORMATION CENTER | 9947 | CNR | Parks |  | Cathedral Gorge | 1996 | 1200 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0273ADA4 | ADA ACCESSIBLE COUNTER | 0273 | The plastic laminate countertop in the gift shop is not ADA compliant. This project would provide funding for the removal of the existing countertop and installation of a new plastic laminate countertop. Section 904.4 of the ADA Standards for Accessible Design states that a portion of the counter surface that is 36" long minimum and 36" high maximum above the finish floor shall be provided. This project will provide an accessible counter space in accordance with this requirement. The 2018 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | REGIONAL INFORMATION CENTER | 9947 | CNR | Parks |  | Cathedral Gorge | 1996 | 1200 | 2017-04-05 | Immediate to Two Years | Currently Critical | 1 | 12750
0273ADA1 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0273 | This building contains a water fountain that is not ADA compliant. The 2018 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | REGIONAL INFORMATION CENTER | 9947 | CNR | Parks |  | Cathedral Gorge | 1996 | 1200 | 2017-04-05 | Immediate to Two Years | Currently Critical | 1 | 2000
0273SFT2 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 0273 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | REGIONAL INFORMATION CENTER | 9947 | CNR | Parks |  | Cathedral Gorge | 1996 | 1200 | 2017-04-05 | Immediate to Two Years | Currently Critical | 1 | 9000
0273HVA1 | ELECTRIC HEATER REPLACEMENT | 0273 | There are six electric heaters in the building that have reached the end of their expected life. This project recommends replacing the electric heaters. The estimate includes removal and disposal of the existing equipment. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | REGIONAL INFORMATION CENTER | 9947 | CNR | Parks |  | Cathedral Gorge | 1996 | 1200 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
0273ADA3 | ADA DOOR HARDWARE | 0273 | The two exterior entrance doors are on an accessible path of travel, but the door hardware and threshold are not compliant. This project would provide for ADA compliant door hardware and threshold on the exterior door. ADA complaint signage is also included in this project. ADAAG Guidelines - 2010 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | REGIONAL INFORMATION CENTER | 9947 | CNR | Parks |  | Cathedral Gorge | 1996 | 1200 | 2017-04-05 | Immediate to Two Years | Currently Critical | 1 | 2800
0273ADA2 | ADA SIGNAGE | 0273 | The building is lacking ADA signage. ADA regulations pertaining to building access, route of travel and restrooms have established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances, route of travel inside the building and restrooms. ADAAG Guidelines - 2010 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | REGIONAL INFORMATION CENTER | 9947 | CNR | Parks |  | Cathedral Gorge | 1996 | 1200 | 2017-04-05 | Immediate to Two Years | Currently Critical | 1 | 2000
0466EXT2 | EXTERIOR FINISHES | 0466 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting, and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BDSP SHADE RAMADA - LOOP B | 9948 | CNR | Parks |  | Beaver Dam | 1964 | 310 | 2017-04-05 | Four to Ten Years | Long-Term Needs | 3 | 3100
0459EXT1 | COMFORT STATION REPLACEMENT | 0459 | The Out House was built in 1964 and has not been in use for over 12 years. The building is dilapidated, deteriorating, and has reached the end of its useful life. It has also been identified by State Health as problematic due to the infiltration of human waste into the local sub soils and ultimately, the local water table. This project would provide funding for the demolition of the building and replacement with a new CXT unit. The estimate includes hazardous waste remediation in compliance with all local, state, and federal health codes. This project or a portion thereof was previously recommended in the FCA report dated 09/23/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | BDSP OUT HOUSE | 9948 | CNR | Parks |  | Beaver Dam | 1964 | 140 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0460EXT1 | EXTERIOR FINISHES | 0460 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is cleaning and sealing of the concrete masonry unit walls, painting the wood siding and eaves, and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted, and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/23/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | BDSP GENERATOR BUILDING | 9948 | CNR | Parks |  | Beaver Dam | 1980 | 64 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 640
0460EXT2 | EXTERIOR DOOR REPLACEMENT | 0460 | The exterior metal door is damaged from age, general wear and tear, and has reached the end of its expected life. This project would provide for the replacement of the door assembly with a new metal door, frame and hardware. Removal and disposal of the existing door is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/23/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | BDSP GENERATOR BUILDING | 9948 | CNR | Parks |  | Beaver Dam | 1980 | 64 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
0460EXT3 | ROOF REPLACEMENT | 0460 | The asphalt roof on the building was in poor condition and had active leaks at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new single-ply roofing system. This will allow for the roof to qualify for the statewide roofing warranty and preventative maintenance agreement programs. | BDSP GENERATOR BUILDING | 9948 | CNR | Parks |  | Beaver Dam | 1980 | 64 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 960
0460EXT4 | WINDOW REPLACEMENT | 0460 | The window is original, single pane construction in metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the window with a dual pane, higher efficiency unit. This estimate is for the replacement of 1 unit. Removal and disposal of the existing window is included in this estimate. | BDSP GENERATOR BUILDING | 9948 | CNR | Parks |  | Beaver Dam | 1980 | 64 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 750
0460SFT1 | EXTERIOR LANDING INSTALLATION | 0460 | Section 1008.1 of the 2012 IBC describes the requirements for doors including floor elevations and landings. The floor or landing shall be at the same elevation on each side of the door; the exterior landing shall not exceed a 2% slope and shall have a length measured in the direction of travel of not less than 44 inches. The landing for the door does not comply with this code and poses a safety hazard. This project would provide for the installation of a compliant landing for the door. | BDSP GENERATOR BUILDING | 9948 | CNR | Parks |  | Beaver Dam | 1980 | 64 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0465EXT1 | EXTERIOR FINISHES | 0465 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting of the wood framing and eaves, and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/23/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | BDSP PUMP HOUSE | 9948 | CNR | Parks |  | Beaver Dam | 1970 | 42 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 420
0465SIT1 | SITE DRAINAGE UPGRADES | 0465 | The grade does not slope away effectively from the building. Water has pooled against the foundation. In the winter months, as the water freezes against the foundation, over time, this can cause damage to the foundation. It is recommended per IBC 1804.3 Site Grading the ground immediately adjacent to the foundation shall be sloped away from the building at a slope of not less than one vertical in 20 units horizontal (5-percent slope) for a minimum distance of 10 feet (3048 mm) measured perpendicular to the face of the wall. This project would create a 5% slope away from the buildings. Additional drainage swales shall be installed, as needed. It is recommended that the grading be completed within 2-3 years. | BDSP PUMP HOUSE | 9948 | CNR | Parks |  | Beaver Dam | 1970 | 42 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0506EXT2 | DEMOLISH STRUCTURE | 0506 | The building is an old storage shed that is no longer in use and is severely damaged. It is recommended that this structure be demolished and for the pit below to be filled-in, per the guidelines of the Nevada State Division of Environmental Protection and any local requirements. | BDSP STORAGE SHED | 9948 | CNR | Parks |  | Beaver Dam | 1995 | 192 | 2017-04-05 | Immediate to Two Years | Currently Critical | 1 | 500
0465EXT2 | ROOF REPLACEMENT | 0465 | The corrugated metal roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a standing seam metal roofing system. This estimate includes removal and disposal of the old roof. | BDSP PUMP HOUSE | 9948 | CNR | Parks |  | Beaver Dam | 1970 | 42 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 630
1284EXT1 | EXTERIOR FINISHES | 1284 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding and sealing, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be stained and painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | CAVE LAKE OFFICE/ SHOP | 9946 | CNR | Parks |  | Cave Lake | 1981 | 1360 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 13600
1280ELE1 | WIRING CLEANUP | 1280 | The wiring is disorganized and not in proper electrical boxes, particularly the old main service wires. This creates a safety issue during repairs or upgrades. This project would provide for organization, proper labeling and for the wiring to be placed in electrical boxes per NEC 2017. | RESTROOM #1 - LAKEVIEW CAMPGROUND | 9946 | CNR | Parks |  | Cave Lake | 1981 | 380 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
1288EXT1 | EXTERIOR FINISHES | 1288 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project should coincide with the siding replacement project. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | RESTROOM #2 - DAY USE | 9946 | CNR | Parks |  | Cave Lake | 1981 | 330 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3300
1284SFT3 | SMOKE CARBON MONOXIDE ALARM INSTALLATION | 1284 | Section 907.2.11 of the 2018 IBC and 2018 IFC explains the requirements for smoke alarms in dwelling units including installing and maintaining smoke alarms in each sleeping room and on the ceiling or wall outside of each separate sleeping area in the immediate vicinity of bedrooms. IFC 2018 Section 908.7 carbon monoxide alarms group I or R occupancies located in a building containing a fuel-burning appliance or in a building which has an attached garage shall be equipped with single-station carbon monoxide alarm. The carbon monoxide alarm shall be listed as complying with UL 2034 and be installed and maintained in accordance with NFPA 720 and the manufacturer’s instructions. State Fire Marshal NAC 477.915 (3) requires that smoke detectors and carbon monoxide alarms be connected to the wiring of the building with a battery backup. This project would provide funding for the purchase and installation of a smoke alarm and combo smoke alarm and carbon monoxide alarm in accordance with these codes. | CAVE LAKE OFFICE/ SHOP | 9946 | CNR | Parks |  | Cave Lake | 1981 | 1360 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
1284SFT4 | SAFETY CABINETS | 1284 | The building contains many different paints, stains, and other hazardous products located on open shelves and on the floor. This does not meet OSHA standards or IFC for hazardous materials containment. This project would provide a self-closing hazardous storage container in the building and install placards on the building exterior in accordance with OSHA 1910.106 (d) and IFC Chapter 57 Section 5704.3.2.1.3. | CAVE LAKE OFFICE/ SHOP | 9946 | CNR | Parks |  | Cave Lake | 1981 | 1360 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
1284SFT5 | FLUE CLEANING | 1284 | At the time of the survey the chimney flue had a buildup of creosote deposits and other debris. Creosote buildup in chimneys can lead to chimney fires or flue blockages. Flue blockage, which may be caused by creosote or other debris, such as animal nesting, can cause dangerous fumes to be forced into the building. It is recommended that the chimney flue be swept to clean and maintain the flue system. The Chimney Safety Institute of America recommends that open masonry fireplaces be cleaned at 1/4" of sooty buildup, and sooner if there is any glaze present in the system. Per NFPA 211 it is recommended that this should be performed once a year. | CAVE LAKE OFFICE/ SHOP | 9946 | CNR | Parks |  | Cave Lake | 1981 | 1360 | 2017-05-23 | Immediate to Two Years | Currently Critical | 1 | 2000
1284INT3 | JANITORS CLOSET REPAIRS | 1284 | The mop sink in the Janitors Closet is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide FRP to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | CAVE LAKE OFFICE/ SHOP | 9946 | CNR | Parks |  | Cave Lake | 1981 | 1360 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
1284ENR1 | LIGHTING UPGRADE | 1284 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | CAVE LAKE OFFICE/ SHOP | 9946 | CNR | Parks |  | Cave Lake | 1981 | 1360 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10880
1284SFT1 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 1284 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC 2018 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | CAVE LAKE OFFICE/ SHOP | 9946 | CNR | Parks |  | Cave Lake | 1981 | 1360 | 2017-05-23 | Immediate to Two Years | Currently Critical | 1 | 1360
1288ELE1 | WIRING CLEANUP | 1288 | The wiring is disorganized and not in proper electrical boxes. This creates a safety issue during repairs or upgrades. This project would provide for organization, proper labeling and for the wiring to be placed in electrical boxes per NEC 2017. | RESTROOM #2 - DAY USE | 9946 | CNR | Parks |  | Cave Lake | 1981 | 330 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
1280EXT1 | EXTERIOR FINISHES | 1280 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | RESTROOM #1 - LAKEVIEW CAMPGROUND | 9946 | CNR | Parks |  | Cave Lake | 1981 | 380 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3800
1284INT1 | INTERIOR FINISHES | 1284 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and adequately prepared to receive the coating. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | CAVE LAKE OFFICE/ SHOP | 9946 | CNR | Parks |  | Cave Lake | 1981 | 1360 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 13600
1294INT2 | KITCHEN REMODEL | 1294 | The kitchen was is in fair to poor condition at the time of the survey. The cabinets and equipment are showing signs of general wear and tear and are approaching the end of their expected life. This project recommends the replacement of the existing kitchen cabinets, countertops, fixtures and equipment with mid-range, high quality components. | RESIDENCE #1 - LAKEVIEW | 9946 | CNR | Parks |  | Cave Lake | 1981 | 1200 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35000
1294INT1 | INTERIOR FINISHES | 1294 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | RESIDENCE #1 - LAKEVIEW | 9946 | CNR | Parks |  | Cave Lake | 1981 | 1200 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
1295SFT1 | SMOKE DETECTOR UPGRADE | 1295 | IRC 2018 Section R314 and R315.3 explains the requirements for smoke alarms in dwelling units. This includes: installing and maintaining smoke alarms in each sleeping room; having a carbon monoxide and smoke detector on the ceiling or wall outside of each sleeping area; in the immediate vicinity of bedrooms when an alteration, repair or addition requiring a permit occurs. IRC 2018, requires that smoke detectors and carbon monoxide alarms be UL rated. State Fire Marshal NAC 477.915 (3) requires that smoke detectors be connected to the wiring in a building and include a battery for emergency backup power. This project would provide funding for the purchase and installation of smoke alarms and carbon monoxide alarms in accordance with IRC and NAC laws. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | RESIDENCE #2 - ELK FLAT | 9946 | CNR | Parks |  | Cave Lake | 1991 | 1008 | 2017-05-23 | Immediate to Two Years | Currently Critical | 1 | 2500
1295ENR1 | GENERATOR REPLACEMENT | 1295 | There is a propane-fired generator on site that has reached the end of its expected life and is no longer operating. The generator provides backup power when the photovoltaic system cannot keep up with demand. It is recommended that a new 12 kW propane-fired generator be installed. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | RESIDENCE #2 - ELK FLAT | 9946 | CNR | Parks |  | Cave Lake | 1991 | 1008 | 2017-05-23 | Immediate to Two Years | Currently Critical | 1 | 25000
1295INT1 | INTERIOR FINISHES | 1295 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next three to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | RESIDENCE #2 - ELK FLAT | 9946 | CNR | Parks |  | Cave Lake | 1991 | 1008 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10080
1295EXT1 | EXTERIOR FINISHES | 1295 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | RESIDENCE #2 - ELK FLAT | 9946 | CNR | Parks |  | Cave Lake | 1991 | 1008 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10080
1295EXT2 | ROOF REPLACEMENT | 1295 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next two to three years with a new 50 year asphalt composition shingle roof and new underlayment. This estimate includes removal and disposal of the old roof. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | RESIDENCE #2 - ELK FLAT | 9946 | CNR | Parks |  | Cave Lake | 1991 | 1008 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15120
1294HVA1 | HEATER REPLACEMENT | 1294 | The building is heated by one propane-fired furnace. It is original to the building and is reaching the end of its useful life. This project provides for disposal of the existing furnace and the replacement with a new propane-fired furnace to include the connections to the existing utilities and cleaning the ductwork. | RESIDENCE #1 - LAKEVIEW | 9946 | CNR | Parks |  | Cave Lake | 1981 | 1200 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
1280HVA1 | HEATER REPLACEMENT | 1280 | The building is heated by one wall mounted propane-fired heating unit. It is original to the building and is reaching the end of its useful life. This project provides for disposal of the existing unit and replacement with a new propane-fired unit including connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | RESTROOM #1 - LAKEVIEW CAMPGROUND | 9946 | CNR | Parks |  | Cave Lake | 1981 | 380 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
1294EXT2 | ROOF REPLACEMENT | 1294 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition shingle roof and new underlayment. This estimate includes removal and disposal of the old roof. | RESIDENCE #1 - LAKEVIEW | 9946 | CNR | Parks |  | Cave Lake | 1981 | 1200 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18000
1280SFT1 | FIRE EXTINGUISHER INSTALLATION | 1280 | The building does not have a portable fire extinguisher available. International Fire Code Section 906 requires that portable fire extinguishers shall be installed in B occupancies. They shall be provided for employee use and selected and distributed based on the classes of anticipated workplace fires and on the size and degree of hazard which would affect their use. This project would provide funding for the purchase and installation of 1 fire extinguisher, cabinet, and the hardware necessary to install it. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | RESTROOM #1 - LAKEVIEW CAMPGROUND | 9946 | CNR | Parks |  | Cave Lake | 1981 | 380 | 2017-05-23 | Immediate to Two Years | Currently Critical | 1 | 500
1280INT1 | INTERIOR FINISHES | 1280 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | RESTROOM #1 - LAKEVIEW CAMPGROUND | 9946 | CNR | Parks |  | Cave Lake | 1981 | 380 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3800
1284SIT1 | CONCRETE APRON REPLACEMENT | 1284 | The exterior concrete apron at the shop area has extensive cracking and spalling and is due for replacement. This project would provide for the installation of a new 200 square foot, 4" thick concrete slab-on-grade apron at the vehicle garage doors. Removal and disposal of the existing concrete is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | CAVE LAKE OFFICE/ SHOP | 9946 | CNR | Parks |  | Cave Lake | 1981 | 1360 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
1284PLM1 | WATER HEATER REPLACEMENT | 1284 | There is a 50 gallon propane-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new propane-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | CAVE LAKE OFFICE/ SHOP | 9946 | CNR | Parks |  | Cave Lake | 1981 | 1360 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1750
1284HVA1 | HEATER REPLACEMENT | 1284 | The building is heated by two wall mounted propane-fired heating units. They are original to the building and are reaching the end of their useful life. This project provides for the disposal of the existing units and the replacement of new propane-fired units including all connections to the utilities. | CAVE LAKE OFFICE/ SHOP | 9946 | CNR | Parks |  | Cave Lake | 1981 | 1360 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
1284SFT2 | FIRE ALARM SYSTEM INSTALLATION | 1284 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2009 Section 7 and the 2018 IFC. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | CAVE LAKE OFFICE/ SHOP | 9946 | CNR | Parks |  | Cave Lake | 1981 | 1360 | 2017-05-23 | Immediate to Two Years | Currently Critical | 1 | 5440
1294PLM1 | WATER HEATER REPLACEMENT | 1294 | There is a 50 gallon propane-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new propane-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | RESIDENCE #1 - LAKEVIEW | 9946 | CNR | Parks |  | Cave Lake | 1981 | 1200 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1750
1295ENR2 | WINDOW REPLACEMENT | 1295 | The windows are original, dual pane construction in a metal frame. These older windows have damaged seals, are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 8 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | RESIDENCE #2 - ELK FLAT | 9946 | CNR | Parks |  | Cave Lake | 1991 | 1008 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
1280PLM1 | WATER HEATER REPLACEMENT | 1280 | There is an on-demand propane-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new on-demand propane-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | RESTROOM #1 - LAKEVIEW CAMPGROUND | 9946 | CNR | Parks |  | Cave Lake | 1981 | 380 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
1289EXT1 | EXTERIOR FINISHES | 1289 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is replacing the wood trim around the building, sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the trim be replaced and the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | RESTROOM #3 - ELK FLAT | 9946 | CNR | Parks |  | Cave Lake | 1991 | 380 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3800
1288ADA1 | ADA SIDEWALK REPLACEMENT | 1288 | The concrete sidewalk around the building is in need of replacement. It is cracked, spalling and in some areas it exceeds a 2% slope. This project would provide for the removal and replacement of the concrete sidewalks. 1500 SF of 4" thick concrete was used for this estimate. The 2018 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | RESTROOM #2 - DAY USE | 9946 | CNR | Parks |  | Cave Lake | 1981 | 330 | 2017-05-23 | Immediate to Two Years | Currently Critical | 1 | 22500
1294SFT1 | SMOKE DETECTOR UPGRADE | 1294 | IRC 2018 Section R314 and R315.3 explains the requirements for smoke alarms in dwelling units. This includes: installing and maintaining smoke alarms in each sleeping room; having a carbon monoxide and smoke detector on the ceiling or wall outside of each sleeping area; in the immediate vicinity of bedrooms when an alteration, repair or addition requiring a permit occurs. IRC 2018 require that smoke detectors and carbon monoxide alarms be UL rated. State Fire Marshal NAC 477.915 (3) requires that smoke detectors be connected to the wiring in a building and include a battery for emergency backup power. This project would provide funding for the purchase and installation of smoke alarms and carbon monoxide alarms in accordance with IRC and NAC laws. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | RESIDENCE #1 - LAKEVIEW | 9946 | CNR | Parks |  | Cave Lake | 1981 | 1200 | 2017-05-23 | Immediate to Two Years | Currently Critical | 1 | 1000
1288INT1 | INTERIOR FINISHES | 1288 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | RESTROOM #2 - DAY USE | 9946 | CNR | Parks |  | Cave Lake | 1981 | 330 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3300
1288EXT2 | EXTERIOR SIDING REPLACEMENT | 1288 | The restroom has painted T1-11 siding that is in poor condition and due for replacement. It is cracking and buckling from exposure and will no longer hold paint. This project recommends removing the T1-11 siding and replacing it with new Cementitious T1-11. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | RESTROOM #2 - DAY USE | 9946 | CNR | Parks |  | Cave Lake | 1981 | 330 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1520
1288ENR1 | HEATER REPLACEMENT | 1288 | The building is heated by one wall mounted propane-fired heating unit. It is original to the building and is reaching the end of its useful life. This project provides for disposal of the existing unit and replacement with a new energy efficient propane-fired unit including connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | RESTROOM #2 - DAY USE | 9946 | CNR | Parks |  | Cave Lake | 1981 | 330 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
1289INT4 | RESTROOM REMODEL | 1289 | The restrooms in the building were in poor condition at the time of the survey. They are original to the building and are due for a complete remodel. This project would provide for a complete remodel of the restroom fixtures, hardware, floor and wall finishes. | RESTROOM #3 - ELK FLAT | 9946 | CNR | Parks |  | Cave Lake | 1991 | 380 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
1289PLM1 | WATER HEATER REPLACEMENT | 1289 | There is an on-demand propane-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new on-demand propane-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | RESTROOM #3 - ELK FLAT | 9946 | CNR | Parks |  | Cave Lake | 1991 | 380 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
1289EXT4 | EXTERIOR SIDING REPLACEMENT | 1289 | The restroom has painted T1-11 siding that is in poor condition and due for replacement. It is cracking and buckling from exposure and will no longer hold paint. This project recommends removing the T1-11 siding and replacing it with new Cementitious T1-11. | RESTROOM #3 - ELK FLAT | 9946 | CNR | Parks |  | Cave Lake | 1991 | 380 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1600
1289SFT1 | BATTERY STORAGE | 1289 | Section 608 of the 2018 IFC explains the requirements for stationary storage of battery systems. Batteries shall have safety caps, spill control and neutralization, mechanical ventilation and/or cabinet ventilation, supervision over the mechanical ventilation, building or cabinet signage, seismically braced and a smoke alarm. This project will provide funding for the requirements of Section 608 of the 2018 IFC proper way to store, charge and/or use batteries indoors. | RESTROOM #3 - ELK FLAT | 9946 | CNR | Parks |  | Cave Lake | 1991 | 380 | 2017-05-23 | Immediate to Two Years | Currently Critical | 1 | 25000
1294EXT1 | EXTERIOR FINISHES | 1294 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | RESIDENCE #1 - LAKEVIEW | 9946 | CNR | Parks |  | Cave Lake | 1981 | 1200 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
1289INT2 | SHOWER REPAIRS | 1289 | There are two shower rooms in the building that are showing signs of failure in the walls and should be scheduled for repairs. The walls are constructed of gypsum board covered by FRP. The gypsum board is failing in the wet environment and should be replaced with a cementitious backerboard. This project would provide for removing the gypsum board and replacing it with a more appropriate wall board, such as Hardiboard, covered with new FRP. Removal and disposal of the existing materials is included in the estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | RESTROOM #3 - ELK FLAT | 9946 | CNR | Parks |  | Cave Lake | 1991 | 380 | 2017-05-23 | Immediate to Two Years | Currently Critical | 1 | 7500
1284ADA1 | ADA RESTROOM UPGRADE | 1284 | The building does not have an accessible restroom. The existing restroom does not meet the ADA requirements. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom. Items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2018 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | CAVE LAKE OFFICE/ SHOP | 9946 | CNR | Parks |  | Cave Lake | 1981 | 1360 | 2017-05-23 | Immediate to Two Years | Currently Critical | 1 | 15000
1284SIT2 | SITE BOLLARDS | 1284 | There are two above ground fuel tanks on the site, one for diesel and unleaded gasoline, and the other holds propane for the building. These tanks do not have adequate bollard coverage. Per IFC 2018 Section 312 Vehicle Impact Protection, there needs to be steel posts installed, not less than 4 inches in diameter and filled with concrete. The spacing shall not be more than 4 feet between posts on center and located not less than 3 feet from each gas tank. This project would provide funding for eight new bollards to be located in front of the tanks. | CAVE LAKE OFFICE/ SHOP | 9946 | CNR | Parks |  | Cave Lake | 1981 | 1360 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
1284ADA2 | ADA UPGRADES | 1284 | Section 4.13.9 of the ADAAG states that handles, pulls, latches, locks and other operating devices on accessible doors shall have a shape that is easy to grasp with one hand and does not require tight grasping, tight pinching, or twisting of the wrist to operate. Lever-operated mechanisms, push-type mechanisms, and U-shaped handles are acceptable designs. It is recommended that proper lever hardware be installed in this building to meet these requirements. | CAVE LAKE OFFICE/ SHOP | 9946 | CNR | Parks |  | Cave Lake | 1981 | 1360 | 2017-05-23 | Immediate to Two Years | Currently Critical | 1 | 5000
1280INT3 | JANITORS CLOSET REPAIRS | 1280 | The mop sink is mounted adjacent to OSB and is showing signs of water damage. This project would provide FRP to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | RESTROOM #1 - LAKEVIEW CAMPGROUND | 9946 | CNR | Parks |  | Cave Lake | 1981 | 380 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
1289INT3 | JANITORS CLOSET REPAIRS | 1289 | The mop sink in the plumbing chase is mounted adjacent to studs without a wall backing and is showing signs of water damage. This project would provide for a Cementitious Backer and FRP to be installed on the walls adjacent to the mop sink. The Cementitious Backer and FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | RESTROOM #3 - ELK FLAT | 9946 | CNR | Parks |  | Cave Lake | 1991 | 380 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
1289HVA1 | HEATER REPLACEMENT | 1289 | The building is heated by one wall mounted propane-fired heating unit. It is original to the building and is reaching the end of its useful life. This project provides for disposal of the existing unit and replacement with a new propane-fired unit including connections to utilities. | RESTROOM #3 - ELK FLAT | 9946 | CNR | Parks |  | Cave Lake | 1991 | 380 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
1289EXT3 | EXTERIOR DOOR REPLACEMENT | 1289 | The exterior metal doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the seven door assemblies with new metal doors, frames and hardware. Removal and disposal of the existing doors is included in this estimate. | RESTROOM #3 - ELK FLAT | 9946 | CNR | Parks |  | Cave Lake | 1991 | 380 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 21000
1293EXT2 | GARAGE DOOR REPLACEMENT | 1293 | The garage door is original to the building and has deteriorated from weather exposure. Because it is constructed of wood it is harder to maintain. It is recommended for a new door to be installed. | EQUIPMENT STORAGE BUILDING | 9946 | CNR | Parks |  | Cave Lake | 1981 | 204 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
1293EXT1 | EXTERIOR FINISHES | 1293 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. This project includes the cost for sanding, priming and painting and the caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | EQUIPMENT STORAGE BUILDING | 9946 | CNR | Parks |  | Cave Lake | 1981 | 204 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2040
1289INT1 | INTERIOR FINISHES | 1289 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next 2-3 years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | RESTROOM #3 - ELK FLAT | 9946 | CNR | Parks |  | Cave Lake | 1991 | 380 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3800
2259ADA1 | ADA PARKING SPACE | 2259 | The ADA provides for accessibility to sites and services for people with physical limitations. A concrete parking area and passenger loading area are necessary to comply with ADA requirements. This project would provide for a concrete van accessible ADA parking and loading space and walkway to the restroom. This will require regrading, installing P.C. concrete, striping, signage and any other necessary upgrades. NRS 338.180, IBC - 2018, ICC/ANSI A117.1 - 2009 and ADAAG - 2010 were referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | CXT RESTROOM #3 - OVERLOOK TRAILHEAD | 9946 | CNR | Parks |  | Cave Lake | 2002 | 112 | 2017-05-23 | Immediate to Two Years | Currently Critical | 1 | 2500
2257EXT1 | EXTERIOR/ INTERIOR FINISHES | 2257 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. Epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 2-3 years and for this project to be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | CXT RESTROOM #1 - BOAT RAMP | 9946 | CNR | Parks |  | Cave Lake | 2002 | 112 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2240
2259EXT1 | EXTERIOR/ INTERIOR FINISHES | 2259 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. Epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | CXT RESTROOM #3 - OVERLOOK TRAILHEAD | 9946 | CNR | Parks |  | Cave Lake | 2002 | 112 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2240
2258ADA1 | ADA PARKING SPACE | 2258 | The ADA provides for accessibility to sites and services for people with physical limitations. A concrete parking area and passenger loading area are necessary to comply with ADA requirements. This project would provide for a concrete van accessible ADA parking and loading space and walkway to the existing sidewalk. This will require regrading, installing P.C. concrete, striping, signage and any other necessary upgrades. The 2018 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | CXT RESTROOM #2 - GROUP USE AREA | 9946 | CNR | Parks |  | Cave Lake | 2002 | 112 | 2017-05-23 | Immediate to Two Years | Currently Critical | 1 | 2500
2258EXT1 | EXTERIOR/ INTERIOR FINISHES | 2258 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. Epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | CXT RESTROOM #2 - GROUP USE AREA | 9946 | CNR | Parks |  | Cave Lake | 2002 | 112 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2240
2257PLM1 | SEPTIC SYSTEM REPLACEMENT | 2257 | The septic system serving the restroom is failing. This project recommends replacing the septic tank. The estimate includes abandoning and filling the old septic tank and the installation of a new tank and leach field. This estimate is for an engineered system which will conform to all required environmental rules and regulations including NDEP. | CXT RESTROOM #1 - BOAT RAMP | 9946 | CNR | Parks |  | Cave Lake | 2002 | 112 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 100000
2257ADA1 | ADA PARKING SPACE | 2257 | The ADA provides for accessibility to sites and services for people with physical limitations. A concrete parking area and passenger loading area are necessary to comply with ADA requirements. This project would provide for a concrete van accessible ADA parking and loading space and walkway to the restroom. This will require regrading, installing P.C. concrete, striping, signage and any other necessary upgrades. NRS 338.180, IBC - 2018, ICC/ANSI A117.1 - 2009 and ADAAG - 2010 were referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | CXT RESTROOM #1 - BOAT RAMP | 9946 | CNR | Parks |  | Cave Lake | 2002 | 112 | 2017-05-23 | Immediate to Two Years | Currently Critical | 1 | 2500
3021INT1 | INTERIOR FINISHES | 3021 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and adequately prepared to receive the coating. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | CAVE LAKE INFORMATION BOOTH | 9946 | CNR | Parks |  | Cave Lake | 1991 | 96 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 960
9946SIT2 | CRACK FILL & SEAL ASPHALT PAVING | 9946 | It is important to maintain the asphalt concrete paving on the site. This project would provide for: minor crack filling; slurry sealing of the paving site wide, including parking areas; the turnout at the information kiosk; the boat ramp access, the maintenance yard and striping. All other paving is maintained by NDOT. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 50,000 square feet of asphalt area was used to generate this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | CAVE LAKE STATE PARK SITE | 9946 | CNR | Parks |  | Cave Lake |  |  | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 62500
3019EXT1 | EXTERIOR FINISHES | 3019 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | FISH CLEANING STATION | 9946 | CNR | Parks |  | Cave Lake | 2003 | 100 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
3020EXT1 | EXTERIOR/ INTERIOR FINISHES | 3020 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior and interior of the building. Included in the cost is sanding and sealing the wood framing. It is recommended that the wood framing be sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | LAKEVIEW CAMPGROUND YURT | 9946 | CNR | Parks |  | Cave Lake | 2003 | 160 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 320
3021ADA1 | ADA PARKING SPACE | 3021 | The ADA provides for accessibility to sites and services for people with physical limitations. A concrete parking area and passenger loading area are necessary to comply with ADA requirements. This project would provide for a concrete van accessible ADA parking and loading space and walkway to the information booth. This will require regrading, installing P.C. concrete, striping, signage and any other necessary upgrades. NRS 338.180, IBC - 2018, ICC/ANSI A117.1 - 2009 and ADAAG - 2010 were referenced for this project. | CAVE LAKE INFORMATION BOOTH | 9946 | CNR | Parks |  | Cave Lake | 1991 | 96 | 2017-05-23 | Immediate to Two Years | Currently Critical | 1 | 2500
3021EXT1 | EXTERIOR FINISHES | 3021 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding and sealing the wood and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CAVE LAKE INFORMATION BOOTH | 9946 | CNR | Parks |  | Cave Lake | 1991 | 96 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 480
3022EXT1 | EXTERIOR FINISHES | 3022 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding and sealing the wood and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | ELK FLAT INFORMATION KIOSK | 9946 | CNR | Parks |  | Cave Lake | 2003 | 15 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 960
3022EXT2 | ROOF REPLACEMENT | 3022 | The corrugated metal roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a standing seam metal roofing system. This estimate includes removal and disposal of the old roof. | ELK FLAT INFORMATION KIOSK | 9946 | CNR | Parks |  | Cave Lake | 2003 | 15 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1440
9946ADA3 | ADA UPGRADES - LAKEVIEW CAMPGROUND | 9946 | The Lakeview Campground currently has one accessible space that is well graded, but is not in compliance with ADA regulations. Upgrades to the campsite should include 20'-0" wide concrete drive aisles for RV/ tent trailer sites and accessible amenities on an accessible route including grills, picnic tables, fire rings and water & electric utilities. This project provides for upgrading the existing accessible campsite to a fully compliant accessible campsite. NRS 338.180, IBC - 2018, ICC/ANSI A117.1 - 2009 and ADAAG – 2010 were referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | CAVE LAKE STATE PARK SITE | 9946 | CNR | Parks |  | Cave Lake |  |  | 2017-05-23 | Immediate to Two Years | Currently Critical | 1 | 8750
9946ADA4 | ADA UPGRADES - DAY USE | 9946 | The ADA provides for accessibility to sites and services for people with physical limitations. A compliant path of travel from the accessible parking space to the restroom and picnic area and an accessible picnic table are necessary to comply with ADA accessibility requirements. This project provides funding for a compliant path of travel and an accessible picnic table. NRS 338.180, IBC - 2018, ICC/ANSI A117.1 - 2009 and ADAAG - 2010 were referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | CAVE LAKE STATE PARK SITE | 9946 | CNR | Parks |  | Cave Lake |  |  | 2017-05-23 | Immediate to Two Years | Currently Critical | 1 | 10000
9946ADA5 | ADA UPGRADES - GROUP USE | 9946 | The ADA provides for accessibility to sites and services for people with physical limitations. The Group Use area does not have an accessible path of travel to the restroom, picnic area or presentation area. This project provides funding to install a compliant path of travel from the accessible parking space to these three areas as well as upgrading the picnic table to an accessible table. NRS 338.180, IBC - 2018, ICC/ANSI A117.1 - 2009 and ADAAG - 2010 were referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | CAVE LAKE STATE PARK SITE | 9946 | CNR | Parks |  | Cave Lake |  |  | 2017-05-23 | Immediate to Two Years | Currently Critical | 1 | 20000
9946ENR1 | PHOTOVOLTAIC EQUIPMENT REPLACEMENT | 9946 | The existing photovoltaic equipment site wide is over 25 years old. This original equipment has a design life of 7 years. The batteries no longer hold a full charge and replacement parts are no longer available. This project will replace the photovoltaic equipment site wide including, but not limited to: the solar panels; tracking systems; control panels; inverters and the batteries. The removal and the disposal of the existing equipment are included in this estimate. This project will provide for new photovoltaic equipment for the Cave Lake Office/ Shop, the two residences, three restrooms and the Fish Cleaning Station. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | CAVE LAKE STATE PARK SITE | 9946 | CNR | Parks |  | Cave Lake |  |  | 2017-05-23 | Immediate to Two Years | Currently Critical | 1 | 260000
9946ADA1 | ADA UPGRADES - BOAT DOCK | 9946 | The ADA provides for accessibility to sites and services for people with physical limitations. The existing ADA parking space at the boat dock does not meet the ADA requirements. The boat dock has a picnic area that should be ADA accessible. This project provides funding to bring the existing ADA parking space up to code including the removal of the asphalt and replacement with P.C. concrete, updated signage, re-striping, re-grading and any other necessary upgrades. The project funding will also provide for an accessible path of travel from the parking space and an accessible picnic table at the picnic area. NRS 338.180, IBC - 2018, ICC/ANSI A117.1 - 2009 and ADAAG - 2010 were referenced for this project. This project should be implemented concurrently with the BOAT DOCK REPAIRS project. This project or a portion thereof was previously recommended in the FCA report dated 04/11/2002 and 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | CAVE LAKE STATE PARK SITE | 9946 | CNR | Parks |  | Cave Lake |  |  | 2017-05-23 | Immediate to Two Years | Currently Critical | 1 | 25000
9946SIT3 | BOAT DOCK REPAIRS | 9946 | The boat dock has an area covered by concrete pavers which is settling and due for repairs. The settled area causes a tripping hazard and will continue to settle due to ponding water. This project would provide for the removal of the existing pavers, adding fill, compacting and installing new pavers. This project should be implemented concurrently with the ADA UPGRADES - BOAT DOCK project. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | CAVE LAKE STATE PARK SITE | 9946 | CNR | Parks |  | Cave Lake |  |  | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6250
3020SFT1 | EXTERIOR HANDRAIL REPLACEMENT | 3020 | The exterior stairs and deck have handrails and a guardrail that do not meet building code requirements for safety. The gripping surfaces are incorrect, they are not continuous from the top to bottom landings and the deck is lacking a guardrail. This project recommends the installation of guardrails and handrails in accordance with the 2018 IBC Section 1012 and 1013. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | LAKEVIEW CAMPGROUND YURT | 9946 | CNR | Parks |  | Cave Lake | 2003 | 160 | 2017-05-23 | Immediate to Two Years | Currently Critical | 1 | 1000
9946SFT1 | STAIR REPLACEMENT - GROUP USE | 9946 | There is a flight of stairs in the group use area that provides access to the shoreline. The stairs are made of wood that are set in the dirt and they do not have the proper handrails per IBC. This project would provide for replacing the existing stairs with concrete steps and compliant handrails in accordance with IBC Section 1012. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | CAVE LAKE STATE PARK SITE | 9946 | CNR | Parks |  | Cave Lake |  |  | 2017-05-23 | Immediate to Two Years | Currently Critical | 1 | 15000
0881ADA1 | ADA RESTROOM REMODEL | 0881 | The restroom does not meet the Americans with Disabilities Act (ADA) regulations. A retrofit is necessary to comply with ICC/ANSI A117.1-1998 Sections 603 - 604, 2018 IBC Chapter 11 and the Americans with Disabilities Act Accessibility Guidelines (ADAAG). Given the current configuration of the restroom, the work will include the installation of a new toilet, sink, grab bars, faucets, mirrors, dispensers and hardware. Some minor design work will be required and may impact the final cost estimate. This estimate is for one Unisex restroom facility. The removal and disposal of the old restroom fixtures is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 08/21/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/20/2007. | NDF OFFICE | 9976 | CNR | Forestry |  | Ely | 1987 | 1220 | 2017-05-24 | Immediate to Two Years | Currently Critical | 1 | 45000
0881INT2 | REMODEL INTERIOR | 0881 | The interior fixtures and finishes are in general disrepair and the building is due for a complete remodel. This project would provide for removal and replacement of the flooring, doors and frames, cabinetry, trim and baseboards and any other interior finishes and fixtures in need of replacement at the time. This project should be concurrent with all other projects having to do with the interior of the building including the fire safety, lighting upgrade and ADA projects. | NDF OFFICE | 9976 | CNR | Forestry |  | Ely | 1987 | 1220 | 2017-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30500
0881ENR1 | LIGHTING UPGRADE | 0881 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 08/21/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/20/2007. | NDF OFFICE | 9976 | CNR | Forestry |  | Ely | 1987 | 1220 | 2017-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3660
0881INT1 | INTERIOR FINISHES | 0881 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 08/21/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/20/2007. | NDF OFFICE | 9976 | CNR | Forestry |  | Ely | 1987 | 1220 | 2017-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6100
0881PLM2 | REPLACE WATER HEATER | 0881 | The average life span of a water heater is eight to ten years. The existing 30 gallon propane water heater in the building has reached the end of its expected life and is not energy efficient. This project would provide for the removal and disposal of the old water heater and installation of a new 30 gallon propane water heater. | NDF OFFICE | 9976 | CNR | Forestry |  | Ely | 1987 | 1220 | 2017-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1200
0881HVA1 | REPLACE HVAC EQUIPMENT | 0881 | Several heating and cooling units throughout the building are original and have reached the end of their expected life. This project would provide for replacement of the window mounted evaporative cooler and two electric baseboard heaters and includes removal and disposal of the existing units and all required connections to utilities. | NDF OFFICE | 9976 | CNR | Forestry |  | Ely | 1987 | 1220 | 2017-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
0882HVA1 | REPLACE CEILING MOUNTED HEATER | 0882 | The building is heated by one ceiling mounted gas heater. It is original to the building and is reaching the end of its useful life. This project provides for disposal of the existing unit and replacement of the unit and associated connections to utilities. | NDF GARAGE/STORAGE | 9976 | CNR | Forestry |  | Ely | 1987 | 1495 | 2017-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0881SFT2 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0881 | The existing exit signs in this building are older types and should be replaced with new self-illuminated or LED style signs with battery-backed internal systems. Emergency exit lighting should be installed and/or replaced to provide illumination along the egress route. This project or a portion thereof was previously recommended in the FCA report dated 08/21/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/20/2007. | NDF OFFICE | 9976 | CNR | Forestry |  | Ely | 1987 | 1220 | 2017-05-24 | Immediate to Two Years | Currently Critical | 1 | 5000
0881SFT1 | FIRE ALARM SYSTEM UPGRADE | 0881 | This building is equipped with an automatic fire detection and alarm system, but the system is antiquated. It is recommended that the fire detection and alarm system be upgraded. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2018 IBC Chapter 9, Section 907.2.1 and the State Fire Marshal's requirements. This project or a portion thereof was previously recommended in the FCA report dated 08/21/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/20/2007. | NDF OFFICE | 9976 | CNR | Forestry |  | Ely | 1987 | 1220 | 2017-05-24 | Immediate to Two Years | Currently Critical | 1 | 3660
0881PLM1 | 4" BACKFLOW, SHUTOFF, VAULT, AND POWER | 0881 | State Health law now mandates backflow prevention devices be installed on all domestic, fire protection and irrigation systems to prevent contamination. This project makes allowance for installing a 4" reduced pressure backflow prevention assembly, required fittings, an above ground vault, and allowance for 200 feet of 1" conduit to provide power for the required heat source inside the vault. This project or a portion thereof was previously recommended in the FCA report dated 08/21/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/20/2007. | NDF OFFICE | 9976 | CNR | Forestry |  | Ely | 1987 | 1220 | 2017-05-24 | Four to Ten Years | Long-Term Needs | 3 | 25000
0881ADA2 | SIGNAGE FOR ADA COMPLIANCE | 0881 | The building is lacking ADA signage. Americans with Disabilities Act (ADA) regulations pertaining to parking, building access, route of travel and restrooms has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances, route of travel inside the building and restrooms. IBC - 2018, ICC/ANSI A117.1 - 2003 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2003 were referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 08/21/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/20/2007. | NDF OFFICE | 9976 | CNR | Forestry |  | Ely | 1987 | 1220 | 2017-05-24 | Immediate to Two Years | Currently Critical | 1 | 1500
0880EXT1 | EXTERIOR FINISHES | 0880 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | NDF FIRE HOUSE STORAGE | 9976 | CNR | Forestry |  | Ely | 1987 | 660 | 2017-05-24 | Four to Ten Years | Long-Term Needs | 3 | 6600
0880INT1 | INTERIOR FINISHES | 0880 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | NDF FIRE HOUSE STORAGE | 9976 | CNR | Forestry |  | Ely | 1987 | 660 | 2017-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3300
0880ENR1 | LIGHTING UPGRADE | 0880 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. Any electrical wiring upgrades are not included in this estimate. | NDF FIRE HOUSE STORAGE | 9976 | CNR | Forestry |  | Ely | 1987 | 660 | 2017-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1980
0880HVA1 | REPLACE CEILING MOUNTED HEATER | 0880 | The building is heated by one ceiling mounted gas heater. It is original to the building and is reaching the end of its useful life. This project provides for disposal of the existing unit and replacement of the unit and associated utility connections. | NDF FIRE HOUSE STORAGE | 9976 | CNR | Forestry |  | Ely | 1987 | 660 | 2017-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0882EXT1 | EXTERIOR FINISHES | 0882 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | NDF GARAGE/STORAGE | 9976 | CNR | Forestry |  | Ely | 1987 | 1495 | 2017-05-24 | Four to Ten Years | Long-Term Needs | 3 | 7475
0882INT1 | INTERIOR FINISHES | 0882 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | NDF GARAGE/STORAGE | 9976 | CNR | Forestry |  | Ely | 1987 | 1495 | 2017-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7475
0882SFT1 | REBUILD HANDRAILS / GUARDRAILS | 0882 | The handrails and guardrails at the stairway and storage mezzanine do not meet the building code requirements in their current configuration. This project would provide for the removal of the existing wood framed railing and replacement with new wood framed handrails and guardrail that will meet the 2018 IBC code Chapter 10, Section 1012 and 1013. | NDF GARAGE/STORAGE | 9976 | CNR | Forestry |  | Ely | 1987 | 1495 | 2017-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
0881EXT1 | EXTERIOR FINISHES | 0881 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | NDF OFFICE | 9976 | CNR | Forestry |  | Ely | 1987 | 1220 | 2017-05-24 | Four to Ten Years | Long-Term Needs | 3 | 6100
2270SIT1 | SIDEWALK REPLACEMENT | 2270 | The exterior walkway from the garage and driveway up to the entrance of the house does not meet code and is a safety hazard. The ramp/ walkway does not have acceptable slopes or proper landings nor does it have handrails. Due to the effects of the extreme weather conditions of the area, particularly ice and snow on the walkway, the existing sloped concrete surface poses a significant injury risk. This project would provide for an upgrade to the ramp/ walkway to make it fully compliant with 2018 IBC Chapter 10. A combination of concrete sloped walks and steps with handrails is suggested. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/11/2017. | RANGER RESIDENCE | 9942 | CNR | Parks |  | Ward Charcoal Ovens | 1995 | 2400 | 2017-07-11 | Immediate to Two Years | Currently Critical | 1 | 11200
2270EXT1 | EXTERIOR FINISHES | 2270 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/11/2017. | RANGER RESIDENCE | 9942 | CNR | Parks |  | Ward Charcoal Ovens | 1995 | 2400 | 2017-07-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 27360
2270EXT3 | WINDOW REPLACEMENT | 2270 | The windows are original, double pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 5 units. Removal and disposal of the existing windows is included in this estimate. | RANGER RESIDENCE | 9942 | CNR | Parks |  | Ward Charcoal Ovens | 1995 | 2400 | 2017-07-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8400
2270HVA1 | HEATER REPLACEMENT | 2270 | There are five wall mounted heaters in the building that have reached the end of their expected life. This project recommends replacing the heaters with a packaged unit and new ductwork. The estimate includes removal and disposal of the existing equipment. | RANGER RESIDENCE | 9942 | CNR | Parks |  | Ward Charcoal Ovens | 1995 | 2400 | 2017-07-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
2270INT2 | BASEMENT FLOOR REPAIRS | 2270 | The concrete floor in the basement is worn and damaged and should be resurfaced. This project provides for cleaning and repairing the existing concrete floor, applying a bonding agent, pouring a new polymer surface and applying an appropriate finish product. | RANGER RESIDENCE | 9942 | CNR | Parks |  | Ward Charcoal Ovens | 1995 | 2400 | 2017-07-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9408
2270EXT2 | OVERHEAD DOOR REPLACEMENT | 2270 | There is a 10'x12' overhead garage door which is damaged and does not function properly. It is original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead door and purchase and installation of a new door. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/11/2017. | RANGER RESIDENCE | 9942 | CNR | Parks |  | Ward Charcoal Ovens | 1995 | 2400 | 2017-07-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7840
2270SFT2 | REMOVE AWNING | 2270 | There is a metal awning attached to the roof on the west side of the building near the front door. The main structure was not designed to carry this additional lateral load and the awning structure itself is not in good condition. It is recommended to remove and dispose of the structure. Included in the estimate is removing and disposing of the awning as well as patching the roof and concrete patio where attachments were made. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/11/2017. | RANGER RESIDENCE | 9942 | CNR | Parks |  | Ward Charcoal Ovens | 1995 | 2400 | 2017-07-11 | Immediate to Two Years | Currently Critical | 1 | 1120
2270ENR1 | LIGHTING UPGRADE | 2270 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | RANGER RESIDENCE | 9942 | CNR | Parks |  | Ward Charcoal Ovens | 1995 | 2400 | 2017-07-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 21504
2270INT1 | INTERIOR FINISHES | 2270 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/11/2017. | RANGER RESIDENCE | 9942 | CNR | Parks |  | Ward Charcoal Ovens | 1995 | 2400 | 2017-07-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 27360
2270SFT1 | INTERIOR STAIRWAY REPLACEMENT | 2270 | The stairs and handrails between the first floor and the basement do not meet the sections 1009 and 1012 requirements of the 2018 IBC. This project would provide for the rebuilding of the stairway to provide for a code compliant stairway. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/11/2017. | RANGER RESIDENCE | 9942 | CNR | Parks |  | Ward Charcoal Ovens | 1995 | 2400 | 2017-07-11 | Immediate to Two Years | Currently Critical | 1 | 10080
2271EXT1 | EXTERIOR/ INTERIOR FINISHES | 2271 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/11/2017. | WELL HOUSE | 9942 | CNR | Parks |  | Ward Charcoal Ovens | 2001 | 80 | 2017-07-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1792
2272EXT1 | EXTERIOR FINISHES | 2272 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/11/2017. | RAMADA #1 - DAY USE | 9942 | CNR | Parks |  | Ward Charcoal Ovens |  | 240 | 2017-07-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1075.2
2273EXT1 | EXTERIOR FINISHES | 2273 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/11/2017. | RAMADA #2 - DAY USE | 9942 | CNR | Parks |  | Ward Charcoal Ovens |  | 240 | 2017-07-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1075.2
2274EXT2 | HISTORIC BUILDING MAINTENANCE | 2274 | The structure is made of unreinforced stone masonry. It is over 100 years old and there are numerous areas where the mortar is failing, missing and not sealed properly. This is also an exhibit for the park and requires maintenance time to display the artifacts and maintain the signage. This project would provide for the cleaning, repair and re-pointing of the stone work and maintaining the exhibit. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | OVEN #1 | 9942 | CNR | Parks |  | Ward Charcoal Ovens | 1876 | 600 | 2017-07-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10080
2275EXT2 | HISTORIC BUILDING MAINTENANCE | 2275 | The structure is made of unreinforced stone masonry. It is over 100 years old and there are numerous areas where the mortar is failing, missing and not sealed properly. This is also an exhibit for the park and requires maintenance time to display the artifacts and maintain the signage. This project would provide for the cleaning, repair and re-pointing of the stone work and maintaining the exhibit. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | OVEN #2 | 9942 | CNR | Parks |  | Ward Charcoal Ovens | 1876 | 600 | 2017-07-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10080
2276EXT2 | HISTORIC BUILDING MAINTENANCE | 2276 | The structure is made of unreinforced stone masonry. It is over 100 years old and there are numerous areas where the mortar is failing, missing and not sealed properly. This is also an exhibit for the park and requires maintenance time to display the artifacts and maintain the signage. This project would provide for the cleaning, repair and re-pointing of the stone work and maintaining the exhibit. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | OVEN #3 | 9942 | CNR | Parks |  | Ward Charcoal Ovens | 1876 | 600 | 2017-07-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10080
2277EXT2 | HISTORIC BUILDING MAINTENANCE | 2277 | The structure is made of unreinforced stone masonry. It is over 100 years old and there are numerous areas where the mortar is failing, missing and not sealed properly. This is also an exhibit for the park and requires maintenance time to display the artifacts and maintain the signage. This project would provide for the cleaning, repair and re-pointing of the stone work and maintaining the exhibit. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | OVEN #4 | 9942 | CNR | Parks |  | Ward Charcoal Ovens | 1876 | 600 | 2017-07-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10080
2278EXT2 | HISTORIC BUILDING MAINTENANCE | 2278 | The structure is made of unreinforced stone masonry. It is over 100 years old and there are numerous areas where the mortar is failing, missing and not sealed properly. This is also an exhibit for the park and requires maintenance time to display the artifacts and maintain the signage. This project would provide for the cleaning, repair and re-pointing of the stone work and maintaining the exhibit. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | OVEN #5 | 9942 | CNR | Parks |  | Ward Charcoal Ovens | 1876 | 600 | 2017-07-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10080
2279EXT2 | HISTORIC BUILDING MAINTENANCE | 2279 | The structure is made of unreinforced stone masonry. It is over 100 years old and there are numerous areas where the mortar is failing, missing and not sealed properly. This is also an exhibit for the park and requires maintenance time to display the artifacts and maintain the signage. This project would provide for the cleaning, repair and re-pointing of the stone work and maintaining the exhibit. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | OVEN #6 | 9942 | CNR | Parks |  | Ward Charcoal Ovens | 1876 | 600 | 2017-07-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10080
2270PLM1 | WATER HEATER REPLACEMENT | 2270 | There is a 50 gallon electric water heater in the basement. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 3-4 years. It is recommended that a new propane-fired water heater be installed for more efficient use of energy. This estimate includes: 100 feet of gas pipe, fittings, couplers, and labor for installation. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/11/2017. | RANGER RESIDENCE | 9942 | CNR | Parks |  | Ward Charcoal Ovens | 1995 | 2400 | 2017-07-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4200
2164EXT1 | EXTERIOR FINISHES | 2164 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/11/2017. | RAMADA #3 - DAY USE | 9942 | CNR | Parks |  | Ward Charcoal Ovens | 0 | 104 | 2017-07-11 | Four to Ten Years | Long-Term Needs | 3 | 465.92
2270SFT3 | SMOKE AND CARBON MONOXIDE ALARM INSTALLATION | 2270 | IRC 2018 Section R314 and R315.3 explain the requirements for smoke alarms in dwelling units. This includes: installing and maintaining smoke alarms in each sleeping room; having a carbon monoxide and smoke detector on the ceiling or wall outside of each sleeping area; in the immediate vicinity of bedrooms when an alteration, repair or addition requiring a permit occurs. IRC 2018 requires that smoke detectors and carbon monoxide alarms be UL rated. State Fire Marshal NAC 477.915 (3) requires that smoke detectors be connected to the wiring in a building and include a battery for emergency backup power. This project would provide funding for the purchase and installation of smoke alarms and carbon monoxide alarms in accordance with IRC and NAC laws. | RANGER RESIDENCE | 9942 | CNR | Parks |  | Ward Charcoal Ovens | 1995 | 2400 | 2017-07-11 | Immediate to Two Years | Currently Critical | 1 | 2800
3018EXT1 | EXTERIOR/ INTERIOR FINISHES | 3018 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/11/2017. | CXT COMFORT STATION #4 - CAMPGROUND | 9942 | CNR | Parks |  | Ward Charcoal Ovens | 2009 | 104 | 2017-07-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2329.6
3017EXT1 | EXTERIOR/ INTERIOR FINISHES | 3017 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/11/2017. | CXT COMFORT STATION #3 - CAMPGROUND | 9942 | CNR | Parks |  | Ward Charcoal Ovens | 2009 | 104 | 2017-07-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2329.6
3016EXT1 | EXTERIOR/ INTERIOR FINISHES | 3016 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/11/2017. | CXT COMFORT STATION #2 - CAMPGROUND | 9942 | CNR | Parks |  | Ward Charcoal Ovens | 2009 | 104 | 2017-07-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2329.6
3016ADA1 | ADA ACCESSIBLE PATH OF TRAVEL | 3016 | The ADA provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the office are necessary to comply with ADA accessibility requirements. This project would provide for a concrete van accessible ADA parking and loading space and concrete walkway to the existing sidewalk. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2018 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. 750 square feet of concrete was used for this estimate. It is recommended that this project coincide with the paving project. | CXT COMFORT STATION #2 - CAMPGROUND | 9942 | CNR | Parks |  | Ward Charcoal Ovens | 2009 | 104 | 2017-07-11 | Immediate to Two Years | Currently Critical | 1 | 33600
9942EXT1 | EXTERIOR FINISHES, SHADE RAMADAS | 9942 | There are 15 steel shade ramadas in the campground which are 100 s.f. each for a total of 1,500 square feet. It is important to maintain the finish, weather resistance and appearance of the structures. This project would provide for painting of the structures and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structures. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/11/2017. | WARD CHARCOAL OVENS STATE HISTORIC PARK | 9942 | CNR | Parks |  | Ward Charcoal Ovens |  |  | 2017-07-11 | Four to Ten Years | Long-Term Needs | 3 | 6720
9942ADA1 | ADA PARKING SPACE UPGRADES | 9942 | The ADA provides for accessibility to sites and services for people with physical limitations. A concrete parking area and passenger loading area near the Group Ramada are necessary to comply with ADA requirements. This project would provide for a concrete van accessible ADA parking and loading space and compliant path of travel to the Group Ramada and the restroom. This will require regrading, installing P.C. concrete, striping, signage and any other necessary upgrades. NRS 338.180, IBC - 2018, ICC/ANSI A117.1 - 2009 and ADAAG - 2010 were referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/11/2002 and 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/11/2017. | WARD CHARCOAL OVENS STATE HISTORIC PARK | 9942 | CNR | Parks |  | Ward Charcoal Ovens |  |  | 2017-07-11 | Immediate to Two Years | Currently Critical | 1 | 15000
3015EXT1 | EXTERIOR/ INTERIOR FINISHES | 3015 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/11/2017. | CXT COMFORT STATION #1 - DAY USE | 9942 | CNR | Parks |  | Ward Charcoal Ovens | 0 | 104 | 2017-07-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2329.6
3014EXT1 | EXTERIOR FINISHES | 3014 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/11/2017. | GROUP RAMADA - CAMPGROUND | 9942 | CNR | Parks |  | Ward Charcoal Ovens | 2009 | 400 | 2017-07-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1792
3017ADA1 | ADA ACCESSIBLE PATH OF TRAVEL | 3017 | The ADA provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the office are necessary to comply with ADA accessibility requirements. This project would provide for a concrete van accessible ADA parking and loading space and concrete walkway to the existing sidewalk. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2018 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. 750 square feet of concrete was used for this estimate. It is recommended that this project coincide with the paving project. | CXT COMFORT STATION #3 - CAMPGROUND | 9942 | CNR | Parks |  | Ward Charcoal Ovens | 2009 | 104 | 2017-07-11 | Immediate to Two Years | Currently Critical | 1 | 33600
9942ADA2 | ADA UPGRADES | 9942 | The ADA provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the Day Use restroom are necessary to comply with ADA requirements. This project would provide for a concrete van accessible ADA parking and loading space and path of travel to the existing sidewalk. This will require regrading, installing P.C. concrete, striping, signage and any other necessary upgrades. NRS 338.180, IBC - 2018, ICC/ANSI A117.1 - 2009 and ADAAG - 2010 were referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/11/2017. | WARD CHARCOAL OVENS STATE HISTORIC PARK | 9942 | CNR | Parks |  | Ward Charcoal Ovens |  |  | 2017-07-11 | Immediate to Two Years | Currently Critical | 1 | 7840
1681ADA2 | ADA RAMP HANDRAIL INSTALLATION | 1681 | This building has an ADA accessible ramp located on the east side of the building. This ramp is on the accessible path of travel from the accessible parking space to the entrance of the building. The ramp does not have handrails or edge protection which are required for ADA compliance. This project would provide for installing handrails on the ramp including proper returns, gripping surfaces and edge protection to make it fully ADA compliant. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | MORMON FORT VISITORS CENTER | 9913 | CNR | Parks |  | Las Vegas | 2005 | 5000 | 2017-12-12 | Immediate to Two Years | Currently Critical | 1 | 5000
1905EXT2 | ROOF REPLACEMENT | 1905 | The hot-mopped tar roof on this building was in poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed and fitted with rain gutters in the next 2-3 years to be consistent with the roofing program. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. | HISTORIC FORT MUSEUM | 9913 | CNR | Parks |  | Las Vegas | 1855 | 1000 | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
1905EXT3 | WINDOW REPLACEMENT | 1905 | The windows are older single pane construction in a wooden frame. These older windows are drafty and the wooden frames have deteriorated significantly. This project recommends replacing the windows with dual pane units. This estimate is for the replacement of 10 units including wooden frames. Additional costs are included due to the historic nature of the building and that the window frames will need to be replicated based on the existing windows. Removal and disposal of the existing windows is included in this estimate. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. | HISTORIC FORT MUSEUM | 9913 | CNR | Parks |  | Las Vegas | 1855 | 1000 | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
1905EXT1 | EXTERIOR/ INTERIOR FINISHES | 1905 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior and interior of the structure. Included in the cost is basic adobe maintenance by the staff as well as funds for adobe specialists to come out once a year. These costs should be sufficient to allow the specialists to spend two days per year at the Museum over the next four years. This project should be scheduled on a cyclical basis to maintain the integrity of the Museum. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. | HISTORIC FORT MUSEUM | 9913 | CNR | Parks |  | Las Vegas | 1855 | 1000 | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
1905SEC1 | SECURITY SYSTEM INSTALLATION | 1905 | The building does not have a security system. This project recommends motion detection and window and door sensors be installed and interfaced with the sitewide security system. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. | HISTORIC FORT MUSEUM | 9913 | CNR | Parks |  | Las Vegas | 1855 | 1000 | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
1681EXT2 | PUBLIC ENTRANCE STAIRWAY INSTALLATION | 1681 | The entrance to the building is often overlooked by visitors and is generally uninviting. Without a stairway from the parking lot to the front door, visitors have a hard time discerning where the entrance to the Visitors Center is. This project would provide for installing a concrete stairway in front of the entrance to the building. The stairway shall be designed to comply with all adopted building codes and the ADA accessibility guidelines. | MORMON FORT VISITORS CENTER | 9913 | CNR | Parks |  | Las Vegas | 2005 | 5000 | 2017-12-12 | Four to Ten Years | Long-Term Needs | 3 | 20000
1905ELE1 | ELECTRICAL UPGRADE | 1905 | The building is equipped with a knob and tube electrical system. This type of system is no longer used and replacement parts are impossible to find. The main disadvantage of this electrical system is that there is no safety grounding conductor. Also, as the cotton and rubber wire insulation ages, it becomes dry and brittle and becomes easily damaged. It is recommended the entire system be upgraded to a modern electrical system. The existing knob and tube system could remain in place to display the historical nature of the Museum. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. | HISTORIC FORT MUSEUM | 9913 | CNR | Parks |  | Las Vegas | 1855 | 1000 | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
1681HVA1 | HVAC DUCTING REPLACEMENT | 1681 | The existing HVAC system employs a collapsible ducting system. This system makes a lot of noise in such a way that it startles visitors in the building. It is not a system that is appropriate for a museum type setting and it is recommended to install rigid ducting in its place. This project would provide for the removal of the existing ducting and installation of new rigid ducting including attachment to ceiling, supply and return diffusers and balancing by a licensed HVAC contractor. | MORMON FORT VISITORS CENTER | 9913 | CNR | Parks |  | Las Vegas | 2005 | 5000 | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3500
1681SEC1 | SECURITY UPGRADES | 1681 | The site and buildings have experienced break-ins in the recent past. The Visitors Center was compromised by breaking a window in the Conference Room. Currently, the windows are not alarmed and the alarm sensors in the building did not detect the intruder quickly. Part of the reason for the delay in detection may have been that some of the motion sensors are not located properly. They are located too high on the walls and some are blocked by displays. This project would provide for upgrading the security system by relocating the existing sensors and alarming the doors and windows. Alternatively, the windows could be provided with an exterior security shutter to prevent vandalism and break-ins. | MORMON FORT VISITORS CENTER | 9913 | CNR | Parks |  | Las Vegas | 2005 | 5000 | 2017-12-12 | Immediate to Two Years | Currently Critical | 1 | 25000
1681ENR1 | OCCUPANCY SENSOR INSTALLATION | 1681 | There are no occupancy sensors installed in the building to control lighting. It is recommended to install sensors in order to reduce energy costs. Occupancy sensors will be installed in restrooms, conference rooms, utility rooms and other low occupancy. This project provides for purchase and installation of 6 sensors. | MORMON FORT VISITORS CENTER | 9913 | CNR | Parks |  | Las Vegas | 2005 | 5000 | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
1681PLM2 | BACKFLOW PREVENTER INVESTIGATION | 1681 | There is a backflow preventer on the main water line coming into the building. It is leaking and should be scheduled for replacement. There may be a pressure problem with the incoming water main. The psi valve is maxed out indicating the pressure is above 100 psi. This may be the cause of the broken prevention valve and should be analyzed by a licensed plumber. This project would provide for employing a licensed plumber to replace the backflow preventer and to analyze the system. | MORMON FORT VISITORS CENTER | 9913 | CNR | Parks |  | Las Vegas | 2005 | 5000 | 2017-12-12 | Immediate to Two Years | Currently Critical | 1 | 1000
1681INT2 | FLOORING MAINTENANCE | 1681 | The concrete floor sealant is damaged and reaching the end of its useful life. It is recommended that the concrete be stripped and re-sealed in order to extend the concretes' useful life. This project would provide for stripping the concrete and applying a new coat of sealant in the next 2-3 years. | MORMON FORT VISITORS CENTER | 9913 | CNR | Parks |  | Las Vegas | 2005 | 5000 | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
1905SFT1 | FIRE ALARM SYSTEM INSTALLATION | 1905 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2006 Section 7 and the 2006 International Fire Code. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. | HISTORIC FORT MUSEUM | 9913 | CNR | Parks |  | Las Vegas | 1855 | 1000 | 2017-12-12 | Immediate to Two Years | Currently Critical | 1 | 4000
1681PLM1 | WATER HEATER REPLACEMENT | 1681 | There is a 5 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new on-demand electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | MORMON FORT VISITORS CENTER | 9913 | CNR | Parks |  | Las Vegas | 2005 | 5000 | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
1681EXT1 | EXTERIOR FINISHES | 1681 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MORMON FORT VISITORS CENTER | 9913 | CNR | Parks |  | Las Vegas | 2005 | 5000 | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
1681INT1 | INTERIOR FINISHES | 1681 | The interior finishes are in fair condition. It is recommended that the painted interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | MORMON FORT VISITORS CENTER | 9913 | CNR | Parks |  | Las Vegas | 2005 | 5000 | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
1681ADA1 | ADA SIGNAGE | 1681 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | MORMON FORT VISITORS CENTER | 9913 | CNR | Parks |  | Las Vegas | 2005 | 5000 | 2017-12-12 | Immediate to Two Years | Currently Critical | 1 | 750
1681ENR2 | PHOTOVOLTAIC POWER SYSTEM INSTALLATION | 1681 | There is no natural gas service to the site. All of the equipment including HVAC and water heating is powered solely by electricity. This makes the building an ideal candidate for photovoltaic power which could be installed on the roof. A photovoltaic power system would eliminate electricity costs and could be fitted with a reverse power meter to sell power back to the electric company. This project would provide for the purchase and installation of a 15 kW photovoltaic system including solar panels, deep cycle solar batteries, a reverse power meter and all associated electrical boxes and hardware to connect it to the main electrical service. | MORMON FORT VISITORS CENTER | 9913 | CNR | Parks |  | Las Vegas | 2005 | 5000 | 2017-12-12 | Four to Ten Years | Long-Term Needs | 3 | 150000
2864EXT1 | EXTERIOR FINISHES | 2864 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting the exposed wood features, repairing and sealing the stone and masonry work and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted and sealed in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MORMOM FORT PUMP HOUSE | 9913 | CNR | Parks |  | Las Vegas | 1999 | 140 | 2017-12-12 | Four to Ten Years | Long-Term Needs | 3 | 700
2397ENV1 | SAFETY CABINETS | 2397 | The shop contains many different oils, paints, stains and other hazardous products on open shelves and work benches. This does not meet OSHA standards for hazardous materials containment. This project would provide for the purchase of two hazardous materials storage containers and installing placards on the building exterior in accordance with OSHA 1910.106 (d). | MORMON FORT VEHICLE SHOP | 9913 | CNR | Parks |  | Las Vegas | 1999 | 1176 | 2017-12-12 | Immediate to Two Years | Currently Critical | 1 | 5000
2397SFT1 | FIRE SUPPRESSION SYSTEM INSTALLATION | 2397 | The building is partly a B occupancy per the 2006 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. | MORMON FORT VEHICLE SHOP | 9913 | CNR | Parks |  | Las Vegas | 1999 | 1176 | 2017-12-12 | Immediate to Two Years | Currently Critical | 1 | 8232
2397EXT1 | EXTERIOR FINISHES | 2397 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting the stucco, sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MORMON FORT VEHICLE SHOP | 9913 | CNR | Parks |  | Las Vegas | 1999 | 1176 | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5880
2398EXT1 | EXTERIOR FINISHES | 2398 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting the stucco walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MORMON FORT RESTROOM | 9913 | CNR | Parks |  | Las Vegas | 1999 | 240 | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1200
2397INT1 | INTERIOR FINISHES | 2397 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | MORMON FORT VEHICLE SHOP | 9913 | CNR | Parks |  | Las Vegas | 1999 | 1176 | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5880
2397EXT2 | GUTTER INSTALLATION | 2397 | The building does not have gutters or downspouts to control the runoff from the roof. The water currently sheet drains off the roof causing extensive erosion to the built-up dirt slope around the foundation. This will eventually lead to failure of the foundation undermining the integrity of the entire structure. This project would provide funding for the installation of a seamless gutter and downspout system for the building. | MORMON FORT VEHICLE SHOP | 9913 | CNR | Parks |  | Las Vegas | 1999 | 1176 | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
2397SFT2 | FIRE ALARM SYSTEM INSTALLATION | 2397 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2006 Section 7 and the 2006 International Fire Code. | MORMON FORT VEHICLE SHOP | 9913 | CNR | Parks |  | Las Vegas | 1999 | 1176 | 2017-12-12 | Immediate to Two Years | Currently Critical | 1 | 4704
2864PLM2 | PUMP AND FILTER REPLACEMENT | 2864 | There is a man made stream with a pond at the bottom that is due for a new water pump and filter. The existing pumps and filters were designed for a swimming pool application, not a large stream and pond with continuously running pumps. It is recommended to replace the pumps with a new 5 H.P. fountain water pump system including a large solids filter and a microfilter. This project includes removal and disposal of the existing pumps and filters and all required connections to utilities. | MORMOM FORT PUMP HOUSE | 9913 | CNR | Parks |  | Las Vegas | 1999 | 140 | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
2864PLM1 | BACKFLOW PREVENTER INVESTIGATION | 2864 | There is a backflow preventer on the main water line coming into the building. It is leaking and should be replaced immediately. There may be a pressure problem with the incoming water main. This may be the cause of the broken prevention valve and should be analyzed by a licensed plumber. This project would provide for employing a licensed plumber to replace the backflow preventer and to analyze the system. | MORMOM FORT PUMP HOUSE | 9913 | CNR | Parks |  | Las Vegas | 1999 | 140 | 2017-12-12 | Immediate to Two Years | Currently Critical | 1 | 1000
2398ADA1 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 2398 | This building contains a water fountain. The 2006 IBC Section 1109.5 states where a water fountain is provided, at least half should be accessible. This project would provide funding for the purchase and installation of a new accessible fixed high/ low ADA drinking fountain. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | MORMON FORT RESTROOM | 9913 | CNR | Parks |  | Las Vegas | 1999 | 240 | 2017-12-12 | Immediate to Two Years | Currently Critical | 1 | 3000
2397SEC1 | SECURITY SYSTEM INSTALLATION | 2397 | The building does not have a security system. This project recommends motion detection and window and door sensors be installed and interfaced with the site wide security system. | MORMON FORT VEHICLE SHOP | 9913 | CNR | Parks |  | Las Vegas | 1999 | 1176 | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5880
2397ENR1 | LIGHTING UPGRADE | 2397 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in the restroom and office areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | MORMON FORT VEHICLE SHOP | 9913 | CNR | Parks |  | Las Vegas | 1999 | 1176 | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
2900INT1 | INTERIOR FINISHES | 2900 | The interior finishes are in fair condition. It is recommended that the interior concrete masonry unit walls are cleaned and sealed at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | MORMOM FORT SOUTH RESTROOM | 9913 | CNR | Parks |  | Las Vegas | 2005 | 600 | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
2864INT1 | INTERIOR FINISHES | 2864 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | MORMOM FORT PUMP HOUSE | 9913 | CNR | Parks |  | Las Vegas | 1999 | 140 | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 700
2900INT2 | FLOORING MAINTENANCE | 2900 | The concrete floor sealant is damaged and reaching the end of its useful life. It is recommended that the concrete be stripped and re-sealed in order to extend the concretes' useful life. This project would provide for stripping the concrete and applying a new coat of sealant in the next 2-3 years. | MORMOM FORT SOUTH RESTROOM | 9913 | CNR | Parks |  | Las Vegas | 2005 | 600 | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
2900ENR1 | OCCUPANCY SENSOR INSTALLATION | 2900 | There are no occupancy sensors installed in the building to control lighting. It is recommended to install sensors in order to reduce energy costs. Occupancy sensors will be installed in each restroom. This project provides for purchase and installation of 2 sensors. | MORMOM FORT SOUTH RESTROOM | 9913 | CNR | Parks |  | Las Vegas | 2005 | 600 | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
2900INT3 | COUNTERTOP MAINTENANCE | 2900 | The concrete countertop sealant is damaged and reaching the end of its useful life. It is recommended that the concrete be stripped and re-sealed in order to extend the concretes' useful life. This project would provide for stripping the concrete and applying a new coat of sealant in the next 2-3 years. | MORMOM FORT SOUTH RESTROOM | 9913 | CNR | Parks |  | Las Vegas | 2005 | 600 | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 200
2900ADA1 | ADA SIGNAGE | 2900 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | MORMOM FORT SOUTH RESTROOM | 9913 | CNR | Parks |  | Las Vegas | 2005 | 600 | 2017-12-12 | Immediate to Two Years | Currently Critical | 1 | 900
2398ENR1 | LIGHTING UPGRADE | 2398 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in the restrooms for additional savings. Any electrical wiring upgrades are not included in this estimate. | MORMON FORT RESTROOM | 9913 | CNR | Parks |  | Las Vegas | 1999 | 240 | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 360
2398INT1 | INTERIOR FINISHES | 2398 | The interior finishes are in fair condition. It is recommended that the painted interior walls be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | MORMON FORT RESTROOM | 9913 | CNR | Parks |  | Las Vegas | 1999 | 240 | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1200
2399EXT1 | EXTERIOR/ INTERIOR FINISHES | 2399 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior and interior of the building excluding the roof. Included in the cost is cleaning and repairing the brick masonry as needed and caulking of any penetrations. It is recommended that the building be repaired and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MORMON FORT TOWER | 9913 | CNR | Parks |  | Las Vegas | 1999 | 200 | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
2900EXT1 | EXTERIOR FINISHES | 2900 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units, painting or sealing the exposed wood and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MORMOM FORT SOUTH RESTROOM | 9913 | CNR | Parks |  | Las Vegas | 2005 | 600 | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
9913SIT2 | ASPHALT PAVING INSTALLATION | 9913 | The access road from the parking lot to the Maintenance Shop and the parking area in front of the Maintenance Shop are not paved. This project would provide asphalt cement paving for a 10' wide access road and paving the parking area at the maintenance shop. The estimate includes grading, 6" base, compaction and installation of 4" thick asphalt cement paving. A drainage swale should be incorporated into the access road at the slope going down to the parking lot. | OLD LAS VEGAS MORMON FORT STATE PARK | 9913 | CNR | Parks |  | Las Vegas | 0 |  | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35000
9913SEC1 | FENCE UPGRADE | 9913 | The landscape fence on the south side of the site is not tall enough to keep people from climbing over it. Vandals and thieves have accessed the property by climbing over the fence and it is recommended to add height to the fence to prevent this. This project would provide for adding concrete masonry units to the existing fence to raise the height of the fence by 3 feet. | OLD LAS VEGAS MORMON FORT STATE PARK | 9913 | CNR | Parks |  | Las Vegas | 0 |  | 2017-12-12 | Immediate to Two Years | Currently Critical | 1 | 8000
9913ADA3 | ADA SIGNAGE | 9913 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | OLD LAS VEGAS MORMON FORT STATE PARK | 9913 | CNR | Parks |  | Las Vegas | 0 |  | 2017-12-12 | Immediate to Two Years | Currently Critical | 1 | 2500
9913SIT5 | GRADING AT BONEYARD AREA | 9913 | The site has a drainage problem in the bone yard area on the northwest side of the site. The existing grade does not properly slope towards the storm drain. Water accumulates in several areas adjacent to the drain creating a water and mud problem during inclement weather. This project would provide for grading in this area to slope the grade towards the drain. | OLD LAS VEGAS MORMON FORT STATE PARK | 9913 | CNR | Parks |  | Las Vegas | 0 |  | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
9913ADA2 | GROUP USE AREA IMPROVEMENTS | 9913 | The group use area is not ADA compliant and is not functional as is. This area should be scheduled for improvements. Currently, the picnic tables are under wooden grape vine trellises. The tables are also worn and deteriorated and there are no ADA tables or access. This project would provide for the purchase and installation of 10 new picnic tables including one accessible table, a new shade ramada to cover all of the tables and flatwork to provide ADA access between the new tables and the restroom. | OLD LAS VEGAS MORMON FORT STATE PARK | 9913 | CNR | Parks |  | Las Vegas | 0 |  | 2017-12-12 | Immediate to Two Years | Currently Critical | 1 | 25000
9913SIT3 | WATER FEATURE REPAIRS | 9913 | The man made creek and pond on the site are deteriorating and due for repairs. They are made of free-formed concrete to direct and collect the water. The concrete is settling and shifting and has significant cracking. The cracks allow water to seep into the ground requiring the park to increase their water consumption from the city. The creek and pond have not been equipped with a sufficient pump and filter which have allowed debris and trash to build up and generally to cloud the water. This project would provide for repairing the concrete and cleaning up the creek and pond. The pump and filter equipment will be addressed in the Pump House projects. | OLD LAS VEGAS MORMON FORT STATE PARK | 9913 | CNR | Parks |  | Las Vegas | 0 |  | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
9913SIT1 | FOG / CRACK SEAL ASPHALT PAVING | 9913 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and fog sealing of the paved parking lot. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 25,000 square feet of asphalt area was used to generate this estimate. This project or a portion thereof was previously recommended in the FCA report dated 10/15/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/01/2011. | OLD LAS VEGAS MORMON FORT STATE PARK | 9913 | CNR | Parks |  | Las Vegas | 0 |  | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18750
9913ADA1 | ADA SITE IMPROVEMENTS | 9913 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. Access to the various features throughout the site is necessary to comply with ADA accessibility requirements. This project would provide for an accessible path of travel to the adobe fort, tower, group use area and to a platform to view the battle re-enactments and other performances on the upper portion of the site. This will require regrading, placement of P.C. concrete, signage, ramps, handrails, a concrete viewing platform and any other necessary upgrades. The 2006 IBC, ICC/ANSI A117.1 - 2003 and the most current version of the Americans With Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 10/15/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/01/2011. | OLD LAS VEGAS MORMON FORT STATE PARK | 9913 | CNR | Parks |  | Las Vegas | 0 |  | 2017-12-12 | Immediate to Two Years | Currently Critical | 1 | 100000
9913SIT4 | TREE REMOVAL | 9913 | There are two Mulberry trees that have reached the end of their expected lives and should be removed. The trees are adjacent to the Historic Fort Museum which would incur extensive damage if one of these trees fell on it. Previously, a similar tree fell into the road and caused an emergency road closure and removal of the fallen tree. This project would provide for removal of the two trees next to the Museum by a licensed tree removal company and a survey of the site to determine whether any other trees should be removed. | OLD LAS VEGAS MORMON FORT STATE PARK | 9913 | CNR | Parks |  | Las Vegas | 0 |  | 2017-12-12 | Immediate to Two Years | Currently Critical | 1 | 3000
1907ENV2 | TERMITE CONTROL | 1907 | There are numerous signs throughout this building of insect infestation including Termites. Due to the potential risk of disease and damage to the building, this project provides for treatment and clean up of the insects by a licensed pest control business. It is recommended that the building be treated in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain control of the pests. | RANGER RESIDENCE #1 | 9931 | CNR | Parks |  | Laughlin | 1995 | 1873 | 2017-12-13 | Immediate to Two Years | Currently Critical | 1 | 1000
1907INT1 | INTERIOR FINISHES | 1907 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | RANGER RESIDENCE #1 | 9931 | CNR | Parks |  | Laughlin | 1995 | 1873 | 2017-12-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10500
1907EXT1 | EXTERIOR FINISHES | 1907 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | RANGER RESIDENCE #1 | 9931 | CNR | Parks |  | Laughlin | 1995 | 1873 | 2017-12-13 | Immediate to Two Years | Currently Critical | 1 | 10500
1907ENR1 | WINDOW REPLACEMENT | 1907 | The windows are original, dual pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 10 units. Removal and disposal of the existing windows is included in this estimate. | RANGER RESIDENCE #1 | 9931 | CNR | Parks |  | Laughlin | 1995 | 1873 | 2017-12-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
1908EXT1 | EXTERIOR FINISHES | 1908 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting the stucco and wood, sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | COMFORT STATION #1 - DAY USE | 9931 | CNR | Parks |  | Laughlin | 1995 | 308 | 2017-12-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1540
1908EXT2 | CONCRETE SLAB REPAIRS | 1908 | The concrete slab is settling especially at the corners and has extensive cracking. The grade is shifting away from the building, pulling the concrete with it. The settling and shifting will continue and cause extensive damage to the concrete slab and eventually to the buildings footings. This project would provide for regrading and compacting next to and underneath the slab and replacing the concrete as needed. | COMFORT STATION #1 - DAY USE | 9931 | CNR | Parks |  | Laughlin | 1995 | 308 | 2017-12-13 | Immediate to Two Years | Currently Critical | 1 | 5000
1908ADA1 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 1908 | There is a water fountain in front of the building. The 2006 IBC Section 1109.5 states where a water fountain is provided, at least half should be accessible. This project would provide funding for the purchase and installation of a new accessible fixed high/ low ADA drinking fountain. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | COMFORT STATION #1 - DAY USE | 9931 | CNR | Parks |  | Laughlin | 1995 | 308 | 2017-12-13 | Immediate to Two Years | Currently Critical | 1 | 4000
1908INT1 | INTERIOR FINISHES | 1908 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted and the ceramic tile be repaired at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | COMFORT STATION #1 - DAY USE | 9931 | CNR | Parks |  | Laughlin | 1995 | 308 | 2017-12-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1540
1908ADA3 | ADA RESTROOM REMODEL | 1908 | The Men's and Women's designated ADA restrooms do not entirely meet the Americans with Disabilities Act (ADA) requirements. This project would provide funding for improvements to bring the restrooms into compliance. Improvements may include adjusting existing fixtures or installing new fixtures such as sinks, toilets, hardware, mirrors, fixtures, flooring and paint. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | COMFORT STATION #1 - DAY USE | 9931 | CNR | Parks |  | Laughlin | 1995 | 308 | 2017-12-13 | Immediate to Two Years | Currently Critical | 1 | 5000
1907SIT1 | DRIVEWAY REPLACEMENT | 1907 | The concrete driveway has extensive cracking and settling damage and is due for replacement. This project would provide for the installation of a new 4" thick concrete slab driveway in front of the garage door. Removal and disposal of the existing concrete is included in this estimate. 400 square feet of area was used to generate this estimate. | RANGER RESIDENCE #1 | 9931 | CNR | Parks |  | Laughlin | 1995 | 1873 | 2017-12-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
1907INT2 | COUNTERTOP REPLACEMENT | 1907 | The countertops in the kitchen are showing signs of wear and tear particularly at the Formica edges and corners. The countertops are delaminating and failing. This project recommends the replacement of the existing damaged countertops with heavy duty, quality finishes. This project would provide funding for the removal and replacement of the countertops. | RANGER RESIDENCE #1 | 9931 | CNR | Parks |  | Laughlin | 1995 | 1873 | 2017-12-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
1907EXT2 | GARAGE DOOR REPLACEMENT | 1907 | The overhead garage door is cracked down the middle due to wind exposure and does not function properly. It is original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the overhead garage door and replacement with a new door. | RANGER RESIDENCE #1 | 9931 | CNR | Parks |  | Laughlin | 1995 | 1873 | 2017-12-13 | Immediate to Two Years | Currently Critical | 1 | 2800
2859INT1 | INTERIOR FINISHES | 2859 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | COMFORT STATION #2C - CAMPGROUND | 9931 | CNR | Parks |  | Laughlin | 2007 | 1230 | 2017-12-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6150
2859EXT1 | EXTERIOR FINISHES | 2859 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting the stucco and wood, sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-6 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | COMFORT STATION #2C - CAMPGROUND | 9931 | CNR | Parks |  | Laughlin | 2007 | 1230 | 2017-12-13 | Four to Ten Years | Long-Term Needs | 3 | 6150
2860EXT1 | EXTERIOR FINISHES | 2860 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting the stucco, sealing the concrete masonry units and wood and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-6 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | ENTRANCE STATION | 9931 | CNR | Parks |  | Laughlin | 2007 | 288 | 2017-12-13 | Four to Ten Years | Long-Term Needs | 3 | 1440
2349INT1 | INTERIOR FINISHES | 2349 | The interior finishes are in fair condition. It is recommended that the finished interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project does not apply to the open framed walls and ceilings in the main shop area. | SHOP/MAINTENANCE BUILDING | 9931 | CNR | Parks |  | Laughlin | 1998 | 1600 | 2017-12-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1800
2349HVA1 | A.C. COMPRESSOR REPLACEMENT | 2349 | An air conditioner condenser is installed on the side of this building and the compressor has failed. It was not operational at the time of the survey and should be scheduled for replacement. This project would provide for a new compressor to be installed including all required connections to utilities. The estimate includes removal and disposal of the old unit. | SHOP/MAINTENANCE BUILDING | 9931 | CNR | Parks |  | Laughlin | 1998 | 1600 | 2017-12-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
2349ENR1 | LIGHTING UPGRADE | 2349 | The existing lighting fixtures are the older T-8 fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. T-5 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in the restroom, office, storage rooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | SHOP/MAINTENANCE BUILDING | 9931 | CNR | Parks |  | Laughlin | 1998 | 1600 | 2017-12-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2400
2861INT1 | INTERIOR FINISHES | 2861 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | RANGER RESIDENCE #2 | 9931 | CNR | Parks |  | Laughlin | 2007 | 1400 | 2017-12-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7000
2349ADA1 | ADA PARKING UPGRADES | 2349 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The existing ADA parking space does not entirely meet the requirements of the code, specifically because it is not 18 feet long. This project provides funding to bring the existing ADA parking space up to code including regrading to add length to the parking space, placement of P.C. concrete, updated signage, re-striping, and any other necessary upgrades. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | SHOP/MAINTENANCE BUILDING | 9931 | CNR | Parks |  | Laughlin | 1998 | 1600 | 2017-12-13 | Immediate to Two Years | Currently Critical | 1 | 2000
2862EXT1 | EXTERIOR FINISHES | 2862 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure in the next 5-6 years and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | RESIDENCE #2 CARPORT | 9931 | CNR | Parks |  | Laughlin | 2007 | 200 | 2017-12-13 | Four to Ten Years | Long-Term Needs | 3 | 400
2349SFT1 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 2349 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. | SHOP/MAINTENANCE BUILDING | 9931 | CNR | Parks |  | Laughlin | 1998 | 1600 | 2017-12-13 | Immediate to Two Years | Currently Critical | 1 | 4000
2860INT1 | INTERIOR FINISHES | 2860 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | ENTRANCE STATION | 9931 | CNR | Parks |  | Laughlin | 2007 | 288 | 2017-12-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1440
2349EXT1 | EXTERIOR FINISHES | 2349 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SHOP/MAINTENANCE BUILDING | 9931 | CNR | Parks |  | Laughlin | 1998 | 1600 | 2017-12-13 | Four to Ten Years | Long-Term Needs | 3 | 8000
2861EXT1 | EXTERIOR FINISHES | 2861 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | RANGER RESIDENCE #2 | 9931 | CNR | Parks |  | Laughlin | 2007 | 1400 | 2017-12-13 | Four to Ten Years | Long-Term Needs | 3 | 7000
2349HVA2 | EVAPORATIVE COOLER REPLACEMENT | 2349 | An evaporative cooler is installed on the side of this building that has reached the end of it's useful and expected life and is no longer operational. This project would provide for a new commercial size evaporative cooler to be installed including all required connections to utilities. The estimate includes removal and disposal of the old cooler. | SHOP/MAINTENANCE BUILDING | 9931 | CNR | Parks |  | Laughlin | 1998 | 1600 | 2017-12-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
9931SIT4 | STORAGE STRUCTURE INSTALLATION | 9931 | There is a need for a storage structure in the maintenance area. The trucks, agricultural equipment and building materials are exposed to the sun causing preventable damage and maintenance costs. This project would provide a three sided steel structure 24' x 40' to be constructed in the maintenance yard. | BIG BEND STATE RECREATION AREA SITE | 9931 | CNR | Parks |  | Laughlin | 0 |  | 2017-12-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 62400
9931ADA2 | ADA PARKING, ACCESSIBLE ROUTE | 9931 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. There are several existing ADA parking spaces in the boat ramp and day use areas that are not fully compliant. This project would provide for signage, curb ramps and walkways from the parking spaces to site features. This may require regrading, installing P.C. concrete, striping, signage and any other necessary upgrades. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 05/05/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/02/2011. | BIG BEND STATE RECREATION AREA SITE | 9931 | CNR | Parks |  | Laughlin | 0 |  | 2017-12-13 | Immediate to Two Years | Currently Critical | 1 | 10000
9931SFT1 | RELOCATE SHADE RAMADAS | 9931 | There are five shade ramadas that need to be relocated. They are located on the north side of the day use area near the river. The banks of the river have eroded and are undermining the slabs and footings of the ramadas. This has created a safety hazard around the structures where the public is at risk of tripping, falling off the edge or the slab breaking while people are on it. This project would provide for extracting the ramadas from their existing footings, removing the existing footings and slabs, installing the ramadas in new footings and pouring new slabs. State Parks provided a cost for this project of $5,000 per ramada. | BIG BEND STATE RECREATION AREA SITE | 9931 | CNR | Parks |  | Laughlin | 0 |  | 2017-12-13 | Immediate to Two Years | Currently Critical | 1 | 25000
9931EXT1 | EXTERIOR FINISHES, SHADE RAMADAS | 9931 | There are 43 steel shade ramadas in different locations throughout the site which are 400 s.f. each and a Bus Stop Shelter that is 43 s.f. for a total of 17,243 square feet. It is important to maintain the finish, weather resistance and appearance of the structures. This project would provide for painting of the structures in the next 4-5 years and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structures. | BIG BEND STATE RECREATION AREA SITE | 9931 | CNR | Parks |  | Laughlin | 0 |  | 2017-12-13 | Four to Ten Years | Long-Term Needs | 3 | 34486
9931SIT5 | CXT COMFORT STATION | 9931 | The north side of the day use area does not have a restroom. Given the distance of this area from existing restroom facilities, health concerns exist due to visitors not using the restroom facilities at other areas. It is recommended that a CXT or similar style Men's and Women's comfort station be installed which meets current ADA requirements. This project would provide for the purchase and installation of a two stall CXT restroom including an ADA compliant concrete parking and loading zone adjacent to the restroom. | BIG BEND STATE RECREATION AREA SITE | 9931 | CNR | Parks |  | Laughlin | 0 |  | 2017-12-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 48000
9931SIT3 | SITE DRAINAGE ASSESSMENT | 9931 | There are several areas throughout the site that have drainage problems. A large amount of runoff travels through the property during inclement weather. The drainage features include culverts, ditches and rip rap berms which have eroded over time and no longer control the runoff properly. This project would provide for a site survey and drainage report to be completed by a licensed professional to determine what measures should be taken to prevent future flooding. Future projects may arise from the results of this report. | BIG BEND STATE RECREATION AREA SITE | 9931 | CNR | Parks |  | Laughlin | 0 |  | 2017-12-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
9931SIT2 | CRACK / FOG SEAL ASPHALT PAVING | 9931 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and fog sealing of the three large parking lots and the walkways throughout the day use areas. Striping is included in this estimate. The access roads throughout the site are maintained by NDOT and are not included in this project. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 150,000 square feet of asphalt area was used to generate this estimate. | BIG BEND STATE RECREATION AREA SITE | 9931 | CNR | Parks |  | Laughlin | 0 |  | 2017-12-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 112500
9931SIT6 | ASPHALT PAVING INSTALLATION | 9931 | The access road to the Shop/ Maintenance Building and Ranger Residences and the parking areas around these buildings are not paved. This project would provide asphalt cement paving for a 20' wide access road, for parking around the Residences and paving the vehicle yard around the Shop/ Maintenance Building. The estimate includes grading, 6" base, compaction and installation of 4" thick asphalt cement paving. | BIG BEND STATE RECREATION AREA SITE | 9931 | CNR | Parks |  | Laughlin | 0 |  | 2017-12-13 | Four to Ten Years | Long-Term Needs | 3 | 250000
9931SIT7 | BOAT DOCK DECKING REPLACEMENT | 9931 | The 2x decking on the boat dock is approaching the end of its expected life and should be scheduled for replacement. The decking is warping, bending and desurfacing. It is important for the deck to be smooth and flat to avoid a safety hazard around the boats and water. This project would provide for purchase and installation of new decking for the entire boat dock. Additional bracing may be necessary to provide a solid framework depending on what product is used in the replacement. Removal and disposal of the existing deckng is included in this estimate. | BIG BEND STATE RECREATION AREA SITE | 9931 | CNR | Parks |  | Laughlin | 0 |  | 2017-12-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 36000
9931SIT8 | EROSION/ FLOOD CONTROL | 9931 | The water level of the Colorado river varies by as much as 9 feet depending on the flow controls from the power plants upstream. This is already causing extensive damage to the beach and Day Use areas on the north side of the site and the erosion is ongoing. Approximately 40 feet of beach has already been lost and the erosion is now threatening the ramadas, parking lot and access road. This project would provide for long term erosion controls along the north shoreline to prevent further loss of shoreline and facilities. This project may qualify for one of three FEMA grant programs to alleviate some of the high cost of the work. These are PDM (Pre-Disaster Mitigation), FMA (Flood Mitigation) or RFC (Repetitive Flood Claims) in which the State would need to provide a 25% match. | BIG BEND STATE RECREATION AREA SITE | 9931 | CNR | Parks |  | Laughlin | 0 |  | 2017-12-13 | Immediate to Two Years | Currently Critical | 1 | 4200000
1223EXT1 | EXTERIOR FINISHES | 1223 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/16/2012. | FLAMMABLE STORAGE | 9963 | CNR | Parks |  | Valley of Fire | 1972 | 480 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 480
1278INT1 | INTERIOR FINISHES | 1278 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 04/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/16/2012. | STORAGE (Old Water Treatment Plant) | 9963 | CNR | Parks |  | Valley of Fire | 1964 | 323 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1615
1278EXT1 | EXTERIOR FINISHES | 1278 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/16/2012. | STORAGE (Old Water Treatment Plant) | 9963 | CNR | Parks |  | Valley of Fire | 1964 | 323 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1615
1223INT1 | INTERIOR FINISHES | 1223 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. This project or a portion thereof was previously recommended in the FCA report dated 04/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/16/2012. | FLAMMABLE STORAGE | 9963 | CNR | Parks |  | Valley of Fire | 1972 | 480 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2400
1222EXT1 | EXTERIOR FINISHES | 1222 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. This project should be completed on a cyclical basis based on environmental conditions. | EAST MAP RAMADA | 9963 | CNR | Parks |  | Valley of Fire | 1974 | 900 | 2018-05-23 | Four to Ten Years | Long-Term Needs | 3 | 4500
1278EXT2 | DEMOLISH STRUCTURE | 1278 | The structure is dilapidated and deteriorating and has reached the end of its useful life. It is approaching 50 years of age and has rodent and insect infestations. This project would provide funding for the demolition and disposal of the building. | STORAGE (Old Water Treatment Plant) | 9963 | CNR | Parks |  | Valley of Fire | 1964 | 323 | 2018-05-23 | Four to Ten Years | Long-Term Needs | 3 | 3230
1223EXT3 | EXTERIOR DOOR REPLACEMENT | 1223 | The exterior metal doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the double door assembly with new metal doors, frames and hardware. Removal and disposal of the existing doors is included in this estimate. | FLAMMABLE STORAGE | 9963 | CNR | Parks |  | Valley of Fire | 1972 | 480 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
2866EXT1 | EXTERIOR FINISHES | 2866 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | RESIDENCE #2 | 9963 | CNR | Parks |  | Valley of Fire | 2008 | 1404 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7020
2718EXT1 | EXTERIOR FINISHES | 2718 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/16/2012. | WELL/PUMP HOUSE | 9963 | CNR | Parks |  | Valley of Fire | 1998 | 100 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
2718INT1 | INTERIOR FINISHES | 2718 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 04/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/16/2012. | WELL/PUMP HOUSE | 9963 | CNR | Parks |  | Valley of Fire | 1998 | 100 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
2720EXT1 | EXTERIOR FINISHES | 2720 | It is important to maintain the finish, weather resistance and appearance of the structures. This project would provide funding to protect the exterior of the structures excluding the roof. Included in the cost is sealing and re-pointing the stone to maintain its natural look. It is recommended that the structures be sealed and re-pointed as needed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/16/2012. | CABINS | 9963 | CNR | Parks |  | Valley of Fire | 1935 | 588 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5880
2865EXT1 | EXTERIOR FINISHES | 2865 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | RESIDENCE #1 | 9963 | CNR | Parks |  | Valley of Fire | 2008 | 1404 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7020
2224INT1 | INTERIOR FINISHES | 2224 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. This project or a portion thereof was previously recommended in the FCA report dated 04/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/16/2012. | WEST FEE BOOTH | 9963 | CNR | Parks |  | Valley of Fire | 1998 | 100 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
2224EXT1 | EXTERIOR FINISHES | 2224 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units, painting the metal panels and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/16/2012. | WEST FEE BOOTH | 9963 | CNR | Parks |  | Valley of Fire | 1998 | 100 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
2867INT1 | INTERIOR FINISHES | 2867 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | RESIDENCE #5 | 9963 | CNR | Parks |  | Valley of Fire | 2008 | 1404 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7020
2867EXT1 | EXTERIOR FINISHES | 2867 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | RESIDENCE #5 | 9963 | CNR | Parks |  | Valley of Fire | 2008 | 1404 | 2018-05-23 | Four to Ten Years | Long-Term Needs | 3 | 7020
2866INT1 | INTERIOR FINISHES | 2866 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | RESIDENCE #2 | 9963 | CNR | Parks |  | Valley of Fire | 2008 | 1404 | 2018-05-23 | Four to Ten Years | Long-Term Needs | 3 | 7020
2865SFT1 | EXTERIOR STAIR HANDRAIL REPLACEMENT | 2865 | The stair handrails on the exterior steps are older and do not meet code for safety. The gripping surfaces are incorrect, they are not continuous from the top to bottom landings and they do not appear to be structurally capable of resisting loads of 50 plf as prescribed in the building code. The code also requires a guardrail anywhere there is an elevation change that exceeds 30 inches. This project recommends the installation of handrails at the stairs and guardrails around the perimeter of the patio in accordance with IBC Section 1012. | RESIDENCE #1 | 9963 | CNR | Parks |  | Valley of Fire | 2008 | 1404 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
2870EXT1 | EXTERIOR FINISHES | 2870 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units, painting the metal trim and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CAMPGROUND EXPANSION COMFORT STATION | 9963 | CNR | Parks |  | Valley of Fire | 2007 | 525 | 2018-05-23 | Four to Ten Years | Long-Term Needs | 3 | 2625
2865INT1 | INTERIOR FINISHES | 2865 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | RESIDENCE #1 | 9963 | CNR | Parks |  | Valley of Fire | 2008 | 1404 | 2018-05-23 | Four to Ten Years | Long-Term Needs | 3 | 7020
2869EXT1 | EXTERIOR FINISHES | 2869 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | RESIDENCE STORAGE SHED #2 | 9963 | CNR | Parks |  | Valley of Fire | 2008 | 100 | 2018-05-23 | Four to Ten Years | Long-Term Needs | 3 | 500
2870INT1 | INTERIOR FINISHES | 2870 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | CAMPGROUND EXPANSION COMFORT STATION | 9963 | CNR | Parks |  | Valley of Fire | 2007 | 525 | 2018-05-23 | Four to Ten Years | Long-Term Needs | 3 | 2625
2898EXT1 | EXTERIOR/ INTERIOR FINISHES | 2898 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CABINS SST COMFORT STATION | 9963 | CNR | Parks |  | Valley of Fire | 2007 | 180 | 2018-05-23 | Four to Ten Years | Long-Term Needs | 3 | 900
2870PLM1 | WATER HEATER REPLACEMENT | 2870 | There is an 80 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 4-5 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | CAMPGROUND EXPANSION COMFORT STATION | 9963 | CNR | Parks |  | Valley of Fire | 2007 | 525 | 2018-05-23 | Four to Ten Years | Long-Term Needs | 3 | 2000
2897EXT1 | EXTERIOR/ INTERIOR FINISHES | 2897 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | LOOP B UPPER SST COMFORT STATION | 9963 | CNR | Parks |  | Valley of Fire | 2007 | 180 | 2018-05-23 | Four to Ten Years | Long-Term Needs | 3 | 900
2896EXT1 | EXTERIOR/ INTERIOR FINISHES | 2896 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | LOOP B LOWER SST COMFORT STATION | 9963 | CNR | Parks |  | Valley of Fire | 2007 | 180 | 2018-05-23 | Four to Ten Years | Long-Term Needs | 3 | 900
2868EXT1 | EXTERIOR FINISHES | 2868 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | RESIDENCE STORAGE SHED #1 | 9963 | CNR | Parks |  | Valley of Fire | 2008 | 100 | 2018-05-23 | Four to Ten Years | Long-Term Needs | 3 | 500
2899EXT1 | EXTERIOR/ INTERIOR FINISHES | 2899 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | EAST ENTRANCE SST COMFORT STATION | 9963 | CNR | Parks |  | Valley of Fire | 2007 | 180 | 2018-05-23 | Four to Ten Years | Long-Term Needs | 3 | 900
2719EXT1 | EXTERIOR FINISHES | 2719 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/16/2012. | RESIDENCE 3 STORAGE | 9963 | CNR | Parks |  | Valley of Fire | 1995 | 220 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1100
2875ADA1 | ADA PARKING SIGNS | 2875 | The existing ADA signage for the 9 accessible parking spaces do not reflect the most currect maximum fine amount. This project would provide for a new sticker reflecting the most currnet maximum fine information to be installed. | CAMPGROUND EXPANSION RAMADA #5 | 9963 | CNR | Parks |  | Valley of Fire | 2007 | 150 | 2018-05-23 | Immediate to Two Years | Currently Critical | 1 | 1512
2893EXT1 | EXTERIOR/ INTERIOR FINISHES | 2893 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MOUSE'S TANK SST COMFORT STATION #2 | 9963 | CNR | Parks |  | Valley of Fire | 2007 | 180 | 2018-05-23 | Four to Ten Years | Long-Term Needs | 3 | 900
2894ELE1 | EXTERIOR/ INTERIOR FINISHES | 2894 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MOUSE'S TANK SST COMFORT STATION #1 | 9963 | CNR | Parks |  | Valley of Fire | 2007 | 180 | 2018-05-23 | Four to Ten Years | Long-Term Needs | 3 | 900
2895EXT1 | EXTERIOR/ INTERIOR FINISHES | 2895 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | RAINBOW VISTA SST COMFORT STATION | 9963 | CNR | Parks |  | Valley of Fire | 2007 | 78 | 2018-05-23 | Four to Ten Years | Long-Term Needs | 3 | 390
3154INT1 | INTERIOR FINISHES | 3154 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | WHITE DOME COMFORT STATION | 9963 | CNR | Parks |  | Valley of Fire | 1974 | 240 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1200
9963SIT6 | ASPHALT PAVING REPLACEMENT (MAINTENANCE YARD) | 9963 | The asphalt paving in the maintenance yard area is failing, with significant alligatoring, settling and cracks observed. This project covers the removal and replacement of the existing asphalt in the maintenance yard up to the access road that NDOT maintains. Striping for safety, parking and loading zones is included in this estimate. 24,000 square feet was used to generate this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/16/2012. | VALLEY OF FIRE STATE PARK SITE | 9963 | CNR | Parks |  | Valley of Fire | 1935 |  | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 120000
9963EXT5 | EXTERIOR FINISHES, RAMADAS | 9963 | There are 80 steel shade ramadas and 4 steel carports in different locations throughout the site which add up to a total of 28,890 square feet. It is important to maintain the finish, weather resistance and appearance of the structures. This project would provide for painting of the structures and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structures. This project or a portion thereof was previously recommended in the FCA report dated 04/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/16/2012. | VALLEY OF FIRE STATE PARK SITE | 9963 | CNR | Parks |  | Valley of Fire | 1935 |  | 2018-05-23 | Four to Ten Years | Long-Term Needs | 3 | 57780
9963ENV4 | COMPOSTING TOILET MODIFICATIONS | 9963 | The Valley of Fire State Park has two Clivus composting comfort stations. These are 'dry' restroom facilities with a holding tank located under the building. This system, working via microbial action, breaks down the wastes. This type of system does not work well at its remote location. They are very labor intensive. Due to their intermittent use and desert location, the composting mass has been drying out, which interrupts the decomposition process and makes the materials difficult to remove. To remedy this, staff has to manually haul water and sawdust to the comfort station and then mix it with the waste. This project recommends the installation of a moistening system, available from the manufacturer, which introduces a few gallons of water into the tank to keep the composting process operational year round. This project or a portion thereof was previously recommended in the FCA report dated 04/11/2002 and 04/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/16/2012. | VALLEY OF FIRE STATE PARK SITE | 9963 | CNR | Parks |  | Valley of Fire | 1935 |  | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
3151EXT1 | EXTERIOR FINISHES | 3151 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units, painting the metal trim and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | VOF ADMINISTRATION BUILDING | 9963 | CNR | Parks |  | Valley of Fire | 2009 | 1184 | 2018-05-23 | Four to Ten Years | Long-Term Needs | 3 | 5920
3152EXT1 | EXTERIOR FINISHES | 3152 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units, painting the metal trim and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | VISITORS CENTER COMFORT STATION | 9963 | CNR | Parks |  | Valley of Fire | 2009 | 450 | 2018-05-23 | Four to Ten Years | Long-Term Needs | 3 | 2250
3153EXT1 | EXTERIOR FINISHES | 3153 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | WATER TREATMENT SHED | 9963 | CNR | Parks |  | Valley of Fire | 0 | 32 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 100
9963PLM1 | REPLACE UNDERGROUND WATER PIPE, ROAD | 9963 | The Valley of Fire State Park is served by wells for domestic water use. The piping that serves the "loop road" is of an older thin walled blue plastic. The pipe requires frequent service and repair due to the age and condition of the system. This project recommends replacing the existing water main with a new, Schedule 80 plastic pipe system. The park is operational year round, so it will be necessary to trench, lay the pipe, backfill and make connections concurrent with ongoing park activities. Two (2) miles of piping was used for this estimate including trenching and backfill. This project or a portion thereof was previously recommended in the FCA report dated 04/11/2002 and 04/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/16/2012. | VALLEY OF FIRE STATE PARK SITE | 9963 | CNR | Parks |  | Valley of Fire | 1935 |  | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 316800
3154EXT1 | EXTERIOR FINISHES | 3154 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | WHITE DOME COMFORT STATION | 9963 | CNR | Parks |  | Valley of Fire | 1974 | 240 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1200
3151INT1 | INTERIOR FINISHES | 3151 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | VOF ADMINISTRATION BUILDING | 9963 | CNR | Parks |  | Valley of Fire | 2009 | 1184 | 2018-05-23 | Four to Ten Years | Long-Term Needs | 3 | 5920
3154ADA1 | ADA RESTROOM REMODEL | 3154 | The comfort station does not have an ADA accessible restroom. The existing restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | WHITE DOME COMFORT STATION | 9963 | CNR | Parks |  | Valley of Fire | 1974 | 240 | 2018-05-23 | Immediate to Two Years | Currently Critical | 1 | 7000
9963PLM2 | REPLACE UNDERGROUND WATER PIPE, VISITORS CENTER | 9963 | The Valley of Fire State Park is served by wells for domestic water use. A portion of the piping between the main well house and the Visitors Center at the north end of the park is of an older 4" ductile iron. The pipe requires frequent service and repair due to the age and condition of the system. This project recommends replacing the existing main with a new, Schedule 80 plastic pipe system. The park is operational year round, so it will be necessary to trench, lay the pipe, backfill and make connections concurrent with ongoing park activities. 1-1/2 miles of pipe was used for this estimate including trenching and backfill. This project or a portion thereof was previously recommended in the FCA report dated 04/11/2002 and 04/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/16/2012. | VALLEY OF FIRE STATE PARK SITE | 9963 | CNR | Parks |  | Valley of Fire | 1935 |  | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 237600
9963SIT7 | FUEL TANK REPLACEMENT | 9963 | The above ground fuel storage tank and distribution system was installed in 1996. Staff noted that it has had leaks, the pumps have been repaired several times and the totalizer is inaccurate. The tank and delivery system has reached the end of its useful life and should be scheduled for replacement. This project recommends replacing the 2,000 gallon capacity storage tank and the associated pumping system. The estimate includes removal and disposal of the existing equipment. | VALLEY OF FIRE STATE PARK SITE | 9963 | CNR | Parks |  | Valley of Fire | 1935 |  | 2018-05-23 | Immediate to Two Years | Currently Critical | 1 | 25000
9963PLM4 | WATER TANK REPLACEMENT | 9963 | There are a total of 6 water storage tanks at the site. Four of them are older underground steel tanks including 2 - 5,000 gallon tanks near the maintenance yard and 2 - 1,600 gallon above ground tanks at the Group Use Area. The average life span of a water storage tank is forty to fifty years. These tank were installed in 1964. With the passage of time the tanks have deteriorated and should be scheduled for replacement in the next 3-4 years. This project would provide for new water storage tanks to be installed including connections to existing utilities. | VALLEY OF FIRE STATE PARK SITE | 9963 | CNR | Parks |  | Valley of Fire | 1935 |  | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35000
9963ADA3 | ADA ACCESSIBLE PARKING | 9963 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel at 6 Comfort Stations across the site are necessary to comply with ADA accessibility requirements. This project would provide for a concrete van accessible ADA parking and loading space and concrete walkway to the existing sidewalk at the Atlatl, West Entrance, Mouse's Tank #1 & #2, Rainbow Vista and East Entrance Comfort Stations. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | VALLEY OF FIRE STATE PARK SITE | 9963 | CNR | Parks |  | Valley of Fire | 1935 |  | 2018-05-23 | Immediate to Two Years | Currently Critical | 1 | 15000
9963ADA2 | ARCH ROCK CAMPGROUND ADA UPGRADES | 9963 | The designated ADA accessible campsite at the Arch Rock campground does not meet current accessibility guidelines. Required features of an accessible campsite may include a 20'-0" wide drive aisle for RV/ tent trailer sites and accessible amenities on an accessible route to existing restroom including the grill, picnic table, fire ring and water & electric utilities. This project provides for upgrading one existing campsite at Arch Rock to accessible campsites. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | VALLEY OF FIRE STATE PARK SITE | 9963 | CNR | Parks |  | Valley of Fire | 1935 |  | 2018-05-23 | Immediate to Two Years | Currently Critical | 1 | 10000
9963PLM3 | WELL REPLACEMENT | 9963 | According to staff, the existing well is currently about 1,100 feet deep and has a 6" diameter casing that has deteriorated and is bent in several places. It is no longer reliable and should be scheduled for replacement. It is recommended to cap and abandon the existing well, drill a new well and install new casing and pumps as needed. | VALLEY OF FIRE STATE PARK SITE | 9963 | CNR | Parks |  | Valley of Fire | 1935 |  | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 125000
3153PLM1 | WATER TREATMENT SYSTEM REPLACEMENT | 3153 | The existing automatic chlorine injection system in the building is older and the State Health Department has recommended an upgrade to the system. Poor production from the system causes wear and tear on the domestic water supply lines, plumbing fixtures and HVAC equipment. This project would provide for the replacement of the existing system with new equipment. This project would also provide for a chemical treatment program including an updated chemicals control system, service and employee training provided by a qualified water treatment vendor. The annual maintenance fee charged by the water treatment vendor would be determined after an investigation of the water system is complete. These annual costs are not included in this project cost. For budgeting purposes, a $12,000 fee is suggested. | WATER TREATMENT SHED | 9963 | CNR | Parks |  | Valley of Fire | 0 | 32 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
9963EXT4 | ATLATL ROCK SITE UPGRADES | 9963 | There is an exterior stair system that provides access to the Atlatl Rock petroglyphs site. The paint on the stairs and guardrails is peeling, and some metal is exposed to the elements. The Lexan panel at the top of the stairs has become cloudy and has many scratches due to wind and sand as well as vandalism. This project provides for cleaning and prep of the stringers, guardrails and other structural elements, and the application of an epoxy-based paint and replacing the Lexan panel with a more durable product. This work should be performed off season, to minimize interruption of access to the site. This project or a portion thereof was previously recommended in the FCA report dated 04/11/2002 and 04/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/16/2012. | VALLEY OF FIRE STATE PARK SITE | 9963 | CNR | Parks |  | Valley of Fire | 1935 |  | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0555EXT1 | EXTERIOR FINISHES | 0555 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/16/2012. | VOF MAINTENANCE SHOP | 9963 | CNR | Parks |  | Valley of Fire | 1972 | 6000 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
0556EXT2 | ROOF REPLACEMENT | 0556 | The corrugated metal roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a standing seam metal roofing system. This estimate includes removal and disposal of the old roofing. | VOF STORAGE #1 | 9963 | CNR | Parks |  | Valley of Fire | 1966 | 648 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7776
0556EXT1 | EXTERIOR FINISHES | 0556 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the wood trim and caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/16/2012. | VOF STORAGE #1 | 9963 | CNR | Parks |  | Valley of Fire | 1966 | 648 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 648
0557EXT1 | EXTERIOR FINISHES | 0557 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units, painting the wood trim and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/16/2012. | VOF STORAGE #2 | 9963 | CNR | Parks |  | Valley of Fire | 1966 | 420 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2100
0557EXT2 | ROOF REPLACEMENT | 0557 | The rolled asphalt roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new rolled asphalt roof and new underlayments. This estimate includes removal and disposal of the old roofing. | VOF STORAGE #2 | 9963 | CNR | Parks |  | Valley of Fire | 1966 | 420 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5040
0558EXT2 | EXTERIOR FINISHES | 0558 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/16/2012. | VALLEY OF FIRE VISITORS CENTER | 9963 | CNR | Parks |  | Valley of Fire | 1968 | 6724 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 33620
0558EXT3 | WINDOW REPLACEMENT | 0558 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 48 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/16/2012. | VALLEY OF FIRE VISITORS CENTER | 9963 | CNR | Parks |  | Valley of Fire | 1968 | 6724 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 48000
0558INT2 | INTERIOR FINISHES | 0558 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | VALLEY OF FIRE VISITORS CENTER | 9963 | CNR | Parks |  | Valley of Fire | 1968 | 6724 | 2018-05-23 | Four to Ten Years | Long-Term Needs | 3 | 33620
0565EXT2 | ROOF REPAIRS | 0565 | The roof flashing around the plumbing vent and the skylights was not installed properly and all three of the skylights are broken. This project would provide funds for repairing the roof. The estimate includes installing proper flashing at all roof penetrations, replacing the skylights and caulking and painting the flashing. | SMALL CAMPGROUND A COMFORT STATION | 9963 | CNR | Parks |  | Valley of Fire | 1975 | 783 | 2018-05-23 | Immediate to Two Years | Currently Critical | 1 | 4500
0555SFT2 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0555 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/16/2012. | VOF MAINTENANCE SHOP | 9963 | CNR | Parks |  | Valley of Fire | 1972 | 6000 | 2018-05-23 | Immediate to Two Years | Currently Critical | 1 | 3000
0565PLM1 | WATER HEATER REPLACEMENT | 0565 | There is a 30 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new on-demand electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | SMALL CAMPGROUND A COMFORT STATION | 9963 | CNR | Parks |  | Valley of Fire | 1975 | 783 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0565ADA1 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0565 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | SMALL CAMPGROUND A COMFORT STATION | 9963 | CNR | Parks |  | Valley of Fire | 1975 | 783 | 2018-05-23 | Immediate to Two Years | Currently Critical | 1 | 2000
0565EXT1 | EXTERIOR FINISHES | 0565 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units, painting the metal trim and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SMALL CAMPGROUND A COMFORT STATION | 9963 | CNR | Parks |  | Valley of Fire | 1975 | 783 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3915
0565INT1 | INTERIOR FINISHES | 0565 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SMALL CAMPGROUND A COMFORT STATION | 9963 | CNR | Parks |  | Valley of Fire | 1975 | 783 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3915
0558PLM1 | WATER HEATER REPLACEMENT | 0558 | There is an 80 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/16/2012. | VALLEY OF FIRE VISITORS CENTER | 9963 | CNR | Parks |  | Valley of Fire | 1968 | 6724 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0555HVA3 | HEAT PUMP REPLACEMENT | 0555 | The two heat pumps serving the building are older and should be scheduled for replacement. They are not energy efficient and have reached the end of their expected and useful lives. This project would provide for installation of two new heat pumps and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing equipment and all required connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 04/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/16/2012. | VOF MAINTENANCE SHOP | 9963 | CNR | Parks |  | Valley of Fire | 1972 | 6000 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
0554ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0554 | This restroom contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | CAMPGROUND A SHOWER BUILDING | 9963 | CNR | Parks |  | Valley of Fire | 1975 | 864 | 2018-05-23 | Immediate to Two Years | Currently Critical | 1 | 2000
0554EXT2 | EXTERIOR FINISHES | 0554 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units, painting the metal eaves and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CAMPGROUND A SHOWER BUILDING | 9963 | CNR | Parks |  | Valley of Fire | 1975 | 864 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4320
0554PLM1 | WATER HEATER REPLACEMENT | 0554 | There is a 50 gallon electric water heater in the building that was installed in 2007. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 4-5 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | CAMPGROUND A SHOWER BUILDING | 9963 | CNR | Parks |  | Valley of Fire | 1975 | 864 | 2018-05-23 | Four to Ten Years | Long-Term Needs | 3 | 1500
0554ADA3 | ADA SIGNAGE | 0554 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | CAMPGROUND A SHOWER BUILDING | 9963 | CNR | Parks |  | Valley of Fire | 1975 | 864 | 2018-05-23 | Immediate to Two Years | Currently Critical | 1 | 1500
0554ADA1 | ADA RESTROOM UPGRADE | 0554 | The building does not have a fully compliant accessible restroom or shower stall. The existing restrooms do not fully meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for remodeling the Men's and Women's restrooms to provide ADA compliant restrooms and showers. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | CAMPGROUND A SHOWER BUILDING | 9963 | CNR | Parks |  | Valley of Fire | 1975 | 864 | 2018-05-23 | Immediate to Two Years | Currently Critical | 1 | 30000
0554ENR1 | LIGHTING UPGRADE | 0554 | The existing interior and exterior lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts and compact florescent lights (CFL's) are suggested. Occupancy sensors will be installed in restrooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | CAMPGROUND A SHOWER BUILDING | 9963 | CNR | Parks |  | Valley of Fire | 1975 | 864 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3024
0555ENR1 | LIGHTING UPGRADE | 0555 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, storage closets and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 03/20/2002 and 04/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/16/2012. | VOF MAINTENANCE SHOP | 9963 | CNR | Parks |  | Valley of Fire | 1972 | 6000 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
0554INT3 | FRP REPLACEMENT | 0554 | The fiberglass reinforced panels (FRP) in the showers are aged and reaching the end of their useful life. It is recommended to schedule the FRP for replacement. This project would provide for removal and disposal of the FRP and installation of new FRP. | CAMPGROUND A SHOWER BUILDING | 9963 | CNR | Parks |  | Valley of Fire | 1975 | 864 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
0555INT1 | INTERIOR FINISHES | 0555 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted and / or sealed at least once in the next 3-4 years and every 5-7 years thereafter to maintain the integrity of the interior of the building. Prior to painting and / or sealing, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 04/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/16/2012. | VOF MAINTENANCE SHOP | 9963 | CNR | Parks |  | Valley of Fire | 1972 | 6000 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
0555INT2 | RESTROOM REMODEL | 0555 | The restroom in the building is in need of a remodel. It is showing signs of wear and tear and should be remodeled. This project would provide for a complete remodel of the restroom including fixtures, hardware, flooring, exhaust fan and wall finishes. | VOF MAINTENANCE SHOP | 9963 | CNR | Parks |  | Valley of Fire | 1972 | 6000 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0555HVA2 | EVAPORATIVE COOLER REPLACEMENT | 0555 | An evaporative cooler is installed on the side of this building. It is severely scaled and has reached the end of it's useful and expected life. This project would provide for a new evaporative cooler to be installed including all required connections to utilities. The estimate includes removal and disposal of the old cooler. This project or a portion thereof was previously recommended in the FCA report dated 04/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/16/2012. | VOF MAINTENANCE SHOP | 9963 | CNR | Parks |  | Valley of Fire | 1972 | 6000 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0555EXT2 | EXTERIOR DOOR REPLACEMENT | 0555 | The 4 exterior metal man doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the doors with new metal doors, frames and hardware. Removal and disposal of the existing doors is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/16/2012. | VOF MAINTENANCE SHOP | 9963 | CNR | Parks |  | Valley of Fire | 1972 | 6000 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
0572EXT1 | COMFORT STATION REPLACEMENT | 0572 | This comfort station was built in 1964. It is dilapidated and deteriorating and no longer meets accessibility guidelines. It is recommended that the building be demolished and replaced with a new restroom facility. This project would provide for the installation of a precast CXT or similar unisex comfort station in the same location as the existing building. The new restroom shall be compliant with the 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design. | GROUP USE AREA COMFORT STATION #7 | 9963 | CNR | Parks |  | Valley of Fire | 1964 | 288 | 2018-05-23 | Immediate to Two Years | Currently Critical | 1 | 20000
0555PLM1 | WATER HEATER REPLACEMENT | 0555 | There is a 40 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/16/2012. | VOF MAINTENANCE SHOP | 9963 | CNR | Parks |  | Valley of Fire | 1972 | 6000 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0566EXT1 | COMFORT STATION REPLACEMENT | 0566 | This comfort station was built in 1964. It is dilapidated and deteriorating and no longer meets accessibility guidelines. It is recommended that the building be demolished and replaced with a new restroom facility. This project would provide for the installation of a precast CXT or similar unisex comfort station in the same location as the existing building. The new restroom shall be compliant with the 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design. | ATLATL ROCK COMFORT STATION | 9963 | CNR | Parks |  | Valley of Fire | 1964 | 288 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0554INT2 | INTERIOR FINISHES | 0554 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | CAMPGROUND A SHOWER BUILDING | 9963 | CNR | Parks |  | Valley of Fire | 1975 | 864 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4320
0519INT1 | INTERIOR FINISHES | 0519 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 04/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/16/2012. | VOF RESIDENCE #3 | 9963 | CNR | Parks |  | Valley of Fire | 1992 | 1400 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7000
0571EXT1 | COMFORT STATION REPLACEMENT | 0571 | This comfort station was built in 1964. It is dilapidated and deteriorating and no longer meets accessibility guidelines. It is recommended that the building be demolished and replaced with a new restroom facility. This project would provide for the installation of a precast CXT or similar unisex comfort station in the same location as the existing building. The new restroom shall be compliant with the 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design. | GROUP USE AREA COMFORT STATION #6 | 9963 | CNR | Parks |  | Valley of Fire | 1964 | 288 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0526EXT2 | EXTERIOR FINISHES | 0526 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/16/2012. | VOF RESIDENCE #4 | 9963 | CNR | Parks |  | Valley of Fire | 1992 | 1400 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7000
0575INT1 | INTERIOR FINISHES | 0575 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted or sealed at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | WEST COMFORT STATION | 9963 | CNR | Parks |  | Valley of Fire | 1979 | 254 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1270
0575EXT1 | EXTERIOR FINISHES | 0575 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units, painting the metal trim and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | WEST COMFORT STATION | 9963 | CNR | Parks |  | Valley of Fire | 1979 | 254 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1270
0575PLM1 | WATER HEATER REPLACEMENT | 0575 | There is a 10 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new on-demand electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | WEST COMFORT STATION | 9963 | CNR | Parks |  | Valley of Fire | 1979 | 254 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0575EXT2 | EXTERIOR DOOR REPLACEMENT | 0575 | The exterior metal doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the three doors with new metal doors, frames and hardware. Removal and disposal of the existing doors is included in this estimate. | WEST COMFORT STATION | 9963 | CNR | Parks |  | Valley of Fire | 1979 | 254 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
0575ADA1 | ADA RESTROOM UPGRADE | 0575 | The Men's and Women's designated ADA restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for construction of two unisex accessible restrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | WEST COMFORT STATION | 9963 | CNR | Parks |  | Valley of Fire | 1979 | 254 | 2018-05-23 | Immediate to Two Years | Currently Critical | 1 | 15000
0526INT1 | INTERIOR FINISHES | 0526 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 04/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/16/2012. | VOF RESIDENCE #4 | 9963 | CNR | Parks |  | Valley of Fire | 1992 | 1400 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7000
0570EXT1 | COMFORT STATION REPLACEMENT | 0570 | This comfort station was built in 1964. It is dilapidated and deteriorating and no longer meets accessibility guidelines. It is recommended that the building be demolished and replaced with a new restroom facility. This project would provide for the installation of a precast CXT or similar unisex comfort station in the same location as the existing building. The new restroom shall be compliant with the 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design. | GROUP USE AREA COMFORT STATION #5 | 9963 | CNR | Parks |  | Valley of Fire | 1964 | 288 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0526PLM1 | WATER HEATER REPLACEMENT | 0526 | There is a 50 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/16/2012. | VOF RESIDENCE #4 | 9963 | CNR | Parks |  | Valley of Fire | 1992 | 1400 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0519PLM1 | WATER HEATER REPLACEMENT | 0519 | There is a 50 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/16/2012. | VOF RESIDENCE #3 | 9963 | CNR | Parks |  | Valley of Fire | 1992 | 1400 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0519EXT2 | EXTERIOR FINISHES | 0519 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/16/2012. | VOF RESIDENCE #3 | 9963 | CNR | Parks |  | Valley of Fire | 1992 | 1400 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7000
0567EXT1 | COMFORT STATION REPLACEMENT | 0567 | This comfort station was built in 1964. It is dilapidated and deteriorating and no longer meets accessibility guidelines. It is recommended that the building be demolished and replaced with a new restroom facility. This project would provide for the installation of a precast CXT or similar unisex comfort station in the same location as the existing building. The new restroom shall be compliant with the 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design. | SEVEN SISTERS COMFORT STATION #2 | 9963 | CNR | Parks |  | Valley of Fire | 1964 | 288 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
1029EXT2 | WINDOW REPLACEMENT | 1029 | The windows are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 6 units. | HEADQUARTERS MAINTENANCE OFFICE | 9929 | CNR | Parks |  | Washoe Lake | 1978 | 250 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
1029INT1 | INTERIOR FINISHES | 1029 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HEADQUARTERS MAINTENANCE OFFICE | 9929 | CNR | Parks |  | Washoe Lake | 1978 | 250 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1250
1029EXT1 | EXTERIOR FINISHES | 1029 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | HEADQUARTERS MAINTENANCE OFFICE | 9929 | CNR | Parks |  | Washoe Lake | 1978 | 250 | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 2500
1029HVA1 | FURNACE INSTALLATION | 1029 | The building does not have any type of heating equipment. This project would provide for installation of a gas fired furnace and includes all required connections to utilities. | HEADQUARTERS MAINTENANCE OFFICE | 9929 | CNR | Parks |  | Washoe Lake | 1978 | 250 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
1029HVA2 | EVAPORATIVE COOLER REPLACEMENT | 1029 | This building is cooled by a wall mounted evaporative cooler located on the south side of the building. This equipment has reached the end of its expected life and should be scheduled for replacement in the next 2 to 3 years. This project would provide for replacement of the evaporative cooler and includes removal and disposal of the existing unit and all required connections to utilities. | HEADQUARTERS MAINTENANCE OFFICE | 9929 | CNR | Parks |  | Washoe Lake | 1978 | 250 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
1029EXT3 | EXTERIOR DOOR REPLACEMENT | 1029 | The existing exterior wood door appears to be original to the building. It is damaged from age and general wear and tear. This project would provide for the replacement and installation of one new wood door, frame and hardware. Removal and disposal of the existing door and painting of the new door is included in this estimate. | HEADQUARTERS MAINTENANCE OFFICE | 9929 | CNR | Parks |  | Washoe Lake | 1978 | 250 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
2793EXT1 | EXTERIOR FINISHES | 2793 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | KIOSK - EQUESTRIAN | 9929 | CNR | Parks |  | Washoe Lake | 0 | 63 | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 315
2799EXT1 | EXTERIOR FINISHES | 2799 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | COMFORT STATION - WETLANDS | 9929 | CNR | Parks |  | Washoe Lake | 0 | 252 | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 1260
2799INT1 | INTERIOR FINISHES | 2799 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | COMFORT STATION - WETLANDS | 9929 | CNR | Parks |  | Washoe Lake | 0 | 252 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1260
2796INT1 | INTERIOR FINISHES | 2796 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | FEE BOOTH - LITTLE WASHOE | 9929 | CNR | Parks |  | Washoe Lake | 0 | 165 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 825
2800EXT1 | EXTERIOR FINISHES | 2800 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | STORAGE SHED - WETLANDS | 9929 | CNR | Parks |  | Washoe Lake | 0 | 64 | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 320
2796EXT1 | EXTERIOR FINISHES | 2796 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | FEE BOOTH - LITTLE WASHOE | 9929 | CNR | Parks |  | Washoe Lake | 0 | 165 | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 825
2794EXT1 | EXTERIOR FINISHES | 2794 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | SOUTH BEACH SANI-HUT STRUCTURE | 9929 | CNR | Parks |  | Washoe Lake | 0 | 36 | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 180
2792EXT1 | EXTERIOR FINISHES | 2792 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | KIOSK -CAMPGROUND LOOP B | 9929 | CNR | Parks |  | Washoe Lake | 0 | 45 | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 225
2791EXT1 | EXTERIOR FINISHES | 2791 | It is important to maintain the finish, weather resistance and appearance of the water tank. This project would provide for the painting of the water tank to maintain it in a good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | WATER TANK | 9929 | CNR | Parks |  | Washoe Lake | 1978 | 707 | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 11312
2798INT1 | INTERIOR FINISHES | 2798 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | COMFORT STATION #2 - LITTLE WASHOE | 9929 | CNR | Parks |  | Washoe Lake | 0 | 112 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 560
2798EXT1 | EXTERIOR FINISHES | 2798 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | COMFORT STATION #2 - LITTLE WASHOE | 9929 | CNR | Parks |  | Washoe Lake | 0 | 112 | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 560
2797INT1 | INTERIOR FINISHES | 2797 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | COMFORT STATION #1 - LITTLE WASHOE | 9929 | CNR | Parks |  | Washoe Lake | 0 | 224 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1120
2797EXT1 | EXTERIOR FINISHES | 2797 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | COMFORT STATION #1 - LITTLE WASHOE | 9929 | CNR | Parks |  | Washoe Lake | 0 | 224 | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 1120
2375EXT1 | EXTERIOR FINISHES | 2375 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | NORTH RAMP GARAGE | 9929 | CNR | Parks |  | Washoe Lake | 1996 | 400 | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 4000
2795EXT1 | EXTERIOR FINISHES | 2795 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | HEADQUARTERS SHED | 9929 | CNR | Parks |  | Washoe Lake | 0 | 64 | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 320
9929PLM1 | REPLACE FREEZE PROOF FIRE HYDRANT | 9929 | There is a freeze proof fire hydrant in Campground A between site's 3 and 4 that is damaged. This project would provide for the replacement of the broken hydrant with a new freeze proof fire hydrant. | WASHOE LAKE STATE PARK SITE | 9929 | CNR | Parks |  | Washoe Lake | 1977 |  | 2018-08-09 | Immediate to Two Years | Currently Critical | 1 | 1200
9929ADA11 | CAMPGROUND B ADA IMPROVEMENTS | 9929 | This project would provide for 2 existing campsites to be upgrades to ADA accessible campsites including new P.C. concrete walkways and pads, signage, parking, remodeling one restroom into an accessible unisex restroom, and remodel one shower into an accessible shower. The IBC - 2006, ICC/ANSI A117.1 - 2003 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2003 were referenced for this project. | WASHOE LAKE STATE PARK SITE | 9929 | CNR | Parks |  | Washoe Lake | 1977 |  | 2018-08-09 | Immediate to Two Years | Currently Critical | 1 | 28000
9929EXT5 | ROOF REPLACEMENT | 9929 | Of the 43 steel shade ramadas, 10 of them were installed in 1980 with asphalt composition shingle roofs. The roofs on these structures were in poor condition at the time of the survey. The extreme temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that these structures be re-roofed in the next two to three years with a new metal roof and underlayments to match the newer Ramadas. | WASHOE LAKE STATE PARK SITE | 9929 | CNR | Parks |  | Washoe Lake | 1977 |  | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18150
9929EXT4 | EXTERIOR FINISHES, SHADE RAMADAS | 9929 | There are 43 steel shade ramadas in different locations throughout the site which measure 11'x11' each for a total of 5,203 square feet. It is important to maintain the finish, weather resistance and appearance of the structures. This project would provide for painting of the structures. This project should be done on a cyclical basis based on environmental conditions. | WASHOE LAKE STATE PARK SITE | 9929 | CNR | Parks |  | Washoe Lake | 1977 |  | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 10406
9929ADA7 | WETLANDS ADA IMPROVEMENTS | 9929 | The Wetlands area has a comfort station and viewing platform which are lacking ADA accessible routes from the parking area. This project would provide for an accessible concrete walkway from the parking area to the comfort station and viewing platform. Signage and ADA parking space striping is included in this estimate. The IBC - 2006, ICC/ANSI A117.1 - 2003 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2003 were referenced for this project. | WASHOE LAKE STATE PARK SITE | 9929 | CNR | Parks |  | Washoe Lake | 1977 |  | 2018-08-09 | Immediate to Two Years | Currently Critical | 1 | 8000
9929SIT4 | SLURRY SEAL ASPHALT PAVING | 9929 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site wide including campground roads, access roads, parking areas and the Headquarters storage yard and parking - access area. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 300,000 square feet of asphalt area was used to generate this estimate. | WASHOE LAKE STATE PARK SITE | 9929 | CNR | Parks |  | Washoe Lake | 1977 |  | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 180000
9929ADA12 | LITTLE WASHOE LAKE ADA IMPROVEMENTS | 9929 | The designated ADA accessible parking area appears to exceed the maximum 2% slope and is missing directional signage to the ADA comfort station. This project would provide for the removal of the A. C. paving at the parking areas and installation of new P. C. parking areas including signage and route of travel to the comfort station. The IBC - 2006, ICC/ANSI A117.1 - 2003 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2003 were referenced for this project. | WASHOE LAKE STATE PARK SITE | 9929 | CNR | Parks |  | Washoe Lake | 1977 |  | 2018-08-09 | Immediate to Two Years | Currently Critical | 1 | 7000
9929ADA10 | CAMPGROUND A ADA IMPROVEMENTS | 9929 | This project would provide for 2 existing campsites to be upgrades to ADA accessible campsites including new P.C. concrete walkways and pads, signage, parking, remodeling one restroom into an accessible unisex restroom, remodel one shower into an accessible shower, and add a new high / low drinking fountain. The IBC - 2006, ICC/ANSI A117.1 - 2003 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2003 were referenced for this project. | WASHOE LAKE STATE PARK SITE | 9929 | CNR | Parks |  | Washoe Lake | 1977 |  | 2018-08-09 | Immediate to Two Years | Currently Critical | 1 | 32000
9929ADA9 | EQUESTRIAN AREA SITE & ADA IMPROVEMENTS | 9929 | There is an equestrian area that is lacking some ADA accessibility items in the comfort station, shade Ramada, parking area, route of travel and walkways. This project would provide for 2 accessible parking stalls, ADA signage, 1 high / low drinking fountain, 1 accessible table at the Ramada, 1 accessible BBQ at the Ramada, remodel one of the restrooms into a unisex ADA compliant restroom and an accessible ramp from the parking area to the restroom. This project also includes the replacement of a damaged pole light. The IBC - 2006, ICC/ANSI A117.1 - 2003 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2003 were referenced for this project. | WASHOE LAKE STATE PARK SITE | 9929 | CNR | Parks |  | Washoe Lake | 1977 |  | 2018-08-09 | Immediate to Two Years | Currently Critical | 1 | 51000
9929ADA8 | DAY USE AREAS ADA IMPROVEMENTS | 9929 | There are 5 day use areas located throughout the park which are in need of miscellaneous ADA improvements. This project would provide for one accessible table, one accessible BBQ and one accessible parking stall in each of the 5 day use areas. Also included is ADA signage, two high/low drinking fountains and removal of AC paving at existing non-compliant ADA parking and accessible routes and replacement with PC concrete pavement and walkways which meet ADA accessibility requirements. The IBC - 2006, ICC/ANSI A117.1 - 2003 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2003 were referenced for this project. | WASHOE LAKE STATE PARK SITE | 9929 | CNR | Parks |  | Washoe Lake | 1977 |  | 2018-08-09 | Immediate to Two Years | Currently Critical | 1 | 95000
0593ADA1 | ADA RESTROOM UPGRADE | 0593 | The Men's and Women's designated ADA restrooms do not meet the Americans with Disabilities Act (ADA) regulations. A retrofit is necessary to comply with 2006 IBC Chapter 11, ICC/ANSI A117.1-1998 Sections 603 - 604 and the Americans with Disabilities Act Accessibility Guidelines (ADAAG). Given the current configuration of the restrooms, the work will include the installation of a new toilet, sink, grab bars, faucets, mirrors, dispensers and hardware. Some minor design work will be required and may impact the final cost estimate. This estimate is for one ADA Unisex restroom facility, the other restroom will be assigned as Unisex as well. The removal and disposal of the old restroom fixtures is included in this estimate. | COMFORT STATION - DAY USE #1 | 9929 | CNR | Parks |  | Washoe Lake | 1978 | 135 | 2018-08-09 | Immediate to Two Years | Currently Critical | 1 | 10000
0483ENR1 | LIGHTING UPGRADE | 0483 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures, ballasts and lighting to current standards, resulting in increased efficiency and reduced costs associated with illumination. Occupancy sensors will be installed in restrooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | HEADQUARTERS OFFICE/SHOP/STORAGE | 9929 | CNR | Parks |  | Washoe Lake | 1979 | 1920 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5760
0593EXT1 | EXTERIOR FINISHES | 0593 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | COMFORT STATION - DAY USE #1 | 9929 | CNR | Parks |  | Washoe Lake | 1978 | 135 | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 1350
0593INT1 | INTERIOR FINISHES | 0593 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | COMFORT STATION - DAY USE #1 | 9929 | CNR | Parks |  | Washoe Lake | 1978 | 135 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 675
0593PLM1 | PLUMBING UPGRADE | 0593 | The Comfort Station plumbing and fixtures (sink) were not operating properly at the time of the survey. This project would provide funds for the repair of the plumbing and fixtures. This will provide for a fully operational comfort station. | COMFORT STATION - DAY USE #1 | 9929 | CNR | Parks |  | Washoe Lake | 1978 | 135 | 2018-08-09 | Immediate to Two Years | Currently Critical | 1 | 2500
0594ADA1 | ADA RESTROOM UPGRADE | 0594 | The Men's and Women's designated ADA restrooms do not meet the Americans with Disabilities Act (ADA) regulations. A retrofit is necessary to comply with 2006 IBC Chapter 11, ICC/ANSI A117.1-1998 Sections 603 - 604 and the Americans with Disabilities Act Accessibility Guidelines (ADAAG). Given the current configuration of the restrooms, the work will include the installation of a new toilet, sink, grab bars, faucets, mirrors, dispensers and hardware. Some minor design work will be required and may impact the final cost estimate. This estimate is for one ADA Unisex restroom facility, the other restroom will be assigned as Unisex as well. The removal and disposal of the old restroom fixtures is included in this estimate. | COMFORT STATION - DAY USE #2 | 9929 | CNR | Parks |  | Washoe Lake | 1978 | 135 | 2018-08-09 | Immediate to Two Years | Currently Critical | 1 | 10000
0594EXT1 | EXTERIOR FINISHES | 0594 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | COMFORT STATION - DAY USE #2 | 9929 | CNR | Parks |  | Washoe Lake | 1978 | 135 | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 1350
0594INT1 | INTERIOR FINISHES | 0594 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | COMFORT STATION - DAY USE #2 | 9929 | CNR | Parks |  | Washoe Lake | 1978 | 135 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 675
0595HVA1 | HEATER REPLACEMENT | 0595 | The building is heated by one wall mounted electric heating unit. It is original to the building and is reaching the end of its useful life. This project provides for disposal of the existing unit and replacement of the unit including connections to utilities. | COMFORT STATION - GROUP USE | 9929 | CNR | Parks |  | Washoe Lake | 1978 | 346 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0483EXT2 | WINDOW REPLACEMENT | 0483 | The windows are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 12 units. | HEADQUARTERS OFFICE/SHOP/STORAGE | 9929 | CNR | Parks |  | Washoe Lake | 1979 | 1920 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
0594PLM1 | PLUMBING UPGRADE | 0594 | The Comfort Station plumbing and fixtures (sink) were not operating properly at the time of the survey. This project would provide funds for the repair of the plumbing and fixtures. This will provide for a fully operational comfort station. | COMFORT STATION - DAY USE #2 | 9929 | CNR | Parks |  | Washoe Lake | 1978 | 135 | 2018-08-09 | Immediate to Two Years | Currently Critical | 1 | 2500
0483SFT1 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0483 | The building is partially a B occupancy per the 2006 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. | HEADQUARTERS OFFICE/SHOP/STORAGE | 9929 | CNR | Parks |  | Washoe Lake | 1979 | 1920 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 26880
0591EXT1 | EXTERIOR FINISHES | 0591 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | NORTH RAMP FEE STATION | 9929 | CNR | Parks |  | Washoe Lake | 1996 | 240 | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 2400
0483ADA1 | MISCELLANEOUS ADA UPGRADES | 0483 | The door hardware, signage and information counter are not ADA compliant. Americans with Disabilities Act (ADA) regulations pertaining to building access, route of travel and restrooms has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances, route of travel inside the building and restrooms. Section 4.13.9 of the Americans with Disabilities Act Accessible Guidelines (ADAAG) states that handles, pulls, latches, locks and other operating devices on accessible doors shall have a shape that is easy to grasp with one hand and does not require tight grasping, tight pinching, or twisting of the wrist to operate. Lever-operated mechanisms, push-type mechanisms, and U-shaped handles are acceptable designs. It is recommended that proper lever hardware be installed in this building to meet these requirements. Section 7.2 of the Americans with Disabilities Act Accessible Guidelines (ADAAG) states that the counter must have a portion which is at least 36" in length with a maximum height of 36" above the finish floor. IBC - 2006, ICC/ANSI A117.1 - 2003 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2003 were referenced for this project. | HEADQUARTERS OFFICE/SHOP/STORAGE | 9929 | CNR | Parks |  | Washoe Lake | 1979 | 1920 | 2018-08-09 | Immediate to Two Years | Currently Critical | 1 | 15000
0483INT2 | INTERIOR DOOR REPLACEMENT | 0483 | The existing interior doors and frames are damaged from abuse and age. This project would provide for the removal of the existing hollow core doors and frames and the purchase and installation of four new solid core wood doors and frames. All hardware, painting and framing materials are included in this estimate. | HEADQUARTERS OFFICE/SHOP/STORAGE | 9929 | CNR | Parks |  | Washoe Lake | 1979 | 1920 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0483EXT3 | EXTERIOR DOOR REPLACEMENT | 0483 | The existing exterior wood doors appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement and installation of four new wood doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. The main entrance door, threshold and hardware is not ADA compliant, this project would provide for ADA compliant door hardware and threshold. | HEADQUARTERS OFFICE/SHOP/STORAGE | 9929 | CNR | Parks |  | Washoe Lake | 1979 | 1920 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
0483ADA2 | ADA RESTROOM UPGRADE | 0483 | The Men's and Women's restrooms do not meet the Americans with Disabilities Act (ADA) regulations. A retrofit is necessary to comply with 2006 IBC Chapter 11, ICC/ANSI A117.1-1998 Sections 603 - 604 and the Americans with Disabilities Act Accessibility Guidelines (ADAAG). Given the current configuration of the restrooms, the work will include the installation of a new toilet, sink, grab bars, faucets, mirrors, dispensers and door hardware. Some minor design work will be required and may impact the final cost estimate. This estimate is for one ADA Unisex restroom facility. The other restroom will be designated Unisex as well. The removal and disposal of the old restroom fixtures is included in this estimate. | HEADQUARTERS OFFICE/SHOP/STORAGE | 9929 | CNR | Parks |  | Washoe Lake | 1979 | 1920 | 2018-08-09 | Immediate to Two Years | Currently Critical | 1 | 10000
0483INT1 | INTERIOR FINISHES | 0483 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HEADQUARTERS OFFICE/SHOP/STORAGE | 9929 | CNR | Parks |  | Washoe Lake | 1979 | 1920 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9600
0595ADA1 | ADA RESTROOM UPGRADE | 0595 | The Men's and Women's designated ADA restrooms do not meet the Americans with Disabilities Act (ADA) regulations. A retrofit is necessary to comply with 2006 IBC Chapter 11, ICC/ANSI A117.1-1998 Sections 603 - 604 and the Americans with Disabilities Act Accessibility Guidelines (ADAAG). Given the current configuration of the restrooms, the work will include the installation of a new toilet, sink, grab bars, faucets, mirrors, dispensers and hardware. Some minor design work will be required and may impact the final cost estimate. This estimate is for one ADA Unisex restroom facility, the other restroom will be assigned as Unisex as well. The removal and disposal of the old restroom fixtures is included in this estimate. | COMFORT STATION - GROUP USE | 9929 | CNR | Parks |  | Washoe Lake | 1978 | 346 | 2018-08-09 | Immediate to Two Years | Currently Critical | 1 | 10000
0483ELE1 | HIGH-SPEED INTERNET INSTALLATION | 0483 | This building is not equipped with a high-speed internet connection. The staff currently uses a dial-up connection to conduct daily business which is time consuming and leaves other responsibilities neglected. In order to provide State employees with responsive access to email and data, the site should be provided with a high-speed internet connection. High-speed internet access fees are not included in the estimated cost. | HEADQUARTERS OFFICE/SHOP/STORAGE | 9929 | CNR | Parks |  | Washoe Lake | 1979 | 1920 | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 2500
0485PLM1 | PLUMBING / RESTROOM REPAIR | 0485 | The Comfort Station plumbing and fixtures were not operating properly at the time of the survey. One of the restroom stalls was not in operation. This project would provide funds for the repair of the plumbing, fixtures and restroom stall. This will provide for a fully operational comfort station. | COMFORT STATION - LOOP A | 9929 | CNR | Parks |  | Washoe Lake | 1985 | 357 | 2018-08-09 | Immediate to Two Years | Currently Critical | 1 | 2500
0482INT1 | INTERIOR FINISHES | 0482 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | COMFORT STATION - LOOP B | 9929 | CNR | Parks |  | Washoe Lake | 1979 | 255 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1275
0483EXT1 | EXTERIOR FINISHES | 0483 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | HEADQUARTERS OFFICE/SHOP/STORAGE | 9929 | CNR | Parks |  | Washoe Lake | 1979 | 1920 | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 19200
0866INT1 | INTERIOR FINISHES | 0866 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | COMFORT STATION - EQUESTRIAN | 9929 | CNR | Parks |  | Washoe Lake | 1980 | 135 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 675
0584EXT1 | EXTERIOR FINISHES | 0584 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | NORTH RAMP RESIDENCE STORAGE SHED | 9929 | CNR | Parks |  | Washoe Lake | 1995 | 96 | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 480
0869EXT1 | EXTERIOR FINISHES | 0869 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | SOUTH BEACH PUMP HOUSE | 9929 | CNR | Parks |  | Washoe Lake | 1978 | 16 | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 160
0868EXT1 | EXTERIOR FINISHES | 0868 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | HEADQUARTERS FEE STATION | 9929 | CNR | Parks |  | Washoe Lake | 1978 | 234 | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 2340
0868INT1 | INTERIOR FINISHES | 0868 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HEADQUARTERS FEE STATION | 9929 | CNR | Parks |  | Washoe Lake | 1978 | 234 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1170
0868SEC1 | LIGHTING TIME SWITCH REPLACEMENT | 0868 | There is a Tork Time Switch installed in the building which controls the exterior lighting including the sign lighting. It was installed in 1982 and is no longer operating. This project would provide for replacement of the time switch and all required connections to utilities. | HEADQUARTERS FEE STATION | 9929 | CNR | Parks |  | Washoe Lake | 1978 | 234 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
0867EXT1 | EXTERIOR FINISHES | 0867 | This large steel shade ramada in the Equestrian Area covers picnic tables and a built-in barbecue. It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure. This project should be done on a cyclical basis based on environmental conditions. | EQUESTRIAN AREA RAMADA | 9929 | CNR | Parks |  | Washoe Lake | 1980 | 625 | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 1250
0867EXT2 | ROOF REPLACEMENT | 0867 | The roof on this structure was in poor condition at the time of the survey. The extreme temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this structure be re-roofed in the next two to three years with a 40 year asphalt composition roofing shingle and new underlayments. | EQUESTRIAN AREA RAMADA | 9929 | CNR | Parks |  | Washoe Lake | 1980 | 625 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9375
0866EXT1 | EXTERIOR FINISHES | 0866 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | COMFORT STATION - EQUESTRIAN | 9929 | CNR | Parks |  | Washoe Lake | 1980 | 135 | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 1350
0866PLM1 | PLUMBING UPGRADE | 0866 | The Comfort Station plumbing and fixtures were not operating properly at the time of the survey. This project would provide funds for the repair of the plumbing and fixtures. This will provide for a fully operational comfort station. | COMFORT STATION - EQUESTRIAN | 9929 | CNR | Parks |  | Washoe Lake | 1980 | 135 | 2018-08-09 | Immediate to Two Years | Currently Critical | 1 | 2500
0485INT1 | INTERIOR FINISHES | 0485 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | COMFORT STATION - LOOP A | 9929 | CNR | Parks |  | Washoe Lake | 1985 | 357 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1785
0866EXT2 | ROOF REPLACEMENT | 0866 | The roof on this building was in poor condition at the time of the survey. The extreme temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next two to three years with a 40 year asphalt composition roofing shingle and new underlayments. | COMFORT STATION - EQUESTRIAN | 9929 | CNR | Parks |  | Washoe Lake | 1980 | 135 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2025
0595EXT1 | EXTERIOR FINISHES | 0595 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | COMFORT STATION - GROUP USE | 9929 | CNR | Parks |  | Washoe Lake | 1978 | 346 | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 3460
0590EXT1 | EXTERIOR FINISHES | 0590 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | NORTH RAMP PUMP HOUSE | 9929 | CNR | Parks |  | Washoe Lake | 1988 | 64 | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 640
0485ADA2 | ACCESSIBLE WATER FOUNTAIN | 0485 | This building has a water fountain. IBC-2006 Section 1109.5 states that where a water fountain is provided, at least half should be accessible. This project would provide funding for the purchase and installation of an ADA compliant high / low water fountain. The installation of the water fountain must comply with ICC/ANSI A117.1-2003 and the most current edition of the Americans with Disabilities Act Accessibility Guidelines (ADAAG). | COMFORT STATION - LOOP A | 9929 | CNR | Parks |  | Washoe Lake | 1985 | 357 | 2018-08-09 | Immediate to Two Years | Currently Critical | 1 | 4000
0482PLM3 | PLUMBING / RESTROOM REPAIR | 0482 | The Comfort Station plumbing and fixtures were not operating properly at the time of the survey. This project would provide funds for the repair of the plumbing and fixtures. This will provide for a fully operational comfort station. | COMFORT STATION - LOOP B | 9929 | CNR | Parks |  | Washoe Lake | 1979 | 255 | 2018-08-09 | Immediate to Two Years | Currently Critical | 1 | 2500
0485EXT1 | EXTERIOR FINISHES | 0485 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | COMFORT STATION - LOOP A | 9929 | CNR | Parks |  | Washoe Lake | 1985 | 357 | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 3570
0484EXT2 | EXTERIOR FINISHES | 0484 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | HEADQUARTERS RANGER RESIDENCE | 9929 | CNR | Parks |  | Washoe Lake | 1979 | 1820 | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 18200
0484INT1 | INTERIOR FINISHES | 0484 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HEADQUARTERS RANGER RESIDENCE | 9929 | CNR | Parks |  | Washoe Lake | 1979 | 1820 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9100
0483SFT3 | INSTALL EXIT SIGNS AND EGRESS LIGHTING | 0483 | The building does not have any emergency lighting and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency exit lighting to provide illumination along the egress route. IBC - 2006 Chapter 10 was referenced for this project. | HEADQUARTERS OFFICE/SHOP/STORAGE | 9929 | CNR | Parks |  | Washoe Lake | 1979 | 1920 | 2018-08-09 | Immediate to Two Years | Currently Critical | 1 | 1500
0598EXT1 | EXTERIOR FINISHES | 0598 | This large steel shade ramada in the North Ramp Area covers a picnic area. It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure. This project should be done on a cyclical basis based on environmental conditions. | NORTH RAMP RAMADA | 9929 | CNR | Parks |  | Washoe Lake | 1988 | 386 | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 772
0595PLM1 | PLUMBING UPGRADE | 0595 | The Comfort Station plumbing and fixtures (sink) were not operating properly at the time of the survey. This project would provide funds for the repair of the plumbing and fixtures. This will provide for a fully operational comfort station. | COMFORT STATION - GROUP USE | 9929 | CNR | Parks |  | Washoe Lake | 1978 | 346 | 2018-08-09 | Immediate to Two Years | Currently Critical | 1 | 2500
0595INT1 | INTERIOR FINISHES | 0595 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | COMFORT STATION - GROUP USE | 9929 | CNR | Parks |  | Washoe Lake | 1978 | 346 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1730
0866EXT4 | REPLACE VAULT DOORS | 0866 | The access to the vault below the building has four steel doors with wooden frames. They are showing signs of wear and deterioration and have reached the end of their expected life. Due to the condition of the doors and frames, this project recommends the installation of new metal doors, metal frames and hardware and includes the disposal of the existing door assemblies. | COMFORT STATION - EQUESTRIAN | 9929 | CNR | Parks |  | Washoe Lake | 1980 | 135 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0585PLM1 | INSTALL WATER SOFTENER / FILTER | 0585 | The water at the site is a well system, the water is full of minerals, and smells bad. This project recommends the installation of a water filtration system to improve water quality and extend the life of plumbing and appliances. This project or a portion thereof was previously recommended in the FCA report dated 06/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2008. | NORTH RAMP RANGER RESIDENCE | 9929 | CNR | Parks |  | Washoe Lake | 1996 | 1280 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0483HVA1 | HVAC UPGRADE | 0483 | This building is cooled by a window mounted evaporative cooler and heated by a wall mounted gas furnace. This equipment has reached the end of its expected life and should be scheduled for replacement in the next 2 to 3 years. This project would provide for replacement of the evaporative cooler and gas fired furnace and includes removal and disposal of the existing units and all required connections to utilities. | HEADQUARTERS OFFICE/SHOP/STORAGE | 9929 | CNR | Parks |  | Washoe Lake | 1979 | 1920 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0585EXT2 | EXTERIOR FINISHES | 0585 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | NORTH RAMP RANGER RESIDENCE | 9929 | CNR | Parks |  | Washoe Lake | 1996 | 1280 | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 12800
0482EXT1 | EXTERIOR FINISHES | 0482 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | COMFORT STATION - LOOP B | 9929 | CNR | Parks |  | Washoe Lake | 1979 | 255 | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 2550
0585INT2 | INTERIOR FINISHES | 0585 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | NORTH RAMP RANGER RESIDENCE | 9929 | CNR | Parks |  | Washoe Lake | 1996 | 1280 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6400
0587INT1 | INTERIOR FINISHES | 0587 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | COMFORT STATION - NORTH RAMP | 9929 | CNR | Parks |  | Washoe Lake | 1988 | 255 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1275
0587PLM1 | PLUMBING /RESTROOM REPAIR | 0587 | The Comfort Station plumbing and fixtures were not operating properly at the time of the survey. One of the restroom stalls was not in operation. This project would provide funds for the repair of the plumbing, fixtures and restroom stall. This will provide for a fully operational comfort station. | COMFORT STATION - NORTH RAMP | 9929 | CNR | Parks |  | Washoe Lake | 1988 | 255 | 2018-08-09 | Immediate to Two Years | Currently Critical | 1 | 2500
0587EXT1 | EXTERIOR FINISHES | 0587 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | COMFORT STATION - NORTH RAMP | 9929 | CNR | Parks |  | Washoe Lake | 1988 | 255 | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 2550
0587EXT2 | REROOF COMFORT STATION | 0587 | The comfort station roof appears to be original to the building. The extreme temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof, and constant exposure to the sun are contributing factors to wear and deterioration. This project would provide for a new 40 year asphalt composition shingle roof including underlayments to be installed. Removal and disposal of the existing roof and underlayment is included in this estimate. | COMFORT STATION - NORTH RAMP | 9929 | CNR | Parks |  | Washoe Lake | 1988 | 255 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3825
0587ADA1 | ADA RESTROOM UPGRADE | 0587 | The Men's and Women's designated ADA restrooms do not meet the Americans with Disabilities Act (ADA) regulations. A retrofit is necessary to comply with 2006 IBC Chapter 11, ICC/ANSI A117.1-1998 Sections 603 - 604 and the Americans with Disabilities Act Accessibility Guidelines (ADAAG). Given the current configuration of the restrooms, the work will include the installation of a new toilet, sink, grab bars, faucets, mirrors, dispensers and hardware. Some minor design work will be required and may impact the final cost estimate. This estimate is for one ADA Unisex restroom facility, the other restroom will be assigned as Unisex as well. The removal and disposal of the old restroom fixtures is included in this estimate. | COMFORT STATION - NORTH RAMP | 9929 | CNR | Parks |  | Washoe Lake | 1988 | 255 | 2018-08-09 | Immediate to Two Years | Currently Critical | 1 | 10000
0481EXT1 | EXTERIOR FINISHES | 0481 | This large steel shade ramada in the Group Area covers picnic tables and a built-in barbecue. It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure. This project should be done on a cyclical basis based on environmental conditions. | GROUP AREA RAMADA | 9929 | CNR | Parks |  | Washoe Lake | 1978 | 5480 | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 10960
0482EXT2 | DOOR SIGNAGE | 0482 | There are no signs on the doors to the building to direct visitors to the correct restroom. This project would provide for purchase and installation of one sign for each restroom and one sign for the utility room. | COMFORT STATION - LOOP B | 9929 | CNR | Parks |  | Washoe Lake | 1979 | 255 | 2018-08-09 | Immediate to Two Years | Currently Critical | 1 | 1200
0482PLM2 | WATER HEATER REPLACEMENT | 0482 | The average life span of a water heater is eight to ten years. The existing 28 gallon natural gas water heater is approaching the end of its expected life and should be scheduled for replacement in the next 2 to 3 years. This project would provide for the removal and disposal of the old water heater and installation of a new 28 gallon water heater. | COMFORT STATION - LOOP B | 9929 | CNR | Parks |  | Washoe Lake | 1979 | 255 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
2342EXT1 | EXTERIOR FINISHES | 2342 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for staining the wood and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NURSERY LATH HOUSE (SOUTH) | 9795 | CNR | Forestry |  | Washoe Valley | 2006 | 9000 | 2018-08-15 | Four to Ten Years | Long-Term Needs | 3 | 12000
2345STR1 | STRUCTURAL ASSESSMENT | 2345 | This structure was built without plans and inspections. This project recommends that a licensed engineer perform a structural investigation to evaluate the construction. Future projects would be based on this report. | NURSERY PLANTING BUILDING STORAGE | 9795 | CNR | Forestry |  | Washoe Valley | 2003 | 540 | 2018-08-15 | Immediate to Two Years | Currently Critical | 1 | 2500
2341EXT1 | EXTERIOR FINISHES | 2341 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for staining of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NURSERY LATH HOUSE (NORTH) | 9795 | CNR | Forestry |  | Washoe Valley | 2006 | 9000 | 2018-08-15 | Four to Ten Years | Long-Term Needs | 3 | 18000
2343EXT2 | LOADING DOCK REPAIRS | 2343 | The hydraulic lift on the loading dock was not functioning properly at the time of the 2009 survey. The lift is original to the building and should be scheduled for repair. This project would provide for a licensed mechanic to repair the lift to it's original working condition. | NURSERY SEED BANK | 9795 | CNR | Forestry |  | Washoe Valley | 1995 | 1450 | 2018-08-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
2343EXT1 | EXTERIOR FINISHES | 2343 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is priming and painting to repair the graffiti damage and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NURSERY SEED BANK | 9795 | CNR | Forestry |  | Washoe Valley | 1995 | 1450 | 2018-08-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7250
2343EXT3 | EXTERIOR LANDING INSTALLATION | 2343 | There is an exterior stairway and ramp from the loading dock which do not have landings and the loading dock area is currently dirt. This project would provide for concrete landings to be installed at the bottom of the ramp and stairs and a concrete slab-on-grade to be installed where trucks make their deliveries. | NURSERY SEED BANK | 9795 | CNR | Forestry |  | Washoe Valley | 1995 | 1450 | 2018-08-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
2344EXT1 | EXTERIOR FINISHES | 2344 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding, priming and painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NURSERY PUMP HOUSE | 9795 | CNR | Forestry |  | Washoe Valley | 2002 | 85 | 2018-08-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 850
2344INT1 | INTERIOR FINISHES | 2344 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next four to five years. Prior to painting, all surfaces should be repaired and prepped. | NURSERY PUMP HOUSE | 9795 | CNR | Forestry |  | Washoe Valley | 2002 | 85 | 2018-08-15 | Four to Ten Years | Long-Term Needs | 3 | 425
2345EXT1 | EXTERIOR FINISHES | 2345 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding, priming and painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NURSERY PLANTING BUILDING STORAGE | 9795 | CNR | Forestry |  | Washoe Valley | 2003 | 540 | 2018-08-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1080
2340EXT1 | EXTERIOR FINISHES | 2340 | It is important to maintain the finish, weather resistance and appearance of the structure. This project recommends work to protect the exterior building envelope including repairs to the exterior membrane and caulking around, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and it is also recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 03/04/2003 and 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | NURSERY GREENHOUSE #2 (WEST) | 9795 | CNR | Forestry |  | Washoe Valley | 2002 | 3000 | 2018-08-15 | Four to Ten Years | Long-Term Needs | 3 | 30000
9795ADA1 | ADA IMPROVEMENTS | 9795 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area, sidewalks and ramps are necessary to comply with ADA requirements. The sidewalks and ramps will provide access to the Office, the public restrooms at the Cook House, the Lath Houses and any other area on the site that the public is allowed to go to view and purchase plants. This project would provide for a concrete van accessible ADA parking, loading space and all necessary walkways and ramps. This will require regrading, installing P.C. concrete, striping, signage, railings and any other necessary upgrades. The 2006 IBC, ICC/ANSI A117.1 - 2003, NRS 338.180 and the most current version of the Americans With Disabilities Act Accessible Guidelines (ADAAG) was used as a reference for this project | WESTERN REGION NDF NURSERY SITE | 9795 | CNR | Forestry |  | Washoe Valley | 0 |  | 2018-08-15 | Immediate to Two Years | Currently Critical | 1 | 55000
9795SFT2 | WATER LINE / FIRE PROTECTION | 9795 | This project would provide for a fire sprinkler supply line to be installed to the public water system if fire sprinklers were to be installed at the site This project also includes 1,000 lineal feet of 6" water main to tie into the existing public water system. Backflow prevention is included in this estimate. The public water system location will need to be verified if this project were to be implemented. | WESTERN REGION NDF NURSERY SITE | 9795 | CNR | Forestry |  | Washoe Valley | 0 |  | 2018-08-15 | Immediate to Two Years | Currently Critical | 1 | 100000
9795SIT2 | IRRIGATION UPGRADE | 9795 | The existing landscape irrigation lines throughout the site are reaching the end of their expected life and should be scheduled for replacement. This project would provide for the removal of the existing irrigation lines and the purchase and installation of new lines. 3,000 linear feet was used to generate this estimate. | WESTERN REGION NDF NURSERY SITE | 9795 | CNR | Forestry |  | Washoe Valley | 0 |  | 2018-08-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
9795ENV1 | 4" BACKFLOW ASSEMBLY, VAULT, AND POWER | 9795 | State Health Law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of back siphonage or backpressure. This project allows for the installation of double check valves or reduced pressure principle backflow preventers as appropriate to the hazard and in appropriate locations near the potential source of contamination. Costs include an above ground vault, and allowance for 200 feet of 1" conduit to provide power for freeze protection. This project or a portion thereof was previously recommended in the FCA report dated 03/04/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/29/2009. | WESTERN REGION NDF NURSERY SITE | 9795 | CNR | Forestry |  | Washoe Valley | 0 |  | 2018-08-15 | Immediate to Two Years | Currently Critical | 1 | 25000
9795ENV4 | BACKUP WELL PUMP REPLACEMENT | 9795 | The nursery has a main well and backup well. The backup well equipment is at the end of its useful life and should be replaced. This project provides for the replacement of the 1.5 hp pump and associated equipment. This project or a portion thereof was previously recommended in the FCA report dated 03/04/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/29/2009. | WESTERN REGION NDF NURSERY SITE | 9795 | CNR | Forestry |  | Washoe Valley | 0 |  | 2018-08-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0894SFT3 | EXTERIOR LANDING INSTALLATION | 0894 | The exterior door from the Shop does not have a code compliant landing. The landing does not comply with 2006 IBC Section 1008.1 which describes the requirements for landings including that the landing not be less than 1/2" below the threshold. This project addresses installing a landing designed to current code. | NURSERY SHOP | 9795 | CNR | Forestry |  | Washoe Valley | 1978 | 480 | 2018-08-15 | Immediate to Two Years | Currently Critical | 1 | 1000
0891SFT1 | FIRE EXTINGUISHER INSTALLATION | 0891 | The building does not have a portable fire extinguisher available. International Fire Code Section 906 requires that portable fire extinguishers shall be installed in S occupancies. They shall be provided for employee use and selected and distributed based on the classes of anticipated workplace fires and on the size and degree of hazard which would affect their use. This project would provide funding for the purchase and installation of 2 fire extinguishers, cabinets, and the hardware necessary to install them. | NURSERY PLANTING BUILDING | 9795 | CNR | Forestry |  | Washoe Valley | 1979 | 900 | 2018-08-15 | Immediate to Two Years | Currently Critical | 1 | 1000
0891INT1 | INTERIOR FINISHES | 0891 | The interior finishes are in fair condition. It is recommended that the interior walls and ceiling be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. | NURSERY PLANTING BUILDING | 9795 | CNR | Forestry |  | Washoe Valley | 1979 | 900 | 2018-08-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
0894EXT2 | WINDOW REPLACEMENT | 0894 | The windows are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 2 units. Removal and disposal of the existing windows is included in this estimate. | NURSERY SHOP | 9795 | CNR | Forestry |  | Washoe Valley | 1978 | 480 | 2018-08-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
0894ENR1 | LIGHTING UPGRADE | 0894 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts to current standards, resulting in increased efficiency and reduced costs associated with illumination. Any electrical wiring upgrades are not included in this estimate. | NURSERY SHOP | 9795 | CNR | Forestry |  | Washoe Valley | 1978 | 480 | 2018-08-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1200
0894EXT1 | EXTERIOR FINISHES | 0894 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NURSERY SHOP | 9795 | CNR | Forestry |  | Washoe Valley | 1978 | 480 | 2018-08-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4800
0889HVA1 | HVAC EQUIPMENT REPLACEMENT | 0889 | The natural gas fired wall heater and the window mounted evaporative cooler are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of a new central HVAC system for the building. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | NURSERY OFFICE | 9795 | CNR | Forestry |  | Washoe Valley | 1900 | 500 | 2018-08-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0894SFT1 | INSTALL SMOKE DETECTOR | 0894 | The building does not have any smoke detectors. Chapter 9 of the 2006 IBC and IFC require smoke detectors to be installed. This project would provide for the installation of electric smoke detectors with a battery backup. | NURSERY SHOP | 9795 | CNR | Forestry |  | Washoe Valley | 1978 | 480 | 2018-08-15 | Immediate to Two Years | Currently Critical | 1 | 500
0894HVA1 | HVAC EQUIPMENT INSTALLATION | 0894 | The building is currently used year round and does not have any source of heating or cooling. This project would provide for installation of a new HVAC system including heating and cooling. | NURSERY SHOP | 9795 | CNR | Forestry |  | Washoe Valley | 1978 | 480 | 2018-08-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7200
0893EXT2 | EXTERIOR DOOR REPLACEMENT | 0893 | The exterior metal man door is damaged from age and general wear and tear and has reached the end of its expected life. This project would provide for the replacement of the door assembly with a new metal door, frame and hardware. Removal and disposal of the existing door is included in this estimate. | NURSERY SEED/REFRIGERATOR BUILDING | 9795 | CNR | Forestry |  | Washoe Valley | 1984 | 600 | 2018-08-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
0893EXT3 | OVERHEAD DOOR REPLACEMENT | 0893 | There is an 10'x8' overhead coiling door on the North side of the building which is damaged and does not function properly. It is original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead coiling door and replacement with a new manually operated overhead coiling door. Removal and disposal of the existing door is included in this estimate. | NURSERY SEED/REFRIGERATOR BUILDING | 9795 | CNR | Forestry |  | Washoe Valley | 1984 | 600 | 2018-08-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0893SFT1 | EXTERIOR LANDING INSTALLATION | 0893 | There is an out-swinging exterior door which swings out over dirt and does not have a landing. This does not comply with 2006 IBC Section 1008.1 which describes the requirements for landings including that the landing not be less than 1/2" below the threshold. This project addresses installing a landing designed to current code. | NURSERY SEED/REFRIGERATOR BUILDING | 9795 | CNR | Forestry |  | Washoe Valley | 1984 | 600 | 2018-08-15 | Immediate to Two Years | Currently Critical | 1 | 500
0893EXT1 | EXTERIOR FINISHES | 0893 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is replacing damaged metal panels, removing dirt around building to below the finish floor elevation and sealing and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be repaired, caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NURSERY SEED/REFRIGERATOR BUILDING | 9795 | CNR | Forestry |  | Washoe Valley | 1984 | 600 | 2018-08-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
0893SFT2 | FIRE EXTINGUISHER INSTALLATION | 0893 | The building does not have a portable fire extinguisher available. International Fire Code Section 906 requires that portable fire extinguishers shall be installed in S occupancies. They shall be provided for employee use and selected and distributed based on the classes of anticipated workplace fires and on the size and degree of hazard which would affect their use. This project would provide funding for the purchase and installation of 2 fire extinguishers, cabinets, and the hardware necessary to install them. | NURSERY SEED/REFRIGERATOR BUILDING | 9795 | CNR | Forestry |  | Washoe Valley | 1984 | 600 | 2018-08-15 | Immediate to Two Years | Currently Critical | 1 | 1000
0894INT1 | INTERIOR FINISHES | 0894 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | NURSERY SHOP | 9795 | CNR | Forestry |  | Washoe Valley | 1978 | 480 | 2018-08-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2400
0889PLM1 | WATER HEATER REPLACEMENT | 0889 | There is a 40 gallon gas-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed. | NURSERY OFFICE | 9795 | CNR | Forestry |  | Washoe Valley | 1900 | 500 | 2018-08-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0890INT2 | VCT FLOORING REPLACEMENT | 0890 | The VCT (vinyl composite tile) flooring in the building is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. Asbestos Containing Material (ACM) may be present and testing of the flooring is recommended prior to proceeding with this project. | NURSERY COOK HOUSE | 9795 | CNR | Forestry |  | Washoe Valley | 1980 | 700 | 2018-08-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6300
0890HVA1 | HVAC EQUIPMENT REPLACEMENT | 0890 | The wood stove, electric heaters and window-mounted evaporative cooler were installed in 1980. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of a new central HVAC system for the building. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | NURSERY COOK HOUSE | 9795 | CNR | Forestry |  | Washoe Valley | 1980 | 700 | 2018-08-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10500
0890EXT2 | WINDOW REPLACEMENT | 0890 | The windows are original, single pane construction in a metal frame. These older windows are drafty, not energy efficient and at least one is broken. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 4 units. Removal and disposal of the existing windows is included in this estimate. | NURSERY COOK HOUSE | 9795 | CNR | Forestry |  | Washoe Valley | 1980 | 700 | 2018-08-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0890INT1 | INTERIOR FINISHES | 0890 | The interior finishes are in poor condition. It is recommended that the damaged interior gypsum board walls and ceilings be removed and replaced and painted in the next two to four years. Prior to painting, all remaining existing surfaces should be repaired and prepped. | NURSERY COOK HOUSE | 9795 | CNR | Forestry |  | Washoe Valley | 1980 | 700 | 2018-08-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7000
0890ADA2 | ADA RESTROOM / REMODEL UPGRADE | 0890 | The Men's and Women's designated public restrooms and restroom access hallway do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for the remodeling of a Men's and Women's ADA accessible restrooms and widening of the hallway to provide minimum clearances for access into the restrooms. These items may include a new sink, toilet, grab bars, door hardware, mirrors, fixtures, exhaust fans, flooring and paint for each restroom and some minor remodeling including some demolition of existing walls and new wall construction; all of which, is non-structural. ADA signage is also included in this estimate. The 2006 IBC, ICC/ANSI A117.1 - 2003, NRS 338.180 and the most current version of the Americans With Disabilities Act Accessible Guidelines (ADAAG) was used as a reference for this project | NURSERY COOK HOUSE | 9795 | CNR | Forestry |  | Washoe Valley | 1980 | 700 | 2018-08-15 | Immediate to Two Years | Currently Critical | 1 | 35000
0890SFT1 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0890 | The building is a B occupancy per the 2006 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. | NURSERY COOK HOUSE | 9795 | CNR | Forestry |  | Washoe Valley | 1980 | 700 | 2018-08-15 | Immediate to Two Years | Currently Critical | 1 | 9800
0890SFT2 | FIRE ALARM SYSTEM INSTALLATION | 0890 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2006 Section 7 and the 2006 International Fire Code. | NURSERY COOK HOUSE | 9795 | CNR | Forestry |  | Washoe Valley | 1980 | 700 | 2018-08-15 | Immediate to Two Years | Currently Critical | 1 | 2800
0890ENR1 | LIGHTING UPGRADE | 0890 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts to current standards, resulting in increased efficiency and reduced costs associated with illumination. Any electrical wiring upgrades are not included in this estimate. | NURSERY COOK HOUSE | 9795 | CNR | Forestry |  | Washoe Valley | 1980 | 700 | 2018-08-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1750
0888EXT1 | EXTERIOR FINISHES | 0888 | It is important to maintain the finish, weather resistance and appearance of the structure. This project recommends work to protect the exterior building envelope including repairs to the exterior membrane and caulking around, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and it is also recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NURSERY GREENHOUSE #1 (EAST) | 9795 | CNR | Forestry |  | Washoe Valley | 1979 | 3000 | 2018-08-15 | Four to Ten Years | Long-Term Needs | 3 | 6000
0889INT1 | INTERIOR FINISHES | 0889 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to three years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | NURSERY OFFICE | 9795 | CNR | Forestry |  | Washoe Valley | 1900 | 500 | 2018-08-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0891EXT1 | EXTERIOR FINISHES | 0891 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is replacing damaged metal panels, removing dirt around building to below the finish floor elevation and sealing and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be repaired, caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NURSERY PLANTING BUILDING | 9795 | CNR | Forestry |  | Washoe Valley | 1979 | 900 | 2018-08-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
0889INT3 | VCT FLOORING REPLACEMENT | 0889 | The VCT (vinyl composite tile) flooring in the building is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. The restroom flooring is addressed in another project. | NURSERY OFFICE | 9795 | CNR | Forestry |  | Washoe Valley | 1900 | 500 | 2018-08-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
0889INT2 | RESTROOM REMODEL | 0889 | The restroom in the building is in poor condition and is due for a complete remodel. This project would provide for a complete remodel including the restroom fixtures, hardware, floor and wall finishes. | NURSERY OFFICE | 9795 | CNR | Forestry |  | Washoe Valley | 1900 | 500 | 2018-08-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
0889EXT1 | EXTERIOR FINISHES | 0889 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NURSERY OFFICE | 9795 | CNR | Forestry |  | Washoe Valley | 1900 | 500 | 2018-08-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0889ADA1 | ADA UPGRADES | 0889 | The access into the building, entrance door, signage and information counter are not ADA compliant. This building is required to have an accessible entrance per the Americans with Disabilities Act (ADA) regulations. This project would provide for an accessible ramp and compliant stairs and handrails to access the building. This project should be coordinated with the ADA parking site project. Americans with Disabilities Act (ADA) regulations pertaining to building access, route of travel and restrooms has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances and route of travel inside the building. Section 4.13.9 of the Americans with Disabilities Act Accessible Guidelines (ADAAG) states that handles, pulls, latches, locks and other operating devices on accessible doors shall have a shape that is easy to grasp with one hand and does not require tight grasping, tight pinching, or twisting of the wrist to operate. Lever-operated mechanisms, push-type mechanisms, and U-shaped handles are acceptable designs. It is recommended that proper lever hardware be installed in this building to meet these requirements. Section 7.2 of the Americans with Disabilities Act Accessible Guidelines (ADAAG) states that the counter must have a portion which is at least 36" in length with a maximum height of 36" above the finish floor. The 2006 IBC, ICC/ANSI A117.1 - 2003, NRS 338.180 and the most current version of the Americans With Disabilities Act Accessible Guidelines (ADAAG) was used as a reference for this project | NURSERY OFFICE | 9795 | CNR | Forestry |  | Washoe Valley | 1900 | 500 | 2018-08-15 | Immediate to Two Years | Currently Critical | 1 | 30000
0889EXT2 | REPLACE ROOF | 0889 | The existing composition roofing system is damaged, has missing shingles and leaks. This project would provide for the replacement of the roof with a standing seam metal roofing system including underlayments. Removal of the existing roofing system is included in this estimate. | NURSERY OFFICE | 9795 | CNR | Forestry |  | Washoe Valley | 1900 | 500 | 2018-08-15 | Immediate to Two Years | Currently Critical | 1 | 27250
0889SFT1 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0889 | The building is a B occupancy per the 2006 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. | NURSERY OFFICE | 9795 | CNR | Forestry |  | Washoe Valley | 1900 | 500 | 2018-08-15 | Immediate to Two Years | Currently Critical | 1 | 10500
0889SFT2 | FIRE ALARM SYSTEM INSTALLATION | 0889 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2006 Section 7 and the 2006 International Fire Code. | NURSERY OFFICE | 9795 | CNR | Forestry |  | Washoe Valley | 1900 | 500 | 2018-08-15 | Immediate to Two Years | Currently Critical | 1 | 2000
0889SFT3 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0889 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2006 Chapter 10 was referenced for this project. | NURSERY OFFICE | 9795 | CNR | Forestry |  | Washoe Valley | 1900 | 500 | 2018-08-15 | Immediate to Two Years | Currently Critical | 1 | 500
0891EXT2 | REPLACE CONCRETE APRONS / LANDINGS | 0891 | The concrete landings and aprons at the exterior doors are damaged, cracking and present a tripping hazard. This project would provide for the removal of the existing concrete and installation of new 4 inch thick concrete landings and aprons. 200 square feet of concrete was used to generate this estimate. | NURSERY PLANTING BUILDING | 9795 | CNR | Forestry |  | Washoe Valley | 1979 | 900 | 2018-08-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
0890PLM1 | WATER HEATER REPLACEMENT | 0890 | There is a 40 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed for more efficient use of energy. This estimate includes: 100 feet of gas pipe, fittings, couplers, and labor for installation. | NURSERY COOK HOUSE | 9795 | CNR | Forestry |  | Washoe Valley | 1980 | 700 | 2018-08-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3750
0890INT3 | INTERIOR DOOR REPLACEMENT | 0890 | The interior doors in this building are hollow core units and are damaged. This project would provide for the installation of new solid core interior doors including frames, lever action door handles, hardware and paint. Removal and disposal of the existing doors is included in this cost estimate. A total of 3 interior doors was used in this estimate. | NURSERY COOK HOUSE | 9795 | CNR | Forestry |  | Washoe Valley | 1980 | 700 | 2018-08-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0890EXT1 | EXTERIOR FINISHES | 0890 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is the sealing and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NURSERY COOK HOUSE | 9795 | CNR | Forestry |  | Washoe Valley | 1980 | 700 | 2018-08-15 | Four to Ten Years | Long-Term Needs | 3 | 1400
1165INT1 | INTERIOR FINISHES | 1165 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next four to five years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | PARK SHOP/OFFICE | 9921 | CNR | Parks |  | Fort Churchill | 1992 | 1200 | 2018-10-09 | Four to Ten Years | Long-Term Needs | 3 | 6000
1318ADA1 | ADA RESTROOM UPGRADE | 1318 | The Men's and Women's designated ADA restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for construction of two unisex accessible restrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. | SHOP/PUBLIC RESTROOM BUILDING | 9921 | CNR | Parks |  | Fort Churchill |  | 759 | 2018-10-09 | Immediate to Two Years | Currently Critical | 1 | 25000
1165HVA1 | AIR CONDITIONER REPLACEMENT | 1165 | Two air conditioners are installed in this building that have reached the end of their useful and expected life. This project would provide for two new air conditioners to be installed including all required connections to utilities. The estimate includes removal and disposal of the old equipment. | PARK SHOP/OFFICE | 9921 | CNR | Parks |  | Fort Churchill | 1992 | 1200 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
1165SIT1 | VEHICLE GATE REPAIRS | 1165 | The vehicle gate on the side of the building is damaged and should be scheduled for repairs. The hinges have broken away from the concrete wall and the gate is currently inoperable. This project would provide for repairing the concrete wall and reattaching the vehicle gate. | PARK SHOP/OFFICE | 9921 | CNR | Parks |  | Fort Churchill | 1992 | 1200 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
1165EXT2 | ROOF REPLACEMENT | 1165 | The wood shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next two to three years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. | PARK SHOP/OFFICE | 9921 | CNR | Parks |  | Fort Churchill | 1992 | 1200 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18000
1165EXT3 | OVERHEAD DOOR REPLACEMENT | 1165 | There are three 8'x8' overhead coiling doors on the building, one of which is damaged and does not function properly. It is original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead coiling door and replacement with a new manually operated overhead coiling door. Removal and disposal of the existing door is included in this estimate. | PARK SHOP/OFFICE | 9921 | CNR | Parks |  | Fort Churchill | 1992 | 1200 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
1165INT2 | FLOORING REPLACEMENT | 1165 | The carpet and VCT (vinyl composite tile) flooring in the office areas are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the carpet and VCT and installation of new carpet and 12x12 VCT with a 6" base. | PARK SHOP/OFFICE | 9921 | CNR | Parks |  | Fort Churchill | 1992 | 1200 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9600
1165EXT1 | EXTERIOR FINISHES | 1165 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | PARK SHOP/OFFICE | 9921 | CNR | Parks |  | Fort Churchill | 1992 | 1200 | 2018-10-09 | Four to Ten Years | Long-Term Needs | 3 | 12000
1165ENR1 | LIGHTING UPGRADE | 1165 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts to current standards, resulting in increased efficiency and reduced costs associated with illumination. Any electrical wiring upgrades are not included in this estimate. | PARK SHOP/OFFICE | 9921 | CNR | Parks |  | Fort Churchill | 1992 | 1200 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
1165INT3 | NONABSORBANT FINISHES | 1165 | 2006 IBC Section 1210 requires the installation of smooth, hard, nonabsorbent surfaces in the following restroom areas: on floors in toilet and bathing rooms that extend upward onto the walls at least 6 inches, within 2 feet of the sides of urinals and water closets to a height of 4 feet above the floor and in shower compartments to a height not less than 70 inches above the drain inlet. This project recommends the installation of Fiberglass Reinforced Panel (FRP) or an equal material to comply with this code section. | PARK SHOP/OFFICE | 9921 | CNR | Parks |  | Fort Churchill | 1992 | 1200 | 2018-10-09 | Immediate to Two Years | Currently Critical | 1 | 3000
1413INT1 | INTERIOR FINISHES | 1413 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 08/08/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/09/2009. | RESIDENCE #3 - DEPAOLI RANCH | 9921 | CNR | Parks |  | Fort Churchill | 1983 | 2128 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10640
1318ADA2 | ADA SIGNAGE | 1318 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. | SHOP/PUBLIC RESTROOM BUILDING | 9921 | CNR | Parks |  | Fort Churchill |  | 759 | 2018-10-09 | Immediate to Two Years | Currently Critical | 1 | 600
1318EXT2 | ROOF REPLACEMENT | 1318 | The wood shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next two to three years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. | SHOP/PUBLIC RESTROOM BUILDING | 9921 | CNR | Parks |  | Fort Churchill |  | 759 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11385
1318ENR1 | LIGHTING UPGRADE | 1318 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts to current standards, resulting in increased efficiency and reduced costs associated with illumination. Any electrical wiring upgrades are not included in this estimate. | SHOP/PUBLIC RESTROOM BUILDING | 9921 | CNR | Parks |  | Fort Churchill |  | 759 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1898
1318EXT3 | EXTERIOR DOOR REPLACEMENT | 1318 | The existing exterior wood door appears to be original to the building. It is damaged from age and general wear and tear and is not wide enough to accommodate the needs of the staff. This project would provide for widening the doorway to 36" and replacing the wood door with a new metal door, frame and hardware. Removal and disposal of the existing door and painting of the new door is included in this estimate. | SHOP/PUBLIC RESTROOM BUILDING | 9921 | CNR | Parks |  | Fort Churchill |  | 759 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
1318EXT1 | EXTERIOR FINISHES | 1318 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SHOP/PUBLIC RESTROOM BUILDING | 9921 | CNR | Parks |  | Fort Churchill |  | 759 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7590
1413EXT2 | EXTERIOR FINISHES | 1413 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | RESIDENCE #3 - DEPAOLI RANCH | 9921 | CNR | Parks |  | Fort Churchill | 1983 | 2128 | 2018-10-09 | Four to Ten Years | Long-Term Needs | 3 | 21280
1413EXT3 | ROOF REPLACEMENT | 1413 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next two to three years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. | RESIDENCE #3 - DEPAOLI RANCH | 9921 | CNR | Parks |  | Fort Churchill | 1983 | 2128 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25536
1413SFT2 | EXTERIOR LANDING INSTALLATION | 1413 | Section R311.4.3 of the 2006 IBC describes the requirements for landings at exterior doors. The landing shall not be more than 7 3/4 inches below the top of the threshold and shall have a minumum dimension of 36 inches measured in the direction of travel. The rear exterior door does not comply with this code and poses a safety hazard. This project would provide for the installation of a compliant landing for the door. | RESIDENCE #3 - DEPAOLI RANCH | 9921 | CNR | Parks |  | Fort Churchill | 1983 | 2128 | 2018-10-09 | Immediate to Two Years | Currently Critical | 1 | 2500
1413SFT1 | INSTALL SMOKE DETECTORS | 1413 | The 2006 IBC and 2006 IFC, section 907.2.10.1.2 requires smoke detectors in dwelling units be installed in each sleeping room and on the ceiling or wall outside of each separate sleeping area in the immediate vicinity of bedrooms. State Fire Marshal NAC 477.915 (3) requires that smoke detectors be connected to the building wiring with a battery backup. This project would provide funding for the purchase and installation of smoke detectors. This project or a portion thereof was previously recommended in the FCA report dated 08/08/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/09/2009. | RESIDENCE #3 - DEPAOLI RANCH | 9921 | CNR | Parks |  | Fort Churchill | 1983 | 2128 | 2018-10-09 | Immediate to Two Years | Currently Critical | 1 | 1000
1413EXT4 | WINDOW REPLACEMENT | 1413 | The windows are original, dual pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 10 units. Removal and disposal of the existing windows is included in this estimate. | RESIDENCE #3 - DEPAOLI RANCH | 9921 | CNR | Parks |  | Fort Churchill | 1983 | 2128 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
1474EXT1 | DISCONTINUE BUILDING USE | 1474 | The residence contains numerous code and safety issues including, but not limited to an upper level exterior door without a deck or stairway, rodent infestation, broken or missing doors and windows, possible asbestos contamination and broken or missing electrical fixtures. This project recommends that the residence be secured by boarding up exterior openings and weather proof the exterior to prevent further damage. The electrical service should be disconnected and the public/personnel should not be allowed to enter or use this building. This project or a portion thereof was previously recommended in the FCA report dated 03/07/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/09/2009. | RESIDENCE #4 - DEPAOLI RANCH | 9921 | CNR | Parks |  | Fort Churchill | 1945 | 1380 | 2018-10-09 | Immediate to Two Years | Currently Critical | 1 | 10000
1318INT1 | INTERIOR FINISHES | 1318 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SHOP/PUBLIC RESTROOM BUILDING | 9921 | CNR | Parks |  | Fort Churchill |  | 759 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3795
2405EXT2 | EXTERIOR DOOR REPLACEMENT | 2405 | The existing exterior wood doors appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement of the wood doors with new metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | PUMP HOUSE #1 - RANGER RESIDENCE | 9921 | CNR | Parks |  | Fort Churchill | 1997 | 400 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
2403EXT1 | EXTERIOR/ INTERIOR FINISHES | 2403 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CXT RESTROOM #2 - GROUP CAMP | 9921 | CNR | Parks |  | Fort Churchill | 2000 | 196 | 2018-10-09 | Four to Ten Years | Long-Term Needs | 3 | 830
2405SFT1 | EXTERIOR STAIR HANDRAIL INSTALLATION | 2405 | The existing wood exterior stairs at the entry and the concrete stairs going to the basement are lacking handrails as required in the 2006 IBC Chapter 10, Section 1012. This project would provide for a tubular steel framed handrail to be installed at both stairs. | PUMP HOUSE #1 - RANGER RESIDENCE | 9921 | CNR | Parks |  | Fort Churchill | 1997 | 400 | 2018-10-09 | Immediate to Two Years | Currently Critical | 1 | 7500
2406EXT1 | EXTERIOR FINISHES | 2406 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the masonry, staining the wood members and caulking of the penetrations. It is recommended that the building be sealed, stained and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | PUMP HOUSE #2 - RESIDENCE #1 | 9921 | CNR | Parks |  | Fort Churchill | 1980 | 64 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 640
2405EXT1 | EXTERIOR FINISHES | 2405 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | PUMP HOUSE #1 - RANGER RESIDENCE | 9921 | CNR | Parks |  | Fort Churchill | 1997 | 400 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
2405INT1 | INTERIOR FINISHES | 2405 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | PUMP HOUSE #1 - RANGER RESIDENCE | 9921 | CNR | Parks |  | Fort Churchill | 1997 | 400 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
2402EXT1 | EXTERIOR/ INTERIOR FINISHES | 2402 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CXT RESTROOM #1 - BUCKLAND | 9921 | CNR | Parks |  | Fort Churchill | 2007 | 196 | 2018-10-09 | Four to Ten Years | Long-Term Needs | 3 | 830
2988EXT1 | EXTERIOR/ INTERIOR FINISHES | 2988 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CXT FIRE PROTECTION PUMP HOUSE-BUCKLAND | 9921 | CNR | Parks |  | Fort Churchill | 2006 | 220 | 2018-10-09 | Four to Ten Years | Long-Term Needs | 3 | 2200
2386EXT2 | ROOF REPLACEMENT | 2386 | The rolled asphalt roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next two to three years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. | BLACKSMITH SHOP | 9921 | CNR | Parks |  | Fort Churchill | 1935 | 195 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2925
2386EXT1 | EXTERIOR FINISHES | 2386 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BLACKSMITH SHOP | 9921 | CNR | Parks |  | Fort Churchill | 1935 | 195 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1950
2385EXT1 | EXTERIOR FINISHES | 2385 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BUCKLAND STATION KIOSK | 9921 | CNR | Parks |  | Fort Churchill | 2001 | 16 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 175
9921ENV3 | PEST CONTROL CONTRACT | 9921 | Many of the buildings throughout the site are in need of pest control. Mice, rats, pigeons and other pests are damaging the buildings and leaving droppings. Due to the potential risk of disease, this project provides for treatment, clean up and prevention of these pests by a licensed pest control company. It is recommended that this project be scheduled on a cyclical basis to maintain control of the pests. | FORT CHURCHILL STATE PARK SITE | 9921 | CNR | Parks |  | Fort Churchill | 1860 |  | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
9921ADA2 | RUINS ADA ACCESS PROGRAM ACCESSIBILITY | 9921 | The Fort Churchill ruins are open to the public for viewing and historic education. There is no designated ADA access to this area. This project would provide for an ADA accessible location inside of the public area of the Museum/ Visitor Center for an audio/ visual (A/V) presentation of the ruins which may not be ADA accessible. This project includes funds for an audio/ visual consultant to outline and document a typical walking tour of the ruins and purchase and installation of all required A/V equipment including signage, TDD equipment and minor remodeling of the public area of the building as required to accommodate this program. The 2006 IBC, ICC/ANSI A117.1 - 2003, NRS 338.180 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | FORT CHURCHILL STATE PARK SITE | 9921 | CNR | Parks |  | Fort Churchill | 1860 |  | 2018-10-09 | Immediate to Two Years | Currently Critical | 1 | 20000
9921SFT1 | FIRE HOSE REPLACEMENT | 9921 | There are several fire hose sheds around the site. Three of the hoses are cracked and leaking and are due for replacement. This project would provide for the replacement of three 200 foot by 1.5 inch diameter fire hoses. | FORT CHURCHILL STATE PARK SITE | 9921 | CNR | Parks |  | Fort Churchill | 1860 |  | 2018-10-09 | Immediate to Two Years | Currently Critical | 1 | 1500
9921SIT1 | RESEAL ASPHALT PARKING AND ROADS | 9921 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site wide including access roads and parking areas. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 400,000 square feet of asphalt area was used to generate this estimate. This project or a portion thereof was previously recommended in the FCA report dated 08/08/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/09/2009. | FORT CHURCHILL STATE PARK SITE | 9921 | CNR | Parks |  | Fort Churchill | 1860 |  | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 300000
9921SIT2 | BRIDGE REPAIRS | 9921 | There are two wooden vehicle bridges on the site that are in need of repairs. One bridge is near the entrance to the campground and one is near the entrance to the group area. Both bridges are structurally sound, but the top layer of lumber is deteriorating and should be scheduled for replacement. This project would provide for the removal and replacement of the deteriorating boards and associated hardware. | FORT CHURCHILL STATE PARK SITE | 9921 | CNR | Parks |  | Fort Churchill | 1860 |  | 2018-10-09 | Immediate to Two Years | Currently Critical | 1 | 10000
9921ENV2 | RESIDENCE SEPTIC TANK SYSTEM MAINTENANCE | 9921 | There are 4 residences each with a septic tank and associated leach fields. They are in need of pumping to maintain the integrity of the leach lines and fields. This project would provide for the pumping of Residence 1, 2, 3, and 5. Residence 4 is vacant and is not connected to any utilities. It is recommended that this project be scheduled on a cyclical basis based on usage. | FORT CHURCHILL STATE PARK SITE | 9921 | CNR | Parks |  | Fort Churchill | 1860 |  | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0488ADA2 | EXTERIOR HANDRAIL REPLACEMENT | 0488 | The handrails on the stairs and ramps around the exterior of the building are older and do not meet code for safety or accessibility. The gripping surfaces are incorrect, they are not continuous from the top to bottom landings and/ or they are installed on only one side of the stair or ramp. This project recommends replacement of the handrails in accordance with NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2003. The removal and disposal of the existing handrails is included in the estimate. | MUSEUM/VISITOR CENTER | 9921 | CNR | Parks |  | Fort Churchill | 1935 | 1300 | 2018-10-09 | Immediate to Two Years | Currently Critical | 1 | 6000
0488ADA1 | ADA SIGNAGE | 0488 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. | MUSEUM/VISITOR CENTER | 9921 | CNR | Parks |  | Fort Churchill | 1935 | 1300 | 2018-10-09 | Immediate to Two Years | Currently Critical | 1 | 750
0488HVA1 | HVAC EQUIPMENT INSTALLATION | 0488 | The building does not have any HVAC equipment other than wood burning stoves. It is recommended to condition this building to provide comfort for visitors and preserve the displays and artifacts in the building. This project would provide for the installation of a central HVAC system for the building. | MUSEUM/VISITOR CENTER | 9921 | CNR | Parks |  | Fort Churchill | 1935 | 1300 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 39000
0490EXT2 | ROOF REPLACEMENT | 0490 | The wood shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next two to three years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. | GROUP RAMADA | 9921 | CNR | Parks |  | Fort Churchill | 1976 | 1430 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 17160
0491EXT1 | COMFORT STATION REPLACEMENT | 0491 | This comfort station was built in 1963. It is dilapidated and deteriorating and no longer meets accessibility guidelines. It is recommended that the building be demolished and replaced with a new restroom facility. This project would provide for the installation of a precast CXT or similar unisex comfort station to be located near the ADA accessible parking space. An ADA accessible route of travel from the parking space to the comfort station is included in this estimate. The new restroom and route of travel shall be compliant with the 2006 IBC, ICC/ANSI A117.1 - 2003, NRS 338.180 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG). | COMFORT STATION #2 - CAMPGROUND | 9921 | CNR | Parks |  | Fort Churchill | 1963 | 147 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 22000
0492EXT1 | COMFORT STATION REPLACEMENT | 0492 | This comfort station was built in 1963. It is dilapidated and deteriorating and no longer meets accessibility guidelines. It is recommended that the building be demolished and replaced with a new restroom facility. This project would provide for the installation of a precast CXT or similar unisex comfort station to be located near the ADA accessible parking space. An ADA accessible route of travel from the parking space to the comfort station is included in this estimate. The new restroom and route of travel shall be compliant with the 2006 IBC, ICC/ANSI A117.1 - 2003, NRS 338.180 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG). | COMFORT STATION #3 - CAMPGROUND | 9921 | CNR | Parks |  | Fort Churchill | 1963 | 147 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 22000
0500EXT1 | COMFORT STATION REPLACEMENT | 0500 | This comfort station was built in 1963. It is dilapidated and deteriorating and no longer meets accessibility guidelines. It is recommended that the building be demolished and replaced with a new restroom facility. This project would provide for the installation of a precast CXT or similar unisex comfort station to be located near the ADA accessible parking space. An ADA accessible route of travel from the parking space to the comfort station is included in this estimate. The new restroom and route of travel shall be compliant with the 2006 IBC, ICC/ANSI A117.1 - 2003, NRS 338.180 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG). | COMFORT STATION #4 - PICNIC | 9921 | CNR | Parks |  | Fort Churchill | 1963 | 147 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 22000
0490INT1 | CONCRETE REPLACEMENT | 0490 | The concrete slab floor in the structure is in need of replacement. Settling and heaving has caused cracking and spalling of the concrete. This project would provide for the removal and replacement of the concrete floor. 1430 SF of 4" thick concrete was used for this estimate. | GROUP RAMADA | 9921 | CNR | Parks |  | Fort Churchill | 1976 | 1430 | 2018-10-09 | Immediate to Two Years | Currently Critical | 1 | 14300
0488SEC1 | SECURITY SYSTEM ASSESSMENT | 0488 | The security system has been disabled due to too many false alarms. It is recommended that a security system specialist evaluate the system to determine any deficiencies in order to bring the system back on line. Future projects would be based on this report. | MUSEUM/VISITOR CENTER | 9921 | CNR | Parks |  | Fort Churchill | 1935 | 1300 | 2018-10-09 | Immediate to Two Years | Currently Critical | 1 | 1000
0488SFT1 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0488 | The building is a B occupancy per the 2006 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. | MUSEUM/VISITOR CENTER | 9921 | CNR | Parks |  | Fort Churchill | 1935 | 1300 | 2018-10-09 | Immediate to Two Years | Currently Critical | 1 | 18200
0488EXT2 | ROOF REPLACEMENT | 0488 | The wood shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next two to three years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. | MUSEUM/VISITOR CENTER | 9921 | CNR | Parks |  | Fort Churchill | 1935 | 1300 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15600
0488INT1 | INTERIOR FINISHES | 0488 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | MUSEUM/VISITOR CENTER | 9921 | CNR | Parks |  | Fort Churchill | 1935 | 1300 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6500
0488EXT1 | EXTERIOR FINISHES | 0488 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MUSEUM/VISITOR CENTER | 9921 | CNR | Parks |  | Fort Churchill | 1935 | 1300 | 2018-10-09 | Four to Ten Years | Long-Term Needs | 3 | 13000
0487EXT1 | EXTERIOR FINISHES | 0487 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding, priming and painting. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | ADOBE BRICK STORAGE SHELTER | 9921 | CNR | Parks |  | Fort Churchill | 1981 | 516 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 750
0487EXT2 | ROOF REPLACEMENT | 0487 | The wood shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next two to three years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. | ADOBE BRICK STORAGE SHELTER | 9921 | CNR | Parks |  | Fort Churchill | 1981 | 516 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6192
0486EXT1 | COMFORT STATION REPLACEMENT | 0486 | This comfort station was built in 1963. It is dilapidated and deteriorating and no longer meets accessibility guidelines. It is recommended that the building be demolished and replaced with a new restroom facility. This project would provide for the installation of a precast CXT or similar unisex comfort station in the same location as the existing building. An ADA accessible parking space and route of travel to the comfort station is included in this estimate. The new restroom, parking space and route of travel shall be compliant with the 2006 IBC, ICC/ANSI A117.1 - 2003, NRS 338.180 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG). | COMFORT STATION #1 - GROUP CAMP | 9921 | CNR | Parks |  | Fort Churchill | 1963 | 147 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0501EXT1 | COMFORT STATION REPLACEMENT | 0501 | This comfort station was built in 1979. It is dilapidated and deteriorating and no longer meets accessibility guidelines. It is recommended that the building be demolished and replaced with a new restroom facility. This project would provide for the installation of a precast CXT or similar unisex comfort station in the same location as the existing building. An ADA accessible parking space and route of travel to the comfort station is included in this estimate. The new restroom, parking space and route of travel shall be compliant with the 2006 IBC, ICC/ANSI A117.1 - 2003, NRS 338.180 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG). | ADA ACCESSIBLE COMFORT STATION #1 | 9921 | CNR | Parks |  | Fort Churchill | 1979 | 140 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0490EXT1 | EXTERIOR FINISHES | 0490 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding, priming and painting the wood supports and painting the masonry. It is recommended that the building be painted, sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | GROUP RAMADA | 9921 | CNR | Parks |  | Fort Churchill | 1976 | 1430 | 2018-10-09 | Four to Ten Years | Long-Term Needs | 3 | 3575
0488ENR1 | LIGHTING UPGRADE | 0488 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts to current standards, resulting in increased efficiency and reduced costs associated with illumination. Any electrical wiring upgrades are not included in this estimate. | MUSEUM/VISITOR CENTER | 9921 | CNR | Parks |  | Fort Churchill | 1935 | 1300 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3250
0964INT2 | RESTROOM REMODEL | 0964 | The restroom in the residence is original to the building and in overall poor condition. The finishes, fixtures, cabinets, toilet, shower and exhaust fan are showing signs of wear and deterioration. This project would provide for a complete remodel of the restroom. The removal and disposal of the existing fixtures and finishes is included in this estimate. | RESIDENCE #2 - DEPAOLI RANCH | 9921 | CNR | Parks |  | Fort Churchill | 1983 | 2166 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0539SFT1 | INSTALL SMOKE DETECTORS | 0539 | The 2006 IBC and 2006 IFC, section 907.2.10.1.2 requires smoke detectors in dwelling units be installed in each sleeping room and on the ceiling or wall outside of each separate sleeping area in the immediate vicinity of bedrooms. State Fire Marshal NAC 477.915 (3) requires that smoke detectors be connected to the building wiring with a battery backup. This project would provide funding for the purchase and installation of smoke detectors. This project or a portion thereof was previously recommended in the FCA report dated 08/08/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/09/2009. | RESIDENCE #5 - GHIGLIA RANCH | 9921 | CNR | Parks |  | Fort Churchill | 1950 | 1026 | 2018-10-09 | Immediate to Two Years | Currently Critical | 1 | 1000
0488SFT2 | FIRE ALARM SYSTEM INSTALLATION | 0488 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2006 Section 7 and the 2006 International Fire Code. | MUSEUM/VISITOR CENTER | 9921 | CNR | Parks |  | Fort Churchill | 1935 | 1300 | 2018-10-09 | Immediate to Two Years | Currently Critical | 1 | 9100
0539HVA1 | EXHAUST VENT REPAIR | 0539 | The exhaust fan for the restroom currently vents into the attic space. The vent should continue through the roof and exhaust to the outside. This project would provide for the purchase and installation of a new exhaust vent roof jack and additional piping to connect the existing vent to the roof jack. | RESIDENCE #5 - GHIGLIA RANCH | 9921 | CNR | Parks |  | Fort Churchill | 1950 | 1026 | 2018-10-09 | Immediate to Two Years | Currently Critical | 1 | 500
0539INT2 | INTERIOR FINISHES | 0539 | The interior finishes are in good condition. It is recommended that the interior walls be painted at least once in the next five to six years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | RESIDENCE #5 - GHIGLIA RANCH | 9921 | CNR | Parks |  | Fort Churchill | 1950 | 1026 | 2018-10-09 | Four to Ten Years | Long-Term Needs | 3 | 5130
0539EXT1 | EXTERIOR FINISHES | 0539 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. The wood siding is failing and will no longer hold additional coats of paint. The stone chimney is also failing and will collapse if not replaced soon. Included in the cost is replacing and painting the wood siding, replacing the stone chimney and sealing and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be repaired, caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 08/08/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/09/2009. | RESIDENCE #5 - GHIGLIA RANCH | 9921 | CNR | Parks |  | Fort Churchill | 1950 | 1026 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
0539INT3 | REPLACE KITCHEN COUNTERTOPS | 0539 | The countertops in the kitchen are showing signs of wear and tear particularly at the Formica edges and corners. The countertops are delaminating and failing. This project recommends the replacement of the existing damaged countertops with heavy duty, quality finishes. This project would provide funding for the removal and replacement of the countertops. | RESIDENCE #5 - GHIGLIA RANCH | 9921 | CNR | Parks |  | Fort Churchill | 1950 | 1026 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
0541INT1 | INTERIOR FINISHES | 0541 | The interior finishes are in good condition. It is recommended that the interior walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | BUCKLAND STATION HISTORIC BUILDING | 9921 | CNR | Parks |  | Fort Churchill | 1870 | 4056 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20280
0541EXT1 | EXTERIOR FINISHES | 0541 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BUCKLAND STATION HISTORIC BUILDING | 9921 | CNR | Parks |  | Fort Churchill | 1870 | 4056 | 2018-10-09 | Four to Ten Years | Long-Term Needs | 3 | 40560
0963EXT2 | ROOF REPLACEMENT | 0963 | The wood shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next two to three years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. | CANNON SHELTER | 9921 | CNR | Parks |  | Fort Churchill | 1992 | 400 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
0963EXT1 | EXTERIOR/ INTERIOR FINISHES | 0963 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior and interior of the building. Included in the cost is power washing, priming and painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CANNON SHELTER | 9921 | CNR | Parks |  | Fort Churchill | 1992 | 400 | 2018-10-09 | Four to Ten Years | Long-Term Needs | 3 | 4000
0964EXT1 | EXTERIOR FINISHES | 0964 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 08/08/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/09/2009. | RESIDENCE #2 - DEPAOLI RANCH | 9921 | CNR | Parks |  | Fort Churchill | 1983 | 2166 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 21660
0964INT1 | INTERIOR FINISHES | 0964 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 08/08/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/09/2009. | RESIDENCE #2 - DEPAOLI RANCH | 9921 | CNR | Parks |  | Fort Churchill | 1983 | 2166 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10830
0502EXT1 | COMFORT STATION REPLACEMENT | 0502 | This comfort station was built in 1979. It is dilapidated and deteriorating and no longer meets accessibility guidelines. It is recommended that the building be demolished and replaced with a new restroom facility. This project would provide for the installation of a precast CXT or similar unisex comfort station in the same location as the existing building. The new restroom shall be compliant with the 2006 IBC, ICC/ANSI A117.1 - 2003, NRS 338.180 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG). | ADA ACCESSIBLE COMFORT STATION #2 | 9921 | CNR | Parks |  | Fort Churchill | 1979 | 140 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0964EXT6 | CHIMNEY REPLACEMENT | 0964 | The metal chimney flue is original to the building and should be scheduled for replacement. The flue does not properly vent the wood burning fireplace. This project would provide for the replacement of the flue and related chimney accessories. Removal and disposal of the existing materials is included in this estimate. | RESIDENCE #2 - DEPAOLI RANCH | 9921 | CNR | Parks |  | Fort Churchill | 1983 | 2166 | 2018-10-09 | Four to Ten Years | Long-Term Needs | 3 | 2500
0539EXT2 | WINDOW REPLACEMENT | 0539 | The windows are original, single pane construction in a wooden frame. These older windows are drafty, not energy efficient and the wooden frames have deteriorated significantly. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 14 units including wooden frames. Removal and disposal of the existing windows is included in this estimate. | RESIDENCE #5 - GHIGLIA RANCH | 9921 | CNR | Parks |  | Fort Churchill | 1950 | 1026 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 21000
0964CUL1 | OVEN REPLACEMENT | 0964 | There is a propane fired oven in the kitchen that is not operating. It has reached the end of it's useful and expected life and should be scheduled for replacement. This project would provide for a new oven/ cook top to be installed including all required connections to utilities. The estimate includes removal and disposal of the old oven. | RESIDENCE #2 - DEPAOLI RANCH | 9921 | CNR | Parks |  | Fort Churchill | 1983 | 2166 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0964EXT2 | ROOF REPLACEMENT | 0964 | The wood shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next two to three years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. | RESIDENCE #2 - DEPAOLI RANCH | 9921 | CNR | Parks |  | Fort Churchill | 1983 | 2166 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 32490
0964HVA1 | EVAPORATIVE COOLER REPLACEMENT | 0964 | An evaporative cooler is installed on the side of this building and is severely scaled and has reached the end of it's useful and expected life. This project would provide for a new evaporative cooler to be installed including all required connections to utilities. The estimate includes removal and disposal of the old cooler. | RESIDENCE #2 - DEPAOLI RANCH | 9921 | CNR | Parks |  | Fort Churchill | 1983 | 2166 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0964SFT2 | EXTERIOR LANDING INSTALLATION | 0964 | Section R311.4.3 of the 2006 IBC describes the requirements for landings at exterior doors. The landing shall not be more than 7 3/4 inches below the top of the threshold and shall have a minimum dimension of 36 inches measured in the direction of travel. There are two doors that do not comply with this code and pose a safety hazard. This project would provide for the installation of compliant landings for each door. | RESIDENCE #2 - DEPAOLI RANCH | 9921 | CNR | Parks |  | Fort Churchill | 1983 | 2166 | 2018-10-09 | Immediate to Two Years | Currently Critical | 1 | 5000
0964EXT5 | SCREEN DOOR REPLACEMENT | 0964 | The screen door at the entry is damaged from age and general wear and tear and has reached the end of its expected life. This project would provide for the replacement of the screen door. Removal and disposal of the existing door is included in this estimate. | RESIDENCE #2 - DEPAOLI RANCH | 9921 | CNR | Parks |  | Fort Churchill | 1983 | 2166 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 750
0964EXT4 | SLIDING GLASS DOOR REPLACEMENT | 0964 | The sliding glass door is damaged from age and general wear and tear and has reached the end of its expected life. This project would provide for the replacement of the sliding glass door assembly with a new door, frame and hardware. Removal and disposal of the existing door is included in this estimate. | RESIDENCE #2 - DEPAOLI RANCH | 9921 | CNR | Parks |  | Fort Churchill | 1983 | 2166 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0965INT1 | INTERIOR FINISHES | 0965 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 08/08/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/09/2009. | RESIDENCE #1 - DEPAOLI RANCH | 9921 | CNR | Parks |  | Fort Churchill | 1983 | 1600 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
0965SFT1 | INSTALL SMOKE DETECTORS | 0965 | The 2006 IBC and 2006 IFC, section 907.2.10.1.2 requires smoke detectors in dwelling units be installed in each sleeping room and on the ceiling or wall outside of each separate sleeping area in the immediate vicinity of bedrooms. State Fire Marshal NAC 477.915 (3) requires that smoke detectors be connected to the building wiring with a battery backup. This project would provide funding for the purchase and installation of smoke detectors. This project or a portion thereof was previously recommended in the FCA report dated 08/08/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/09/2009. | RESIDENCE #1 - DEPAOLI RANCH | 9921 | CNR | Parks |  | Fort Churchill | 1983 | 1600 | 2018-10-09 | Immediate to Two Years | Currently Critical | 1 | 1000
0965SFT2 | EXTERIOR LANDING INSTALLATION | 0965 | Section R311.4.3 of the 2006 IBC describes the requirements for landings at exterior doors. The landing shall not be more than 7 3/4 inches below the top of the threshold and shall have a minimum dimension of 36 inches measured in the direction of travel. There are two doors that do not comply with this code and pose a safety hazard. This project would provide for the installation of compliant landings for each door. | RESIDENCE #1 - DEPAOLI RANCH | 9921 | CNR | Parks |  | Fort Churchill | 1983 | 1600 | 2018-10-09 | Immediate to Two Years | Currently Critical | 1 | 5000
0965HVA1 | EVAPORATIVE COOLER REPLACEMENT | 0965 | An evaporative cooler is installed on the side of this building and is severely scaled and has reached the end of it's useful and expected life. This project would provide for a new evaporative cooler to be installed including all required connections to utilities. The estimate includes removal and disposal of the old cooler. | RESIDENCE #1 - DEPAOLI RANCH | 9921 | CNR | Parks |  | Fort Churchill | 1983 | 1600 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0965EXT3 | ROOF REPLACEMENT | 0965 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next two to three years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. | RESIDENCE #1 - DEPAOLI RANCH | 9921 | CNR | Parks |  | Fort Churchill | 1983 | 1600 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19200
0965EXT2 | EXTERIOR FINISHES | 0965 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | RESIDENCE #1 - DEPAOLI RANCH | 9921 | CNR | Parks |  | Fort Churchill | 1983 | 1600 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16000
0964SFT1 | INSTALL SMOKE DETECTORS | 0964 | The 2006 IBC and 2006 IFC, section 907.2.10.1.2 requires smoke detectors in dwelling units be installed in each sleeping room and on the ceiling or wall outside of each separate sleeping area in the immediate vicinity of bedrooms. State Fire Marshal NAC 477.915 (3) requires that smoke detectors be connected to the building wiring with a battery backup. This project would provide funding for the purchase and installation of smoke detectors. This project or a portion thereof was previously recommended in the FCA report dated 08/08/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/09/2009. | RESIDENCE #2 - DEPAOLI RANCH | 9921 | CNR | Parks |  | Fort Churchill | 1983 | 2166 | 2018-10-09 | Immediate to Two Years | Currently Critical | 1 | 1000
0539HVA2 | EVAPORATIVE COOLER REPLACEMENT | 0539 | An evaporative cooler is installed on the roof of this building. It is reaching the end of it's useful and expected life and should be scheduled for replacement. This project would provide for a new evaporative cooler to be installed including all required connections to utilities. The estimate includes removal and disposal of the old cooler. | RESIDENCE #5 - GHIGLIA RANCH | 9921 | CNR | Parks |  | Fort Churchill | 1950 | 1026 | 2018-10-09 | Four to Ten Years | Long-Term Needs | 3 | 3000
1013EXT1 | HISTORIC BUILDING MAINTENANCE | 1013 | The wood structure is over 100 years old and there are numerous areas where the wood is splitting, warping and deteriorating. This is also an exhibit for the park and requires maintenance time to display the artifacts and maintain the signage. This project would provide for sealing the wood, caulking the flashing, fixtures and windows, replacing metal roof panels as needed, replacing wood siding as needed and maintaining the exhibit in a state of arrested decay. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | PHILLIPS HOUSE | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1896 | 483 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7245
1035EXT1 | HISTORIC BUILDING MAINTENANCE | 1035 | The wood and stone structure is over 100 years old and there are numerous areas where the wood is splitting, warping and deteriorating. This is also an exhibit for the park and requires maintenance time to display the artifacts and maintain the signage. This project would provide for sealing the wood, cleaning, repair and re-pointing of the stone work, caulking the flashing, fixtures and windows, replacing wood shake roof shingles as needed, replacing wood siding as needed and maintaining the exhibit in a state of arrested decay. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | STORE WAREHOUSE | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1896 | 464 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6960
1034EXT1 | HISTORIC BUILDING MAINTENANCE | 1034 | The wood structure is over 100 years old and there are numerous areas where the wood is splitting, warping and deteriorating. This is also an exhibit for the park and requires maintenance time to display the artifacts and maintain the signage. This project would provide for sealing the wood, caulking the flashing, fixtures and windows, replacing wood shake roof shingles as needed, replacing wood siding as needed and maintaining the exhibit in a state of arrested decay. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | TIFFELS CABIN/STAGECOACH STOP | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1896 | 693 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10395
1028ADA1 | BUILDING REPLACEMENT | 1028 | The restroom is approaching the end of its expected life and should be scheduled for replacement. Although it has an ADA sign on it, it is not compliant with current ADA requirements. This project would provide for the demolition and disposal of the existing structure and installation of an ADA compliant precast CXT or similar unisex comfort station to be located adjacent to an ADA accessible parking space. An ADA accessible route of travel from the parking to the comfort station is included in this estimate. | RESTROOM B - CAMPGROUND | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1970 | 100 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
1012EXT1 | HISTORIC BUILDING MAINTENANCE | 1012 | The wood structure is over 100 years old and there are numerous areas where the wood is splitting, warping and deteriorating. This project would provide for replacing wood siding and roofing as needed and maintaining the exhibit in a state of arrested decay. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BALL MILL | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1896 | 1200 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2400
1011EXT1 | HISTORIC BUILDING MAINTENANCE | 1011 | The wood structure is over 100 years old and there are numerous areas where the wood is splitting, warping and deteriorating. This is also an exhibit for the park and requires maintenance time to display the artifacts and maintain the signage. This project would provide for sealing the wood, caulking the flashing, fixtures and windows, replacing metal roof panels as needed, replacing wood siding as needed and maintaining the exhibit in a state of arrested decay. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MACHINE SHOP | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1896 | 2150 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 32250
1010EXT1 | HISTORIC BUILDING MAINTENANCE | 1010 | The wood structure is over 100 years old and there are numerous areas where the wood is splitting, warping and deteriorating. This is also an exhibit for the park and requires maintenance time to display the artifacts and maintain the signage. This project would provide for sealing the wood, caulking the flashing, fixtures and windows, replacing wood shake roof shingles as needed, replacing wood siding as needed and maintaining the exhibit in a state of arrested decay. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | ITALIAN HOUSE | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1896 | 462 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6930
1009EXT1 | HISTORIC BUILDING MAINTENANCE | 1009 | The wood structure is over 100 years old and there are numerous areas where the wood is splitting, warping and deteriorating. This project would provide for replacing wood siding and roofing as needed and maintaining the exhibit in a state of arrested decay. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOIST SHACK | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1896 | 336 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 672
1001EXT1 | HISTORIC BUILDING MAINTENANCE | 1001 | The wood structure is over 100 years old and there are numerous areas where the wood is splitting, warping and deteriorating. This is also an exhibit for the park and requires maintenance time to display the artifacts and maintain the signage. This project would provide for sealing the wood, caulking the flashing, fixtures and windows, replacing metal roof panels as needed, replacing wood siding as needed and maintaining the exhibit in a state of arrested decay. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BERLIN MILL | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1896 | 9945 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 149175
1007EXT1 | EXTERIOR/ INTERIOR FINISHES | 1007 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CXT COMFORT STATION C - FOSSIL HOUSE | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1985 | 60 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 600
1006EXT1 | EXTERIOR/ INTERIOR FINISHES | 1006 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | COMFORT STATION B - CAMPGROUND | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1985 | 60 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 600
1005EXT1 | EXTERIOR/ INTERIOR FINISHES | 1005 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | COMFORT STATION A - CAMPGROUND | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1985 | 60 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 600
1004EXT1 | HISTORIC BUILDING MAINTENANCE | 1004 | The wood structure is over 50 years old and there are numerous areas where the wood is splitting, warping and deteriorating. This is also an exhibit for the park and requires maintenance time to display the artifacts and maintain the signage. This project would provide for sealing the wood, caulking the flashing, fixtures and windows, replacing rolled asphalt roofing as needed, replacing wood siding as needed and maintaining the exhibit in a state of arrested decay. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CAMP SHED | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1954 | 560 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8400
1003EXT1 | HISTORIC BUILDING MAINTENANCE | 1003 | The wood structure is over 50 years old and there are numerous areas where the wood is splitting, warping and deteriorating. This is also an exhibit for the park and requires maintenance time to display the artifacts and maintain the signage. This project would provide for sealing the wood, caulking the flashing, fixtures and windows, replacing rolled asphalt roofing as needed, replacing wood siding as needed and maintaining the exhibit in a state of arrested decay. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BOBTOWN BOXCAR | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1954 | 300 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
1002EXT1 | HISTORIC BUILDING MAINTENANCE | 1002 | The wood structure is over 50 years old and there are numerous areas where the wood is splitting, warping and deteriorating. This is also an exhibit for the park and requires maintenance time to display the artifacts and maintain the signage. This project would provide for sealing the wood, caulking the flashing, fixtures and windows, replacing rolled asphalt roofing as needed, replacing wood siding as needed and maintaining the exhibit in a state of arrested decay. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CAMP CABIN | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1954 | 458 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6870
1008EXT1 | HISTORIC BUILDING MAINTENANCE | 1008 | The wood structure is over 100 years old and there are numerous areas where the wood is splitting, warping and deteriorating. This is also an exhibit for the park and requires maintenance time to display the artifacts and maintain the signage. This project would provide for sealing the wood, caulking the flashing, fixtures and windows, replacing wood shake roof shingles as needed, replacing wood siding as needed and maintaining the exhibit in a state of arrested decay. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | STEVENS HOUSE | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1896 | 462 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6930
1032EXT1 | HISTORIC BUILDING MAINTENANCE | 1032 | The wood structure is over 100 years old and there are numerous areas where the wood is splitting, warping and deteriorating. This is also an exhibit for the park and requires maintenance time to display the artifacts and maintain the signage. This project would provide for sealing the wood, caulking the flashing, fixtures and windows, replacing metal roof panels as needed, replacing wood siding as needed and maintaining the exhibit in a state of arrested decay. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | WATSON HOUSE | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1896 | 483 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7245
1000EXT1 | HISTORIC BUILDING MAINTENANCE | 1000 | The wood structure is over 100 years old and there are numerous areas where the wood is splitting, warping and deteriorating. This is also an exhibit for the park and requires maintenance time to display the artifacts and maintain the signage. This project would provide for sealing the wood, caulking the flashing, fixtures and windows, replacing wood shake roof shingles as needed, replacing wood siding as needed and maintaining the exhibit in a state of arrested decay. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | ASSAY OFFICE | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1896 | 576 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8640
2576EXT1 | EXTERIOR FINISHES | 2576 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SEASONAL CABIN #1 | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 2006 | 248 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1240
2576INT1 | INTERIOR FINISHES | 2576 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SEASONAL CABIN #1 | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 2006 | 248 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1240
2577INT1 | INTERIOR FINISHES | 2577 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SEASONAL CABIN #2 | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 2006 | 248 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1240
2379EXT1 | EXTERIOR FINISHES | 2379 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing and staining the wood and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be stained and caulked in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BLACKSMITH SHOP - DIANA MINE | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 2003 | 400 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
2577EXT1 | EXTERIOR FINISHES | 2577 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SEASONAL CABIN #2 | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 2006 | 248 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1240
3101EXT1 | EXTERIOR FINISHES | 3101 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing and staining the wood and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be stained and caulked in the next 5-6 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | RANGER RESIDENCE #2 | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 2011 | 1112 | 2019-06-13 | Four to Ten Years | Long-Term Needs | 3 | 5560
9922EXT1 | EXTERIOR FINISHES, SHADE RAMADAS | 9922 | There are 14 wood shade ramadas in the campground which are 120 s.f. each for a total of 3,360 square feet. It is important to maintain the finish, weather resistance and appearance of the structures. This project would provide for staining the structures and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structures. | BERLIN ICHTHYOSAUR STATE PARK SITE | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 0 |  | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3360
9922ADA2 | CAMPGROUND ADA UPGRADES | 9922 | According to proposed US Access Board regulations, a campground with 2-25 camping spaces shall have 2 accessible spaces spaced throughout the campground to provide as many campsite options as possible. Of the 14 available spaces, the campground currently does not have any accessible spaces. Other regulations include 20'-0" wide drive aisles for RV/ tent trailer sites and accessible amenities on an accessible route including grills, picnic tables, fire rings and water & electric utilities. These guidelines are not official at this time, but are expected to be incorporated into the ADAAG soon. This project provides for upgrading two existing campsites to accessible campsites. | BERLIN ICHTHYOSAUR STATE PARK SITE | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 0 |  | 2019-06-13 | Immediate to Two Years | Currently Critical | 1 | 20000
9922PLM1 | HOSE BIB REPLACEMENTS | 9922 | There are 9 frost-proof hose bibs throughout the campground that have reached the end of their expected life. Many are damaged by freezing temperatures and have active leaks and should be replaced in the next one to two years. This project would provide for the removal and disposal of the existing hose bibs and purchase and installation of new frost proof hose bibs at all 9 locations. | BERLIN ICHTHYOSAUR STATE PARK SITE | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 0 |  | 2019-06-13 | Immediate to Two Years | Currently Critical | 1 | 13500
9922SFT1 | FIRE DEFENSE UPGRADE | 9922 | In the summer of 2002 the Nevada Division of Forestry performed a Wild Land Fire Risk Assessment on this facility. Several factors are taken into consideration when performing these assessments such as type of building and roofing materials, what kind of water supply is available, fuel density, defensible space, topography, who responds in case of fire, how far away the responding party, is, etc. The Berlin Ichthyosaur Park was given a Risk Assessment Rating of 85 points. This rating is well into the Extreme Danger Category of 75 and above. The Park was also assessed by the State Fire Marshal's office in the summer of 2003. Recommendations from these assessments include thinning and treatment of fuels, removal of ladder fuels, creating defensible space, reseeding, and addition of a water storage tank dedicated to the existing fire suppression hydrant system. Also obtain additional fire fighting apparatus and provide training to park personnel. Address the need for a reliable source of electrical power. Provide secondary emergency egress from park and develop areas of refuge (Safety Zones) for visitors to take shelter in the event of a fire. Develop evacuation/emergency procedures and establish a more dependable means of communication from the Park to local resources. This project or a portion thereof was previously recommended in the FCA report dated 07/28/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2011. | BERLIN ICHTHYOSAUR STATE PARK SITE | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 0 |  | 2019-06-13 | Immediate to Two Years | Currently Critical | 1 | 1500000
3101INT1 | INTERIOR FINISHES | 3101 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 7-8 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | RANGER RESIDENCE #2 | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 2011 | 1112 | 2019-06-13 | Four to Ten Years | Long-Term Needs | 3 | 5560
9922ADA1 | ADA PARKING SPACES | 9922 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. A concrete parking area and passenger loading area are necessary in seven locations throughout the park to comply with ADA requirements. This project would provide for a concrete van accessible ADA parking and loading space at the Visitor's Center/ Park Office, Restroom A - Visitor's Center, Restroom B - Campground, Comfort Station A - Campground, Comfort Station B - Campground, Comfort Station C - Fossil House and the Fossil House. This will require regrading, installing P.C. concrete, striping, signage and any other necessary upgrades. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 07/28/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2011. | BERLIN ICHTHYOSAUR STATE PARK SITE | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 0 |  | 2019-06-13 | Immediate to Two Years | Currently Critical | 1 | 21000
3104ADA1 | BUILDING REPLACEMENT | 3104 | The restroom is approaching the end of its expected life and should be scheduled for replacement. Although it has an ADA sign on it, it is not compliant with current ADA requirements. This project would provide for the demolition and disposal of the existing structure and installation of an ADA compliant precast CXT or similar unisex comfort station to be located adjacent to an ADA accessible parking space. An ADA accessible route of travel from the parking to the comfort station is included in this estimate. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2003 were referenced for this project. | RESTROOM A - VISITORS CENTER | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1970 | 36 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
3102EXT1 | EXTERIOR FINISHES | 3102 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing and staining the wood and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be stained and caulked in the next 5-6 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | RANGER RESIDENCE #2 GARAGE | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 2011 | 774 | 2019-06-13 | Four to Ten Years | Long-Term Needs | 3 | 3870
9922EXT2 | WALL REPAIRS - FOSSIL HOUSE AREA | 9922 | The large concrete wall that displays a life size image of an Ichthyosaur next to the Fossil House is due for repairs. It has developed large vertical cracks in several areas and the top is spalling and crumbling. This project provides for filling the cracks and patching the spalled and crumbled areas to protect the display from further damage. | BERLIN ICHTHYOSAUR STATE PARK SITE | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 0 |  | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0468EXT1 | EXTERIOR FINISHES | 0468 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing and staining the wood and caulking of the windows, flashing, fixtures and all other penetrations. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the building be stained and caulked in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | VISITOR'S CENTER/PARK OFFICE | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1896 | 880 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4400
0468ADA1 | ADA UPGRADES | 0468 | The Visitor's Center/ Park Office is lacking an accessible entrance into the building and path of travel inside the building. The building is open to the public, requiring it to have an accessible entrance and interior path of travel per the Americans with Disabilities Act (ADA) regulations. This project would provide for an accessible ramp to access the building, accessible door and hardware and accessible path of travel inside the building to all programs, exhibits and areas open to the public. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. The State Historic Preservation Office should be consulted prior to project implementation. | VISITOR'S CENTER/PARK OFFICE | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1896 | 880 | 2019-06-13 | Immediate to Two Years | Currently Critical | 1 | 15000
0467EXT1 | EXTERIOR FINISHES | 0467 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing and staining the wood and caulking of the fiberglass panels, windows, flashing, fixtures and all other penetrations. It is recommended that the building be stained and caulked in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | FOSSIL HOUSE | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1966 | 4300 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 21500
0467ADA1 | ADA UPGRADES | 0467 | The Fossil House is lacking an accessible path of travel inside the building and to the museum exhibits. The building is open to the public, requiring it to have an accessible path of travel per the Americans with Disabilities Act (ADA) regulations. This project would provide for an accessible path of travel throughout the museum including an accessible ramp, handrail/guardrails and modifications to the paver walkway to bring the slopes into compliance. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. Alternatively, an ADA accessible location could be provided inside the building for an audio/visual (A/V) presentation of the exhibit areas which are not ADA accessible. | FOSSIL HOUSE | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1966 | 4300 | 2019-06-13 | Immediate to Two Years | Currently Critical | 1 | 100000
0473EXT2 | ROOF REPLACEMENT | 0473 | The wood shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayments. Metal roofing to match fossil house is also an option. This estimate includes removal and disposal of the old roofing. | FOSSIL HOUSE STORAGE | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1970 | 150 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1800
0473EXT1 | EXTERIOR FINISHES | 0473 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing and staining the wood and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be stained and caulked in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | FOSSIL HOUSE STORAGE | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1970 | 150 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 750
0472EXT1 | HISTORIC BUILDING MAINTENANCE | 0472 | The wood and adobe brick structure is over 100 years old and there are numerous areas where the adobe is failing and the wood is splitting, warping and deteriorating. This is also an exhibit for the park and requires maintenance time to display the artifacts and maintain the signage. This project would provide for cleaning, repair and re-pointing of the adobe brick work, sealing the wood, caulking the flashing, fixtures and windows, replacing wood siding as needed and maintaining the exhibit in a state of arrested decay. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | ADOBE HOUSE | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1863 | 544 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8160
0471EXT1 | HISTORIC BUILDING MAINTENANCE | 0471 | The wood structure is over 100 years old and there are numerous areas where the wood is splitting, warping and deteriorating. This is also an exhibit for the park and requires maintenance time to display the artifacts and maintain the signage. This project would provide for sealing the wood, caulking the flashing, fixtures and windows, replacing metal roof panels as needed, replacing wood siding as needed and maintaining the exhibit in a state of arrested decay. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | FOSTERS BLACKSMITH SHOP | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1896 | 480 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7200
0470ADA1 | BUILDING REPLACEMENT | 0470 | The restroom is approaching the end of its expected life and should be scheduled for replacement. Although it has an ADA sign on it, it is not compliant with current ADA requirements. This project would provide for the demolition and disposal of the existing structure and installation of an ADA compliant precast CXT or similar unisex comfort station to be located adjacent to an ADA accessible parking space. An ADA accessible route of travel from the parking to the comfort station is included in this estimate. | RESTROOM - PICNIC AREA | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1970 | 150 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0468INT1 | INTERIOR FINISHES | 0468 | The interior finishes are in fair condition. It is recommended that the historic wallpapered walls and ceilings be maintained in a state of arrested decay and the painted walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. | VISITOR'S CENTER/PARK OFFICE | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1896 | 880 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4400
0467INT1 | INTERIOR FINISHES | 0467 | The interior finishes are in fair condition. It is recommended that the interior concrete be sealed, the wood plywood, beams and posts be cleaned and stained and the metal hardware and bolts be tightened or replaced as needed at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to staining, all surfaces should be repaired and prepped. | FOSSIL HOUSE | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1966 | 4300 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 21500
0469INT2 | INTERIOR FINISHES | 0469 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | RANGER RESIDENCE - MINE FORMAN'S HOUSE | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1896 | 750 | 2019-06-13 | Four to Ten Years | Long-Term Needs | 3 | 3750
0469INT3 | FLOORING REPLACEMENT | 0469 | The sheet vinyl and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new sheet vinyl with a 6" base and heavy duty commercial grade carpet in the next 3-4 years. | RANGER RESIDENCE - MINE FORMAN'S HOUSE | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1896 | 750 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5250
0469SFT1 | SMOKE DETECTOR UPGRADE | 0469 | The 2006 IBC and 2006 IFC, section 907.2.10.1.2 requires smoke detectors in dwelling units be installed in each sleeping room and on the ceiling or wall outside of each separate sleeping area in the immediate vicinity of bedrooms. State Fire Marshal NAC 477.915 (3) requires that smoke detectors be connected to the building wiring with a battery backup. The existing smoke detectors are not hard wired to the buildings electrical system. This project would provide funding for replacing the existing battery powered smoke detectors and the purchase and installation of new smoke detectors. | RANGER RESIDENCE - MINE FORMAN'S HOUSE | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1896 | 750 | 2019-06-13 | Immediate to Two Years | Currently Critical | 1 | 750
0469INT4 | KITCHEN REMODEL | 0469 | The kitchen is in fair to poor condition. The cabinets and equipment are showing signs of general wear and tear and are approaching the end of their expected life. This project recommends the replacement of the existing kitchen cabinets, counters, fixtures and equipment with mid range, high quality components. | RANGER RESIDENCE - MINE FORMAN'S HOUSE | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1896 | 750 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
0469INT5 | RESTROOM REMODEL | 0469 | The restroom in the residence is in overall poor condition and should be scheduled for a remodel. The finishes, fixtures, cabinets, toilet, shower and exhaust fan are showing signs of wear and deterioration. This project would provide for a complete remodel of the restroom. The removal and disposal of the existing fixtures and finishes is included in this estimate. | RANGER RESIDENCE - MINE FORMAN'S HOUSE | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1896 | 750 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0469PLM1 | WATER HEATER REPLACEMENT | 0469 | There is a 50 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | RANGER RESIDENCE - MINE FORMAN'S HOUSE | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1896 | 750 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0469HVA1 | HVAC UPGRADE | 0469 | The existing HVAC system consists of a wood burning stove, several small propane fired unit heaters and no cooling equipment. There is a need for cooling equipment to provide a comfortable living environment in the summer. This project would provide for replacing the existing heaters with an exterior ground mounted packaged unit that provides heating as well as air conditioning. An electric unit would be most economical if it is solely powered by the solar array electrical system as opposed to a propane fired unit. | RANGER RESIDENCE - MINE FORMAN'S HOUSE | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1896 | 750 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
0469EXT1 | EXTERIOR FINISHES | 0469 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing and staining the wood and caulking of the windows, flashing, fixtures and all other penetrations. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the building be stained and caulked in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | RANGER RESIDENCE - MINE FORMAN'S HOUSE | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1896 | 750 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3750
1336INT3 | SHOWER AND RESTROOM REMODEL | 1336 | The restrooms and shower rooms are original to the building and in overall poor condition. The finishes, fixtures, cabinets, toilets, showers and exhaust fans are showing signs of wear and deterioration. This project would provide for a complete remodel of the restrooms and shower rooms. The removal and disposal of the existing fixtures and finishes is included in this estimate. | SEASONAL EMPLOYEES BASE CAMP | 9959 | CNR | Parks |  | Lahontan SRA | 1976 | 588 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
1331SFT2 | EXTERIOR LANDING / HANDRAIL INSTALLATION | 1331 | Section R311.4.3 of the 2006 IBC Residential Building Code describes the requirements for landings at exterior doors. The landing shall not be more than 7 3/4 inches below the top of the threshold and shall have a minumum dimension of 36 inches measured in the direction of travel. The exterior landing at the entry door does not comply with this code and poses a safety hazard. This project would provide for the installation of a compliant landing for the door and installation of handrails as required by Chapter 10 of the 2006 IBC. | LD RESIDENCE #3 | 9959 | CNR | Parks |  | Lahontan SRA | 1923 | 890 | 2019-06-19 | Immediate to Two Years | Currently Critical | 1 | 2500
1331ENR3 | EVAPORATIVE COOLER REPLACEMENT | 1331 | An evaporative cooler is installed on the side of this building and is severely scaled and has reached the end of it's useful and expected life. This project would provide for a new evaporative cooler to be installed including all required connections to utilities. The estimate includes removal and disposal of the old cooler. | LD RESIDENCE #3 | 9959 | CNR | Parks |  | Lahontan SRA | 1923 | 890 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
1331ENR1 | WINDOW REPLACEMENT | 1331 | The windows are older, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 8 units. Removal and disposal of the existing windows is included in this estimate. | LD RESIDENCE #3 | 9959 | CNR | Parks |  | Lahontan SRA | 1923 | 890 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
1331INT1 | INTERIOR FINISHES | 1331 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | LD RESIDENCE #3 | 9959 | CNR | Parks |  | Lahontan SRA | 1923 | 890 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4450
1331ENR2 | FURNACE REPLACEMENT | 1331 | The building is heated by a propane-fired furnace. It is original to the building, not energy efficient and is reaching the end of its useful life. This project provides for disposal of the existing unit and replacement with a new propane-fired unit including connections to utilities. | LD RESIDENCE #3 | 9959 | CNR | Parks |  | Lahontan SRA | 1923 | 890 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
1331INT2 | FLOORING REPLACEMENT | 1331 | The sheet vinyl and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the next 2-3 years. This project or a portion thereof was previously recommended in the FCA report dated 06/02/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/15/2010. | LD RESIDENCE #3 | 9959 | CNR | Parks |  | Lahontan SRA | 1923 | 890 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6230
1331EXT5 | ROOF REPAIRS | 1331 | The roof design is inadequate and is contributing to the premature deterioration of the building. There are leaks on the west side of the roof between the two gable ends where the cricket is not sufficient. The cricket needs to be rebuilt to create a steeper slope. This will ensure that rain and snow does not accumulate on the roof and cause leaks. | LD RESIDENCE #3 | 9959 | CNR | Parks |  | Lahontan SRA | 1923 | 890 | 2019-06-19 | Immediate to Two Years | Currently Critical | 1 | 1500
1336PLM1 | WATER HEATER REPLACEMENT | 1336 | There is a 50 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | SEASONAL EMPLOYEES BASE CAMP | 9959 | CNR | Parks |  | Lahontan SRA | 1976 | 588 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
1338EXT1 | EXTERIOR FINISHES | 1338 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry, staining the wood and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SS2 COMFORT STATION - BOAT LAUNCH | 9959 | CNR | Parks |  | Lahontan SRA | 1974 | 400 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 2000
1331PLM1 | WATER HEATER REPLACEMENT | 1331 | There is a 50 gallon propane-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 6-7 years. It is recommended that a new propane-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | LD RESIDENCE #3 | 9959 | CNR | Parks |  | Lahontan SRA | 1923 | 890 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 1500
1336ENR1 | WINDOW REPLACEMENT | 1336 | The windows are original, single pane construction in a metal frame. These older windows are drafty, not energy efficient and at least one is broken. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 6 units. Removal and disposal of the existing windows is included in this estimate. | SEASONAL EMPLOYEES BASE CAMP | 9959 | CNR | Parks |  | Lahontan SRA | 1976 | 588 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
1336EXT1 | EXTERIOR FINISHES | 1336 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 7-8 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SEASONAL EMPLOYEES BASE CAMP | 9959 | CNR | Parks |  | Lahontan SRA | 1976 | 588 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 2940
1336INT1 | INTERIOR FINISHES | 1336 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SEASONAL EMPLOYEES BASE CAMP | 9959 | CNR | Parks |  | Lahontan SRA | 1976 | 588 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2940
1336EXT2 | ROOF REPLACEMENT | 1336 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing and underlayments. | SEASONAL EMPLOYEES BASE CAMP | 9959 | CNR | Parks |  | Lahontan SRA | 1976 | 588 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5880
1336INT2 | KITCHEN REMODEL | 1336 | The kitchen is in fair to poor condition. The cabinets and equipment are showing signs of general wear and tear and are approaching the end of their expected life. This project recommends the replacement of the existing kitchen cabinets, counters, fixtures and equipment with mid range, high quality components. | SEASONAL EMPLOYEES BASE CAMP | 9959 | CNR | Parks |  | Lahontan SRA | 1976 | 588 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
1336ENR2 | LIGHTING UPGRADE | 1336 | The existing lighting fixtures are the older incandescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. CFL (compact flourescent lamps) are suggested. Occupancy sensors will be installed in restrooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | SEASONAL EMPLOYEES BASE CAMP | 9959 | CNR | Parks |  | Lahontan SRA | 1976 | 588 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 588
1337ADA1 | ADA SIGNAGE | 1337 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage for the parking space does not comply with this criteria. This project would provide funding for purchase and installation of an ADA parking sign which was missing from the ADA parking space at the time of the survey. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | VIRGINIA BEACH SST RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 2000 | 128 | 2019-06-19 | Immediate to Two Years | Currently Critical | 1 | 1000
1331EXT2 | EXTERIOR DOOR REPLACEMENT | 1331 | The front exterior wood door appears to be original to the building. It is damaged from age and general wear and tear. This project would provide for the replacement of the wood door with a new metal door, frame and hardware. Removal and disposal of the existing door and painting of the new door is included in this estimate. | LD RESIDENCE #3 | 9959 | CNR | Parks |  | Lahontan SRA | 1923 | 890 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 750
1338INT1 | INTERIOR FINISHES | 1338 | The interior finishes are in fair condition. It is recommended that the Fiberglass Reinforced Panels are power washed and re-caulked and the ceramic tiles are repaired and sealed as needed. This project should be done at least once in the next 2-3 years and scheduled on a cyclical basis to maintain the integrity of the structure. | SS2 COMFORT STATION - BOAT LAUNCH | 9959 | CNR | Parks |  | Lahontan SRA | 1974 | 400 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
1327EXT1 | EXTERIOR FINISHES | 1327 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is cleaning and sealing the wood and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | LD GARAGE #3 | 9959 | CNR | Parks |  | Lahontan SRA | 1923 | 400 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
1337EXT1 | EXTERIOR/ INTERIOR FINISHES | 1337 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | VIRGINIA BEACH SST RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 2000 | 128 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 1280
1322EXT1 | EXTERIOR FINISHES | 1322 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry, staining the wood and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NORTH SHORE MARINA CLIVUS RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 1984 | 460 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 2300
1320INT1 | INTERIOR FINISHES | 1320 | The interior finishes are in fair condition. It is recommended that the Fiberglass Reinforced Panels are power washed and re-caulked and the ceramic tiles are repaired and sealed as needed. This project should be done at least once in the next 2-3 years and scheduled on a cyclical basis to maintain the integrity of the structure. | OVERLOOK CXT COMFORT STATION | 9959 | CNR | Parks |  | Lahontan SRA | 2006 | 204 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1020
1320EXT1 | EXTERIOR FINISHES | 1320 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry, staining the wood and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | OVERLOOK CXT COMFORT STATION | 9959 | CNR | Parks |  | Lahontan SRA | 2006 | 204 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1020
1321ELE1 | SOLAR PANEL REPLACEMENT | 1321 | The power to the building is provided by a photovoltaic system. The solar panels have been broken by vandals and should be scheduled for replacement. This project provides for the purchase and installation of two roof-mounted solar panels. | BLACKBIRD POINT SST RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 2003 | 128 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
1321EXT1 | EXTERIOR/ INTERIOR FINISHES | 1321 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BLACKBIRD POINT SST RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 2003 | 128 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1280
1322INT1 | INTERIOR FINISHES | 1322 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | NORTH SHORE MARINA CLIVUS RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 1984 | 460 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2300
1347INT1 | FLOOR REPAIRS | 1347 | The painted concrete floor in the building is damaged and should be scheduled for repairs. This project would provide for stripping the concrete, filling the cracks and applying a new coat of paint in the next 2-3 years. | SS MECHANICAL BUILDING NORTH | 9959 | CNR | Parks |  | Lahontan SRA | 1978 | 480 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 960
1322ADA1 | ADA UPGRADES | 1322 | The existing Americans with Disabilities Act (ADA) designated route of travel to the restroom does not meet current accessibility requirements. Included in this project is installing edge protection on the ramp leading up to the restroom and adding ADA signage. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | NORTH SHORE MARINA CLIVUS RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 1984 | 460 | 2019-06-19 | Immediate to Two Years | Currently Critical | 1 | 2000
1324ADA1 | ADA PARKING SIGN | 1324 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage for the parking space does not comply with this criteria. This project would provide funding for purchase and installation of an ADA parking sign which was missing from the ADA parking space at the time of the survey. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | DRUM POINT SST RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 2003 | 128 | 2019-06-19 | Immediate to Two Years | Currently Critical | 1 | 1000
1328ENR1 | WINDOW REPLACEMENT | 1328 | The windows are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 5 units. Removal and disposal of the existing windows is included in this estimate. | SS ENTRANCE STATION | 9959 | CNR | Parks |  | Lahontan SRA | 1986 | 300 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3750
1326EXT1 | EXTERIOR FINISHES | 1326 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is cleaning and sealing the wood and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | LD STORAGE #2 | 9959 | CNR | Parks |  | Lahontan SRA | 1923 | 120 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 600
1330ENR1 | FURNACE REPLACEMENT | 1330 | The building is heated by a propane-fired furnace. It is original to the building, not energy efficient and is reaching the end of its useful life. This project provides for disposal of the existing unit and replacement with a new propane-fired unit including connections to utilities. | LD RESIDENCE #2 | 9959 | CNR | Parks |  | Lahontan SRA | 1981 | 1056 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
1328ENR2 | LIGHTING UPGRADE | 1328 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | SS ENTRANCE STATION | 9959 | CNR | Parks |  | Lahontan SRA | 1986 | 300 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 750
1339EXT1 | EXTERIOR/ INTERIOR FINISHES | 1339 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SS4 SST RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 1998 | 204 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 1020
1328INT1 | INTERIOR FINISHES | 1328 | The interior finishes are in fair condition. It is recommended that the painted gypsum board interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SS ENTRANCE STATION | 9959 | CNR | Parks |  | Lahontan SRA | 1986 | 300 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
1328EXT1 | EXTERIOR FINISHES | 1328 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SS ENTRANCE STATION | 9959 | CNR | Parks |  | Lahontan SRA | 1986 | 300 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
1330INT1 | FLOORING REPLACEMENT | 1330 | The sheet vinyl and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the next 2-3 years. This project or a portion thereof was previously recommended in the FCA report dated 06/02/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/15/2010. | LD RESIDENCE #2 | 9959 | CNR | Parks |  | Lahontan SRA | 1981 | 1056 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5600
1330ENR2 | WINDOW REPLACEMENT | 1330 | The windows are original, dual pane construction in a metal frame. These older windows are drafty and not energy efficient. The windows leak and some were damaged during high winds in 2002. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 10 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 06/02/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/15/2010. | LD RESIDENCE #2 | 9959 | CNR | Parks |  | Lahontan SRA | 1981 | 1056 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
1330SFT2 | EXTERIOR LANDING INSTALLATION | 1330 | Section R311.4.3 of the 2006 IBC Residential Building Code describes the requirements for landings at exterior doors. The landing shall not be more than 7 3/4 inches below the top of the threshold and shall have a minumum dimension of 36 inches measured in the direction of travel. The front entry door does not comply with this code and poses a safety hazard. This project would provide for the installation of a compliant landing for the door. | LD RESIDENCE #2 | 9959 | CNR | Parks |  | Lahontan SRA | 1981 | 1056 | 2019-06-19 | Immediate to Two Years | Currently Critical | 1 | 1000
1330EXT2 | EXTERIOR FINISHES | 1330 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 7-8 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | LD RESIDENCE #2 | 9959 | CNR | Parks |  | Lahontan SRA | 1981 | 1056 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 5280
1330PLM1 | WATER HEATER REPLACEMENT | 1330 | There is a 50 gallon propane-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new propane-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | LD RESIDENCE #2 | 9959 | CNR | Parks |  | Lahontan SRA | 1981 | 1056 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
1324EXT1 | EXTERIOR/ INTERIOR FINISHES | 1324 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | DRUM POINT SST RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 2003 | 128 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 1280
1350INT2 | KITCHEN REMODEL | 1350 | The kitchen is in fair to poor condition. The cabinets and equipment are showing signs of general wear and tear and are approaching the end of their expected life. This project recommends the replacement of the existing kitchen cabinets, counters, fixtures and equipment with mid range, high quality components. This project or a portion thereof was previously recommended in the FCA report dated 06/02/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/15/2010. | SS RANGER RESIDENCE | 9959 | CNR | Parks |  | Lahontan SRA | 1981 | 900 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
1322ENR1 | LIGHTING UPGRADE | 1322 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts or compact flourescent light bulbs are suggested. Occupancy sensors will be installed in restrooms, conference rooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | NORTH SHORE MARINA CLIVUS RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 1984 | 460 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
1351EXT1 | EXTERIOR FINISHES | 1351 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SS MAINTENANCE SHOP | 9959 | CNR | Parks |  | Lahontan SRA | 1980 | 1200 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 3600
1351INT1 | INTERIOR FINISHES | 1351 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings in the office and restroom area be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SS MAINTENANCE SHOP | 9959 | CNR | Parks |  | Lahontan SRA | 1980 | 1200 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
1350ENR1 | WINDOW REPLACEMENT | 1350 | The windows are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 9 units. Removal and disposal of the existing windows is included in this estimate. | SS RANGER RESIDENCE | 9959 | CNR | Parks |  | Lahontan SRA | 1981 | 900 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6750
1350EXT2 | EXTERIOR DOOR REPLACEMENT | 1350 | The exterior wood door at the entry appears to be original to the building. It is damaged from age and general wear and tear. This project would provide for the replacement of the wood door with a new metal door, frame and hardware. Removal and disposal of the existing door and painting of the new door is included in this estimate. | SS RANGER RESIDENCE | 9959 | CNR | Parks |  | Lahontan SRA | 1981 | 900 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 750
1350EXT3 | ROOF REPLACEMENT | 1350 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing and underlayments. | SS RANGER RESIDENCE | 9959 | CNR | Parks |  | Lahontan SRA | 1981 | 900 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
1350SFT2 | EXTERIOR LANDING / HANDRAIL INSTALLATION | 1350 | Section R311.4.3 of the 2006 IBC Residential Building Code describes the requirements for landings at exterior doors. The landing shall not be more than 7 3/4 inches below the top of the threshold and shall have a minimum dimension of 36 inches measured in the direction of travel. The front entry landing does not comply with this code and poses a safety hazard. This project would provide for the installation of a compliant landing for the door. Also included are handrails to be installed at the steps as required by Chapter 10 of the 2006 IBC. | SS RANGER RESIDENCE | 9959 | CNR | Parks |  | Lahontan SRA | 1981 | 900 | 2019-06-19 | Immediate to Two Years | Currently Critical | 1 | 1200
1350INT3 | INTERIOR FINISHES | 1350 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 06/02/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/15/2010. | SS RANGER RESIDENCE | 9959 | CNR | Parks |  | Lahontan SRA | 1981 | 900 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
1350ENR2 | EVAPORATIVE COOLER REPLACEMENT | 1350 | An evaporative cooler is installed on the roof of this building and is severely scaled and has reached the end of it's useful and expected life. This project would provide for a new evaporative cooler to be installed including all required connections to utilities. The estimate includes removal and disposal of the old cooler. This project or a portion thereof was previously recommended in the FCA report dated 06/02/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/15/2010. | SS RANGER RESIDENCE | 9959 | CNR | Parks |  | Lahontan SRA | 1981 | 900 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
1350INT1 | FLOORING REPLACEMENT | 1350 | The sheet vinyl and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 4" base and heavy duty commercial grade carpet in the next 2-3 years. This project or a portion thereof was previously recommended in the FCA report dated 06/02/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/15/2010. | SS RANGER RESIDENCE | 9959 | CNR | Parks |  | Lahontan SRA | 1981 | 900 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6300
1347EXT1 | EXTERIOR FINISHES | 1347 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SS MECHANICAL BUILDING NORTH | 9959 | CNR | Parks |  | Lahontan SRA | 1978 | 480 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 2400
1346EXT1 | EXTERIOR FINISHES | 1346 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SS GARAGE #3 | 9959 | CNR | Parks |  | Lahontan SRA | 1981 | 200 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 1000
1346EXT2 | ROOF REPLACEMENT | 1346 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. | SS GARAGE #3 | 9959 | CNR | Parks |  | Lahontan SRA | 1981 | 200 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
1342ELE1 | SOLAR PANEL REPLACEMENT | 1342 | The power to the building is provided by a photovoltaic system. The solar panels have been broken by vandals and should be scheduled for replacement. This project provides for the purchase and installation of two roof-mounted solar panels. | SS10 SST RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 2003 | 204 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
1340EXT1 | EXTERIOR/ INTERIOR FINISHES | 1340 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SS6 SST RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 1998 | 128 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 1280
1350SFT1 | SMOKE DETECTOR INSTALLATION | 1350 | The 2006 IBC and 2006 IFC, section 907.2.10.1.2 requires smoke detectors in dwelling units be installed in each sleeping room and on the ceiling or wall outside of each separate sleeping area in the immediate vicinity of bedrooms. State Fire Marshal NAC 477.915 (3) requires that smoke detectors be connected to the building wiring with a battery backup. This project would provide funding for the purchase and installation of smoke detectors. This project or a portion thereof was previously recommended in the FCA report dated 06/02/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/15/2010. | SS RANGER RESIDENCE | 9959 | CNR | Parks |  | Lahontan SRA | 1981 | 900 | 2019-06-19 | Immediate to Two Years | Currently Critical | 1 | 1000
1341EXT1 | EXTERIOR/ INTERIOR FINISHES | 1341 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SS8 SST RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 2003 | 128 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 1280
1345EXT2 | ROOF REPLACEMENT | 1345 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. | SS GARAGE #2 | 9959 | CNR | Parks |  | Lahontan SRA | 1981 | 200 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
1342EXT1 | EXTERIOR/ INTERIOR FINISHES | 1342 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SS10 SST RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 2003 | 204 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 2040
1343EXT1 | EXTERIOR FINISHES | 1343 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry, sanding, priming and painting the wood and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | LD ENTRANCE STATION | 9959 | CNR | Parks |  | Lahontan SRA | 1979 | 300 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 1500
1343INT1 | INTERIOR FINISHES | 1343 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | LD ENTRANCE STATION | 9959 | CNR | Parks |  | Lahontan SRA | 1979 | 300 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
1343ENR1 | WINDOW REPLACEMENT | 1343 | The windows are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 5 units. Removal and disposal of the existing windows is included in this estimate. | LD ENTRANCE STATION | 9959 | CNR | Parks |  | Lahontan SRA | 1979 | 300 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3750
1343ENR2 | LIGHTING UPGRADE | 1343 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in the restroom and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | LD ENTRANCE STATION | 9959 | CNR | Parks |  | Lahontan SRA | 1979 | 300 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
1343ENR3 | EVAPORATIVE COOLER REPLACEMENT | 1343 | An evaporative cooler is installed on the side of this building and is severely scaled and has reached the end of it's useful and expected life. This project would provide for a new evaporative cooler to be installed including all required connections to utilities. The estimate includes removal and disposal of the old cooler. | LD ENTRANCE STATION | 9959 | CNR | Parks |  | Lahontan SRA | 1979 | 300 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
1344EXT2 | ROOF REPLACEMENT | 1344 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. | SS GARAGE #1 | 9959 | CNR | Parks |  | Lahontan SRA | 1981 | 200 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
1344EXT1 | EXTERIOR FINISHES | 1344 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SS GARAGE #1 | 9959 | CNR | Parks |  | Lahontan SRA | 1981 | 200 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 1000
1345EXT1 | EXTERIOR FINISHES | 1345 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SS GARAGE #2 | 9959 | CNR | Parks |  | Lahontan SRA | 1981 | 200 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 1000
2578ENR1 | LIGHTING UPGRADE | 2578 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, conference rooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | SS RANGER STATION | 9959 | CNR | Parks |  | Lahontan SRA | 2005 | 1000 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
2578ADA1 | ADA RESTROOM UPGRADES | 2578 | The designated accessible restroom does not entirely meet the Americans with Disabilities Act (ADA) requirements. The flush handle is on the wrong side of the toilet and there is no vertical grab bar. There may be other minor variances from the code as well. When the upgrade is designed a full inspection should be made to identify all necessary upgrades. This project would provide funding for upgrades to bring the restroom into full compliance with the ADA. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | SS RANGER STATION | 9959 | CNR | Parks |  | Lahontan SRA | 2005 | 1000 | 2019-06-19 | Immediate to Two Years | Currently Critical | 1 | 2500
2365EXT1 | EXTERIOR FINISHES | 2365 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry, staining the wood and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SS3 COMFORT STATION | 9959 | CNR | Parks |  | Lahontan SRA | 1974 | 900 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 4500
2578EXT1 | EXTERIOR FINISHES | 2578 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SS RANGER STATION | 9959 | CNR | Parks |  | Lahontan SRA | 2005 | 1000 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 5000
2578INT1 | INTERIOR FINISHES | 2578 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SS RANGER STATION | 9959 | CNR | Parks |  | Lahontan SRA | 2005 | 1000 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
2361EXT1 | EXTERIOR/ INTERIOR FINISHES | 2361 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SS12 SST RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 2007 | 128 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 1280
2362EXT1 | EXTERIOR/ INTERIOR FINISHES | 2362 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CATFISH CUT SST RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 2003 | 128 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 1280
2363EXT1 | EXTERIOR/ INTERIOR FINISHES | 2363 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SS3 NORTH SST RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 1987 | 208 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 2080
2364EXT1 | EXTERIOR/ INTERIOR FINISHES | 2364 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SS3 SOUTH SST RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 1987 | 208 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 2080
2365INT1 | INTERIOR FINISHES | 2365 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SS3 COMFORT STATION | 9959 | CNR | Parks |  | Lahontan SRA | 1974 | 900 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
2366EXT1 | EXTERIOR/ INTERIOR FINISHES | 2366 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SS5 NORTH SST RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 2006 | 128 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 1280
2367EXT1 | EXTERIOR/ INTERIOR FINISHES | 2367 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SS5 SOUTH SST RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 1998 | 208 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 2080
2370INT1 | INTERIOR FINISHES | 2370 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SS7 BEACH COMFORT STATION | 9959 | CNR | Parks |  | Lahontan SRA | 1974 | 900 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
2372EXT1 | EXTERIOR/ INTERIOR FINISHES | 2372 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SS9 SST RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 1997 | 208 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 2080
2371EXT1 | EXTERIOR/ INTERIOR FINISHES | 2371 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SS7 BEACH SST RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 1997 | 208 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 2080
2373ELE1 | SOLAR PANEL REPLACEMENT | 2373 | The power to the building is provided by a photovoltaic system. The solar panels have been broken by vandals and should be scheduled for replacement. This project provides for the purchase and installation of two roof-mounted solar panels. | SS11 SST RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 1997 | 128 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
2365PLM1 | WATER HEATER REPLACEMENT | 2365 | There is a 20 gallon propane-fired water heater in the closet. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 5-6 years. It is recommended that a new propane-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | SS3 COMFORT STATION | 9959 | CNR | Parks |  | Lahontan SRA | 1974 | 900 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 1250
2368PLM1 | WATER HEATER REPLACEMENT | 2368 | There is a 20 gallon propane-fired water heater in the closet. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 5-6 years. It is recommended that a new propane-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | SS7 SOUTH COMFORT STATION | 9959 | CNR | Parks |  | Lahontan SRA | 1974 | 900 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 1250
2373EXT1 | EXTERIOR/ INTERIOR FINISHES | 2373 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SS11 SST RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 1997 | 128 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 1280
2370PLM1 | WATER HEATER REPLACEMENT | 2370 | There is a 20 gallon propane-fired water heater in the closet. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 5-6 years. It is recommended that a new propane-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | SS7 BEACH COMFORT STATION | 9959 | CNR | Parks |  | Lahontan SRA | 1974 | 900 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 1250
2370EXT1 | EXTERIOR FINISHES | 2370 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry, staining the wood and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SS7 BEACH COMFORT STATION | 9959 | CNR | Parks |  | Lahontan SRA | 1974 | 900 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 4500
2369INT1 | INTERIOR FINISHES | 2369 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SS7 CENTER COMFORT STATION | 9959 | CNR | Parks |  | Lahontan SRA | 1974 | 900 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
2369EXT1 | EXTERIOR FINISHES | 2369 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry, staining the wood and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SS7 CENTER COMFORT STATION | 9959 | CNR | Parks |  | Lahontan SRA | 1974 | 900 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 4500
2369PLM1 | WATER HEATER REPLACEMENT | 2369 | There is a 20 gallon propane-fired water heater in the closet. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 5-6 years. It is recommended that a new propane-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | SS7 CENTER COMFORT STATION | 9959 | CNR | Parks |  | Lahontan SRA | 1974 | 900 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 1250
2368INT1 | INTERIOR FINISHES | 2368 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SS7 SOUTH COMFORT STATION | 9959 | CNR | Parks |  | Lahontan SRA | 1974 | 900 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
2368EXT1 | EXTERIOR FINISHES | 2368 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry, staining the wood and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SS7 SOUTH COMFORT STATION | 9959 | CNR | Parks |  | Lahontan SRA | 1974 | 900 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 4500
3056EXT2 | ROOF REPLACEMENT | 3056 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. | LD GARAGE #4 | 9959 | CNR | Parks |  | Lahontan SRA | 1923 | 400 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
3058EXT1 | EXTERIOR FINISHES | 3058 | It is important to maintain the finish, weather resistance and appearance of the water tank. This project would provide for the painting of the water tank and caulking of the joints to maintain it in a good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | WATER TANK #1 | 9959 | CNR | Parks |  | Lahontan SRA | 1974 | 1256 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
3055EXT1 | EXTERIOR FINISHES | 3055 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | METAL STORAGE BUILDING | 9959 | CNR | Parks |  | Lahontan SRA | 2009 | 240 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 720
3057EXT2 | ROOF REPLACEMENT | 3057 | The corrugated metal roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a standing seam metal roofing system. This estimate includes removal and disposal of the old roofing. | LD GARAGE #5 | 9959 | CNR | Parks |  | Lahontan SRA | 1923 | 400 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
3054EXT1 | EXTERIOR FINISHES | 3054 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | WATER TREATMENT PLANT | 9959 | CNR | Parks |  | Lahontan SRA | 2000 | 400 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 1200
3057EXT1 | EXTERIOR FINISHES | 3057 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | LD GARAGE #5 | 9959 | CNR | Parks |  | Lahontan SRA | 1923 | 400 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1200
3056EXT1 | EXTERIOR FINISHES | 3056 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | LD GARAGE #4 | 9959 | CNR | Parks |  | Lahontan SRA | 1923 | 400 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1200
3059EXT1 | EXTERIOR FINISHES | 3059 | It is important to maintain the finish, weather resistance and appearance of the water tank. This project would provide for the painting of the water tank and caulking of the joints to maintain it in a good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | WATER TANK #2 | 9959 | CNR | Parks |  | Lahontan SRA | 1974 | 1256 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 7500
3060EXT1 | EXTERIOR FINISHES | 3060 | It is important to maintain the finish, weather resistance and appearance of the water tank. This project would provide for the painting of the water tank and caulking of the joints to maintain it in a good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | WATER TANK #3 | 9959 | CNR | Parks |  | Lahontan SRA | 1978 | 1256 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 7500
9959ENR1 | EXTERIOR SOLAR SITE LIGHTING INSTALLATION | 9959 | The parking areas at the LD1 Comfort Station, North Boat Launch and SS Boat Launch have pole lights that are difficult to maintain and not energy efficient. This project would provide for the replacement of the existing lights with solar powered LED exterior light fixtures. The existing light heads can be replaced with the new LED lights, but additional lighting should be provided as well including 20 foot tall poles and 30" diameter raised concrete bases. This installation will eliminate the need for trenching and electrical connections. The estimate is based on replacement and / or installation of 20 light fixtures. | LAHONTAN STATE RECREATION AREA SITE | 9959 | CNR | Parks |  | Lahontan SRA | 0 |  | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 150000
3053ENR3 | FURNACE REPLACEMENT | 3053 | The building is heated by an oil fired furnace. It is original to the building, not energy efficient and is reaching the end of its useful life. This project provides for disposal of the existing unit and replacement with a new propane-fired unit including connections to utilities. | LD RESIDENCE #4 | 9959 | CNR | Parks |  | Lahontan SRA | 1930 | 1400 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
9959SIT1 | SLURRY SEAL ASPHALT PAVING | 9959 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site wide including access roads and parking areas at the LD1 Day Use Comfort Station, Overlook Comfort Station, Silver Springs Boat Launch and the Silver Springs Ranger Residence. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 200,000 square feet of asphalt area was used to generate this estimate. This project or a portion thereof was previously recommended in the FCA report dated 06/02/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/15/2010. | LAHONTAN STATE RECREATION AREA SITE | 9959 | CNR | Parks |  | Lahontan SRA | 0 |  | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 100000
3047INT1 | INTERIOR FINISHES | 3047 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SS DAY USE COMFORT STATION NORTH | 9959 | CNR | Parks |  | Lahontan SRA | 1974 | 900 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
3047INT2 | RESTROOM FIXTURE REPLACEMENT | 3047 | The fixtures in two of the restroom stalls have been pieced out for repairs to other restrooms. These two stalls are closed to the public and should be upgraded in order to bring them back into a functioning condition. This project would provide for the purchase and installation of the fixtures including the water closets, urinals, lavatories, faucets, and all dispensers. | SS DAY USE COMFORT STATION NORTH | 9959 | CNR | Parks |  | Lahontan SRA | 1974 | 900 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
3047EXT1 | EXTERIOR FINISHES | 3047 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry, staining the wood and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SS DAY USE COMFORT STATION NORTH | 9959 | CNR | Parks |  | Lahontan SRA | 1974 | 900 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 4500
3047PLM1 | WATER HEATER REPLACEMENT | 3047 | There is a 15 gallon propane-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new propane-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | SS DAY USE COMFORT STATION NORTH | 9959 | CNR | Parks |  | Lahontan SRA | 1974 | 900 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
9959SIT4 | ASPHALT PAVING INSTALLATION | 9959 | The maintenance yard and parking lot next to the Regional Headquarters building is not paved. This project would provide 100,000 square feet of asphalt cement paving for this area. The estimate includes grading, 6" base, compaction and installation of 4" thick asphalt cement paving. | LAHONTAN STATE RECREATION AREA SITE | 9959 | CNR | Parks |  | Lahontan SRA | 0 |  | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 300000
3050EXT1 | EXTERIOR FINISHES | 3050 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the Ramada and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | RIVER CAMP RAMADA | 9959 | CNR | Parks |  | Lahontan SRA | 2008 | 144 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 288
9959SIT2 | CARPORT STRUCTURE INSTALLATION | 9959 | There are approximately 10 state vehicles parked in the parking lot next to the Regional Headquarters building at any given time. The vehicles include boats and work trucks that deteriorate rapidly due to exposure to the elements. This project would provide materials and labor to construct a steel carport capable of protecting 10 vehicles to be built in the parking lot. | LAHONTAN STATE RECREATION AREA SITE | 9959 | CNR | Parks |  | Lahontan SRA | 0 |  | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 75000
3053EXT1 | EXTERIOR FINISHES | 3053 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | LD RESIDENCE #4 | 9959 | CNR | Parks |  | Lahontan SRA | 1930 | 1400 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7000
3053INT2 | KITCHEN FLOORING REPLACEMENT | 3053 | The sheet vinyl flooring in the kitchen was installed poorly and should be scheduled for replacement. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 4" base. 150 square feet was used to generate this estimate. | LD RESIDENCE #4 | 9959 | CNR | Parks |  | Lahontan SRA | 1930 | 1400 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1050
3053ENR1 | WINDOW REPLACEMENT | 3053 | The windows are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 6 units. Removal and disposal of the existing windows is included in this estimate. | LD RESIDENCE #4 | 9959 | CNR | Parks |  | Lahontan SRA | 1930 | 1400 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
3051EXT1 | EXTERIOR FINISHES | 3051 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for staining the wood on the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NORTH SHORE MARINA KIOSK | 9959 | CNR | Parks |  | Lahontan SRA | 1974 | 192 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1920
3049EXT1 | EXTERIOR/ INTERIOR FINISHES | 3049 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | EQUESTRIAN CAMPGROUND SST RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 2010 | 128 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 1280
3048PLM1 | WATER HEATER REPLACEMENT | 3048 | There is a 15 gallon propane-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new propane-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | SS DAY USE COMFORT STATION SOUTH | 9959 | CNR | Parks |  | Lahontan SRA | 1974 | 900 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
3048INT1 | INTERIOR FINISHES | 3048 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SS DAY USE COMFORT STATION SOUTH | 9959 | CNR | Parks |  | Lahontan SRA | 1974 | 900 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
3053SFT4 | SMOKE DETECTOR INSTALLATION | 3053 | The 2006 IBC and 2006 IFC, section 907.2.10.1.2 requires smoke detectors in dwelling units be installed in each sleeping room and on the ceiling or wall outside of each separate sleeping area in the immediate vicinity of bedrooms. State Fire Marshal NAC 477.915 (3) requires that smoke detectors be connected to the building wiring with a battery backup. This project would provide funding for the purchase and installation of smoke detectors. | LD RESIDENCE #4 | 9959 | CNR | Parks |  | Lahontan SRA | 1930 | 1400 | 2019-06-19 | Immediate to Two Years | Currently Critical | 1 | 1000
3053INT1 | INTERIOR FINISHES | 3053 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | LD RESIDENCE #4 | 9959 | CNR | Parks |  | Lahontan SRA | 1930 | 1400 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7000
3053ENR2 | EVAPORATIVE COOLER REPLACEMENT | 3053 | An evaporative cooler is installed on the side of this building and is severely scaled and has reached the end of it's useful and expected life. This project would provide for a new evaporative cooler to be installed including all required connections to utilities. The estimate includes removal and disposal of the old cooler. | LD RESIDENCE #4 | 9959 | CNR | Parks |  | Lahontan SRA | 1930 | 1400 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
3052EXT1 | EXTERIOR FINISHES | 3052 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SS MECHANICAL BUILDING SOUTH | 9959 | CNR | Parks |  | Lahontan SRA | 1978 | 480 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 2400
3048EXT1 | EXTERIOR FINISHES | 3048 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/23/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | SS DAY USE COMFORT STATION SOUTH | 9959 | CNR | Parks |  | Lahontan SRA | 1974 | 900 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 720
3053EXT3 | ROOF REPLACEMENT | 3053 | The asphalt composition shingle roof on this building was in fair to poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 4-5 years with a new 50 year asphalt composition roofing shingles and new underlayments. This estimate includes removal and disposal of the old roofing and underlayments | LD RESIDENCE #4 | 9959 | CNR | Parks |  | Lahontan SRA | 1930 | 1400 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 14000
3053SFT3 | STOVE OIL TANK RELOCATION | 3053 | There is an above ground stove oil storage tank located on the side of the building. According to Table 3504.2.1 of the 2006 International Fire Code, flammable gases must be stored at least 5 feet away from a building of non-rated construction. This project would provide for relocating the stove oil storage tank to comply with the code. | LD RESIDENCE #4 | 9959 | CNR | Parks |  | Lahontan SRA | 1930 | 1400 | 2019-06-19 | Immediate to Two Years | Currently Critical | 1 | 1000
3053SFT2 | EXTERIOR STAIR / HANDRAIL REPLACEMENT | 3053 | The exterior concrete stairs at the entry door are due for replacement. They are cracked and crumbling and have reached the end of their useful life. The new landing and stairs should comply with the current adopted building code. Section R311.4.3 of the 2006 IBC describes the requirements for landings at exterior doors. The landing shall not be more than 7 3/4 inches below the top of the threshold and shall have a minimum dimension of 36 inches measured in the direction of travel. This project would provide for removal of the existing stairs and installation of a compliant landing, handrails and stairs for the entrance. | LD RESIDENCE #4 | 9959 | CNR | Parks |  | Lahontan SRA | 1930 | 1400 | 2019-06-19 | Immediate to Two Years | Currently Critical | 1 | 3500
3053PLM1 | PLUMBING / WASTE LINE REPLACEMENT | 3053 | The plumbing and waste system is older and in poor condition. Most of the system appears to be original to the building and should be scheduled for replacement. This project recommends replacing all of the water and sewer lines in the building. This estimate includes removal and disposal of the existing system as required. | LD RESIDENCE #4 | 9959 | CNR | Parks |  | Lahontan SRA | 1930 | 1400 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 21000
0543EXT1 | EXTERIOR/ INTERIOR FINISHES | 0543 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | LD6 SST RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 1997 | 128 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 1280
0493INT2 | FLOORING REPLACEMENT | 0493 | The carpet and sheet vinyl in the front office section of the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the next 4-5 years. | REGIONAL HEADQUARTERS/MAINTENANCE SHOP | 9959 | CNR | Parks |  | Lahontan SRA | 1980 | 4550 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 7000
0494EXT1 | EXTERIOR FINISHES | 0494 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting the wood, cleaning and sealing the masonry and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | OLD WELL HOUSE (VACANT) | 9959 | CNR | Parks |  | Lahontan SRA | 1960 | 64 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 200
0540EXT1 | EXTERIOR/ INTERIOR FINISHES | 0540 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | LD3 SST RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 1997 | 204 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 2040
0493EXT1 | EXTERIOR FINISHES | 0493 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | REGIONAL HEADQUARTERS/MAINTENANCE SHOP | 9959 | CNR | Parks |  | Lahontan SRA | 1980 | 4550 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 13650
0494EXT2 | ROOF REPLACEMENT | 0494 | The wood shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. | OLD WELL HOUSE (VACANT) | 9959 | CNR | Parks |  | Lahontan SRA | 1960 | 64 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 300
0493SFT1 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0493 | The building is a partial B occupancy per the 2006 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. | REGIONAL HEADQUARTERS/MAINTENANCE SHOP | 9959 | CNR | Parks |  | Lahontan SRA | 1980 | 4550 | 2019-06-19 | Immediate to Two Years | Currently Critical | 1 | 31850
0493ENR2 | LIGHTING UPGRADE | 0493 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, conference rooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | REGIONAL HEADQUARTERS/MAINTENANCE SHOP | 9959 | CNR | Parks |  | Lahontan SRA | 1980 | 4550 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6825
0493ADA2 | ADA ACCESSIBLE COUNTER | 0493 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The front office has a service counter for the public to approach which does not meet current codes. Section 7.2 of the Americans with Disabilities Act Accessible Guidelines (ADAAG) states that the counter must have a portion which is at least 36" in length with a maximum height of 36" above the finish floor. This project will provide an accessible counter space in accordance with this requirement. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | REGIONAL HEADQUARTERS/MAINTENANCE SHOP | 9959 | CNR | Parks |  | Lahontan SRA | 1980 | 4550 | 2019-06-19 | Immediate to Two Years | Currently Critical | 1 | 1500
0493INT1 | INTERIOR FINISHES | 0493 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | REGIONAL HEADQUARTERS/MAINTENANCE SHOP | 9959 | CNR | Parks |  | Lahontan SRA | 1980 | 4550 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 22750
0544EXT1 | EXTERIOR FINISHES | 0544 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry, staining the wood and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | LD7 CLIVUS RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 1984 | 240 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 1200
0544INT1 | INTERIOR FINISHES | 0544 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | LD7 CLIVUS RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 1984 | 240 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1200
0493ADA3 | ADA SIGNAGE | 0493 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | REGIONAL HEADQUARTERS/MAINTENANCE SHOP | 9959 | CNR | Parks |  | Lahontan SRA | 1980 | 4550 | 2019-06-19 | Immediate to Two Years | Currently Critical | 1 | 1000
0495EXT2 | ROOF REPLACEMENT | 0495 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. | OLD DISTRICT HEADQUARTERS | 9959 | CNR | Parks |  | Lahontan SRA | 1930 | 860 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8600
0498EXT1 | EXTERIOR FINISHES | 0498 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding and sealing the wood and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | LD GARAGE #1 | 9959 | CNR | Parks |  | Lahontan SRA | 1923 | 400 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
0497EXT1 | EXTERIOR/ INTERIOR FINISHES | 0497 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | LD2 SST RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 1997 | 128 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 1280
0496ADA1 | RESTROOM REMODEL | 0496 | The building has six separate restroom stalls, but no shower stalls. The maintenance staff indicated the need to remodel two of the stalls to provide showers. This project would provide for a complete remodel of two of the stalls to provide shower facilities, one of which shall comply with ADA accessible guidelines. The removal and disposal of the existing fixtures and finishes is included in this estimate. | LD1 DAY USE COMFORT STATION | 9959 | CNR | Parks |  | Lahontan SRA | 1974 | 900 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16000
0496PLM1 | WATER HEATER REPLACEMENT | 0496 | There is a 20 gallon propane-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 5-6 years. It is recommended that a new propane-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | LD1 DAY USE COMFORT STATION | 9959 | CNR | Parks |  | Lahontan SRA | 1974 | 900 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 1000
0496ENR1 | LIGHTING UPGRADE | 0496 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in each room for additional savings. Any electrical wiring upgrades are not included in this estimate. | LD1 DAY USE COMFORT STATION | 9959 | CNR | Parks |  | Lahontan SRA | 1974 | 900 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
0496SFT1 | GFCI DUPLEX OUTLET REPLACEMENT | 0496 | There are six outlets in the restrooms throughout the building which are not GFCI. These outlets should be changed to GFCI type outlets per the NEC. This project would provide for the purchase and installation of six GFCI duplex outlets. | LD1 DAY USE COMFORT STATION | 9959 | CNR | Parks |  | Lahontan SRA | 1974 | 900 | 2019-06-19 | Immediate to Two Years | Currently Critical | 1 | 300
0542EXT1 | EXTERIOR/ INTERIOR FINISHES | 0542 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | LD5 SST RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 1997 | 204 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 2040
0499ENR1 | EVAPORATIVE COOLER REPLACEMENT | 0499 | An evaporative cooler is installed on the roof of this building and is severely scaled and has reached the end of it's useful and expected life. This project would provide for a new evaporative cooler to be installed including all required connections to the existing ductwork and utilities in the gable end of the residence.. The estimate includes removal and disposal of the old roof mounted evaporative cooler and any required patching of the roof. | LD RESIDENCE #1 | 9959 | CNR | Parks |  | Lahontan SRA | 1981 | 1056 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3500
0589EXT1 | EXTERIOR/ INTERIOR FINISHES | 0589 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | LD9 SST RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 1997 | 128 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 1280
0499EXT4 | EXTERIOR FINISHES | 0499 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | LD RESIDENCE #1 | 9959 | CNR | Parks |  | Lahontan SRA | 1981 | 1056 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 5280
0499INT2 | INTERIOR FINISHES | 0499 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 5-6 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | LD RESIDENCE #1 | 9959 | CNR | Parks |  | Lahontan SRA | 1981 | 1056 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 5280
0499ENR2 | LIGHTING UPGRADE | 0499 | The existing lighting fixtures are the older incandescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. CFL (compact flourescent lamps) are suggested. Occupancy sensors will be installed in restrooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | LD RESIDENCE #1 | 9959 | CNR | Parks |  | Lahontan SRA | 1981 | 1056 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
0499INT1 | FLOORING REPLACEMENT | 0499 | The sheet vinyl and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the next 2-3 years. This project or a portion thereof was previously recommended in the FCA report dated 06/02/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/15/2010. | LD RESIDENCE #1 | 9959 | CNR | Parks |  | Lahontan SRA | 1981 | 1056 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4900
0496INT1 | INTERIOR FINISHES | 0496 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | LD1 DAY USE COMFORT STATION | 9959 | CNR | Parks |  | Lahontan SRA | 1974 | 900 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
0496EXT1 | EXTERIOR FINISHES | 0496 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry, staining the wood and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | LD1 DAY USE COMFORT STATION | 9959 | CNR | Parks |  | Lahontan SRA | 1974 | 900 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
0495EXT1 | EXTERIOR FINISHES | 0495 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | OLD DISTRICT HEADQUARTERS | 9959 | CNR | Parks |  | Lahontan SRA | 1930 | 860 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4300
0494EXT3 | EXTERIOR DOOR REPLACEMENT | 0494 | The existing exterior wood door appears to be original to the building. It is damaged from age and general wear and tear. This project would provide for the replacement of the wood door with a new metal door, frame and hardware. Removal and disposal of the existing door and painting of the new door is included in this estimate. | OLD WELL HOUSE (VACANT) | 9959 | CNR | Parks |  | Lahontan SRA | 1960 | 64 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
0493ENR1 | WINDOW REPLACEMENT | 0493 | The windows in the front office are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 5 units. Removal and disposal of the existing windows is included in this estimate. | REGIONAL HEADQUARTERS/MAINTENANCE SHOP | 9959 | CNR | Parks |  | Lahontan SRA | 1980 | 4550 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3750
0493SFT2 | FIRE ALARM SYSTEM INSTALLATION | 0493 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2006 Section 7 and the 2006 International Fire Code. | REGIONAL HEADQUARTERS/MAINTENANCE SHOP | 9959 | CNR | Parks |  | Lahontan SRA | 1980 | 4550 | 2019-06-19 | Immediate to Two Years | Currently Critical | 1 | 13650
0599EXT1 | EXTERIOR/ INTERIOR FINISHES | 0599 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | LD11 SST RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 2005 | 128 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 1280
0493ENR3 | HEATER INSTALLATION | 0493 | Two of the garage bays have broken or missing heating equipment and they are uncomfortably cold in the winter. It is recommended to install new heating equipment in these occupied areas to ensure a comfortable work environment. This project would provide for the purchase and installation of two propane fired heaters including all required connections to existing utilities. | REGIONAL HEADQUARTERS/MAINTENANCE SHOP | 9959 | CNR | Parks |  | Lahontan SRA | 1980 | 4550 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7000
0592EXT2 | EXTERIOR DOOR REPLACEMENT | 0592 | The exterior metal doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of three door assemblies with new metal doors, frames and hardware. Removal and disposal of the existing doors is included in this estimate. | LD10 CLIVUS RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 1984 | 240 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
0592INT1 | INTERIOR FINISHES | 0592 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | LD10 CLIVUS RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 1984 | 240 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1200
0493SFT3 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0493 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2006 Chapter 10 was referenced for this project. | REGIONAL HEADQUARTERS/MAINTENANCE SHOP | 9959 | CNR | Parks |  | Lahontan SRA | 1980 | 4550 | 2019-06-19 | Immediate to Two Years | Currently Critical | 1 | 1500
0592EXT1 | EXTERIOR FINISHES | 0592 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry, staining the wood and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | LD10 CLIVUS RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 1984 | 240 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 1200
0499SFT2 | EXTERIOR LANDING / HANDRAIL INSTALLATION | 0499 | Section R311.4.3 of the 2006 IBC Residential building Code describes the requirements for landings at exterior doors. The landing shall not be more than 7 3/4 inches below the top of the threshold and shall have a minumum dimension of 36 inches measured in the direction of travel. The front entry landing does not comply with this code and poses a safety hazard. This project would provide for the installation of a compliant landing for the door and handrails at the steps as required by Chapter 10 of the 2006 IBC. | LD RESIDENCE #1 | 9959 | CNR | Parks |  | Lahontan SRA | 1981 | 1056 | 2019-06-19 | Immediate to Two Years | Currently Critical | 1 | 2500
9926SIT5 | CRACK FILL & SEAL PARKING AND ROAD | 9926 | The existing AC paving is in fair condition; however, there are significant areas of alligatoring and at least three locations of complete failure. This project would provide for patching, crack fill, slurry seal, and striping of the paved areas at Cave Rock including the entrance road. This project should be scheduled on a cyclical basis based on environmental conditions and should be implemented in the next two years. This project or a portion thereof was previously recommended in the FCA report dated 05/27/2012. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2020. | LAKE TAHOE NEVADA-CAVE ROCK STATE PARK | 9926 | CNR | Parks |  | Lake Tahoe/Cave Rock | 1977 |  | 2020-05-27 | Immediate to Two Years | Currently Critical | 1 | 22750
9926SIT2 | EROSION / SLOPE MITIGATION | 9926 | The site continues to have some areas with steep slopes that have stacked railroad ties for slope stabilization which are damaged, and some are failing. Some of the failed retaining walls have been replaced with stacked boulder retaining walls. This project would continue the replacement of the failing wood retaining walls. In addition, it is recommended that an additional wall be added on the east side of the Comfort Station to enable proper slope drainage away from the building. This project should be implemented concurrently with the DRAINAGE UPGRADES project under Building #0597. | LAKE TAHOE NEVADA-CAVE ROCK STATE PARK | 9926 | CNR | Parks |  | Lake Tahoe/Cave Rock | 1977 |  | 2020-05-27 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0597EXT3 | DRAINAGE UPGRADES | 0597 | The grade does not slope away effectively from the east side of the Comfort Station. It is recommended per IBC 1804.4 grading the ground immediately adjacent to the foundation shall be sloped away from the building at a slope of not less than one vertical unit in 20 units horizontal (5-percent slope). It is recommended that the grading be completed within 2 - 3 years. This project should be implemented concurrently with the EROSION / SLOPE MITIGATION project. | CAVE ROCK COMFORT STATION | 9926 | CNR | Parks |  | Lake Tahoe/Cave Rock | 1977 | 448 | 2020-05-27 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
0597ADA1 | ADA MODIFICATIONS | 0597 | The existing Men's and Women's restrooms are not fully ADA compliant. This project would provide for modifications to the entrance into the restrooms including reworking the concrete ramp and privacy walls, installing the wall mounted dispensers at the proper location, and other improvements as required. ADA signage is also included in this estimate. The 2018 IBC, ICC/ANSI A117.1, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 05/27/2012. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2020. | CAVE ROCK COMFORT STATION | 9926 | CNR | Parks |  | Lake Tahoe/Cave Rock | 1977 | 448 | 2020-05-27 | Immediate to Two Years | Currently Critical | 1 | 18000
0597INT1 | INTERIOR FINISHES | 0597 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | CAVE ROCK COMFORT STATION | 9926 | CNR | Parks |  | Lake Tahoe/Cave Rock | 1977 | 448 | 2020-05-27 | Four to Ten Years | Long-Term Needs | 3 | 2240
0597EXT2 | EXTERIOR FINISHES | 0597 | The exterior finishes are in good condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the doors, wood siding and trim, and caulking of the door frames, wood siding and trim as needed, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CAVE ROCK COMFORT STATION | 9926 | CNR | Parks |  | Lake Tahoe/Cave Rock | 1977 | 448 | 2020-05-27 | Four to Ten Years | Long-Term Needs | 3 | 2240
0588INT1 | INTERIOR FINISHES | 0588 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. | CAVE ROCK FEE STATION | 9926 | CNR | Parks |  | Lake Tahoe/Cave Rock | 2016 | 128 | 2020-05-27 | Four to Ten Years | Long-Term Needs | 3 | 510
0588EXT1 | EXTERIOR FINISHES | 0588 | The exterior is in good condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the doors, wood siding and trim, and caulking of the door frames, wood siding and trim as needed, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CAVE ROCK FEE STATION | 9926 | CNR | Parks |  | Lake Tahoe/Cave Rock | 2016 | 128 | 2020-05-27 | Four to Ten Years | Long-Term Needs | 3 | 510
0588EXT2 | OVERHEAD COILING WINDOW SECURITY SASH | 0588 | There are three overhead coiling window security sashes on the building one of which is damaged and does not function properly. It is original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of one manually operated overhead coiling sash and replacement with a new manually operated overhead coiling sash. Removal and disposal of the existing door is included in this estimate. | CAVE ROCK FEE STATION | 9926 | CNR | Parks |  | Lake Tahoe/Cave Rock | 2016 | 128 | 2020-05-27 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
1299EXT1 | EXTERIOR FINISHES | 1299 | The exterior finishes are in poor condition. It is important to maintain the finish, weather resistance, and appearance of the structure. It is recommended that the structure be painted in the next 3 - 4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | GROUP RAMADA | 9883 | CNR | Parks |  | Rye Patch SRA | 1976 | 968 | 2020-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2900
1299ADA1 | ADA ACCESSIBLE PATH OF TRAVEL | 1299 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. A concrete parking area and passenger loading area for the Group Ramada are necessary to comply with ADA requirements. This project would provide for a concrete van accessible ADA parking and loading space, and walkway to the existing sidewalk. This will require regrading, installing P.C. concrete, striping, signage, and any other necessary upgrades. NRS 338.180, IBC - 2018, ICC/ANSI A117.1 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 05/31/2012. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2020. | GROUP RAMADA | 9883 | CNR | Parks |  | Rye Patch SRA | 1976 | 968 | 2020-06-04 | Immediate to Two Years | Currently Critical | 1 | 15000
1298EXT4 | EXTERIOR FINISHES | 1298 | The exterior finishes are in good condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting, and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | PARK OFFICE & GARAGE | 9883 | CNR | Parks |  | Rye Patch SRA | 1978 | 1080 | 2020-06-04 | Four to Ten Years | Long-Term Needs | 3 | 5400
1296EXT1 | EXTERIOR FINISHES | 1296 | The exterior finishes are in good condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting, and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | RAMADA #8 | 9883 | CNR | Parks |  | Rye Patch SRA | 1976 | 264 | 2020-06-04 | Four to Ten Years | Long-Term Needs | 3 | 1300
1298SFT3 | FIRE ALARM SYSTEM INSTALLATION | 1298 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1 Section 7 and the 2018 International Fire Code. This project or a portion thereof was previously recommended in the FCA report dated 05/31/2012. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2020. | PARK OFFICE & GARAGE | 9883 | CNR | Parks |  | Rye Patch SRA | 1978 | 1080 | 2020-06-04 | Immediate to Two Years | Currently Critical | 1 | 5400
1298ADA1 | ADA RESTROOM UPGRADE | 1298 | The building does not have an accessible restroom. The existing restroom does not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. NRS 338.180, IBC - 2018, ICC/ANSI A117.1 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 05/31/2012. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2020. | PARK OFFICE & GARAGE | 9883 | CNR | Parks |  | Rye Patch SRA | 1978 | 1080 | 2020-06-04 | Immediate to Two Years | Currently Critical | 1 | 18000
1298HVA2 | HEATER REPLACEMENT | 1298 | The building is heated by one wall mounted propane-fired heating unit. It is original to the building and is reaching the end of its useful life. This project provides for disposal of the existing unit and replacement with a new propane-fired unit including connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 05/31/2012. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2020. | PARK OFFICE & GARAGE | 9883 | CNR | Parks |  | Rye Patch SRA | 1978 | 1080 | 2020-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
1298ADA3 | ADA PARKING SPACE | 1298 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. A concrete parking area and passenger loading area for the Park Office & Garage are necessary to comply with ADA requirements. This project would provide for a concrete van accessible ADA parking and loading space and walkway to the existing sidewalk. This will require regrading, installing P.C. concrete, striping, signage and any other necessary upgrades. NRS 338.180, IBC - 2018, ICC/ANSI A117.1 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 05/31/2012. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2020. | PARK OFFICE & GARAGE | 9883 | CNR | Parks |  | Rye Patch SRA | 1978 | 1080 | 2020-06-04 | Immediate to Two Years | Currently Critical | 1 | 15000
1298INT2 | INTERIOR FINISHES | 1298 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | PARK OFFICE & GARAGE | 9883 | CNR | Parks |  | Rye Patch SRA | 1978 | 1080 | 2020-06-04 | Four to Ten Years | Long-Term Needs | 3 | 5400
1298ENR2 | WATER HEATER REPLACEMENT | 1298 | There is a 15 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new on-demand electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 05/31/2012. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2020. | PARK OFFICE & GARAGE | 9883 | CNR | Parks |  | Rye Patch SRA | 1978 | 1080 | 2020-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
1298SFT1 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 1298 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2018 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 05/31/2012. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2020. | PARK OFFICE & GARAGE | 9883 | CNR | Parks |  | Rye Patch SRA | 1978 | 1080 | 2020-06-04 | Immediate to Two Years | Currently Critical | 1 | 1500
1298EXT5 | OVERHEAD DOOR REPLACEMENT | 1298 | There are two overhead rollup doors on the south side of the building which are damaged and do not function properly. They are original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead doors and replacement with new manually operated overhead doors. Removal and disposal of the existing doors is included in this estimate. | PARK OFFICE & GARAGE | 9883 | CNR | Parks |  | Rye Patch SRA | 1978 | 1080 | 2020-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 17400
1297INT1 | INTERIOR FINISHES | 1297 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. | ENTRANCE STATION | 9883 | CNR | Parks |  | Rye Patch SRA | 1976 | 48 | 2020-06-04 | Four to Ten Years | Long-Term Needs | 3 | 240
1297EXT2 | ROOF REPLACEMENT | 1297 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2 - 3 years with a new 50 year asphalt composition shingle roof and new underlayments. This estimate includes removal and disposal of the old roof. This project or a portion thereof was previously recommended in the FCA report dated 05/31/2012. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2020. | ENTRANCE STATION | 9883 | CNR | Parks |  | Rye Patch SRA | 1976 | 48 | 2020-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 900
1297ELE1 | ELECTRICAL UPGRADE | 1297 | The building has a pvc feeder conduit mounted to the exterior of the building and is used to supply its electrical power. The conduit is damaged and pulling away from the wall. This project would replace the exterior feeder conduit. In addition, since this is a portable structure, it appears to require a flexible conduit connector between the ground and structure. | ENTRANCE STATION | 9883 | CNR | Parks |  | Rye Patch SRA | 1976 | 48 | 2020-06-04 | Immediate to Two Years | Currently Critical | 1 | 1000
1298SIT1 | CONCRETE APRON UPGRADE | 1298 | The exterior concrete apron in front of the overhead doors has extensive cracking, is too small, and is due for an upgrade. This project would provide for the installation of a new 4" thick concrete slab-on-grade apron at the vehicle garage doors. Removal and disposal of the existing concrete is included in this estimate. This project should be implemented concurrently with the ADA PARKING SPACE project. This project or a portion thereof was previously recommended in the FCA report dated 05/31/2012. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2020. | PARK OFFICE & GARAGE | 9883 | CNR | Parks |  | Rye Patch SRA | 1978 | 1080 | 2020-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
1300EXT1 | EXTERIOR FINISHES | 1300 | The exterior finishes are in fair condition. It is important to maintain the finish, weather resistance, and appearance of the structure. It is recommended that the structure be painted in the next 5 - 6 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | RAMADA #01 | 9883 | CNR | Parks |  | Rye Patch SRA | 1976 | 144 | 2020-06-04 | Four to Ten Years | Long-Term Needs | 3 | 700
1297EXT1 | EXTERIOR FINISHES | 1297 | The exterior finishes are in poor condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting, and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2 - 3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | ENTRANCE STATION | 9883 | CNR | Parks |  | Rye Patch SRA | 1976 | 48 | 2020-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 960
1302EXT1 | EXTERIOR FINISHES | 1302 | The exterior finishes are in fair condition. It is important to maintain the finish, weather resistance, and appearance of the structure. It is recommended that the structure be painted in the next 5 - 6 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | RAMADA #03 | 9883 | CNR | Parks |  | Rye Patch SRA | 1976 | 144 | 2020-06-04 | Four to Ten Years | Long-Term Needs | 3 | 700
1303EXT1 | EXTERIOR FINISHES | 1303 | The exterior finishes are in fair condition. It is important to maintain the finish, weather resistance, and appearance of the structure. It is recommended that the structure be painted in the next 5 - 6 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | RAMADA #04 | 9883 | CNR | Parks |  | Rye Patch SRA | 1976 | 144 | 2020-06-04 | Four to Ten Years | Long-Term Needs | 3 | 700
1307EXT1 | EXTERIOR FINISHES | 1307 | The exterior finishes are in fair condition. It is important to maintain the finish, weather resistance, and appearance of the structure. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units, and painting the steel framing. It is recommended that the building be sealed and painted in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | FISH CLEANING STATION | 9883 | CNR | Parks |  | Rye Patch SRA | 1980 | 60 | 2020-06-04 | Four to Ten Years | Long-Term Needs | 3 | 300
1309SFT1 | CARBON MONOXIDE DETECTOR INSTALLATION | 1309 | This building is lacking a carbon monoxide detection system. 2018 IRC R315, IFC 2018 Section 1103.9 (Carbon Monoxide Detection for Existing Buildings) define requirements in Dwelling Units and Sleeping Units (Group I & R Occupancies) for buildings containing fuel-burning appliances. The carbon monoxide alarms shall be listed as complying with UL 2034 and be installed and maintained in accordance with NFPA 720 and the manufacturer’s instructions. This project would provide funding for the purchase and installation of carbon monoxide alarms in accordance with this code. | RESIDENCE #1 | 9883 | CNR | Parks |  | Rye Patch SRA | 1995 | 1440 | 2020-06-04 | Immediate to Two Years | Currently Critical | 1 | 600
1309SFT2 | FIRE SUPPRESSION SYSTEM INSTALLATION | 1309 | This building is an R occupancy. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state regardless of occupancy having a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an "R" occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. | RESIDENCE #1 | 9883 | CNR | Parks |  | Rye Patch SRA | 1995 | 1440 | 2020-06-04 | Four to Ten Years | Long-Term Needs | 3 | 25900
1309EXT1 | EXTERIOR FINISHES | 1309 | The exterior finishes are in poor condition, especially the finishes on the front and rear decks. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting, and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2 - 3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | RESIDENCE #1 | 9883 | CNR | Parks |  | Rye Patch SRA | 1995 | 1440 | 2020-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14400
1309INT2 | INTERIOR FINISHES | 1309 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | RESIDENCE #1 | 9883 | CNR | Parks |  | Rye Patch SRA | 1995 | 1440 | 2020-06-04 | Four to Ten Years | Long-Term Needs | 3 | 14400
1309PLM1 | WATER HEATER REPLACEMENT | 1309 | There is a 40 gallon propane-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 7-8 years. It is recommended that a new propane-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 05/31/2012. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2020. | RESIDENCE #1 | 9883 | CNR | Parks |  | Rye Patch SRA | 1995 | 1440 | 2020-06-04 | Four to Ten Years | Long-Term Needs | 3 | 2500
1298EXT2 | WINDOW REPLACEMENT | 1298 | The 6 windows in the building are original uninsulated windows and are not energy efficient. This project would provide for the removal and replacement of the old windows with new dual pane insulated windows in vinyl frames. This project or a portion thereof was previously recommended in the FCA report dated 05/31/2012. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2020. | PARK OFFICE & GARAGE | 9883 | CNR | Parks |  | Rye Patch SRA | 1978 | 1080 | 2020-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
1301EXT1 | EXTERIOR FINISHES | 1301 | The exterior finishes are in fair condition. It is important to maintain the finish, weather resistance, and appearance of the structure. It is recommended that the structure be painted in the next 5 - 6 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | RAMADA #02 | 9883 | CNR | Parks |  | Rye Patch SRA | 1976 | 144 | 2020-06-04 | Four to Ten Years | Long-Term Needs | 3 | 700
2754EXT2 | GUARDRAIL INSTALLATION | 2754 | It appears that a guardrail is required to be installed around the exterior deck. The height at which a guardrail is required is 30" per IRC 2018 R312.1.1 Where Required: "Guards shall be provided for those portions of open-sided walking surfaces, including stairs, ramps and landings, that are located more than 30 inches (762 mm) measured vertically to the floor or grade below..." This project would provide for the purchase and installation of new guardrails. | MAN CAMP TRAILER | 9883 | CNR | Parks |  | Rye Patch SRA | 2013 | 399 | 2020-06-04 | Immediate to Two Years | Currently Critical | 1 | 7500
2532EXT1 | ROOF REPLACEMENT | 2532 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2 - 3 years with a new 50 year asphalt composition shingle roof and new underlayments. This estimate includes removal and disposal of the old roof. This project or a portion thereof was previously recommended in the FCA report dated 05/31/2012. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2020. | RESIDENCE GARAGE | 9883 | CNR | Parks |  | Rye Patch SRA | 1995 | 400 | 2020-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7200
2754EXT1 | EXTERIOR FINISHES | 2754 | The exterior finishes are in good condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting, and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MAN CAMP TRAILER | 9883 | CNR | Parks |  | Rye Patch SRA | 2013 | 399 | 2020-06-04 | Four to Ten Years | Long-Term Needs | 3 | 2800
2754EXT3 | EGRESS DOOR LANDING ADJUSTMENT | 2754 | Exterior egress doors must have a landing at the elevation of the door. 2018 IRC Section R311.3 states "Landings or finished floors at the required egress door shall be not more than 1-1/2 inches (38 mm) lower than the top of the threshold." This project would provide funding to install landings at each entry door that are contiguous to the two pre-fabricated stair and handrail systems that meet the requirements of Section R311 Means of Egress. | MAN CAMP TRAILER | 9883 | CNR | Parks |  | Rye Patch SRA | 2013 | 399 | 2020-06-04 | Immediate to Two Years | Currently Critical | 1 | 2000
2754INT1 | INTERIOR FINISHES | 2754 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | MAN CAMP TRAILER | 9883 | CNR | Parks |  | Rye Patch SRA | 2013 | 399 | 2020-06-04 | Four to Ten Years | Long-Term Needs | 3 | 2800
2532EXT2 | EXTERIOR FINISHES | 2532 | The exterior finishes are in poor condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting, and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2 - 3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | RESIDENCE GARAGE | 9883 | CNR | Parks |  | Rye Patch SRA | 1995 | 400 | 2020-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2800
3115EXT1 | EXTERIOR FINISHES | 3115 | The exterior finishes are in poor condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting, and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2 - 3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CABIN #2 | 9883 | CNR | Parks |  | Rye Patch SRA | 2012 | 80 | 2020-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 800
3117EXT1 | EXTERIOR FINISHES | 3117 | The exterior finishes are in good condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete, and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | COMFORT STATION - LOWER CAMPGROUND | 9883 | CNR | Parks |  | Rye Patch SRA | 2007 | 204 | 2020-06-04 | Four to Ten Years | Long-Term Needs | 3 | 2040
3118INT1 | INTERIOR FINISHES | 3118 | The interior finishes are in good condition; however, since this is a public restroom a shorter cycle between re-finishing is recommended. It is recommend to power wash the interior walls and ceilings, and replace the Fiberglass Reinforced Panels where necessary at least once in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | COMFORT STATION - GROUP USE | 9883 | CNR | Parks |  | Rye Patch SRA | 2006 | 204 | 2020-06-04 | Four to Ten Years | Long-Term Needs | 3 | 2000
3117INT1 | INTERIOR FINISHES | 3117 | The interior finishes are in good condition; however, since this is a public restroom a shorter cycle between re-finishing is recommended. It is recommend to power wash the interior walls and ceilings, and replace the Fiberglass Reinforced Panels where necessary at least once in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | COMFORT STATION - LOWER CAMPGROUND | 9883 | CNR | Parks |  | Rye Patch SRA | 2007 | 204 | 2020-06-04 | Four to Ten Years | Long-Term Needs | 3 | 2040
3117ADA1 | ADA PARKING SPACE | 3117 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. A concrete parking area and passenger loading area for the Lower Campground Comfort Station are necessary to comply with ADA requirements. This project would provide for a concrete van accessible ADA parking and loading space, and walkway to the existing sidewalk. This will require regrading, installing P.C. concrete, striping, signage, and any other necessary upgrades. NRS 338.180, IBC - 2018, ICC/ANSI A117.1 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | COMFORT STATION - LOWER CAMPGROUND | 9883 | CNR | Parks |  | Rye Patch SRA | 2007 | 204 | 2020-06-04 | Immediate to Two Years | Currently Critical | 1 | 15000
3116EXT1 | EXTERIOR FINISHES | 3116 | The exterior finishes are in good condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete, and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | COMFORT STATION - DAY USE | 9883 | CNR | Parks |  | Rye Patch SRA | 2006 | 120 | 2020-06-04 | Four to Ten Years | Long-Term Needs | 3 | 1200
3116INT1 | INTERIOR FINISHES | 3116 | The interior finishes are in good condition; however, since this is a public restroom a shorter cycle between re-finishing is recommended. It is recommend to power wash the interior walls and ceilings, and replace the Fiberglass Reinforced Panels where necessary at least once in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | COMFORT STATION - DAY USE | 9883 | CNR | Parks |  | Rye Patch SRA | 2006 | 120 | 2020-06-04 | Four to Ten Years | Long-Term Needs | 3 | 1200
3115INT1 | INTERIOR FINISHES | 3115 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. | CABIN #2 | 9883 | CNR | Parks |  | Rye Patch SRA | 2012 | 80 | 2020-06-04 | Four to Ten Years | Long-Term Needs | 3 | 800
9883SIT2 | IRRIGATION UPGRADES | 9883 | The existing landscape irrigation lines for the Group Use area are reaching the end of their expected life and should be scheduled for replacement. This project would provide for the removal of the existing irrigation lines and the purchase and installation of new lines. 2,000 linear feet were used to generate this estimate. This project or a portion thereof was previously recommended in the FCA report dated 05/31/2012. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2020. | RYE PATCH SRA SITE | 9883 | CNR | Parks |  | Rye Patch SRA | 1971 |  | 2020-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
9883PLM1 | WATER STORAGE TANK INSTALLATION | 9883 | There is a 150 gallon water storage tank in the Park Office building. The existing capacity is not enough to support the demand in this area of the park. It is recommended to purchase and install a new larger tank to meet the demand. This project would provide for a new 500 gallon water storage tank to be installed near the Park Office including connections to existing utilities and the radio telemetry system. This project or a portion thereof was previously recommended in the FCA report dated 05/31/2012. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2020. | RYE PATCH SRA SITE | 9883 | CNR | Parks |  | Rye Patch SRA | 1971 |  | 2020-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
9883SFT1 | PICNIC TABLE REPLACEMENT | 9883 | The weather in the Rye Patch SRA is extreme, creating maintenance issues throughout the park. Extreme cold winters and hot summer months are causing premature wear and deterioration to the wood picnic tables. This project would provide for the replacement of the wood picnic tables with powder coated metal frame and resin composite tables. This project or a portion thereof was previously recommended in the FCA report dated 05/31/2012. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2020. | RYE PATCH SRA SITE | 9883 | CNR | Parks |  | Rye Patch SRA | 1971 |  | 2020-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
3114INT1 | INTERIOR FINISHES | 3114 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. | CABIN #1 | 9883 | CNR | Parks |  | Rye Patch SRA | 2012 | 80 | 2020-06-04 | Four to Ten Years | Long-Term Needs | 3 | 800
3118EXT1 | EXTERIOR FINISHES | 3118 | The exterior finishes are in good condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete, and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | COMFORT STATION - GROUP USE | 9883 | CNR | Parks |  | Rye Patch SRA | 2006 | 204 | 2020-06-04 | Four to Ten Years | Long-Term Needs | 3 | 2000
9883SIT6 | EROSION CONTROL | 9883 | Wave action has severely eroded the shoreline which jeopardizes state facilities. The erosion is encroaching on the park entrance kiosk, well house (Building #0477), multiple shore access stairways and utility power pole. If left unchecked, the campground will potentially lose water service along with other facilities as the shoreline erodes. The project will design and construct erosion control improvements to the shoreline at the Rye Patch State Recreation Area. The project scope includes relocation of an undercut utility pole, grading, and placement of riprap. | RYE PATCH SRA SITE | 9883 | CNR | Parks |  | Rye Patch SRA | 1971 |  | 2020-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1030000
9883SIT4 | SITE HANDRAIL PAINTING | 9883 | Existing painted finishes on the hand and safety railings in the park are showing signs of deterioration and are in need of repainting. This project recommends the preparation and repainting of all the hand and safety railings. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized for durability. This project or a portion thereof was previously recommended in the FCA report dated 05/31/2012. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2020. | RYE PATCH SRA SITE | 9883 | CNR | Parks |  | Rye Patch SRA | 1971 |  | 2020-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
3114EXT1 | EXTERIOR FINISHES | 3114 | The exterior finishes are in poor condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting, and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2 - 3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CABIN #1 | 9883 | CNR | Parks |  | Rye Patch SRA | 2012 | 80 | 2020-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 800
9883ADA2 | LOWER CAMPGROUND ADA UPGRADES | 9883 | According to proposed US Access Board regulations, a campground with 51-100 camping spaces should have 4 accessible spaces spaced throughout the campground to provide as many accessible campsite options as possible. The Upper Campground currently has two accessible spaces and the Lower campground does not have any. Other regulations include 20'-0" wide drive aisles for RV/ tent trailer sites and accessible amenities on an accessible route including grills, picnic tables, fire rings, and water and electric utilities. This project provides for upgrading two existing campsites at the Lower Campground to accessible campsites. This project or a portion thereof was previously recommended in the FCA report dated 05/31/2012. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2020. | RYE PATCH SRA SITE | 9883 | CNR | Parks |  | Rye Patch SRA | 1971 |  | 2020-06-04 | Immediate to Two Years | Currently Critical | 1 | 40000
0479ADA3 | ADA RESTROOM UPGRADE | 0479 | The designated unisex ADA accessible restroom is not fully compliant. There is no pipe protection and it is missing a grab bar. A partial retrofit is necessary. This project would provide funding to bring the restroom into full ADA compliance. NRS 338.180, IBC - 2018, ICC/ANSI A117.1 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 05/31/2012. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2020. | COMFORT STATION #4 | 9883 | CNR | Parks |  | Rye Patch SRA | 1976 | 400 | 2020-06-04 | Immediate to Two Years | Currently Critical | 1 | 1000
0476INT1 | INTERIOR FINISHES | 0476 | The interior finishes are in good condition; however, since this is a public restroom a shorter cycle between re-finishing is recommended. It is recommended that the interior walls and ceilings be painted at least once in the next 5 - 6 years, and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | BOAT RAMP COMFORT STATION | 9883 | CNR | Parks |  | Rye Patch SRA | 2000 | 462 | 2020-06-04 | Four to Ten Years | Long-Term Needs | 3 | 4600
0476EXT1 | EXTERIOR FINISHES | 0476 | The exterior finishes are in good condition. It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units, and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BOAT RAMP COMFORT STATION | 9883 | CNR | Parks |  | Rye Patch SRA | 2000 | 462 | 2020-06-04 | Four to Ten Years | Long-Term Needs | 3 | 4600
0477EXT1 | EXTERIOR FINISHES | 0477 | The exterior finishes are in poor condition with special attention and prep needed at the roof facia prior to recoating. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 2 - 3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | WELL HOUSE | 9883 | CNR | Parks |  | Rye Patch SRA | 1980 | 84 | 2020-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1300
0479ADA5 | ADA PARKING SPACE | 0479 | The ADA provides for accessibility to sites and services for people with physical limitations. A concrete parking area and passenger loading area are necessary to comply with ADA requirements. This project would provide for a concrete van accessible ADA parking and loading space, and walkway to the existing sidewalk. This will require regrading, installing concrete, striping, signage, and any other necessary upgrades. The 2018 IBC, ICC/ANSI A117.1, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as a reference for this project. | COMFORT STATION #4 | 9883 | CNR | Parks |  | Rye Patch SRA | 1976 | 400 | 2020-06-04 | Immediate to Two Years | Currently Critical | 1 | 15100
0476ADA2 | ADA RESTROOM UPGRADE | 0476 | The accessible restrooms and showers are not fully compliant. There are no shower seats, exterior door signage, and they are missing grab bars. A partial retrofit is necessary. This project would provide funding to bring the restroom into full ADA compliance. The 2018 IBC, ICC/ANSI A117.1, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 05/31/2012. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2020. | BOAT RAMP COMFORT STATION | 9883 | CNR | Parks |  | Rye Patch SRA | 2000 | 462 | 2020-06-04 | Immediate to Two Years | Currently Critical | 1 | 3000
0479INT1 | INTERIOR FINISHES | 0479 | The interior finishes are in good condition; however, since this is a public restroom a shorter cycle between re-finishing is recommended. It is recommend to power wash the interior walls and ceilings, and replace the Fiberglass Reinforced Panels where necessary at least once in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | COMFORT STATION #4 | 9883 | CNR | Parks |  | Rye Patch SRA | 1976 | 400 | 2020-06-04 | Four to Ten Years | Long-Term Needs | 3 | 2000
0477EXT3 | ROOF REPAIRS | 0477 | The roof sealant and fastener penetrations are due for repair. The sealants are dried out and cracking which will cause leaks in the future. This project would provide funds for reinforcing the seams and fastener penetrations and re-coating to create a durable roofing system. The estimate includes removing the existing sealants and applying new sealants. | WELL HOUSE | 9883 | CNR | Parks |  | Rye Patch SRA | 1980 | 84 | 2020-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1300
0479ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0479 | There is a water fountain attached to the exterior of the building that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. This project or a portion thereof was previously recommended in the FCA report dated 05/31/2012. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2020. | COMFORT STATION #4 | 9883 | CNR | Parks |  | Rye Patch SRA | 1976 | 400 | 2020-06-04 | Immediate to Two Years | Currently Critical | 1 | 5000
0479ADA1 | ADA SIGNAGE | 0479 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2018, ICC/ANSI A117.1 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 05/31/2012. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2020. | COMFORT STATION #4 | 9883 | CNR | Parks |  | Rye Patch SRA | 1976 | 400 | 2020-06-04 | Immediate to Two Years | Currently Critical | 1 | 750
0545EXT2 | DEMOLISH STRUCTURE | 0545 | The structure is dilapidated and deteriorating and has reached the end of its useful life. The structure is approaching 50 years of age, has had continuous roof leaks and the wood has rotted. This project would provide funding for the demolition and disposal of the building. This project or a portion thereof was previously recommended in the FCA report dated 05/31/2012. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2020. | STORAGE BUILDING #2 | 9883 | CNR | Parks |  | Rye Patch SRA | 1966 | 200 | 2020-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0479EXT1 | EXTERIOR FINISHES | 0479 | The exterior finishes are in good condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting, and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | COMFORT STATION #4 | 9883 | CNR | Parks |  | Rye Patch SRA | 1976 | 400 | 2020-06-04 | Four to Ten Years | Long-Term Needs | 3 | 2000
0479ADA4 | ADA SHOWER UPGRADE | 0479 | The designated ADA shower does not fully comply with the ADA accessible guidelines. This project would provide for a new ADA compliant shower seat and any other necessary upgrades to bring the restroom into compliance. NRS 338.180, IBC - 2018, ICC/ANSI A117.1 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 05/31/2012. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2020. | COMFORT STATION #4 | 9883 | CNR | Parks |  | Rye Patch SRA | 1976 | 400 | 2020-06-04 | Immediate to Two Years | Currently Critical | 1 | 1000
2543INT1 | INTERIOR FINISHES | 2543 | The interior finishes are in very poor condition. It is recommended that the interior walls and ceilings be fire taped, patched, and painted at least once in the next 2 - 3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | NDF FIRE TRUCK GARAGE | 9881 | CNR | Forestry |  | Ruby Valley | 0 | 714 | 2020-06-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7100
2543ELE1 | LIGHTING UPGRADE | 2543 | The existing lighting fixtures are older T-12 fluorescent type and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. LED are suggested using the existing wiring and conduit. | NDF FIRE TRUCK GARAGE | 9881 | CNR | Forestry |  | Ruby Valley | 0 | 714 | 2020-06-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
2543EXT1 | EXTERIOR FINISHES | 2543 | The exterior finishes are in good condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NDF FIRE TRUCK GARAGE | 9881 | CNR | Forestry |  | Ruby Valley | 0 | 714 | 2020-06-05 | Four to Ten Years | Long-Term Needs | 3 | 3600
1030EXT2 | ROOF REPLACEMENT | 1030 | The corrugated metal roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2 - 3 years with a standing seam metal roofing system. This estimate includes removal and disposal of the old roofing system. | DAYTON STATE PARK SHOP | 9961 | CNR | Parks |  | Dayton | 1999 | 480 | 2020-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
1228ELE1 | EXTERIOR LIGHTING REPLACEMENT | 1228 | The Ramada has high bay halogen lighting on the interior of the building, but the light fixtures are old and not energy efficient. This project would provide for the replacement of the exterior rated lighting fixtures with new LED light fixtures, using existing wiring. | DAY USE AREA RAMADA | 9961 | CNR | Parks |  | Dayton | 1979 | 2508 | 2020-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
1228EXT1 | EXTERIOR FINISHES | 1228 | The exterior finishes are in poor condition. It is important to maintain the finish, weather resistance, and appearance of the structure. This project would provide for staining or painting of the structure and it is recommended that this project be scheduled in the next 2 - 3 years and on a cyclical basis to maintain the integrity of the structure. | DAY USE AREA RAMADA | 9961 | CNR | Parks |  | Dayton | 1979 | 2508 | 2020-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12500
1228ADA1 | ADA UPGRADES | 1228 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The Ramada requires several upgrades to comply with ADA requirements. There are elevation changes in the concrete flooring that exceed accessible limits, the grill and sink are not accessible and there are no accessible picnic tables. This project would provide for grinding the concrete, replacing the grill and sink, providing at least two accessible picnic tables and any other necessary upgrades to comply with ADA regulations. The 2018 IBC, ICC/ANSI A117.1, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 06/06/2012 has been amended accordingly to reflect conditions observed during the most recent survey date of 06/11/2020. | DAY USE AREA RAMADA | 9961 | CNR | Parks |  | Dayton | 1979 | 2508 | 2020-06-11 | Immediate to Two Years | Currently Critical | 1 | 12000
1030EXT1 | EXTERIOR FINISHES | 1030 | The exterior finishes are in poor condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 2 - 3 years and is recommended on a cyclical basis based on environmental conditions. | DAYTON STATE PARK SHOP | 9961 | CNR | Parks |  | Dayton | 1999 | 480 | 2020-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4800
1030INT1 | INTERIOR FINISHES / FRP INSTALLATION | 1030 | The interior of the shop is stained plywood on the roof and ceiling. This project would provide for the cyclical staining or painting of the interior plywood walls and ceiling. This project also includes installing an FRP wall surround in the restroom. This project or a portion thereof was previously recommended in the FCA report dated 06/06/2012. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/11/2020. | DAYTON STATE PARK SHOP | 9961 | CNR | Parks |  | Dayton | 1999 | 480 | 2020-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4800
1030SFT2 | EXIT SIGN & EGRESS LIGHTING | 1030 | The Park Shop has no exit lighting and emergency egress lighting. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 06/06/2012. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/11/2020. | DAYTON STATE PARK SHOP | 9961 | CNR | Parks |  | Dayton | 1999 | 480 | 2020-06-11 | Immediate to Two Years | Currently Critical | 1 | 2500
1227EXT1 | EXTERIOR & INTERIOR FINISHES | 1227 | The interior and exterior finishes are in poor condition from water scale, plumbing leaks, and weathered wood finishes. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding for the painting the wood portions of the building and repairing any cracks and sealing the stone masonry as well as caulking the window frames, doors and other penetrations excluding the roof. This project includes the exterior and interior finishes. It is recommended that the building be painted in the next 2 - 3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project should be implemented concurrently with the PLUMBING REPLACEMENT project. | COMFORT STATION | 9961 | CNR | Parks |  | Dayton | 1979 | 360 | 2020-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7200
1030EXT3 | EXTERIOR DOOR REPLACEMENT | 1030 | The existing exterior metal door and frame appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement and installation of a new metal door, frame, and hardware. Removal and disposal of the existing door and painting of the new door is included in this estimate. | DAYTON STATE PARK SHOP | 9961 | CNR | Parks |  | Dayton | 1999 | 480 | 2020-06-11 | Four to Ten Years | Long-Term Needs | 3 | 2500
1227PLM1 | PLUMBING REPLACEMENT | 1227 | The plumbing system is older and in poor condition with multiple leaks as well as evidence of past leaks. The system appears to be original to the building and should be scheduled for replacement. The sewer lines should also be inspected for deterioration. This project would provide for replacement all of the water lines including fixture valves in the building. This estimate includes removal and disposal of the existing system as required. | COMFORT STATION | 9961 | CNR | Parks |  | Dayton | 1979 | 360 | 2020-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
1030ENR1 | LIGHTING UPGRADE | 1030 | The existing building lighting fixtures, T-12's are older incandescent type and are not energy efficient. This project will upgrade lighting fixtures to T-5's, with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. This project or a portion thereof was previously recommended in the FCA report dated 06/06/2012. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/112020. | DAYTON STATE PARK SHOP | 9961 | CNR | Parks |  | Dayton | 1999 | 480 | 2020-06-11 | Immediate to Two Years | Currently Critical | 1 | 2500
1062ADA1 | ADA IMPROVEMENTS | 1062 | The Park Office is not ADA accessible. This project would provide for ADA accessibility upgrades including but not limited to a concrete parking and loading space, route of travel to the office, a new concrete walkway / landing at the front entrance and a new threshold for the existing door. Signage is also included in this estimate. he 2018 IBC, ICC/ANSI A117.1, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. 500 square feet of new PC concrete was used for this estimate. This project or a portion thereof was previously recommended in the FCA report dated 06/062012. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/112020. | DAYTON STATE PARK OFFICE | 9961 | CNR | Parks |  | Dayton | 1979 | 200 | 2020-06-11 | Immediate to Two Years | Currently Critical | 1 | 12500
1227EXT2 | TRIM TREES ADJOINING BUILDING | 1227 | The Comfort Station has trees which are growing up against the structure and are in need of trimming. The trees are touching the walls and roof structure and are a maintenance and safety issue. This project recommends that they be trimmed back providing clearance to the structure. | COMFORT STATION | 9961 | CNR | Parks |  | Dayton | 1979 | 360 | 2020-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
1062EXT1 | EXTERIOR FINISHES | 1062 | The exterior finishes are galvanized corrugated metal requiring low maintenance; however, there are portions of T1-11 siding and trim which are in fair condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project recommends work to protect the exterior building envelope other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures and other penetrations to maintain the building in good, weather tight condition. It is recommended that the building be painted, caulked and sealed in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | DAYTON STATE PARK OFFICE | 9961 | CNR | Parks |  | Dayton | 1979 | 200 | 2020-06-11 | Four to Ten Years | Long-Term Needs | 3 | 1000
1062INT1 | INTERIOR FINISHES | 1062 | The interior finishes are in fair condition. The interior of the shop is painted plywood on the roof and ceiling. This project would provide for the cyclical painting of the interior plywood walls and ceiling starting in 4 - 5 years. | DAYTON STATE PARK OFFICE | 9961 | CNR | Parks |  | Dayton | 1979 | 200 | 2020-06-11 | Four to Ten Years | Long-Term Needs | 3 | 2000
1062EXT2 | EXTERIOR DOOR REPLACEMENT | 1062 | The existing exterior wood door and frame appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement and installation of a new metal door, frame, and hardware. Removal and disposal of the existing door and painting of the new door is included in this estimate. | DAYTON STATE PARK OFFICE | 9961 | CNR | Parks |  | Dayton | 1979 | 200 | 2020-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
1227ADA1 | ADA IMPROVEMENTS | 1227 | The existing ADA designated restroom is not 100 % ADA compliant. This project would provide for the required modifications to the restrooms including restroom fixture relocation to provide for clearances and mounting heights of fixtures and equipment and signage. The exterior concrete landing at the door appears to exceed a 2% slope. This project also includes the removal and replacement of the exterior concrete to provide for a code compliant landing. This proposal is for the one designated ADA restroom. The 2018 IBC, ICC/ANSI A117.1, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 06/06/2012 has been amended accordingly to reflect conditions observed during the most recent survey date of 06/11/2020. | COMFORT STATION | 9961 | CNR | Parks |  | Dayton | 1979 | 360 | 2020-06-11 | Immediate to Two Years | Currently Critical | 1 | 15000
9961ADA8 | ADA ACCESSIBLE PATH OF TRAVEL | 9961 | The ADA provides for accessibility to sites and services for people with physical limitations. The two ADA parking and path of travel areas for the Comfort Station and Ramada are failing and do not meet current requirements. Replacing the existing designated areas with one new compliant parking area and path of travel will meet the requirements of both locations. A concrete parking area, passenger loading area and path of travel to the sidewalk connecting both buildings are necessary to comply with ADA accessibility requirements. This project would provide for two concrete van accessible ADA parking and loading space and concrete walkway to the existing sidewalk. This will require regrading, placement of concrete, signage, striping and any other necessary upgrades. The 2018 IBC, ICC/ANSI A117.1, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as a reference for this project. 750 square feet of concrete was used for this estimate. It is recommended that this project coincide with the PATCHING, CRACK FILL & SEAL ASPHALT PAVING and ADA SIDEWALK REPLACEMENT projects. | DAYTON STATE PARK SITE | 9961 | CNR | Parks |  | Dayton | 0 |  | 2020-06-11 | Immediate to Two Years | Currently Critical | 1 | 23500
9961ADA4 | CAMPGROUND ADA UPGRADES | 9961 | According to proposed US Access Board regulations, a campground with 1-25 camping spaces should have at least 1 accessible space. The campground currently does not have an accessible space out of 10 spaces. Other regulations include a 20'-0" wide drive aisle for RV/ tent trailer sites and accessible amenities on an accessible route including the grill, picnic table, fire ring, and water and electric utilities. This project provides for upgrading one existing campsite to be accessible. The 2018 IBC, ICC/ANSI A117.1, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 06/06/2012 has been amended accordingly to reflect conditions observed during the most recent survey date of 06/11/2020. | DAYTON STATE PARK SITE | 9961 | CNR | Parks |  | Dayton | 0 |  | 2020-06-11 | Immediate to Two Years | Currently Critical | 1 | 20000
9961SEC1 | EXTERIOR SOLAR SITE LIGHTING INSTALLATION | 9961 | There is no site lighting in the park which is a security and safety concern. This project would provide for the installation of 5 solar powered LED exterior light fixtures, 20 foot tall poles and 30" diameter raised concrete bases. This installation will eliminate the need for trenching and electrical connections. This project or a portion thereof was previously recommended in the FCA report dated 06/06/2012. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/11/2020. | DAYTON STATE PARK SITE | 9961 | CNR | Parks |  | Dayton | 0 |  | 2020-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 39000
9961SIT3 | ASPHALT PAVING INSTALLATION | 9961 | The yard around the Shop and Office, the campground loop road, and the individual campsite parking areas are not currently paved. This project would provide asphalt concrete paving for the yard, a 10' wide access road around the campground loop, and 10' wide parking spaces at each campsite. The estimate includes grading, compaction and installation of 4" thick asphalt cement. This project or a portion thereof was previously recommended in the FCA report dated 06/06/2012 has been amended accordingly to reflect conditions observed during the most recent survey date of 06/11/2020. | DAYTON STATE PARK SITE | 9961 | CNR | Parks |  | Dayton | 0 |  | 2020-06-11 | Four to Ten Years | Long-Term Needs | 3 | 165000
9961ADA9 | ADA SIDEWALK REPLACEMENT | 9961 | The accessible concrete sidewalks between the Comfort Station and Ramada are in need of replacement. They have cracks and are spalling. This project would provide for the removal and replacement of the concrete sidewalks. 920 SF of 4" thick concrete was used for this estimate. The 2018 IBC, ICC/ANSI A117.1, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as a reference for this project. It is recommended that this project coincide with the ADA ACCESSIBLE PATH OF TRAVEL project. | DAYTON STATE PARK SITE | 9961 | CNR | Parks |  | Dayton | 0 |  | 2020-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4300
9961ADA6 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 9961 | This park has an outdoor water fountain near the Ramada parking area that is not ADA compliant. The 2018 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. The 2018 IBC, ICC/ANSI A117.1, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 06/06/2012 has been amended accordingly to reflect conditions observed during the most recent survey date of 06/11/2020. | DAYTON STATE PARK SITE | 9961 | CNR | Parks |  | Dayton | 0 |  | 2020-06-11 | Immediate to Two Years | Currently Critical | 1 | 5000
9961SIT4 | PATCHING, CRACK FILL & SEAL ASPHALT PAVING | 9961 | It is important to maintain the asphalt concrete paving on the site. This project would provide for patching, minor crack filling and sealing of the Comfort Station and Ramada parking area. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 11,000 square feet of asphalt area was used to generate this estimate. It is recommended that this project coincide with the ADA ACCESSIBLE PATH OF TRAVEL project. | DAYTON STATE PARK SITE | 9961 | CNR | Parks |  | Dayton | 0 |  | 2020-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 22000
9961SIT5 | SITE DRAINAGE UPGRADES | 9961 | Flooding of the Carson River in the past has exposed drainage problems at the site. A culvert on the camping area loop is plugged, and brush and debris have filled the overflow canal. This project would fund the replacement of the culvert with a properly sized culvert and clean the overflow canal of debris. This project should be done prior to the ASPHALT PAVING INSTALLATION project. | DAYTON STATE PARK SITE | 9961 | CNR | Parks |  | Dayton | 0 |  | 2020-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
2443INT1 | INTERIOR FINISHES | 2443 | The interior finishes are in good condition. It is recommended to paint the interior walls and ceilings at least once in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | NDOT EAST OFFICE BLDG | 9909 | CNR | Lands | NDOT | Winnemucca | 0 | 1660 | 2020-06-18 | Four to Ten Years | Long-Term Needs | 3 | 16600
2443SFT2 | FIRE EXTINGUISHER INSTALLATION | 2443 | The building does not have portable fire extinguishers installed, at the time of the survey. International Fire Code Section 906 requires that portable fire extinguishers shall be installed in B occupancies. They shall be provided for employee use, selected, and distributed based on the classes of anticipated workplace fires and on the size and degree of hazard which would affect their use. This project would provide funding for the purchase and installation of 2 fire extinguishers, cabinets, and the hardware necessary to install them. | NDOT EAST OFFICE BLDG | 9909 | CNR | Lands | NDOT | Winnemucca | 0 | 1660 | 2020-06-18 | Immediate to Two Years | Currently Critical | 1 | 600
2443ELE2 | EXTERIOR LIGHTING INSTALLATION | 2443 | The building has incandescent lighting on the exterior of the building; but, the light fixtures are old, failing, and not energy efficient. This project would provide for the replacement of the exterior lighting fixtures with new LED light fixtures using existing wiring. | NDOT EAST OFFICE BLDG | 9909 | CNR | Lands | NDOT | Winnemucca | 0 | 1660 | 2020-06-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
2443SFT1 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 2443 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. | NDOT EAST OFFICE BLDG | 9909 | CNR | Lands | NDOT | Winnemucca | 0 | 1660 | 2020-06-18 | Immediate to Two Years | Currently Critical | 1 | 5000
2443EXT3 | WINDOW REPLACEMENT | 2443 | The windows appear to be original single pane construction with metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 8 units. Removal and disposal of the existing windows is included in this estimate. | NDOT EAST OFFICE BLDG | 9909 | CNR | Lands | NDOT | Winnemucca | 0 | 1660 | 2020-06-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
2443ADA2 | ADA RESTROOM UPGRADE | 2443 | The two restrooms are not ADA compliant; however, they appear large enough to accommodate a complete retrofit. This project would provide funding to bring the restrooms into full ADA compliance. The 2018 IBC, ICC/ANSI A117.1, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as a reference for this project. | NDOT EAST OFFICE BLDG | 9909 | CNR | Lands | NDOT | Winnemucca | 0 | 1660 | 2020-06-18 | Immediate to Two Years | Currently Critical | 1 | 10000
2443ADA1 | ADA PARKING SPACE | 2443 | The ADA provides for accessibility to sites and services for people with physical limitations. A concrete parking area and passenger loading area are necessary to comply with ADA requirements. This project would provide for a concrete van accessible ADA parking, loading space, and walkway to the existing sidewalk. This will require regrading, installing concrete, striping, signage, and any other necessary upgrades. The 2018 IBC, ICC/ANSI A117.1, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as a reference for this project. | NDOT EAST OFFICE BLDG | 9909 | CNR | Lands | NDOT | Winnemucca | 0 | 1660 | 2020-06-18 | Immediate to Two Years | Currently Critical | 1 | 12500
2443ELE1 | ELECTRICAL PANEL UPGRADE | 2443 | The interior electrical panel is recognized as a safety hazard. Federal Pacific Stab-Loc panels were part of a safety recall and should be replaced. This project would provide funding for the installation of a replacement breaker panel, and removal and disposal of the existing panel. | NDOT EAST OFFICE BLDG | 9909 | CNR | Lands | NDOT | Winnemucca | 0 | 1660 | 2020-06-18 | Immediate to Two Years | Currently Critical | 1 | 7500
2443EXT2 | EXTERIOR FINISHES | 2443 | The exterior finishes are in fair condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting, and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NDOT EAST OFFICE BLDG | 9909 | CNR | Lands | NDOT | Winnemucca | 0 | 1660 | 2020-06-18 | Four to Ten Years | Long-Term Needs | 3 | 16600
2443HVA2 | HVAC REPLACEMENT | 2443 | The HVAC roof top unit on the building appears to be more than 20 years old and has insufficient capacity to condition the entire building. It is not energy efficient and has reached the end of its expected and useful life. This project would provide for installation of a new HVAC packaged unit, any required ducting and supply registers, and cleaning of the existing duct work. This project includes removal and disposal of the existing HVAC unit, sealing wall penetrations, and all required connections to utilities. | NDOT EAST OFFICE BLDG | 9909 | CNR | Lands | NDOT | Winnemucca | 0 | 1660 | 2020-06-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
3824EXT1 | EXTERIOR FINISHES | 3824 | The exterior finishes are in good condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project recommends work to protect the exterior building envelope other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that the building be painted in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | PARK MAINTENANCE SHOP | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 0 | 4000 | 2020-06-26 | Four to Ten Years | Long-Term Needs | 3 | 20000
3825EXT1 | EXTERIOR FINISHES | 3825 | The exterior finishes are in poor condition and should be protected against further deterioration if the building is to be preserved. It is important to maintain the finish, weather resistance, and appearance of the building. This project recommends work to protect the exterior building envelope other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that the building be painted in the next 2 - 3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SMOKEHOUSE (VACANT) | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 0 | 350 | 2020-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3500
3824ELE3 | GFCI OUTLET INSTALLATION | 3824 | The existing receptacles in the restroom and on the building exterior appear to be standard duplex receptacles and may not be GFCI protected. The 2017 NEC 210.8 requires all locations on a building exterior and within 6 feet of a water source to have GFCI protection. This project would provide for removing the standard receptacles and installing GFCI receptacles. | PARK MAINTENANCE SHOP | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 0 | 4000 | 2020-06-26 | Immediate to Two Years | Currently Critical | 1 | 250
3824ADA1 | ADA RESTROOM UPGRADE | 3824 | The building does not have an accessible restroom and the current restroom is old and has reached the end of its useful life. The existing restroom does not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom. These items may include a new sink, toilet, hardware, mirrors, fixtures, signage, flooring and paint. The 2018 IBC, ICC/ANSI A117.1, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | PARK MAINTENANCE SHOP | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 0 | 4000 | 2020-06-26 | Immediate to Two Years | Currently Critical | 1 | 18000
9785SFT1 | COMBUSTIBLES REDUCTION FOR FIRE CONTROL | 9785 | The site and certain buildings have significant weed and debris buildup and are a fuel source for fire. Accumulated leaves at the base of structures create a significant fuel path to structure fires during wild land fire events. This project would provide for the removal and disposal of the weeds and debris around all structures on the site. Further site and structure enhancements to increase fire protection can be found on the Nevada State Fire Marshal's website. | WALKER RIVER SRA - PITCHFORK SITE | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 2018 |  | 2020-06-26 | Immediate to Two Years | Currently Critical | 1 | 1500
3825EXT2 | CONSERVE AND PROTECT VACANT BUILDING | 3825 | In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to removing water in the basement, providing drainage away from the building to prevent future water accumulation, pest control, and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. | SMOKEHOUSE (VACANT) | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 0 | 350 | 2020-06-26 | Four to Ten Years | Long-Term Needs | 3 | 8800
3824PLM1 | REPLACE WATER HEATER | 3824 | The water heater tank is showing signs of wear and deterioration. It appears this appliance is original to the building. This project would provide funding for the purchase and installation of a new water heater tank. | PARK MAINTENANCE SHOP | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 0 | 4000 | 2020-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3600
3829EXT1 | EXTERIOR FINISHES | 3829 | The exterior finishes are in fair condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project recommends work to protect the exterior building envelope other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that the building be painted in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | VETERINARY SHED (VACANT) | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 0 | 140 | 2020-06-26 | Four to Ten Years | Long-Term Needs | 3 | 1400
3824INT1 | INTERIOR FINISHES | 3824 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | PARK MAINTENANCE SHOP | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 0 | 4000 | 2020-06-26 | Four to Ten Years | Long-Term Needs | 3 | 20000
3824ELE1 | INTERIOR LIGHTING UPGRADES | 3824 | Select areas of the shop would benefit functionally by replacement of existing lighting with new energy efficient systems. Fluorescent T-12 task lighting on work bench and the office space are suggested to receive complete lighting upgrades using new LED technology. | PARK MAINTENANCE SHOP | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 0 | 4000 | 2020-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
3824SFT2 | STAIRWAY HANDRAIL INSTALLATION | 3824 | The existing interior stair to the mezzanine is lacking handrails as required in the 2018 IBC Chapter 11, Section 1014. This project would provide for tubular steel framed handrails to be installed. Painting is included in this estimate. | PARK MAINTENANCE SHOP | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 0 | 4000 | 2020-06-26 | Immediate to Two Years | Currently Critical | 1 | 1500
3812EXT2 | ROOF REPAIRS | 3812 | Spray foam applied roofing systems are susceptible to physical damage such as falling tree branches and other objects with sharp edges. In addition, if the foam was applied as a retrofit, all roof mounted equipment may not meet the required 8" minimum height above the new finished roof elevation. It is recommended that this roof be inspected annually and patching any areas of the coating that are blistering, cracking, or showing signs of the top waterproof coating wearing away. Additionally, caulking around roof penetrations and/or applying a three coarse mesh/coating repair in areas where caulking won’t suffice. | VISITOR CENTER | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 2001 | 4400 | 2020-06-26 | Immediate to Two Years | Currently Critical | 1 | 8800
3827INT1 | INTERIOR FINISHES | 3827 | The interior finishes are in good condition. It is recommended that the interior OSB (Oriented Strand Board) covered walls and ceilings be painted at least once in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | BROAD SHED | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 0 | 9600 | 2020-06-26 | Four to Ten Years | Long-Term Needs | 3 | 9600
3828EXT2 | ROOF REPLACEMENT | 3828 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. If the building is to be preserved, it is recommended that this building be re-roofed in the next 2 - 3 years with a new 50 year asphalt composition shingle roofing system and new underlayment. This estimate includes removal and disposal of the old roofing system. | LIVESTOCK SHED | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 0 | 2000 | 2020-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 37600
3829EXT2 | GUTTER REPLACEMENT | 3829 | The existing gutter on the building eave has failed completely on the south side. This should be replaced to prevent premature deterioration to the building's finishes and the site's hardscape. This project would replace the existing gutter on both eaves with seamless gutter and new downspouts. | VETERINARY SHED (VACANT) | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 0 | 140 | 2020-06-26 | Immediate to Two Years | Currently Critical | 1 | 3100
3830EXT1 | EXTERIOR FINISHES | 3830 | The exterior finishes are in good condition; however, there is very little maintenance i.e. repainting of the pre-finished metal panels. It is important to maintain the finish, weather resistance, and appearance of the building. This project recommends work to protect the exterior building envelope other than the roof, including caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that the building exterior be re-assessed in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CHURCH SHED | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 0 | 1380 | 2020-06-26 | Four to Ten Years | Long-Term Needs | 3 | 1380
3836EXT3 | ROOF REPLACEMENT | 3836 | The asphalt composition shingle roof on this building was in fair condition at the time of the survey. It is recommended that this building be re-roofed in the next 4 - 5 years with a new 50 year asphalt composition shingle roofing system and new underlayment. This estimate includes removal and disposal of the old roofing system. It is recommended that necessary roof modifications to provide future access for the removal and replacement of the well pump be made at this time. | PUMP HOUSE 2 | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 0 | 225 | 2020-06-26 | Four to Ten Years | Long-Term Needs | 3 | 6800
3836EXT2 | WINDOW REPLACEMENT | 3836 | The windows appear to be original dual pane aluminum frame type with the outer pane broken on one of the two windows. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 2 units. Removal and disposal of the existing windows is included in this estimate. | PUMP HOUSE 2 | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 0 | 225 | 2020-06-26 | Four to Ten Years | Long-Term Needs | 3 | 1000
3836EXT1 | EXTERIOR FINISHES | 3836 | The exterior paint is in fair condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | PUMP HOUSE 2 | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 0 | 225 | 2020-06-26 | Four to Ten Years | Long-Term Needs | 3 | 2600
3836SFT1 | WELL REFURBISHMENT | 3836 | It appears that the existing well and pressure tank are original and may not have been recently inspected. This project would provide funding to inspect and repair the well including the following projects. Investigate the well using a camera to inspect the casing and evaluate the well for the total depth and screened interval. Test the well pumping capacity and test the water quality to determine whether chemical treatment is necessary. Future projects may be based on the results of the investigation and are not part of this project. A future project recommendation is to upgrade the well pump and associated equipment considering the additional function to support fire suppression at the site. This recommendation is due to the distance between the site and the nearest volunteer Fire Department. | PUMP HOUSE 2 | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 0 | 225 | 2020-06-26 | Four to Ten Years | Long-Term Needs | 3 | 25000
3825EXT3 | ROOF REPLACEMENT | 3825 | The asphalt composition shingle roof on this building was in fair condition at the time of the survey. If the building is to be preserved, it is recommended that this building be re-roofed in the next 9 - 10 years with a new 50 year asphalt composition shingle roofing system and new underlayment. This estimate includes removal and disposal of the old roofing system. | SMOKEHOUSE (VACANT) | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 0 | 350 | 2020-06-26 | Four to Ten Years | Long-Term Needs | 3 | 6600
3824ELE2 | EXTERIOR LIGHTING REPLACEMENT | 3824 | The building has perimeter HPS (High Pressure Sodium) lighting on the exterior of the building, but the light fixtures are old and not energy efficient. This project would provide for the replacement of the exterior lighting fixtures with new LED light fixtures, using existing wiring. | PARK MAINTENANCE SHOP | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 0 | 4000 | 2020-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1600
3828EXT1 | EXTERIOR FINISHES | 3828 | The exterior finishes are in poor condition and should be protected against further deterioration if the building is to be preserved. It is important to maintain the finish, weather resistance, and appearance of the building. This project recommends work to protect the exterior building envelope other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that the building be painted in the next 2 - 3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | LIVESTOCK SHED | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 0 | 2000 | 2020-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
3827EXT1 | EXTERIOR FINISHES | 3827 | The exterior finishes are in good condition; however, there is very little maintenance i.e. repainting of the pre-finished metal panels. It is important to maintain the finish, weather resistance, and appearance of the building. This project recommends work to protect the exterior building envelope other than the roof, including caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that the building exterior be re-assessed in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BROAD SHED | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 0 | 9600 | 2020-06-26 | Four to Ten Years | Long-Term Needs | 3 | 9600
4049INT1 | INTERIOR FINISHES | 4049 | The interior finishes are in good condition; however, since this is a public restroom a shorter cycle between re-finishing is recommended. It is recommended that the interior walls and ceilings be painted at least once in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | COMFORT STATION #2 | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 2018 | 370 | 2020-06-26 | Four to Ten Years | Long-Term Needs | 3 | 3700
4049EXT1 | EXTERIOR FINISHES | 4049 | The exterior finishes are in good condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project recommends work to protect the exterior building envelope other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that the building be painted in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | COMFORT STATION #2 | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 2018 | 370 | 2020-06-26 | Four to Ten Years | Long-Term Needs | 3 | 3700
4050INT1 | INTERIOR FINISHES | 4050 | The interior finishes are in good condition; however, since this is a public restroom a shorter cycle between re-finishing is recommended. It is recommended that the interior walls and ceilings be painted at least once in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | COMFORT STATION #3 | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 2019 | 635 | 2020-06-26 | Four to Ten Years | Long-Term Needs | 3 | 6400
4050EXT1 | EXTERIOR FINISHES | 4050 | The exterior finishes are in good condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project recommends work to protect the exterior building envelope other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that the building be painted in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | COMFORT STATION #3 | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 2019 | 635 | 2020-06-26 | Four to Ten Years | Long-Term Needs | 3 | 6400
4051EXT1 | EXTERIOR FINISHES | 4051 | The exterior finishes are in good condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project recommends work to protect the exterior building envelope other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that the building be painted in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | COMFORT STATION #4 | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 2018 | 370 | 2020-06-26 | Four to Ten Years | Long-Term Needs | 3 | 3700
4051INT1 | INTERIOR FINISHES | 4051 | The interior finishes are in good condition; however, since this is a public restroom a shorter cycle between re-finishing is recommended. It is recommended that the interior walls and ceilings be painted at least once in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | COMFORT STATION #4 | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 2018 | 370 | 2020-06-26 | Four to Ten Years | Long-Term Needs | 3 | 3700
4079EXT1 | EXTERIOR FINISHES | 4079 | The exterior finishes are in good condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project recommends work to protect the exterior building envelope other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that the building be painted in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MAN CAMP TRAILER #1 | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 0 | 399 | 2020-06-26 | Four to Ten Years | Long-Term Needs | 3 | 4000
4079INT1 | INTERIOR FINISHES | 4079 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | MAN CAMP TRAILER #1 | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 0 | 399 | 2020-06-26 | Four to Ten Years | Long-Term Needs | 3 | 4000
3820EXT2 | EXTERIOR SIDING REPLACEMENT | 3820 | The residence has painted T1-11 siding that is due for replacement. The existing siding is in poor condition and will no longer hold paint. This project recommends overlaying the T1-11 siding and replacing it with new T1-11 siding finished with an oil-based stain or paint. | BYNUM HOUSE | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 0 | 950 | 2020-06-26 | Immediate to Two Years | Currently Critical | 1 | 2400
3813EXT1 | EXTERIOR FINISHES | 3813 | The exterior finishes are in good condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project recommends work to protect the exterior building envelope other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that the building be painted in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | VISITOR CENTER STORAGE BUILDING | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 2001 | 160 | 2020-06-26 | Four to Ten Years | Long-Term Needs | 3 | 1600
3818EXT1 | EXTERIOR FINISHES | 3818 | The exterior finishes are in good condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project recommends work to protect the exterior building envelope other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that the building be painted in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | GUEST HOUSE | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 2006 | 2850 | 2020-06-26 | Four to Ten Years | Long-Term Needs | 3 | 22800
3812EXT1 | EXTERIOR FINISHES | 3812 | The exterior finishes are in good condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project recommends work to protect the exterior building envelope other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that the building be painted in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | VISITOR CENTER | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 2001 | 4400 | 2020-06-26 | Four to Ten Years | Long-Term Needs | 3 | 26200
3824SFT1 | EXIT SIGN INSTALLATION | 3824 | The building is missing emergency exit signs at the building's exit points. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems. 2018 IFC - Chapter 11 Section 1104.3, was referenced for this project. | PARK MAINTENANCE SHOP | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 0 | 4000 | 2020-06-26 | Immediate to Two Years | Currently Critical | 1 | 400
3812INT1 | INTERIOR FINISHES | 3812 | The interior finishes are in fair condition; however, the existing paint has a flat finish and is not recommended. It is recommended that the interior walls and ceilings be painted at least once in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | VISITOR CENTER | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 2001 | 4400 | 2020-06-26 | Four to Ten Years | Long-Term Needs | 3 | 26200
3812SIT1 | EXTERIOR SITE LIGHTING UPGRADE | 3812 | There is limited site lighting for the access road and parking areas which is a security and safety concern. The occupancy change from R-3 to "A-3" may require upgrade to site lighting and controls. This project would provide for the installation of additional LED exterior light fixtures, replace lamps in existing fixtures with LED lamps, and add lighting control to meet code requirements. | VISITOR CENTER | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 2001 | 4400 | 2020-06-26 | Immediate to Two Years | Currently Critical | 1 | 10000
3819INT1 | INTERIOR FINISHES | 3819 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | GUEST HOUSE DOMESTIC WELL BUILDING | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 2006 | 500 | 2020-06-26 | Four to Ten Years | Long-Term Needs | 3 | 3500
3812INT2 | WOOD FLOORING REFINISH | 3812 | The wood flooring throughout the Visitor Center is in fair condition, showing signs of wear and should be scheduled to be refinished in the next 4 - 5 years. This project would provide for sanding, floor prep, and application of a new floor finish. | VISITOR CENTER | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 2001 | 4400 | 2020-06-26 | Four to Ten Years | Long-Term Needs | 3 | 22000
3879EXT1 | EXTERIOR FINISHES | 3879 | The exterior finishes are in good condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project recommends work to protect the exterior building envelope other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that the building be painted in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | GROUP USE RAMADA #1 | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 2018 | 1320 | 2020-06-26 | Four to Ten Years | Long-Term Needs | 3 | 6600
3814EXT2 | ROOF REPLACEMENT | 3814 | The asphalt composition shingle roof on this building was in fair condition at the time of the survey. However, a spot repair near the ridge on the east end needs to be completed immediately. It is recommended that this building be re-roofed in the next 8 - 10 years with a new 50 year asphalt composition shingle roofing system and new underlayment. This estimate includes removal and disposal of the old roofing system. | 206 HOUSE | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 0 | 1300 | 2020-06-26 | Four to Ten Years | Long-Term Needs | 3 | 24400
3820PLM1 | WATER HEATER REPLACEMENT | 3820 | There is a 40 gallon gas-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 5 - 6 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | BYNUM HOUSE | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 0 | 950 | 2020-06-26 | Four to Ten Years | Long-Term Needs | 3 | 1800
4079EXT2 | EGRESS DOOR LANDING ADJUSTMENT | 4079 | Exterior egress doors must have a landing at the elevation of the door. 2018 IRC Section R311.3 states "Landings or finished floors at the required egress door shall be not more than 1-1/2 inches (38 mm) lower than the top of the threshold." This project would provide funding to re-grade the base under the pre-fabricated stair and handrail system to allow the landing at the top of the stairs to be not more than 1-1/2 inches below the entry door threshold. Finished grade elevation shall slope no more than 1:12 to native grade or the adjacent roadway. | MAN CAMP TRAILER #1 | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 0 | 399 | 2020-06-26 | Immediate to Two Years | Currently Critical | 1 | 1500
3816SFT1 | CARBON MONOXIDE DETECTOR INSTALLATION | 3816 | This building is lacking a carbon monoxide detection system. 2018 IRC R315, IFC 2018 Section 1103.9 (Carbon Monoxide Detection for Existing Buildings) define requirements in Dwelling Units and Sleeping Units (Group I & R Occupancies) for buildings containing fuel-burning appliances. The carbon monoxide alarms shall be listed as complying with UL 2034 and be installed and maintained in accordance with NFPA 720 and the manufacturer’s instructions. This project would provide funding for the purchase and installation of carbon monoxide alarms in accordance with this code. | BRICK HOUSE | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 1930 | 1560 | 2020-06-26 | Immediate to Two Years | Currently Critical | 1 | 900
3814SFT1 | FIRE SUPPRESSION SYSTEM INSTALLATION | 3814 | This building is an R occupancy. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state regardless of occupancy having a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an "R" occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. | 206 HOUSE | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 0 | 1300 | 2020-06-26 | Four to Ten Years | Long-Term Needs | 3 | 23400
3814SFT2 | CARBON MONOXIDE DETECTOR INSTALLATION | 3814 | This building is lacking a carbon monoxide detection system. 2018 IRC R315, IFC 2018 Section 1103.9 (Carbon Monoxide Detection for Existing Buildings) define requirements in Dwelling Units and Sleeping Units (Group I & R Occupancies) for buildings containing fuel-burning appliances. The carbon monoxide alarms shall be listed as complying with UL 2034 and be installed and maintained in accordance with NFPA 720 and the manufacturer’s instructions. This project would provide funding for the purchase and installation of carbon monoxide alarms in accordance with this code. | 206 HOUSE | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 0 | 1300 | 2020-06-26 | Immediate to Two Years | Currently Critical | 1 | 900
3814SFT3 | FIRE EXTINGUISHER INSTALLATION | 3814 | It is recommended that this residence have a fire extinguisher installed similar to the Brick House due to the distance to the nearest fire station. It shall be provided for the occupant's use. The fire extinguisher type shall be selected and located based on the classes of anticipated fires and on the size and degree of hazard which would affect their use. This project would provide funding for the purchase and installation of 1 fire extinguisher, cabinets, and the hardware necessary to install them. | 206 HOUSE | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 0 | 1300 | 2020-06-26 | Immediate to Two Years | Currently Critical | 1 | 300
3814EXT1 | EXTERIOR FINISHES | 3814 | The exterior finishes are in good condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project recommends work to protect the exterior building envelope other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that the building be painted in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | 206 HOUSE | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 0 | 1300 | 2020-06-26 | Four to Ten Years | Long-Term Needs | 3 | 10400
3814INT1 | INTERIOR FINISHES | 3814 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | 206 HOUSE | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 0 | 1300 | 2020-06-26 | Four to Ten Years | Long-Term Needs | 3 | 10400
3815EXT1 | EXTERIOR FINISHES | 3815 | The exterior finishes are in good condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project recommends work to protect the exterior building envelope other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that the building be painted in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | 206 HOUSE DETACHED GARAGE | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 0 | 740 | 2020-06-26 | Four to Ten Years | Long-Term Needs | 3 | 5900
3815INT1 | INTERIOR FINISHES | 3815 | The interior finishes are in fair condition with additional attention on doors and casings. It is recommended that the interior walls and ceilings be painted at least once in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | 206 HOUSE DETACHED GARAGE | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 0 | 740 | 2020-06-26 | Four to Ten Years | Long-Term Needs | 3 | 3000
3816EXT1 | EXTERIOR FINISHES | 3816 | The exterior wood trim and facia are in fair condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project recommends work to protect the exterior building envelope other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that the building be painted in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BRICK HOUSE | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 1930 | 1560 | 2020-06-26 | Four to Ten Years | Long-Term Needs | 3 | 3120
3816INT1 | INTERIOR FINISHES | 3816 | The interior finishes are in good condition with additional attention on doors and casings. It is recommended that the interior walls and ceilings be painted at least once in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | BRICK HOUSE | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 1930 | 1560 | 2020-06-26 | Four to Ten Years | Long-Term Needs | 3 | 12500
4048EXT1 | EXTERIOR FINISHES | 4048 | The exterior finishes are in good condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project recommends work to protect the exterior building envelope other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that the building be painted in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | GROUP USE RAMADA #2 | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 2019 | 1320 | 2020-06-26 | Four to Ten Years | Long-Term Needs | 3 | 6600
3816SFT3 | FIRE SUPPRESSION SYSTEM INSTALLATION | 3816 | This building is an R occupancy. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state regardless of occupancy having a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an "R" occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. | BRICK HOUSE | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 1930 | 1560 | 2020-06-26 | Four to Ten Years | Long-Term Needs | 3 | 28000
3818INT1 | INTERIOR FINISHES | 3818 | The interior finishes are in good condition with additional attention on doors and casings. It is recommended that the interior walls and ceilings be painted at least once in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | GUEST HOUSE | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 2006 | 2850 | 2020-06-26 | Four to Ten Years | Long-Term Needs | 3 | 22800
3817SFT1 | SEISMIC RETROFIT WALLS | 3817 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current code. Visual analysis during the survey found no indication of seismic strengthening of the URM walls. The walls should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | BRICK HOUSE DETACHED GARAGE | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 1930 | 400 | 2020-06-26 | Four to Ten Years | Long-Term Needs | 3 | 30000
3817INT1 | INTERIOR FINISHES | 3817 | The interior finishes are in fair condition considering its use as storage. It is recommended that the interior be visually inspected for any weather intrusion and that any openings be sealed. It is recommended that the interior walls and ceilings be painted at least once in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | BRICK HOUSE DETACHED GARAGE | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 1930 | 400 | 2020-06-26 | Four to Ten Years | Long-Term Needs | 3 | 800
3817EXT1 | EXTERIOR FINISHES | 3817 | The exterior finishes are in fair condition. The paint on the rollup door header and roof facia is showing signs of wear and weather damage. It is important to maintain the finish, weather resistance, and appearance of the building. This project recommends work to protect the exterior building envelope other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that the building be painted in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BRICK HOUSE DETACHED GARAGE | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 1930 | 400 | 2020-06-26 | Four to Ten Years | Long-Term Needs | 3 | 2000
3813INT1 | INTERIOR FINISHES | 3813 | The interior finishes are in good condition. However, it is recommended that leaves and trash be removed to reduce likelihood of pest infestation problems. It is recommended that the interior walls and ceilings be painted at least once in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | VISITOR CENTER STORAGE BUILDING | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 2001 | 160 | 2020-06-26 | Four to Ten Years | Long-Term Needs | 3 | 1600
3817EXT2 | EXTERIOR DOOR REPLACEMENT | 3817 | The exterior wood man door appears to be original to the building. It is damaged from age and general wear and tear. This project would provide for the replacement of the wood door with a new metal door, frame, and hardware. Removal and disposal of the existing door and painting of the new door is included in this estimate. | BRICK HOUSE DETACHED GARAGE | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 1930 | 400 | 2020-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 650
3818SFT1 | CARBON MONOXIDE DETECTOR INSTALLATION | 3818 | This building is lacking a carbon monoxide detection system. 2018 IRC R315, IFC 2018 Section 1103.9 (Carbon Monoxide Detection for Existing Buildings) define requirements in Dwelling Units and Sleeping Units (Group I & R Occupancies) for buildings containing fuel-burning appliances. The carbon monoxide alarms shall be listed as complying with UL 2034 and be installed and maintained in accordance with NFPA 720 and the manufacturer’s instructions. This project would provide funding for the purchase and installation of carbon monoxide alarms in accordance with this code. | GUEST HOUSE | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 2006 | 2850 | 2020-06-26 | Immediate to Two Years | Currently Critical | 1 | 1200
3818SFT2 | FIRE SUPPRESSION SYSTEM INSTALLATION | 3818 | This building is an R occupancy. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state regardless of occupancy having a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an "R" occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. | GUEST HOUSE | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 2006 | 2850 | 2020-06-26 | Four to Ten Years | Long-Term Needs | 3 | 51300
3818SFT3 | FIRE EXTINGUISHER INSTALLATION | 3818 | It is recommended that this residence have a fire extinguisher installed similar to the Brick House due to the distance to the nearest fire station. It shall be provided for the occupant's use. The fire extinguisher type shall be selected and located based on the classes of anticipated fires and on the size and degree of hazard which would affect their use. This project would provide funding for the purchase and installation of 1 fire extinguisher, cabinets, and the hardware necessary to install them. | GUEST HOUSE | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 2006 | 2850 | 2020-06-26 | Immediate to Two Years | Currently Critical | 1 | 300
3820SFT4 | SMOKE ALARM INSTALLATION | 3820 | This building appears to be lacking an operable smoke detection system. 2018 IRC R314, IFC 2018 Section 1103.8 (Single and Multi-station Smoke Alarms for Existing Buildings) in Occupancy Groups I1 & R Occupancies define requirements for existing buildings. State Fire Marshal NAC 477.915 (3) requires that smoke detectors be connected to the wiring of the building with a battery backup. This project would provide funding for the purchase and installation of listed fire alarms in accordance with this code. | BYNUM HOUSE | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 0 | 950 | 2020-06-26 | Immediate to Two Years | Currently Critical | 1 | 1200
3816SFT4 | GFCI OUTLET INSTALLATION | 3816 | The existing receptacles in the kitchen and some bathrooms appear to be standard duplex receptacles and may not be GFCI protected. The 2017 NEC 210.8 requires all locations within 6 feet of a water source to have GFCI protection. This project would provide for removing the standard receptacles and installing GFCI receptacles. | BRICK HOUSE | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 1930 | 1560 | 2020-06-26 | Immediate to Two Years | Currently Critical | 1 | 100
3821INT2 | WALLBOARD REPLACEMENT | 3821 | The wallboard in the entry to the basement stairs is severely damaged and needs to be replaced. This project recommends removing and replacing the damaged sections of wallboard with gypsum drywall, finish, and paint. | BYNUM HOUSE DOMESTIC WELL BUILDING | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 0 | 110 | 2020-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1700
9785SIT1 | SIGNAGE | 9785 | The site is lacking an entry sign at the entry arch to the Pitchfork Site. This project would fund the purchase and installation of signage identifying the State Recreation Area. | WALKER RIVER SRA - PITCHFORK SITE | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 2018 |  | 2020-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
3820ELE1 | GFCI OUTLET INSTALLATION | 3820 | The existing receptacles in the kitchen, bathroom, and on the building exterior appear to be standard duplex receptacles and may not be GFCI protected. The 2017 NEC 210.8 requires all locations on a building exterior and within 6 feet of a water source to have GFCI protection. This project would provide for the removal of the standard receptacles and installation of GFCI receptacles. | BYNUM HOUSE | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 0 | 950 | 2020-06-26 | Immediate to Two Years | Currently Critical | 1 | 200
3821SFT1 | INTERIOR STAIRWAY REPLACEMENT | 3821 | The stairs and handrails between the first floor and the basement do not meet the requirements in the 2018 International Building Code Sections 1009 and 1012. This project would provide funding to remove and replace the stairway and handrail. | BYNUM HOUSE DOMESTIC WELL BUILDING | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 0 | 110 | 2020-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11000
3820EXT1 | EXTERIOR FINISHES | 3820 | The exterior finishes are in poor condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project recommends work to protect the exterior building envelope other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that the building be painted in the next 3 - 4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BYNUM HOUSE | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 0 | 950 | 2020-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3800
3822EXT2 | EXTERIOR DOOR REPLACEMENT | 3822 | The existing exterior wood doors and frames appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement and installation of 3 new wood doors, frames, and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | CHEFS HOUSE | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 0 | 950 | 2020-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1800
3819EXT1 | EXTERIOR FINISHES | 3819 | The exterior paint is in good condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | GUEST HOUSE DOMESTIC WELL BUILDING | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 2006 | 500 | 2020-06-26 | Four to Ten Years | Long-Term Needs | 3 | 5000
3821SFT2 | WELL REFURBISHMENT | 3821 | The existing well casing has a hole cut in the side above the floor with a hardware cloth covering potentially requiring repairs. Additionally, it is unknown when the well water quality was last tested. This project would provide funding to inspect and repair the well including the following projects. Investigate the well using a camera to inspect the casing and evaluate the well for the total depth and screened interval. Test the well pumping capacity and test the water quality to determine whether chemical treatment is necessary. Future projects may be based on the results of the investigation and are not part of this project. A future project recommendation is to upgrade the well pump and associated equipment considering the additional function to support fire suppression at the site. This recommendation is due to the distance between the site and the nearest volunteer Fire Department. | BYNUM HOUSE DOMESTIC WELL BUILDING | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 0 | 110 | 2020-06-26 | Immediate to Two Years | Currently Critical | 1 | 25000
3822SFT2 | SMOKE ALARM INSTALLATION | 3822 | This building appears to be lacking an operable smoke detection system. 2018 IRC R314, IFC 2018 Section 1103.8 (Single and Multi-station Smoke Alarms for Existing Buildings) in Occupancy Groups I1 & R Occupancies define requirements for existing buildings. State Fire Marshal NAC 477.915 (3) requires that smoke detectors be connected to the wiring of the building with a battery backup. This project would provide funding for the purchase and installation of listed fire alarms in accordance with this code. | CHEFS HOUSE | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 0 | 950 | 2020-06-26 | Immediate to Two Years | Currently Critical | 1 | 900
3821EXT5 | ROOF REPLACEMENT | 3821 | The asphalt composition shingle roof and roof sheathing on this building were in poor condition at the time of the survey. It is recommended that this building be re-roofed, including structural repairs to fascia, and sheathing, in the next 2-3 years with a new 50 year asphalt composition shingle roofing system and new underlayment. This estimate includes removal and disposal of the old roofing system. It is recommended that necessary roof modifications to provide future access for the removal and replacement of the well pump be made at this time. | BYNUM HOUSE DOMESTIC WELL BUILDING | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 0 | 110 | 2020-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
3820SFT3 | FIRE SUPPRESSION SYSTEM INSTALLATION | 3820 | This building is an R occupancy. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state regardless of occupancy having a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an "R" occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. | BYNUM HOUSE | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 0 | 950 | 2020-06-26 | Four to Ten Years | Long-Term Needs | 3 | 17100
3821EXT3 | EXTERIOR DOOR REPLACEMENT | 3821 | The 2 exterior wood man doors appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement of the wood doors with new metal doors, frames, and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | BYNUM HOUSE DOMESTIC WELL BUILDING | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 0 | 110 | 2020-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1300
3821EXT2 | EXTERIOR SIDING REPLACEMENT | 3821 | The building has painted T1-11 siding that is due for replacement. The existing siding is in poor condition and will no longer hold paint. This project recommends removing the T1-11 siding and replacing it with new T1-11 siding finished with an oil-based stain or paint. | BYNUM HOUSE DOMESTIC WELL BUILDING | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 0 | 110 | 2020-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2800
3821INT1 | INTERIOR FINISHES | 3821 | The interior finishes are in poor condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2 - 3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project should be implemented concurrently with the WALLBOARD REPLACEMENT project. | BYNUM HOUSE DOMESTIC WELL BUILDING | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 0 | 110 | 2020-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
3821ENV1 | PEST CONTROL | 3821 | There are numerous bird and rodent droppings throughout this building. Due to the potential risk of disease, this project provides for treatment and cleanup of the rodent droppings by a licensed pest control business. Additionally, the building envelope should be sealed up to prevent future infestation until the building can be fully renovated. | BYNUM HOUSE DOMESTIC WELL BUILDING | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 0 | 110 | 2020-06-26 | Immediate to Two Years | Currently Critical | 1 | 2500
3821EXT4 | WINDOW REPLACEMENT | 3821 | The windows are original, single pane construction in a wooden frame. These older windows are drafty, not energy efficient, and the wooden frames have deteriorated significantly. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 2 units including wooden frames. Removal and disposal of the existing windows is included in this estimate. | BYNUM HOUSE DOMESTIC WELL BUILDING | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 0 | 110 | 2020-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
3822INT1 | INTERIOR FINISHES | 3822 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | CHEFS HOUSE | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 0 | 950 | 2020-06-26 | Four to Ten Years | Long-Term Needs | 3 | 7600
3822SFT3 | FIRE SUPPRESSION SYSTEM INSTALLATION | 3822 | This building is an R occupancy. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state regardless of occupancy having a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an "R" occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. | CHEFS HOUSE | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 0 | 950 | 2020-06-26 | Four to Ten Years | Long-Term Needs | 3 | 17100
3822ELE1 | GFCI OUTLET INSTALLATION | 3822 | The existing receptacles in the kitchen appear to be standard duplex receptacles and may not be GFCI protected. The 2017 NEC 210.8 requires all locations within 6 feet of a water source to have GFCI protection. This project would provide for removing the standard receptacles and installing GFCI receptacles. | CHEFS HOUSE | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 0 | 950 | 2020-06-26 | Immediate to Two Years | Currently Critical | 1 | 900
3821ELE1 | ELECTRICAL UPGRADE | 3821 | The building has numerous electrical outlets and switches that are missing covers, missing light fixtures and switches, and the subpanel is missing the dead front. This project would provide for repairs and/or replacement of the damaged electrical devices, installation of 110volt ground fault circuit interrupter (GFCI) outlets, as needed, and upgrading the main panel as required. | BYNUM HOUSE DOMESTIC WELL BUILDING | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 0 | 110 | 2020-06-26 | Immediate to Two Years | Currently Critical | 1 | 2000
3822HVA1 | HVAC EQUIPMENT REPLACEMENT | 3822 | The HVAC split system was installed in 1990. It is not energy efficient and has reached the end of its expected and useful life. This project would provide for the installation of a new HVAC split system and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing equipment and all required connections to utilities. | CHEFS HOUSE | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 0 | 950 | 2020-06-26 | Immediate to Two Years | Currently Critical | 1 | 14300
3820INT1 | INTERIOR FINISHES | 3820 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | BYNUM HOUSE | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 0 | 950 | 2020-06-26 | Four to Ten Years | Long-Term Needs | 3 | 7600
3823ELE2 | GFCI OUTLET INSTALLATION | 3823 | The existing receptacles in the stable appear to be standard duplex receptacles and may not be GFCI protected. The 2017 NEC 210.8 requires all locations within 6 feet of a water source, all receptacles in structures that have a floor located at or below grade level and building exterior shall have GFCI protection. This project would provide for removing the standard receptacles and installing GFCI receptacles. | HORSE STABLE | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 0 | 940 | 2020-06-26 | Immediate to Two Years | Currently Critical | 1 | 250
3878EXT1 | EXTERIOR FINISHES | 3878 | The exterior finishes are in good condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project recommends work to protect the exterior building envelope other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that the building be painted in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | COMFORT STATION #1 | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 2018 | 400 | 2020-06-26 | Four to Ten Years | Long-Term Needs | 3 | 4000
3878INT1 | INTERIOR FINISHES | 3878 | The interior finishes are in good condition; however, since this is a public restroom a shorter cycle between re-finishing is recommended. It is recommended that the interior walls and ceilings be painted at least once in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | COMFORT STATION #1 | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 2018 | 400 | 2020-06-26 | Four to Ten Years | Long-Term Needs | 3 | 4000
3823ELE1 | EXTERIOR LIGHTING REPLACEMENT | 3823 | The building has perimeter lighting on the exterior of the building, but the light fixtures are old, failing, and not energy efficient. This project would provide for the replacement of the exterior lighting fixtures with new LED light fixtures, using existing wiring. | HORSE STABLE | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 0 | 940 | 2020-06-26 | Four to Ten Years | Long-Term Needs | 3 | 3500
3823INT1 | INTERIOR FINISHES | 3823 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HORSE STABLE | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 0 | 940 | 2020-06-26 | Four to Ten Years | Long-Term Needs | 3 | 9400
3823EXT1 | EXTERIOR FINISHES | 3823 | The exterior finishes are in fair condition. The paint on the T1-11 siding is showing signs of wear. It is important to maintain the finish, weather resistance, and appearance of the building. This project recommends work to protect the exterior building envelope other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that the building be painted in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HORSE STABLE | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 0 | 940 | 2020-06-26 | Four to Ten Years | Long-Term Needs | 3 | 9400
3812EXT3 | ROOF REPLACEMENT | 3812 | Spray foam applied roofing systems are not recommended and this roofing system should be replaced in the next 4 years. In addition, it appears that the roof mounted equipment does not meet the required 8" minimum height above the finished roof elevation. It is recommended that this building be re-roofed in the next 4-5 years with a new single-ply roofing system. This will allow for the roof to qualify for the statewide roofing warranty and preventative maintenance agreement programs. This estimate includes removal and disposal of the old roofing system. | VISITOR CENTER | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 2001 | 4400 | 2020-06-26 | Four to Ten Years | Long-Term Needs | 3 | 105600
3820SFT1 | CARBON MONOXIDE DETECTOR INSTALLATION | 3820 | This building is lacking a carbon monoxide detection system. 2018 IRC R315, IFC 2018 Section 1103.9 (Carbon Monoxide Detection for Existing Buildings) define requirements in Dwelling Units and Sleeping Units (Group I & R Occupancies) for buildings containing fuel-burning appliances. The carbon monoxide alarms shall be listed as complying with UL 2034 and be installed and maintained in accordance with NFPA 720 and the manufacturer’s instructions. This project would provide funding for the purchase and installation of carbon monoxide alarms in accordance with this code. | BYNUM HOUSE | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 0 | 950 | 2020-06-26 | Immediate to Two Years | Currently Critical | 1 | 600
3812ADA2 | ADA RAMPS | 3812 | The Visitor Center is lacking an accessible entrance into the building. The new ramp must be on the accessible path of travel from the accessible parking spaces to the entrance of the building. This project would provide for an ADA compliant concrete ramp and handrails. The 2018 IBC, ICC/ANSI A117.1, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | VISITOR CENTER | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 2001 | 4400 | 2020-06-26 | Immediate to Two Years | Currently Critical | 1 | 7500
3820SFT2 | FIRE EXTINGUISHER INSTALLATION | 3820 | It is recommended that this residence have a fire extinguisher installed similar to the Brick House due to the distance to the nearest fire station. It shall be provided for the occupant's use. The fire extinguisher type shall be selected and located based on the classes of anticipated fires and on the size and degree of hazard which would affect their use. This project would provide funding for the purchase and installation of 1 fire extinguisher, cabinets, and the hardware necessary to install them. | BYNUM HOUSE | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 0 | 950 | 2020-06-26 | Immediate to Two Years | Currently Critical | 1 | 300
3822EXT1 | EXTERIOR FINISHES | 3822 | The exterior finishes are in poor condition, particularly at the rear porch and fascia. It is important to maintain the finish, weather resistance, and appearance of the building. This project recommends work to protect the exterior building envelope other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that the building be painted in the next 2 - 3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CHEFS HOUSE | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 0 | 950 | 2020-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7600
3822INT2 | FLOORING REPLACEMENT | 3822 | The vinyl flooring and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new vinyl flooring with a 6" base and heavy duty commercial grade carpet in the next 2-3 years. | CHEFS HOUSE | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 0 | 950 | 2020-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9500
3822PLM1 | WATER HEATER SEISMIC BRACING | 3822 | The water heater is not seismically anchored to the structure. This project would provide funding for seismic bracing of the water heater to the structure. | CHEFS HOUSE | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 0 | 950 | 2020-06-26 | Immediate to Two Years | Currently Critical | 1 | 600
3812SFT1 | SMOKE DETECTOR UPGRADE | 3812 | There are different styles of smoke detectors in the building and may not be communicating properly. This project provides for replacing the older existing units and installing new units where required. State Fire Marshal NAC 477.915 (3) requires that smoke detectors be connected to the building wiring with a battery backup. | VISITOR CENTER | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 2001 | 4400 | 2020-06-26 | Immediate to Two Years | Currently Critical | 1 | 1000
3812SFT2 | EXIT SIGNS | 3812 | The building does not appear to have emergency lighting or exit signs. This project would provide for the purchase and installation of self-illuminated LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC 2018 Chapter 10 and IFC Chapter 11 were referenced for this project. | VISITOR CENTER | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 2001 | 4400 | 2020-06-26 | Immediate to Two Years | Currently Critical | 1 | 7500
3812INT3 | GYPSUM BOARD REPAIR | 3812 | Water leaks and moisture from a leaking skylight in the kitchen has damaged the gypsum board ceiling. Roof leaks that are not corrected may eventually cause structural damage. This project recommends repairing the skylight, removing and replacing the gypsum board, and repainting the kitchen ceiling. | VISITOR CENTER | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 2001 | 4400 | 2020-06-26 | Immediate to Two Years | Currently Critical | 1 | 7500
3822SFT1 | CARBON MONOXIDE DETECTOR INSTALLATION | 3822 | This building is lacking a carbon monoxide detection system. 2018 IRC R315, IFC 2018 Section 1103.9 (Carbon Monoxide Detection for Existing Buildings) define requirements in Dwelling Units and Sleeping Units (Group I & R Occupancies) for buildings containing fuel-burning appliances. The carbon monoxide alarms shall be listed as complying with UL 2034 and be installed and maintained in accordance with NFPA 720 and the manufacturer’s instructions. This project would provide funding for the purchase and installation of carbon monoxide alarms in accordance with this code. | CHEFS HOUSE | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 0 | 950 | 2020-06-26 | Immediate to Two Years | Currently Critical | 1 | 600
3821EXT1 | EXTERIOR FINISHES | 3821 | The exterior paint is in poor condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2 - 3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project should be implemented concurrently with the EXTERIOR SIDING REPLACEMENT project. | BYNUM HOUSE DOMESTIC WELL BUILDING | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 0 | 110 | 2020-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
3812ADA1 | ADA RESTROOM UPGRADE | 3812 | The building does not have an accessible restroom. The existing restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom. These items may include a new sink, toilet, hardware, mirrors, fixtures, signage, flooring and paint. The 2018 IBC, ICC/ANSI A117.1, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | VISITOR CENTER | 9785 | CNR | Parks |  | Walker River SRA/Pitchfork | 2001 | 4400 | 2020-06-26 | Immediate to Two Years | Currently Critical | 1 | 18000
4080INT1 | INTERIOR FINISHES | 4080 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | MAN CAMP #1 | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 399 | 2020-10-20 | Four to Ten Years | Long-Term Needs | 3 | 2800
4080SFT1 | EGRESS DOOR LANDING ADJUSTMENT | 4080 | Section R311.3.1 of the 2018 IRC describes the requirements for landings at exterior egress doors. The landing shall not be more than 1 1/2" inches below the top of the threshold (for doors that swing out over the landing) and shall have a minimum dimension of 36 inches measured in the direction of travel. There are three doors that do not comply with this code and pose a safety hazard. This project would provide for re-grading the earth supporting the prefabricated stair/landing to elevate the landings to within 1 1/2" of the top of threshold. | MAN CAMP #1 | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 399 | 2020-10-20 | Immediate to Two Years | Currently Critical | 1 | 500
4080EXT1 | EXTERIOR FINISHES | 4080 | The exterior finishes are in good condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting, and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MAN CAMP #1 | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 399 | 2020-10-20 | Four to Ten Years | Long-Term Needs | 3 | 2800
4080SFT2 | WATER HEATER SEISMIC BRACING | 4080 | The water heaters are not properly seismically anchored to the structure. The 2018 IRC P2801.8 "...water heaters shall be anchored or strapped in the upper one-third and in the lower one-third of the appliance...". This project would provide funding for the installation of compliant seismic bracing. | MAN CAMP #1 | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 399 | 2020-10-20 | Immediate to Two Years | Currently Critical | 1 | 500
3861EXT1 | EXTERIOR FINISHES | 3861 | The exterior of the buidling is in poor condition. It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2 - 3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SANTA MARGARITA WELL HOUSE | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 150 | 2020-10-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
3858INT1 | INTERIOR FINISHES | 3858 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SANTA MARGARITA HOUSE | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 1400 | 2020-10-22 | Four to Ten Years | Long-Term Needs | 3 | 14000
3858EXT1 | EXTERIOR FINISHES | 3858 | The exterior finishes are in poor condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project recommends work to protect the exterior building envelope other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that the building be painted in the next 3 - 4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SANTA MARGARITA HOUSE | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 1400 | 2020-10-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14000
3858SFT3 | FIRE SUPPRESSION SYSTEM INSTALLATION | 3858 | This building is an R occupancy. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state regardless of occupancy having a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an "R" occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. | SANTA MARGARITA HOUSE | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 1400 | 2020-10-22 | Four to Ten Years | Long-Term Needs | 3 | 25200
3859EXT2 | EXTERIOR FINISHES | 3859 | The exterior finishes are in poor condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project recommends work to protect the exterior building envelope other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that the building be painted in the next 3 - 4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SANTA MARGARITA HOUSE SHED | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 300 | 2020-10-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
3859EXT1 | DRAINAGE UPGRADES | 3859 | The grade does not slope away effectively from the shed and the earth is covering the bottom edge of the siding. It is recommended per IBC 1804.4 grading the ground immediately adjacent to the foundation shall be sloped away from the building at a slope of not less than one vertical unit in 20 units horizontal (5-percent slope). It is recommended that the grading be completed within 2 - 3 years. | SANTA MARGARITA HOUSE SHED | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 300 | 2020-10-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
3860EXT1 | CONSERVE AND PROTECT VACANT BUILDING | 3860 | Until the planning phase for this site is complete and a determination of demolition or rehabilitation is reached, preservation of the structure is recommended. This project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Also included is securing the exterior envelope against water penetration. Roof, windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. | MARGARITA 2 HOUSE | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 1000 | 2020-10-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
3861EXT2 | ROOF REPLACEMENT | 3861 | The wood shake roof on this building was in fair to poor condition at the time of the survey. Additionally, it is less fire resistant than asphalt shingle systems. It is recommended that this building be re-roofed in the next 4 - 5 years with a new 50 year asphalt composition shingle roof and new underlayment. This estimate includes removal and disposal of the old roof. | SANTA MARGARITA WELL HOUSE | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 150 | 2020-10-22 | Four to Ten Years | Long-Term Needs | 3 | 2700
3861PLM1 | REPLACE INSULATION | 3861 | The piping and pressure tank have a layer of insulation inadequately installed to protect against freezing temperatures. Some of the insulation batts have been damaged and removed. This project recommends the existing insulation be replaced with suitable materials. | SANTA MARGARITA WELL HOUSE | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 150 | 2020-10-22 | Immediate to Two Years | Currently Critical | 1 | 1000
3868SFT1 | DEMOLISH STRUCTURE | 3868 | The structure is an old silo set on a wood foundation that is no longer in use. A visual survey of the structure shows no evidence of anchoring to the foundation. In addition, the wood foundation has split making the silo susceptible to toppling. It is recommemded that this structure be demolished due to safety concerns. | SILO 2 | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 250 | 2020-10-22 | Immediate to Two Years | Currently Critical | 1 | 10000
3867EXT1 | CONSERVE AND PROTECT VACANT BUILDING | 3867 | Until the planning phase for this site is complete and a determination of demolition or rehabilitation is reached, preservation of the structure is recommended. This project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Also included is securing the exterior envelope against water penetration. Roof, windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. | SHED 3 | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 300 | 2020-10-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
3861EXT3 | EXTERIOR DOOR REPLACEMENT | 3861 | The exterior wood man door appears to be original to the building. It is damaged from age and general wear and tear. This project would provide for the replacement of the wood door with a new metal door, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | SANTA MARGARITA WELL HOUSE | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 150 | 2020-10-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
3851EXT3 | ROOF REPLACEMENT | 3851 | The wood shake roof on this building was in fair to poor condition at the time of the survey. Additionally, it is less fire resistant than asphalt shinge systems. It is recommended that this building be re-roofed in the next 4 - 5 years with a new 50 year asphalt composition shingle roof and new underlayment. This estimate includes removal and disposal of the old roof. | CHICKEN COOP | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 100 | 2020-10-22 | Four to Ten Years | Long-Term Needs | 3 | 2000
3858HVA1 | EVAPORATIVE COOLER REPLACEMENT | 3858 | An evaporative cooler is installed on the roof of this building. It is severely scaled and has reached the end of its useful and expected life. This project would provide for a new evaporative cooler to be installed including all required connections to utilities. The estimate includes removal and disposal of the old cooler. | SANTA MARGARITA HOUSE | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 1400 | 2020-10-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
3857EXT1 | VEGETATION REMOVAL | 3857 | The building has weeds and organic vegetation which are growing up against the structure and are a fire hazard. This project recommends they be removed to reduce the fire hazard. | RANCH SHED | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 4200 | 2020-10-22 | Immediate to Two Years | Currently Critical | 1 | 500
3858EXT2 | ROOF REPLACEMENT | 3858 | The wood shake roof on this building was in fair to poor condition at the time of the survey. Additionally, it is less fire resistant than asphalt shinge systems. It is recommended that this building be re-roofed in the next 4 - 5 years with a new 50 year asphalt composition shingle roof and new underlayment. This estimate includes removal and disposal of the old roof. | SANTA MARGARITA HOUSE | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 1400 | 2020-10-22 | Four to Ten Years | Long-Term Needs | 3 | 19600
3858SFT1 | CARBON MONOXIDE DETECTOR INSTALLATION | 3858 | This building is lacking sufficient carbon monoxide detection systems. 2018 IRC R315, IFC 2018 Section 1103.9 (Carbon Monoxide Detection for Existing Buildings) define requirements in Dwelling Units and Sleeping Units (Group I & R Occupancies) for buildings containing fuel-burning appliances. They shall be installed in dwelling units outside of each separate sleeping area in the immediate vicinity of the bedrooms. The carbon monoxide alarms shall be listed as complying with UL 2034 and be installed and maintained in accordance to the Authority Having Jurisdiction (AHJ), NFPA 720 and the manufacturer’s instructions. This project would provide funding for the purchase and installation of carbon monoxide alarms in accordance with this code and the AHJ. | SANTA MARGARITA HOUSE | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 1400 | 2020-10-22 | Immediate to Two Years | Currently Critical | 1 | 300
3865EXT1 | CONSERVE AND PROTECT VACANT BUILDING | 3865 | Until the planning phase for this site is complete and a determination of demolition or rehabilitation is reached, preservation of the structure is recommended. This project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Also included is securing the exterior envelope against water penetration. Roof, windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. | SHED | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 650 | 2020-10-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16300
3864EXT1 | CONSERVE AND PROTECT VACANT BUILDING | 3864 | Until the planning phase for this site is complete and a determination of demolition or rehabilitation is reached, preservation of the structure is recommended. This project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Also included is securing the exterior envelope against water penetration. Roof, windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. | BARN 3 | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 1400 | 2020-10-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35000
3863EXT1 | CONSERVE AND PROTECT VACANT BUILDING | 3863 | Until the planning phase for this site is complete and a determination of demolition or rehabilitation is reached, preservation of the structure is recommended. This project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Also included is securing the exterior envelope against water penetration. Roof, windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. | BARN 2 | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 1700 | 2020-10-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 42700
3862EXT1 | CONSERVE AND PROTECT VACANT BUILDING | 3862 | Until the planning phase for this site is complete and a determination of demolition or rehabilitation is reached, preservation of the structure is recommended. This project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Also included is securing the exterior envelope against water penetration. Roof, windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. | SCHOOLHOUSE | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 750 | 2020-10-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18800
3861INT1 | INTERIOR FINISHES | 3861 | The interior finishes are in poor condition It is recommended to stain the interior walls and ceilings at least once in the next 2 - 3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to staining, all surfaces should be repaired and adequately prepared to receive the coating. An epoxy-based stain should be utilized in wet areas for durability. | SANTA MARGARITA WELL HOUSE | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 150 | 2020-10-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
3866EXT1 | CONSERVE AND PROTECT VACANT BUILDING | 3866 | Until the planning phase for this site is complete and a determination of demolition or rehabilitation is reached, preservation of the structure is recommended. This project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Also included is securing the exterior envelope against water penetration. Roof, windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. | SHED 2 | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 1000 | 2020-10-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25100
3843INT1 | INTERIOR FINISHES | 3843 | The interior finishes are in poor condition and in need of re-finishing due to water staining. It is recommended that the interior walls and ceilings be painted at least once in the next 2 - 3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | JACUZZI HOUSE | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 144 | 2020-10-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2900
3845INT1 | INTERIOR FINISHES | 3845 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | COLUMBIA HOUSE | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 1600 | 2020-10-22 | Four to Ten Years | Long-Term Needs | 3 | 12800
3845SFT4 | FIRE SUPPRESSION SYSTEM INSTALLATION | 3845 | This building is an R occupancy. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state regardless of occupancy having a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an "R" occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. | COLUMBIA HOUSE | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 1600 | 2020-10-22 | Four to Ten Years | Long-Term Needs | 3 | 28800
3845SFT3 | CARBON MONOXIDE DETECTOR INSTALLATION | 3845 | This building is lacking a carbon monoxide detection system. 2018 IRC R315, IFC 2018 Section 1103.9 (Carbon Monoxide Detection for Existing Buildings) define requirements in Dwelling Units and Sleeping Units (Group I & R Occupancies) for buildings containing fuel-burning appliances. They shall be installed in dwelling units outside of each separate sleeping area in the immediate vicinity of the bedrooms. The carbon monoxide alarms shall be listed as complying with UL 2034 and be installed and maintained in accordance to the Authority Having Jurisdiction (AHJ), NFPA 720 and the manufacturer’s instructions. This project would provide funding for the purchase and installation of carbon monoxide alarms in accordance with this code and the AHJ. | COLUMBIA HOUSE | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 1600 | 2020-10-22 | Immediate to Two Years | Currently Critical | 1 | 300
3845HVA2 | EVAPORATIVE COOLER REPLACEMENT | 3845 | An evaporative cooler is installed on the roof of this building. It is severely scaled and has reached the end of its useful and expected life. This project would provide for a new evaporative cooler to be installed including all required connections to utilities. The estimate includes removal and disposal of the old cooler. | COLUMBIA HOUSE | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 1600 | 2020-10-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
3845HVA1 | HEATER REPLACEMENT | 3845 | The building is heated by one forced air propane-fired heating unit. It is original to the building and is reaching the end of its useful life. This project provides for disposal of the existing unit and replacement with a new propane-fired unit including connections to utilities. | COLUMBIA HOUSE | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 1600 | 2020-10-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
3845ELE1 | GFCI OUTLET INSTALLATION | 3845 | The existing receptacles in the kitchen and bathrooms appear to be standard duplex receptacles and may not be GFCI protected. The 2017 NEC 210.8 requires all locations within 6 feet of a water source, garages & accessory buildings and outdoors shall have GFCI protection. This project would provide for removing the standard receptacles and installing GFCI receptacles. | COLUMBIA HOUSE | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 1600 | 2020-10-22 | Immediate to Two Years | Currently Critical | 1 | 125
3845SFT1 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 3845 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping prior to entering the building. Alternately, for propane services, consider installation at the tank if the tank feeds multiple buildings. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. | COLUMBIA HOUSE | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 1600 | 2020-10-22 | Immediate to Two Years | Currently Critical | 1 | 5000
3845EXT1 | EXTERIOR FINISHES | 3845 | The exterior finishes are in poor condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project recommends work to protect the exterior building envelope other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that the building be painted in the next 3 - 4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | COLUMBIA HOUSE | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 1600 | 2020-10-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16000
3845SFT2 | FIRE EXTINGUISHER INSTALLATION | 3845 | It is recommended that this residence have a fire extinguisher installed due to the distance to the nearest fire station. It shall be provided for the occupant's use. The fire extinguisher type shall be selected and located based on the classes of anticipated fires and on the size and degree of hazard which would affect their use. This project would provide funding for the purchase and installation of 1 fire extinguisher, cabinets, and the hardware necessary to install them. | COLUMBIA HOUSE | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 1600 | 2020-10-22 | Immediate to Two Years | Currently Critical | 1 | 300
3844EXT2 | ROOF REPLACEMENT | 3844 | The wood shake roof on this building was in fair to poor condition at the time of the survey. Additionally, it is less fire resistant than asphalt shinge systems. It is recommended that this building be re-roofed in the next 4 - 5 years with a new 50 year asphalt composition shingle roof and new underlayment. This estimate includes removal and disposal of the old roof. | RAFTERHOUSE BARN | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 1965 | 2300 | 2020-10-22 | Four to Ten Years | Long-Term Needs | 3 | 32200
3844EXT1 | EXTERIOR FINISHES | 3844 | The exterior finishes are in poor condition, especially the exposed beam ends & fascia. It is important to maintain the finish, weather resistance, and appearance of the building. This project recommends work to protect the exterior building envelope other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that the building be painted in the next 3 - 4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | RAFTERHOUSE BARN | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 1965 | 2300 | 2020-10-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18400
3843ENV1 | PEST CONTROL | 3843 | There are numerous signs inside the building of rodent infestation. Due to the potential risk of disease and damage to the building, this project provides for treatment and clean up of the rodent and insects by a licensed pest control business. It is recommended that the building be treated in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain control of the pests. | JACUZZI HOUSE | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 144 | 2020-10-22 | Immediate to Two Years | Currently Critical | 1 | 500
3843EXT3 | ROOF REPLACEMENT | 3843 | The wood shake roof on this building was in fair to poor condition at the time of the survey. Additionally, it is less fire resistant than asphalt shinge systems. It is recommended that this building be re-roofed in the next 4 - 5 years with a new 50 year asphalt composition shingle roof and new underlayment. This estimate includes removal and disposal of the old roof. | JACUZZI HOUSE | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 144 | 2020-10-22 | Four to Ten Years | Long-Term Needs | 3 | 2000
3856SFT2 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 3856 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping prior to entering the building. Alternately, for propane services, consider installation at the tank if the tank feeds multiple buildings. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. | COLOSSAL SHED | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 23000 | 2020-10-22 | Immediate to Two Years | Currently Critical | 1 | 5000
3842EXT3 | ROOF REPLACEMENT | 3842 | The wood shake roof on this building was in fair to poor condition at the time of the survey. Additionally, it is less fire resistant than asphalt shinge systems. It is recommended that this building be re-roofed in the next 4 - 5 years with a new 50 year asphalt composition shingle roof and new underlayment. This estimate includes removal and disposal of the old roof. | RAFTERHOUSE | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 6300 | 2020-10-22 | Four to Ten Years | Long-Term Needs | 3 | 88200
3842SFT4 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 3842 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping prior to entering the building. Alternately, for propane services, consider installation at the tank if the tank feeds multiple buildings. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. | RAFTERHOUSE | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 6300 | 2020-10-22 | Immediate to Two Years | Currently Critical | 1 | 5000
3851INT1 | CONRETE FLOOR REPAIRS | 3851 | The slab on grade concrete floor is damaged and open to below grade where water piping penetrates the floor. The damaged area needs to be repaired to eliminate rodent infestation. This project should be implemented concurrently with the PEST CONTROL and CONRETE FLOOR REPAIRS. | CHICKEN COOP | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 100 | 2020-10-22 | Immediate to Two Years | Currently Critical | 1 | 500
3842SFT5 | FIRE SUPPRESSION SYSTEM INSTALLATION | 3842 | This building is an R occupancy. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state regardless of occupancy having a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an "R" occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. | RAFTERHOUSE | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 6300 | 2020-10-22 | Four to Ten Years | Long-Term Needs | 3 | 113400
3842HVA1 | HVAC EQUIPMENT REPLACEMENT | 3842 | The HVAC gas forced air unit located in the attic has a corroded exhaust plenum raising concerns on the integrity of the internal heat exchanger. It is not energy efficient and has reached the end of its expected and useful life. This project would provide for the installation of a new HVAC split system and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing equipment and all required connections to utilities. | RAFTERHOUSE | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 6300 | 2020-10-22 | Immediate to Two Years | Currently Critical | 1 | 15000
3842ENV1 | PEST CONTROL | 3842 | There are numerous signs outside this building and in the attic of rodent and insect (mostly wasp) infestations. Due to the potential risk of disease and damage to the building, this project provides for treatment and clean up of the rodent and insects by a licensed pest control business. It is recommended that the building be treated in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain control of the pests. | RAFTERHOUSE | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 6300 | 2020-10-22 | Immediate to Two Years | Currently Critical | 1 | 1500
3843EXT1 | EXTERIOR FINISHES | 3843 | The exterior finishes are in good condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project recommends work to protect the exterior building envelope other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that the building be painted in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | JACUZZI HOUSE | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 144 | 2020-10-22 | Four to Ten Years | Long-Term Needs | 3 | 14400
3842STR1 | STRUCTURAL REPAIRS | 3842 | An exterior visual survey of the northern most part of the residence appears to show a wood foundation supporting a portion of the structure. The wood is showing signs of decay. It is recommended that this portion of the structure be shored up and the foundation be replaced with a concrete stemwall foundation. | RAFTERHOUSE | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 6300 | 2020-10-22 | Immediate to Two Years | Currently Critical | 1 | 35000
3843EXT2 | WINDOW GLAZING REPLACEMENT | 3843 | A window glazing panel in the south wall of the structure is broken and needs replacement. This should be done immediately to prevent weather damage to the interior. | JACUZZI HOUSE | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 144 | 2020-10-22 | Immediate to Two Years | Currently Critical | 1 | 500
3842EXT2 | TREE AND SHRUB PRUNING / REMOVAL | 3842 | The building has trees and shrubs which are growing up against the structure. The trees move in windy conditions, rubbing the roofs and exterior walls, which can cause premature failure of the roof system and voiding roof warranties. The root systems can cause shifting and damage to the foundation. This project recommends that these issues be addressed, before additional damage is done. | RAFTERHOUSE | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 6300 | 2020-10-22 | Immediate to Two Years | Currently Critical | 1 | 5000
3842SFT2 | WATER HEATER SEISMIC BRACING | 3842 | The water heater is not properly seismically anchored to the structure and may be missing a drip pan. The 2018 IRC P2801.8 "...water heaters shall be anchored or strapped in the upper one-third and in the lower one-third of the appliance...". This project would provide funding for compliant seismic bracing and installation of a drip pan under the water heater. | RAFTERHOUSE | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 6300 | 2020-10-22 | Immediate to Two Years | Currently Critical | 1 | 1200
3842SFT1 | CARBON MONOXIDE DETECTOR INSTALLATION | 3842 | This building is lacking sufficient carbon monoxide detection systems. 2018 IRC R315, IFC 2018 Section 1103.9 (Carbon Monoxide Detection for Existing Buildings) define requirements in Dwelling Units and Sleeping Units (Group I & R Occupancies) for buildings containing fuel-burning appliances. They shall be installed in dwelling units outside of each separate sleeping area in the immediate vicinity of the bedrooms. The carbon monoxide alarms shall be listed as complying with UL 2034 and be installed and maintained in accordance to the Authority Having Jurisdiction (AHJ), NFPA 720 and the manufacturer’s instructions. This project would provide funding for the purchase and installation of carbon monoxide alarms in accordance with this code and the AHJ. | RAFTERHOUSE | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 6300 | 2020-10-22 | Immediate to Two Years | Currently Critical | 1 | 600
3842EXT1 | EXTERIOR FINISHES | 3842 | The exterior finishes are in fair condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project recommends work to protect the exterior building envelope other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that the building be painted in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | RAFTERHOUSE | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 6300 | 2020-10-22 | Four to Ten Years | Long-Term Needs | 3 | 50400
3842SFT3 | EXTERIOR STAIR REPLACEMENT | 3842 | The two sets of wood stairs that access the porch are deteriorating and are a safety risk. It appears these stairs are original to the building and a replacement is recommended. | RAFTERHOUSE | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 6300 | 2020-10-22 | Immediate to Two Years | Currently Critical | 1 | 1000
3846EXT2 | ROOF REPLACEMENT | 3846 | The wood shake roof on this building was in fair to poor condition at the time of the survey. Additionally, it is less fire resistant than asphalt shinge systems. It is recommended that this building be re-roofed in the next 4 - 5 years with a new 50 year asphalt composition shingle roof and new underlayment. This estimate includes removal and disposal of the old roof. | STONEHOUSE | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 2650 | 2020-10-22 | Four to Ten Years | Long-Term Needs | 3 | 37100
3842ELE1 | GFCI OUTLET INSTALLATION | 3842 | Some of the existing receptacles on the building exterior appear to be standard duplex receptacles and may not be GFCI protected. The 2017 NEC 210.8 requires all locations within 6 feet of a water source, garages & accessory buildings and outdoors shall have GFCI protection. This project would provide for removing the standard receptacles and installing GFCI receptacles. | RAFTERHOUSE | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 6300 | 2020-10-22 | Immediate to Two Years | Currently Critical | 1 | 125
3847INT2 | INTERIOR DOOR REPLACEMENT | 3847 | This project would provide for the installation of new solid core interior door including frame, lever action door handles, hardware and paint. Removal and disposal of the existing door is included in this cost estimate. | STONEHOUSE ANNEX | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 550 | 2020-10-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
3846SFT4 | WATER HEATER SEISMIC BRACING | 3846 | The water heater is not properly seismically anchored to the structure and may be missing a drip pan. The 2018 IRC P2801.8 "...water heaters shall be anchored or strapped in the upper one-third and in the lower one-third of the appliance...". This project would provide funding for compliant seismic bracing and installation of a drip pan under the water heater. | STONEHOUSE | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 2650 | 2020-10-22 | Immediate to Two Years | Currently Critical | 1 | 600
3847EXT4 | EXTERIOR DOOR REPLACEMENT | 3847 | The 2 exterior wood man doors appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement of the wood doors with new metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | STONEHOUSE ANNEX | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 550 | 2020-10-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
3847HVA1 | HEATER REPLACEMENT | 3847 | The building is heated by one wall mounted propane-fired heating unit. It is original to the building and is reaching the end of its useful life. This project provides for disposal of the existing unit and replacement with a new propane-fired unit including connections to utilities. | STONEHOUSE ANNEX | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 550 | 2020-10-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1800
3847SFT1 | CARBON MONOXIDE DETECTOR INSTALLATION | 3847 | This building is lacking a carbon monoxide detection system. 2018 IRC R315, IFC 2018 Section 1103.9 (Carbon Monoxide Detection for Existing Buildings) define requirements in Dwelling Units and Sleeping Units (Group I & R Occupancies) for buildings containing fuel-burning appliances. They shall be installed in dwelling units outside of each separate sleeping area in the immediate vicinity of the bedrooms. The carbon monoxide alarms shall be listed as complying with UL 2034 and be installed and maintained in accordance to the Authority Having Jurisdiction (AHJ), NFPA 720 and the manufacturer’s instructions. This project would provide funding for the purchase and installation of carbon monoxide alarms in accordance with this code and the AHJ. | STONEHOUSE ANNEX | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 550 | 2020-10-22 | Immediate to Two Years | Currently Critical | 1 | 300
3847EXT2 | ROOF REPLACEMENT | 3847 | The wood shake roof on this building was in fair to poor condition at the time of the survey. Additionally, it is less fire resistant than asphalt shinge systems. It is recommended that this building be re-roofed in the next 4 - 5 years with a new 50 year asphalt composition shingle roof and new underlayment. This estimate includes removal and disposal of the old roof. | STONEHOUSE ANNEX | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 550 | 2020-10-22 | Four to Ten Years | Long-Term Needs | 3 | 7700
3847INT4 | RESTROOM REMODEL | 3847 | The restroom in the building was out of service at the time of the survey. It is original to the building and is due for a complete remodel. This project would provide for a complete remodel of the restroom fixtures, hardware, floor and wall finishes. | STONEHOUSE ANNEX | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 550 | 2020-10-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
3847EXT3 | WINDOW REPLACEMENT | 3847 | The windows are original, single pane construction. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. Removal and disposal of the existing windows is included in this estimate. | STONEHOUSE ANNEX | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 550 | 2020-10-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
3847SFT3 | SMOKE DETECTOR INSTALLATION | 3847 | This building is lacking an adequate smoke detection system. 2018 IRC R314, IFC 2018 Section 1103.8 (Single and Mulit-station Smoke Alarms for Existing Buildings) in Occupancy Groups I1 & R Occupancies define requirements for existing buildings. State Fire Marshal NAC 477.915 (3) requires that smoke detectors be connected to the wiring of the building with a battery backup. This project would provide funding for the purchase and installation of listed fire alarms in accordance with this code. | STONEHOUSE ANNEX | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 550 | 2020-10-22 | Immediate to Two Years | Currently Critical | 1 | 300
3848SFT3 | FIRE EXTINGUISHER INSTALLATION | 3848 | It is recommended that this residence have a fire extinguisher installed due to the distance to the nearest fire station. It shall be provided for the occupant's use. The fire extinguisher type shall be selected and located based on the classes of anticipated fires and on the size and degree of hazard which would affect their use. This project would provide funding for the purchase and installation of 1 fire extinguisher, cabinets, and the hardware necessary to install them. | MERINO HOUSE | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 1600 | 2020-10-22 | Immediate to Two Years | Currently Critical | 1 | 300
3848EXT2 | DECK REPLACEMENT | 3848 | The decking material is severely weather damaged, deteriorated and has reached the end of its useful life. This project would provide for the removal and replacement of failed structural members, and decking with new composite decking material. Removal and disposal of the existing decking is included in this estimate. | MERINO HOUSE | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 1600 | 2020-10-22 | Four to Ten Years | Long-Term Needs | 3 | 3000
3848HVA2 | EVAPORATIVE COOLER REPLACEMENT | 3848 | An evaporative cooler is installed on the roof of this building. It is severely scaled and has reached the end of its useful and expected life. This project would provide for a new evaporative cooler to be installed including all required connections to utilities. The estimate includes removal and disposal of the old cooler. | MERINO HOUSE | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 1600 | 2020-10-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
3848HVA1 | HEATER REPLACEMENT | 3848 | The building is heated by one forced air propane-fired heating unit. It is original to the building and is reaching the end of its useful life. This project provides for disposal of the existing unit and replacement with a new propane-fired unit including connections to utilities. | MERINO HOUSE | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 1600 | 2020-10-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
3848SFT1 | FIRE SUPPRESSION SYSTEM INSTALLATION | 3848 | This building is an R occupancy. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state regardless of occupancy having a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an "R" occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. | MERINO HOUSE | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 1600 | 2020-10-22 | Four to Ten Years | Long-Term Needs | 3 | 28800
3848ELE1 | GFCI OUTLET INSTALLATION | 3848 | The existing receptacles in the kitchen and bathrooms appear to be standard duplex receptacles and may not be GFCI protected. The 2017 NEC 210.8 requires all locations within 6 feet of a water source, garages & accessory buildings and outdoors shall have GFCI protection. This project would provide for removing the standard receptacles and installing GFCI receptacles. | MERINO HOUSE | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 1600 | 2020-10-22 | Immediate to Two Years | Currently Critical | 1 | 125
3847SFT2 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 3847 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping prior to entering the building. Alternately, for propane services, consider installation at the tank if the tank feeds multiple buildings. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. | STONEHOUSE ANNEX | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 550 | 2020-10-22 | Immediate to Two Years | Currently Critical | 1 | 5000
3846SFT6 | SEISMIC RETROFIT WALLS | 3846 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current code. Visual analysis during the survey found no indication of seismic strengthening of the URM walls. The walls should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | STONEHOUSE | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 2650 | 2020-10-22 | Four to Ten Years | Long-Term Needs | 3 | 199000
3842INT1 | INTERIOR FINISHES | 3842 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | RAFTERHOUSE | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 6300 | 2020-10-22 | Four to Ten Years | Long-Term Needs | 3 | 31500
3846SFT2 | CARBON MONOXIDE DETECTOR INSTALLATION | 3846 | This building is lacking a carbon monoxide detection system. 2018 IRC R315, IFC 2018 Section 1103.9 (Carbon Monoxide Detection for Existing Buildings) define requirements in Dwelling Units and Sleeping Units (Group I & R Occupancies) for buildings containing fuel-burning appliances. They shall be installed in dwelling units outside of each separate sleeping area in the immediate vicinity of the bedrooms. The carbon monoxide alarms shall be listed as complying with UL 2034 and be installed and maintained in accordance to the Authority Having Jurisdiction (AHJ), NFPA 720 and the manufacturer’s instructions. This project would provide funding for the purchase and installation of carbon monoxide alarms in accordance with this code and the AHJ. | STONEHOUSE | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 2650 | 2020-10-22 | Immediate to Two Years | Currently Critical | 1 | 300
3846SFT1 | FIRE SUPPRESSION SYSTEM INSTALLATION | 3846 | This building is an R occupancy. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state regardless of occupancy having a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an "R" occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. | STONEHOUSE | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 2650 | 2020-10-22 | Four to Ten Years | Long-Term Needs | 3 | 47700
3846SFT8 | GUARDRAIL INSTALLATION | 3846 | It appears that a guardrail is required to be installed on the top of the masonry wall at the southeast corner of the residence. The height at which a guardrail is required is 30" per IRC 2018 R312.1.1 Where Required: "Guards shall be provided for those portions of open-sided walking surfaces, including stairs, ramps and landings, that are located more than 30 inches (762 mm) measured vertically to the floor or grade below..." This project would provide for the purchase and installation of new guardrails. | STONEHOUSE | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 2650 | 2020-10-22 | Immediate to Two Years | Currently Critical | 1 | 2500
3846EXT1 | EXTERIOR FINISHES | 3846 | The exterior finishes are in poor condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project recommends work to protect the exterior building envelope other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that the building be painted in the next 2 - 3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | STONEHOUSE | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 2650 | 2020-10-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 21200
3847INT3 | FLOORING REPLACEMENT | 3847 | The vinyl and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new linoleum with a 6" base and heavy duty commercial grade carpet in the next 2-3 years. | STONEHOUSE ANNEX | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 550 | 2020-10-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6100
3846SFT5 | SEISMIC RETROFIT ROOF STRUCTURE | 3846 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current codes. Visual analysis during the survey found no indication of seismic strengthening of the roof structure. The roof structure should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | STONEHOUSE | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 2650 | 2020-10-22 | Four to Ten Years | Long-Term Needs | 3 | 124600
3846SFT3 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 3846 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping prior to entering the building. Alternately, for propane services, consider installation at the tank if the tank feeds multiple buildings. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. | STONEHOUSE | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 2650 | 2020-10-22 | Immediate to Two Years | Currently Critical | 1 | 5000
3846SFT7 | FIRE EXTINGUISHER INSTALLATION | 3846 | It is recommended that this residence have a fire extinguisher installed due to the distance to the nearest fire station. It shall be provided for the occupant's use. The fire extinguisher type shall be selected and located based on the classes of anticipated fires and on the size and degree of hazard which would affect their use. This project would provide funding for the purchase and installation of 1 fire extinguisher, cabinets, and the hardware necessary to install them. | STONEHOUSE | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 2650 | 2020-10-22 | Immediate to Two Years | Currently Critical | 1 | 300
3846INT1 | INTERIOR FINISHES | 3846 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | STONEHOUSE | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 2650 | 2020-10-22 | Four to Ten Years | Long-Term Needs | 3 | 13300
3847ELE1 | GFCI OUTLET INSTALLATION | 3847 | The existing receptacles in the kitchen and some bathrooms are standard duplex receptacles and may not be GFCI protected. The 2017 NEC 210.8 requires all locations within 6 feet of a water source, garages & accessory buildings and outdoors shall have GFCI protection. This project would provide for removing the standard receptacles and installing GFCI receptacles. | STONEHOUSE ANNEX | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 550 | 2020-10-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 125
3847EXT1 | EXTERIOR FINISHES | 3847 | The exterior finishes are in poor condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project recommends work to protect the exterior building envelope other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that the building be painted in the next 2 - 3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | STONEHOUSE ANNEX | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 550 | 2020-10-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5500
3847INT1 | INTERIOR FINISHES | 3847 | The interior finishes are in poor condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2 - 3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | STONEHOUSE ANNEX | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 550 | 2020-10-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2750
3847INT5 | KITCHEN REMODEL | 3847 | The small kitchenette is in poor condition. The cabinets and equipment are showing signs of general wear and tear and are approaching the end of their expected life. This project recommends the refurbishment / replacement of the existing kitchen cabinets, countertops, fixtures and equipment with mid range, high quality components. | STONEHOUSE ANNEX | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 550 | 2020-10-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
3846EXT3 | TREE AND SHRUB PRUNING / REMOVAL | 3846 | The building has trees and shrubs which are growing up against the structure. The trees move in windy conditions, rubbing the roofs and exterior walls, which can cause premature failure of the roof system and voiding roof warranties. Additionally, on the north side of the house, a tree is growing up against the wall that needs removal. The root systems can cause shifting and damage to the foundation. This project recommends that these issues be addressed, before additional damage is done. | STONEHOUSE | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 2650 | 2020-10-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
3854EXT1 | EXTERIOR FINISHES | 3854 | The exterior finishes are in poor condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project recommends work to protect the exterior building envelope other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that the building be painted in the next 2 - 3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | PUMP HOUSE #2 | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 350 | 2020-10-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1800
3852EXT1 | DEMOLISH STRUCTURE | 3852 | The structure is delapidated, deteriorating and is a safety concern. It has reached the end of its useful life. This project would provide funding for the demolition and disposal of the building. | ROOST | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 520 | 2020-10-22 | Immediate to Two Years | Currently Critical | 1 | 6500
3842EXT4 | EXTERIOR DOOR REPLACEMENT | 3842 | The exterior french doors are damaged do not seal properly and have reached the end of their expected life. This project would provide for the replacement of the door assembly with new metal doors, frames and hardware. Removal and disposal of the existing doors is included in this estimate. | RAFTERHOUSE | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 6300 | 2020-10-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
3853EXT4 | EXTERIOR DOOR REPLACEMENT | 3853 | The 2 exterior wood man doors appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement of the wood doors with new metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | PUMP HOUSE | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 350 | 2020-10-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
3853ELE1 | GFCI OUTLET INSTALLATION | 3853 | The existing receptacles in the pump house are standard duplex receptacles and may not be GFCI protected. The 2017 NEC 210.8 requires all locations within 6 feet of a water source, garages & accessory buildings and outdoors shall have GFCI protection. This project would provide for removing the standard receptacles and installing GFCI receptacles. | PUMP HOUSE | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 350 | 2020-10-22 | Immediate to Two Years | Currently Critical | 1 | 75
3853PLM1 | PLUMBING REPLACEMENT | 3853 | The existing galvanized piping system in the building is failing in numerous areas and the leaks are causing damage to the building. This project would provide for saw excavation and installation of a new water line lines in the building. This project includes removal of the existing piping and fittings as required. This project should be implemented concurrently with the GYPSUM BOARD REPAIR. | PUMP HOUSE | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 350 | 2020-10-22 | Immediate to Two Years | Currently Critical | 1 | 1500
3853EXT2 | TREE AND SHRUB PRUNING / REMOVAL | 3853 | The building has trees with dead branches overhanging the structure. Additionally, there is organic debris and weeds surrounding the structure that need to be removed to reduce fire hazards and allow proper clearance to the bottom of wood siding. The trees move in windy conditions, rubbing the roofs and exterior walls, which can cause premature failure of the roof system and voiding roof warranties. This project recommends that these issues be addressed, before additional damage is done. | PUMP HOUSE | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 350 | 2020-10-22 | Immediate to Two Years | Currently Critical | 1 | 500
3853INT2 | GYPSUM BOARD REPAIR | 3853 | Water leaks and moisture has damaged the gypsum board in the pump house. The gypsum board must be replaced. This project recommends removing the gypsum board, inspecting for any structural damage and replacing it with green board and repainting the walls. This project should be implemented concurrently with the PLUMBING REPLACEMENT. | PUMP HOUSE | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 350 | 2020-10-22 | Immediate to Two Years | Currently Critical | 1 | 1500
3853EXT1 | EXTERIOR FINISHES | 3853 | The exterior finishes are in poor condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project recommends work to protect the exterior building envelope other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that the building be painted in the next 2 - 3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | PUMP HOUSE | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 350 | 2020-10-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1800
3853INT1 | INTERIOR FINISHES | 3853 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | PUMP HOUSE | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 350 | 2020-10-22 | Four to Ten Years | Long-Term Needs | 3 | 1800
3854ELE1 | GFCI OUTLET INSTALLATION | 3854 | The existing receptacles in the pump house are standard duplex receptacles and may not be GFCI protected. The 2017 NEC 210.8 requires all locations within 6 feet of a water source, garages & accessory buildings and outdoors shall have GFCI protection. This project would provide for removing the standard receptacles and installing GFCI receptacles. | PUMP HOUSE #2 | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 350 | 2020-10-22 | Immediate to Two Years | Currently Critical | 1 | 100
3851EXT2 | EXTERIOR FINISHES | 3851 | The exterior finishes are in good condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project recommends work to protect the exterior building envelope other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that the building be painted in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CHICKEN COOP | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 100 | 2020-10-22 | Four to Ten Years | Long-Term Needs | 3 | 1000
3854SIT1 | DRAINAGE UPGRADES | 3854 | The pump house siding has considerable damage to the siding from soil contact around the building. The grade does not slope away from the building in several areas, especially on the south and west side of the building. This project would create positive flow away from the building by regrading. | PUMP HOUSE #2 | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 350 | 2020-10-22 | Immediate to Two Years | Currently Critical | 1 | 1500
3851EXT1 | EXTERIOR SIDING REPLACEMENT | 3851 | The structure has painted T1-11 siding that is damaged and those damaged areas need to be replaced to eliminate rodent infestation. This project recommends replacing the damaged siding and repaint. This project should be implemented concurrently with the PEST CONTROL and CONRETE FLOOR REPAIRS. | CHICKEN COOP | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 100 | 2020-10-22 | Immediate to Two Years | Currently Critical | 1 | 500
3855EXT1 | EXTERIOR FINISHES | 3855 | The exterior finishes are in poor condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project recommends work to protect the exterior building envelope other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that the building be painted in the next 2 - 3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SILO | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 250 | 2020-10-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
3856SFT3 | WATER HEATER SEISMIC BRACING | 3856 | The water heater is not properly seismically anchored to the structure and is missing a drip pan. The 2018 IRC P2801.8 "...water heaters shall be anchored or strapped in the upper one-third and in the lower one-third of the appliance...". This project would provide funding for the installation of compliant seismic bracing and installation of a drip pan under the water heater. | COLOSSAL SHED | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 23000 | 2020-10-22 | Immediate to Two Years | Currently Critical | 1 | 600
3856ELE1 | TASK LIGHTING UPGRADE | 3856 | The existing task lighting fixtures over the workbench in the shop are the older T-12 fluorescent type, and are not energy efficient. This project will replace the T-12 fixtures with LED strip fixtures, resulting in increased efficiency and improved lighting quality. Any electrical wiring upgrades are not included in this estimate. | COLOSSAL SHED | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 23000 | 2020-10-22 | Four to Ten Years | Long-Term Needs | 3 | 250
3856EXT4 | OVERHEAD DOOR REPLACEMENT | 3856 | There is a 14'x20' overhead coiling door on the south side which is damaged and does not function properly. It is original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead coiling door and replacement with a new overhead coiling door. | COLOSSAL SHED | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 23000 | 2020-10-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
3856ADA2 | ADA RESTROOM UPGRADE | 3856 | The building does not have accessible restrooms and the existing restrooms do not meet the ADA requirements. A complete retrofit is necessary. Typically, ADA does not apply to Group U occupancies, however, an exception exists in 2018 IBC 1103.2.4 #1: "In agricultural buildings, access is required to paved work areas and areas open to the general public." This project would provide funding to upgrade the existing restrooms to accessible restrooms. Items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2018 IBC, ICC/ANSI A117.1, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as a reference for this project. | COLOSSAL SHED | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 23000 | 2020-10-22 | Immediate to Two Years | Currently Critical | 1 | 31100
3856ADA1 | ADA PARKING SPACE | 3856 | The ADA provides for accessibility to sites and services for people with physical limitations. Typically, ADA does not apply to Group U occupancies, however, an exception exists in 2018 IBC 1103.2.4 #1: "In agricultural buildings, access is required to paved work areas and areas open to the general public." A concrete parking area and passenger loading area are necessary to comply with ADA requirements. This project would provide for a concrete van accessible ADA parking and loading space and walkway to the existing sidewalk. This will require regrading, installing concrete, striping, signage and any other necessary upgrades. The 2018 IBC, ICC/ANSI A117.1, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as a reference for this project. | COLOSSAL SHED | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 23000 | 2020-10-22 | Immediate to Two Years | Currently Critical | 1 | 10000
3856EXT3 | ROOF REPLACEMENT | 3856 | The wood shake roof on the building awning was in fair to poor condition at the time of the survey. Additionally, it is less fire resistant than asphalt shinge systems. It is recommended that this building be re-roofed in the next 4 - 5 years with a new 50 year asphalt composition shingle roof and new underlayment. This estimate includes removal and disposal of the old roof. | COLOSSAL SHED | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 23000 | 2020-10-22 | Four to Ten Years | Long-Term Needs | 3 | 8800
3856SFT1 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 3856 | The emergency egress lighting is insufficient and some exit signs are broken. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC 2018 Chapter 10 was referenced for this project. | COLOSSAL SHED | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 23000 | 2020-10-22 | Immediate to Two Years | Currently Critical | 1 | 11500
3856EXT1 | EXTERIOR FINISHES | 3856 | The painted wood awning finishes are in good condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project recommends work to protect the exterior building envelope other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that the building be painted in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | COLOSSAL SHED | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 23000 | 2020-10-22 | Four to Ten Years | Long-Term Needs | 3 | 11500
3856INT1 | INTERIOR FINISHES | 3856 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | COLOSSAL SHED | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 23000 | 2020-10-22 | Four to Ten Years | Long-Term Needs | 3 | 46000
3856EXT2 | VEGETATION REMOVAL | 3856 | The building has weeds and organic vegetation which are growing up against the structure and are a fire hazard. This project recommends they be removed to reduce the fire hazard. | COLOSSAL SHED | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 23000 | 2020-10-22 | Immediate to Two Years | Currently Critical | 1 | 500
3854EXT2 | ROOF REPLACEMENT | 3854 | The wood shake roof on this building was in poor condition at the time of the survey. Additionally, it is less fire resistant than asphalt shinge systems. It is recommended that this building be re-roofed in the next 3 - 4 years with a new 50 year asphalt composition shingle roof and new underlayment. This estimate includes removal and disposal of the old roof. | PUMP HOUSE #2 | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 350 | 2020-10-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4900
3848SFT2 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 3848 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping prior to entering the building. Alternately, for propane services, consider installation at the tank if the tank feeds multiple buildings. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. | MERINO HOUSE | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 1600 | 2020-10-22 | Immediate to Two Years | Currently Critical | 1 | 5000
3849INT1 | INTERIOR FINISHES | 3849 | The interior finishes are in fair condition. The non-finished interior of the shed is excluded from this project. It is recommended that the interior walls and ceilings be painted at least once in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | MERINO SHED | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 2700 | 2020-10-22 | Four to Ten Years | Long-Term Needs | 3 | 8100
9784SFT0 | COMBUSTIBLES REDUCTION FOR FIRE CONTROL | 9784 | The site and certain buildings have significant weed and debris buildup and are a fuel source for fire. Accumulated leaves at the base of structures create a significant fuel path to structure fires during wild land fire events. This project would provide for the removal and disposal of the weeds and debris around all structures on the site. Further site and structure enhancements to increase fire protection can be found on the Nevada State Fire Marshal's website. | WALKER RIVER SRA - RAFTER 7 RANCH SITE | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 2018 |  | 2020-10-22 | Immediate to Two Years | Currently Critical | 1 | 5000
3848INT1 | INTERIOR FINISHES | 3848 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | MERINO HOUSE | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 1600 | 2020-10-22 | Four to Ten Years | Long-Term Needs | 3 | 12800
3849EXT1 | EXTERIOR FINISHES | 3849 | The exterior painted finishes are in poor condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project recommends work to protect the exterior building envelope other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that the building be painted in the next 2 - 3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MERINO SHED | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 2700 | 2020-10-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 21600
3848EXT1 | EXTERIOR FINISHES | 3848 | The exterior finishes are in fair condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project recommends work to protect the exterior building envelope other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that the building be painted in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MERINO HOUSE | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 1600 | 2020-10-22 | Four to Ten Years | Long-Term Needs | 3 | 16000
3849EXT2 | ROOF REPLACEMENT | 3849 | The corrugated metal roof on this building was in fair condition at the time of the survey. It is recommended that this building be re-roofed in the next 8 - 10 years with a standing seam metal roofing system. This estimate includes removal and disposal of the old roofing system. | MERINO SHED | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 2700 | 2020-10-22 | Four to Ten Years | Long-Term Needs | 3 | 48600
4082EXT1 | EXTERIOR FINISHES | 4082 | The exterior of the buidling is in poor condition. It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2 - 3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SHED 4 | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 300 | 2020-10-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2400
4081EXT1 | DEMOLISH STRUCTURE | 4081 | The structure is a shed set on a wood foundation that is no longer in use. A visual survey of the structure shows significant deterioration of the wood foundation, roofing, door and interior and exterior finishes. It is recommended that this structure be demolished due to safety concerns and cost of refurbishment. | SATELLITE COMM HUT (abandoned) | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 80 | 2020-10-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
3853EXT3 | ROOF REPLACEMENT | 3853 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 3-4 years with a new 50 year asphalt composition roofing shingle and new underlayment. This estimate includes removal and disposal of the old roofing system. | PUMP HOUSE | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 350 | 2020-10-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4900
3850EXT1 | DEMOLISH STRUCTURE | 3850 | The structure is delapidated, deteriorating and is a safety concern. It has reached the end of its useful life. This project would provide funding for the demolition and disposal of the building. | DORMITORY | 9784 | CNR | Parks |  | Walker River SRA/Rafter 7 | 0 | 1800 | 2020-10-22 | Immediate to Two Years | Currently Critical | 1 | 22600
3869SFT3 | CARBON MONOXIDE DETECTOR INSTALLATION | 3869 | This building is lacking a carbon monoxide detection system. 2018 IRC R315, IFC 2018 Section 1103.9 (Carbon Monoxide Detection for Existing Buildings) define requirements in Dwelling Units and Sleeping Units (Group I & R Occupancies) for buildings containing fuel-burning appliances. They shall be installed in dwelling units outside of each separate sleeping area in the immediate vicinity of the bedrooms. The carbon monoxide alarms shall be listed as complying with UL 2034 and be installed and maintained in accordance to the Authority Having Jurisdiction (AHJ), NFPA 720 and the manufacturer’s instructions. This project would provide funding for the purchase and installation of carbon monoxide alarms in accordance with this code and the AHJ. | LEWIS RESIDENCE | 9783 | CNR | Parks |  | Walker River SRA/Flying M | 1930 | 2000 | 2020-12-15 | Immediate to Two Years | Currently Critical | 1 | 300
3869SFT2 | FIRE SUPPRESSION SYSTEM INSTALLATION | 3869 | This building is an R occupancy. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state regardless of occupancy having a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an "R" occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. | LEWIS RESIDENCE | 9783 | CNR | Parks |  | Walker River SRA/Flying M | 1930 | 2000 | 2020-12-15 | Four to Ten Years | Long-Term Needs | 3 | 0
3869EXT2 | ROOF REPLACEMENT | 3869 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayment. This estimate includes removal and disposal of the old roofing system. | LEWIS RESIDENCE | 9783 | CNR | Parks |  | Walker River SRA/Flying M | 1930 | 2000 | 2020-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 28000
3869INT1 | INTERIOR FINISHES | 3869 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | LEWIS RESIDENCE | 9783 | CNR | Parks |  | Walker River SRA/Flying M | 1930 | 2000 | 2020-12-15 | Four to Ten Years | Long-Term Needs | 3 | 16000
3870ELE1 | GFCI OUTLET INSTALLATION | 3870 | The existing receptacles in the barn appear to be standard duplex receptacles and may not be GFCI protected. The 2017 NEC 210.8 requires all locations within 6 feet of a water source, garages & accessory buildings and outdoors shall have GFCI protection. This project would provide for removing the standard receptacles and installing GFCI receptacles. | LEWIS BARN | 9783 | CNR | Parks |  | Walker River SRA/Flying M | 0 | 2200 | 2020-12-15 | Immediate to Two Years | Currently Critical | 1 | 100
3869EXT1 | EXTERIOR FINISHES | 3869 | The exterior finishes, expecially the exposed painted wood surfaces are in poor condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project recommends work to protect the exterior building envelope other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that the building be painted in the next 3 - 4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | LEWIS RESIDENCE | 9783 | CNR | Parks |  | Walker River SRA/Flying M | 1930 | 2000 | 2020-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
3869SFT1 | FIRE EXTINGUISHER INSTALLATION | 3869 | It is recommended that this residence have a fire extinguisher installed due to the distance to the nearest fire station. It shall be provided for the occupant's use. The fire extinguisher type shall be selected and located based on the classes of anticipated fires and on the size and degree of hazard which would affect their use. This project would provide funding for the purchase and installation of 1 fire extinguisher, cabinets, and the hardware necessary to install them. | LEWIS RESIDENCE | 9783 | CNR | Parks |  | Walker River SRA/Flying M | 1930 | 2000 | 2020-12-15 | Immediate to Two Years | Currently Critical | 1 | 300
1896EXT1 | REPAIR / REPLACE DOORS & GLAZING | 1896 | Per 2003 IBC 2406.3, safety glass is required when a fixed window is located within two feet of the door. This project recommends replacement of the two windows on the south side and one on the west side with safety glazing. The doors in the building have damaged or missing hardware. This project would replace the door hardware on all of the doors. The wall and overhead door in the gymnasium area have been damaged. The extent of the damage within the wall is not known. The door should be replaced and the wall framing members should be exposed to inspect and repair as necessary. This project or a portion there of was previously recommended in the FCA report dated 5/4/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 8/17/2006. | MULTI-PURPOSE BUILDING (VACANT) | 9986 | Correct | SSCC |  | Silver Springs | 1991 | 8170 | 2006-08-17 | Immediate to Two Years | Currently Critical | 1 | 17000
1895EXT1 | DOOR AND WINDOW MODIFICATIONS | 1895 | The exterior door to the loading dock is too small for the use intended; it is a single three-foot-wide door. A set of double doors will provide easier access to transport freight into the storage area. This project would provide for a new 6'-0"x7'-0" set of doors including frame, painting and hardware. Modifications to the structure are included in this estimate. Two windows in the dining area have seals broken and moisture stains, which makes visibility difficult. The broken seal reduces the insulation factor of these windows. New replacements are recommended. These are located on the east side. This project or a portion there of was previously recommended in the FCA report dated 5/4/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 8/17/2006. | CULINARY/DINING (VACANT) | 9986 | Correct | SSCC |  | Silver Springs | 1991 | 4150 | 2006-08-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
1895ADA1 | ADA SIGNAGE | 1895 | The ADA has established signage criteria for all permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with these criteria and should be replaced. This project or a portion there of was previously recommended in the FCA report dated 5/4/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 8/17/2006. | CULINARY/DINING (VACANT) | 9986 | Correct | SSCC |  | Silver Springs | 1991 | 4150 | 2006-08-17 | Immediate to Two Years | Currently Critical | 1 | 12349.698
1895ELE1 | LIGHTING UPGRADE | 1895 | Existing building lighting fixtures, T-12s, are older fluorescent type and are not energy efficient. This project will upgrade lighting fixtures to T-8s, with electronic ballasts resulting in increased efficiency and reduced costs associated with illumination. | CULINARY/DINING (VACANT) | 9986 | Correct | SSCC |  | Silver Springs | 1991 | 4150 | 2006-08-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14525
1895EXT2 | EXTERIOR FINISHES | 1895 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. This building is a metal sided building and required mostly caulking and sealing of doors windows, penetrations, etc. This project should be done on an as needed basis with at least a once a year inspection of the exterior with special attention paid to the south and west sides of the structure. This estimate is for a one time complete exterior inspection, caulk and seal which may be used for future operating budget requests by the using agency. This project or a portion there of was previously recommended in the FCA report dated 5/4/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 8/17/2006. | CULINARY/DINING (VACANT) | 9986 | Correct | SSCC |  | Silver Springs | 1991 | 4150 | 2006-08-17 | Four to Ten Years | Long-Term Needs | 3 | 6225
1895INT2 | INTERIOR FINISHES | 1895 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next four to six years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This structure should be painted every five to seven years to maintain it's integrity. This project or a portion there of was previously recommended in the FCA report dated 5/4/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 8/17/2006. | CULINARY/DINING (VACANT) | 9986 | Correct | SSCC |  | Silver Springs | 1991 | 4150 | 2006-08-17 | Four to Ten Years | Long-Term Needs | 3 | 20750
1895HVA1 | TYPE 2 HOOD INSTALLATION FOR DISHWASHER | 1895 | The Uniform Mechanical Code, Section 508.1, requires exhaust hoods be installed above commercial grade dishwashing machines. This dishwasher does not have an exhaust hood. This project would provide for the installation of a Type II exhaust hood to be mounted over the dishwasher including all required ducting to the roof, cutting the roof penetration and sealing of all roof penetrations. Connections to utility systems is also included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 5/4/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 8/17/2006. | CULINARY/DINING (VACANT) | 9986 | Correct | SSCC |  | Silver Springs | 1991 | 4150 | 2006-08-17 | Immediate to Two Years | Currently Critical | 1 | 18500
1896INT3 | INTERIOR FINISHES | 1896 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next four to six years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This structure should be painted every five to seven years to maintain it's integrity. | MULTI-PURPOSE BUILDING (VACANT) | 9986 | Correct | SSCC |  | Silver Springs | 1991 | 8170 | 2006-08-17 | Four to Ten Years | Long-Term Needs | 3 | 24510
1896INT1 | LAUNDRY ROOM REMODEL | 1896 | The laundry room is not vented and an exhaust fan should be installed. Combustion-air ducts are needed for the laundry room from the exterior of the building. There is some damage to the gypsum board from moisture and this project includes funds for repair of the gypsum board and installation of FRP on the walls adjacent to the washers and dryers. This project or a portion there of was previously recommended in the FCA report dated 5/4/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 8/17/2006. | MULTI-PURPOSE BUILDING (VACANT) | 9986 | Correct | SSCC |  | Silver Springs | 1991 | 8170 | 2006-08-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12500
1896PLM1 | REPLACE WATER HEATERS | 1896 | The existing water heaters are old and have reached the end of their expected life. This project would provide for the removal, disposal, and replacement of two 25 gallon gas fired water heaters including all required connections to utilities. | MULTI-PURPOSE BUILDING (VACANT) | 9986 | Correct | SSCC |  | Silver Springs | 1991 | 8170 | 2006-08-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2400
1896ADA1 | ADA / RESTROOM REMODEL PROJECT | 1896 | The Americans With Disabilities Act (ADA) requires complying drinking fountains in the building. An estimate for an ADA compliant drinking fountain is included with this project. ADA legislation pertaining to building access has established signage criteria for all permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with these criteria. This project provides funds for ADA signage. The water closet and lavatories in the restroom adjacent to the gym are worn from years of use. It is recommended that the fixtures in all the bathrooms be replaced. This estimate includes the removal and replacement of the toilet and two sinks including faucets. This project or a portion there of was previously recommended in the FCA report dated 5/4/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 8/17/2006. | MULTI-PURPOSE BUILDING (VACANT) | 9986 | Correct | SSCC |  | Silver Springs | 1991 | 8170 | 2006-08-17 | Immediate to Two Years | Currently Critical | 1 | 15000
1896ELE1 | LIGHTING UPGRADE | 1896 | Existing building lighting fixtures, T-12s, are older fluorescent type and are not energy efficient. This project will upgrade lighting fixtures to T-8s, with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. This project or a portion there of was previously recommended in the FCA report dated 5/4/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 8/17/2006. | MULTI-PURPOSE BUILDING (VACANT) | 9986 | Correct | SSCC |  | Silver Springs | 1991 | 8170 | 2006-08-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 28595
2029INT1 | INTERIOR FINISHES | 2029 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next four to six years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This structure should be painted every five to seven years to maintain it's integrity. | GENERATOR BUILDING (VACANT) | 9986 | Correct | SSCC |  | Silver Springs | 1991 | 725 | 2006-08-17 | Four to Ten Years | Long-Term Needs | 3 | 3625
2029EXT1 | EXTERIOR FINISHES | 2029 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. This structure should be painted every five to seven years to maintain it's integrity. | GENERATOR BUILDING (VACANT) | 9986 | Correct | SSCC |  | Silver Springs | 1991 | 725 | 2006-08-17 | Four to Ten Years | Long-Term Needs | 3 | 3625
1896EXT2 | EXTERIOR FINISHES | 1896 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. This building is a metal sided building and required mostly caulking and sealing of doors windows, penetrations, etc. This project should be done on an as needed basis with at least a once a year inspection of the exterior with special attention paid to the south and west sides of the structure. This estimate is for a one time complete exterior inspection, caulk and seal which may be used for future operating budget requests by the using agency. This project or a portion there of was previously recommended in the FCA report dated 5/4/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 8/17/2006. | MULTI-PURPOSE BUILDING (VACANT) | 9986 | Correct | SSCC |  | Silver Springs | 1991 | 8170 | 2006-08-17 | Four to Ten Years | Long-Term Needs | 3 | 12255
1352INT1 | INTERIOR FINISHES | 1352 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next four to six years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA report dated 5/4/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 8/17/2006. | WELL HOUSE (VACANT) | 9986 | Correct | SSCC |  | Silver Springs | 1991 | 168 | 2006-08-17 | Four to Ten Years | Long-Term Needs | 3 | 840
1352EXT1 | EXTERIOR FINISHES | 1352 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. This project or a portion there of was previously recommended in the FCA report dated 5/4/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 8/17/2006. | WELL HOUSE (VACANT) | 9986 | Correct | SSCC |  | Silver Springs | 1991 | 168 | 2006-08-17 | Four to Ten Years | Long-Term Needs | 3 | 1680
1896STR1 | STRUCTURAL ASSESSMENT | 1896 | An upper level storage mezzanine has been constructed inside of the Building. The 2003 IBC has a minimum requirement of 125p.s.f. for light storage in non-residential spaces. There is no record of a CIP project or structural plans for this construction and it could be a potential safety issue due to collapse. This project recommends that a licensed engineer perform a structural investigation to assess the load carrying capacity of this area. Future projects would be based on this report. | MULTI-PURPOSE BUILDING (VACANT) | 9986 | Correct | SSCC |  | Silver Springs | 1991 | 8170 | 2006-08-17 | Immediate to Two Years | Currently Critical | 1 | 5000
2690EXT1 | EXTERIOR FINISHES | 2690 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior of the water tank, other than the roof, including painting, staining, or other applied finishes, and caulking penetrations to maintain the building in good, weather tight condition. This structure should be painted every five to seven years to maintain it's integrity. | WATER TOWER | 9986 | Correct | SSCC |  | Silver Springs | 0 | 1134 | 2006-08-17 | Four to Ten Years | Long-Term Needs | 3 | 10000
2689EXT1 | EXTERIOR FINISHES | 2689 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. This structure should be painted every five to seven years to maintain it's integrity. | TOOL SHED (VACANT) | 9986 | Correct | SSCC |  | Silver Springs | 0 | 120 | 2006-08-17 | Four to Ten Years | Long-Term Needs | 3 | 600
9986SFT1 | INSTALL SEISMIC GAS SHUT OFF VALVE | 9986 | Agreements reached between the Nevada Risk Management Office and the State of Nevada's Insurance Underwriter require Seismic Gas Shutoff Valves (SGSV's) on all gas services to all State buildings. This project would install a SGSV to the gas main line serving the buildings on site. | SILVER SPRINGS CONSERVATION CAMP SITE | 9986 | Correct | SSCC |  | Silver Springs | 1991 |  | 2006-08-17 | Immediate to Two Years | Currently Critical | 1 | 4500
0711SFT2 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0711 | The existing exit signs in this building are older types and should be replaced with new self-illuminated or LED style signs with battery-backed internal systems. Emergency exit lighting should be installed and/or replaced to provide illumination along the egress route. This project or a portion there of was previously recommended in the FCA report dated 5/4/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 8/17/2006. | HOUSING UNIT (VACANT) | 9986 | Correct | SSCC |  | Silver Springs | 1991 | 11242 | 2006-08-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 22484
0711EXT1 | EXTERIOR FINISHES | 0711 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. This structure should be painted every five to seven years to maintain it's integrity. This project or a portion there of was previously recommended in the FCA report dated 5/4/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 8/17/2006. | HOUSING UNIT (VACANT) | 9986 | Correct | SSCC |  | Silver Springs | 1991 | 11242 | 2006-08-17 | Four to Ten Years | Long-Term Needs | 3 | 56210
0711INT2 | INTERIOR FINISHES | 0711 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next four to six years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This structure should be painted every five to seven years to maintain it's integrity. This project or a portion there of was previously recommended in the FCA report dated 5/4/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 8/17/2006. | HOUSING UNIT (VACANT) | 9986 | Correct | SSCC |  | Silver Springs | 1991 | 11242 | 2006-08-17 | Four to Ten Years | Long-Term Needs | 3 | 56210
0711ADA1 | ADA PROJECTS | 0711 | ADA legislation pertaining to building access has established signage criteria for all permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with these criteria and should be installed. No accessible shower stall is present in the inmate housing area. ADA accessibility to at least one shower stall is recommended. Removing two existing showers and adding one accessible would be the most cost effective in one of the housing wings. Plumbing modifications are included in this estimate. The same situation exists in the toilet rooms; an accessible toilet is required in each wing. It is recommended to remove two existing toilet stalls and add one accessible stall. Plumbing modifications are included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 5/4/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 8/17/2006. | HOUSING UNIT (VACANT) | 9986 | Correct | SSCC |  | Silver Springs | 1991 | 11242 | 2006-08-17 | Immediate to Two Years | Currently Critical | 1 | 60000
0711HVA2 | BOILER REPLACEMENT | 0711 | There are 4 existing gas fired boilers which provide heat for the entire building. They were installed in 1991 and are original to the housing unit. The life expectancy of these units is 20 to 25 years with proper maintenance and water treatment programs. This project would provide for the removal and replacement of the 4 boilers with 4 new 765 MBH gas fired boilers. This project should be requested in a CIP in about 8 to 10 years. This project does not address any piping replacement, only connections to existing systems. | HOUSING UNIT (VACANT) | 9986 | Correct | SSCC |  | Silver Springs | 1991 | 11242 | 2006-08-17 | Four to Ten Years | Long-Term Needs | 3 | 68000
0711ELE1 | LIGHTING UPGRADE | 0711 | Existing building lighting fixtures, T-12s, are older fluorescent type and are not energy efficient. This project will upgrade lighting fixtures to T-8s, with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. This project or a portion there of was previously recommended in the FCA report dated 5/4/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 8/17/2006. | HOUSING UNIT (VACANT) | 9986 | Correct | SSCC |  | Silver Springs | 1991 | 11242 | 2006-08-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 39347
0711HVA1 | REPLACE BATHROOM EXHAUST FANS | 0711 | The exhaust fans in the shower room and bathrooms do not operate properly or do not work at all. This project would provide for the removal and replacement of the exhaust fans including connections to existing utilities. This project or a portion there of was previously recommended in the FCA report dated 5/4/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 8/17/2006. | HOUSING UNIT (VACANT) | 9986 | Correct | SSCC |  | Silver Springs | 1991 | 11242 | 2006-08-17 | Immediate to Two Years | Currently Critical | 1 | 9000
0711INT1 | BATHROOM AND SHOWER ROOM RENOVATION | 0711 | The countertops in the restrooms and shower rooms in each wing show signs of wear, deterioration and are damaged. There are three wings with restrooms. Extensive use, combined with repetitive water being spilled, has caused the laminate top to separate from the wooden underlayment and should be replaced. A problem exists with the drain system in the shower rooms. The drains clog frequently, possibly due to improper installation or debris. Because the floor is a concrete slab, the work to repair this problem is extensive. This portion of the project provides for an inspection of the waste lines with a video camera to determine the extent of the problem. Future projects may result from the findings and are not included in this estimate. This project also includes remodeling of the existing showers, with includes at a minimum removal of all tile and plumbing fixtures, gypsum board repair and installation of new stainless steel shower units. This project or a portion there of was previously recommended in the FCA report dated 5/4/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 8/17/2006. | HOUSING UNIT (VACANT) | 9986 | Correct | SSCC |  | Silver Springs | 1991 | 11242 | 2006-08-17 | Immediate to Two Years | Currently Critical | 1 | 180000
0966SFT2 | FIRE ALARM SYSTEM UPGRADE | 0966 | This building is equipped with an automatic fire detection and alarm system, but the system is antiquated. It is recommended that the fire detection and alarm system be upgraded. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2006 IBC Chapter 9, Section 907.2.6.3 and the State Fire Marshal's requirements. This project or a portion thereof was previously recommended in the FCA report dated 12/01/2001. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2007. | BARRACKS/ADMINISTRATION | 9968 | Correct | TLVCC |  | Indian Springs | 1990 | 6112 | 2007-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0966PLM2 | REMODEL BARRACKS RESTROOM | 0966 | The restroom in the barracks section of the building is in general disrepair and is due for a complete remodel. This project provides for new sinks, toilets, partitions, plumbing fixtures, cabinets and all interior finishes for the restroom. Minor plumbing and room redesign may be required and is included in this estimate. | BARRACKS/ADMINISTRATION | 9968 | Correct | TLVCC |  | Indian Springs | 1990 | 6112 | 2007-04-05 | Immediate to Two Years | Currently Critical | 1 | 80000
0966EXT1 | EXTERIOR FINISHES | 0966 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 3 to 4 years and is recommended on a cyclical basis based on environmental conditions. | BARRACKS/ADMINISTRATION | 9968 | Correct | TLVCC |  | Indian Springs | 1990 | 6112 | 2007-04-05 | Four to Ten Years | Long-Term Needs | 3 | 25000
0966INT1 | INTERIOR FINISHES | 0966 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 12/01/2001. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2007. | BARRACKS/ADMINISTRATION | 9968 | Correct | TLVCC |  | Indian Springs | 1990 | 6112 | 2007-04-05 | Four to Ten Years | Long-Term Needs | 3 | 25000
0966HVA1 | REPLACE EVAPORATIVE COOLERS | 0966 | A number of evaporative coolers have been installed throughout the building. They are in fair condition and it is recommended that these units be replaced in two to four years as they are reaching the end of their expected life. Six (6) units were used for this estimate. This project or a portion thereof was previously recommended in the FCA report dated 12/01/2001. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2007. | BARRACKS/ADMINISTRATION | 9968 | Correct | TLVCC |  | Indian Springs | 1990 | 6112 | 2007-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18000
0966SFT1 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0966 | The existing exit signs in this building are older types and should be replaced with new self-illuminated or LED style signs with battery-backed internal systems. Emergency exit lighting should be installed and/or replaced to provide illumination along the egress route. This project or a portion thereof was previously recommended in the FCA report dated 12/01/2001. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2007. | BARRACKS/ADMINISTRATION | 9968 | Correct | TLVCC |  | Indian Springs | 1990 | 6112 | 2007-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0966EXT2 | REPLACE EXTERIOR DOORS | 0966 | The five existing exterior metal doors and frames appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement and installation of five new hollow metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. The main entrance door hall have ADA accessible hardware including lever action door handles and threshold. | BARRACKS/ADMINISTRATION | 9968 | Correct | TLVCC |  | Indian Springs | 1990 | 6112 | 2007-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0966ENR1 | LIGHTING UPGRADE | 0966 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures, ballasts and lighting to current standards, resulting in increased efficiency and reduced costs associated with illumination. Occupancy sensors will be installed in restrooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 12/01/2001. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2007. | BARRACKS/ADMINISTRATION | 9968 | Correct | TLVCC |  | Indian Springs | 1990 | 6112 | 2007-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
2010HVA2 | HVAC SYSTEM REPLACEMENT | 2010 | The building is heated by two roof-top furnaces and cooled by one air conditioner on grade. One of the heating units has been decommissioned in order to provide parts for the other unit. In turn, the ducting has been re-routed to accommodate for the loss of one unit. This equipment is original to the building and has reached the end of its expected life. This project recommends replacing the roof-top heaters, the air conditioning condenser unit and routing the ductwork back to the original design. The estimate includes removal and disposal of the existing equipment. | CULINARY/DINING | 9984 | Correct | SCC |  | Carson City | 1994 | 3750 | 2008-04-29 | Immediate to Two Years | Currently Critical | 1 | 120000
2010INT4 | KITCHEN EQUIPMENT UPGRADE | 2010 | The kitchen cooking equipment is original to the building and is reaching the end of its lifetime. It is recommended that the equipment be scheduled for replacement in the next two to three years, including the Baxter oven, refrigerator and freezer equipment and the Mars Air Door unit on the back door. This project provides for the removal and disposal of the existing equipment and replacement with new equipment. This estimate is a lump some for budgeting purposes. | CULINARY/DINING | 9984 | Correct | SCC |  | Carson City | 1994 | 3750 | 2008-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 100000
2010INT3 | SUSPENDED ACOUSTICAL CEILING TILE REPLACEMENT | 2010 | The Dining space in this building has a suspended acoustical ceiling tile system. The system is original to the building and has reached the end of its expected life. The metal frame is bent and rusted in many areas and a number of the ceiling tiles are damaged and stained. This project recommends replacing the suspended acoustical ceiling tile system including the tiles. Removal and disposal of the existing ceiling system is included in this estimate. | CULINARY/DINING | 9984 | Correct | SCC |  | Carson City | 1994 | 3750 | 2008-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
2010INT1 | INTERIOR FINISHES | 2010 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | CULINARY/DINING | 9984 | Correct | SCC |  | Carson City | 1994 | 3750 | 2008-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18750
2011EXT1 | REPLACE ROOF | 2011 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. The extreme temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next two to four years with a 50 year asphalt composition roofing shingle and new underlayments. This project or a portion thereof was previously recommended in the FCA report dated 8/22/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2008. | HOUSING UNIT 01 | 9984 | Correct | SCC |  | Carson City | 1994 | 3920 | 2008-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 39200
2011EXT2 | EXTERIOR FINISHES | 2011 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | HOUSING UNIT 01 | 9984 | Correct | SCC |  | Carson City | 1994 | 3920 | 2008-04-29 | Four to Ten Years | Long-Term Needs | 3 | 39200
2011INT2 | INTERIOR FINISHES | 2011 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HOUSING UNIT 01 | 9984 | Correct | SCC |  | Carson City | 1994 | 3920 | 2008-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19600
2011HVA1 | EVAPORATIVE COOLER REPLACEMENT | 2011 | This building is cooled by three roof mounted evaporative coolers. This equipment will reach the end of its expected life in the next 5 to 6 years and should be scheduled for replacement in that time frame. The estimate includes removal and disposal of the existing equipment. | HOUSING UNIT 01 | 9984 | Correct | SCC |  | Carson City | 1994 | 3920 | 2008-04-29 | Four to Ten Years | Long-Term Needs | 3 | 12000
2011ADA1 | RESTROOM REMODEL | 2011 | The restroom and shower room are in overall poor condition. The countertops in each room show signs of wear and deterioration. Extensive use, combined with repetitive water being spilled, has caused the laminate top to separate from the wooden underlayment and should be replaced. The tile on the floors and walls of the bathrooms are damaged and worn and should be replaced. This project provides for a complete remodel of the restroom and shower room which should include an ADA compliant toilet stall, shower and sink with all ADA complaint fixtures. The existing exhaust fans are undersized and should be replaced with commercial grade exhaust fans. The removal and disposal of the old fixtures and finishes is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 8/22/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2008. | HOUSING UNIT 01 | 9984 | Correct | SCC |  | Carson City | 1994 | 3920 | 2008-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 275000
2012EXT1 | REPLACE ROOF | 2012 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. The extreme temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next two to four years with a 50 year asphalt composition roofing shingle and new underlayments. This project or a portion thereof was previously recommended in the FCA report dated 8/22/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2008. | HOUSING UNIT 02 | 9984 | Correct | SCC |  | Carson City | 1994 | 3920 | 2008-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 39200
2012ADA1 | RESTROOM REMODEL | 2012 | The restroom and shower room are in overall poor condition. The countertops in each room show signs of wear and deterioration. Extensive use, combined with repetitive water being spilled, has caused the laminate top to separate from the wooden underlayment and should be replaced. The tile on the floors and walls of the bathrooms are damaged and worn and should be replaced. This project provides for a complete remodel of the restroom and shower room which should include an ADA compliant toilet stall, shower and sink with all ADA complaint fixtures. The existing exhaust fans are undersized and should be replaced with commercial grade exhaust fans. The removal and disposal of the old fixtures and finishes is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 8/22/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2008. | HOUSING UNIT 02 | 9984 | Correct | SCC |  | Carson City | 1994 | 3920 | 2008-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 275000
2012INT3 | INTERIOR FINISHES | 2012 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HOUSING UNIT 02 | 9984 | Correct | SCC |  | Carson City | 1994 | 3920 | 2008-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19600
2012EXT2 | EXTERIOR FINISHES | 2012 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | HOUSING UNIT 02 | 9984 | Correct | SCC |  | Carson City | 1994 | 3920 | 2008-04-29 | Four to Ten Years | Long-Term Needs | 3 | 39200
2012HVA1 | EVAPORATIVE COOLER REPLACEMENT | 2012 | This building is cooled by three roof mounted evaporative coolers. This equipment will reach the end of its expected life in the next 5 to 6 years and should be scheduled for replacement in that time frame. The estimate includes removal and disposal of the existing equipment. | HOUSING UNIT 02 | 9984 | Correct | SCC |  | Carson City | 1994 | 3920 | 2008-04-29 | Four to Ten Years | Long-Term Needs | 3 | 12000
2010ADA1 | ADA RESTROOM UPGRADE | 2010 | The restroom does not meet the Americans with Disabilities Act (ADA) regulations. A retrofit is necessary to comply with 2006 IBC Chapter 11, ICC/ANSI A117.1-1998 Sections 603 - 604 and the Americans with Disabilities Act Accessibility Guidelines (ADAAG). Given the current configuration of the restroom, the work will include the installation of a new toilet, sink, grab bars, faucets, mirrors, dispensers and hardware. Some minor design work will be required and may impact the final cost estimate. This estimate is for one unisex restroom facility. The removal and disposal of the old restroom fixtures is included in this estimate. | CULINARY/DINING | 9984 | Correct | SCC |  | Carson City | 1994 | 3750 | 2008-04-29 | Immediate to Two Years | Currently Critical | 1 | 25000
2010INT5 | REPLACE VINYL COMPOSITION TILE | 2010 | The existing vinyl composition tile (VCT) in the dining, corridors and storage areas is extremely worn, damaged and should be replaced. This project would provide for the removal and replacement of the VCT. | CULINARY/DINING | 9984 | Correct | SCC |  | Carson City | 1994 | 3750 | 2008-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15400
2010EXT2 | EXTERIOR FINISHES | 2010 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | CULINARY/DINING | 9984 | Correct | SCC |  | Carson City | 1994 | 3750 | 2008-04-29 | Four to Ten Years | Long-Term Needs | 3 | 37500
2010ELE1 | REPLACE WALL MOUNTED ELECTRICAL HEATER | 2010 | The existing wall mounted electric baseboard heater is damaged and inoperable. This project would provide for the removal and replacement of the heater. | CULINARY/DINING | 9984 | Correct | SCC |  | Carson City | 1994 | 3750 | 2008-04-29 | Immediate to Two Years | Currently Critical | 1 | 1000
2010ELE2 | MISCELLANEOUS ELECTRICAL REPAIRS | 2010 | The electrical subpanel has some broken circuit breaker safety caps and is not properly labeled. There is an electrical cord from the walk-in coolers ran through the wall into a damaged duplex outlet located in the dry storage room. This project would provide the repairs necessary to bring these items into compliance with codes and adopted standards. | CULINARY/DINING | 9984 | Correct | SCC |  | Carson City | 1994 | 3750 | 2008-04-29 | Immediate to Two Years | Currently Critical | 1 | 500
2010EXT1 | REPLACE ROOF | 2010 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. The extreme temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next two to four years with a 50 year asphalt composition roofing shingle and new underlayments. This project or a portion thereof was previously recommended in the FCA report dated 8/22/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2008. | CULINARY/DINING | 9984 | Correct | SCC |  | Carson City | 1994 | 3750 | 2008-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 37500
2009HVA1 | EVAPORATIVE COOLER REPLACEMENT | 2009 | This building is cooled by an evaporative cooler located on grade on the south side of the building. This unit will reach the end of its expected life in the next 8 to 10 years and should be scheduled for replacement in that time frame. The estimate includes removal and disposal of the existing equipment. | CONTROL ROOM | 9984 | Correct | SCC |  | Carson City | 1994 | 1875 | 2008-04-29 | Four to Ten Years | Long-Term Needs | 3 | 4000
2009INT3 | INTERIOR FINISHES | 2009 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | CONTROL ROOM | 9984 | Correct | SCC |  | Carson City | 1994 | 1875 | 2008-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9375
2009EXT2 | EXTERIOR FINISHES | 2009 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | CONTROL ROOM | 9984 | Correct | SCC |  | Carson City | 1994 | 1875 | 2008-04-29 | Four to Ten Years | Long-Term Needs | 3 | 18750
2009EXT1 | REPLACE ROOF | 2009 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. The extreme temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next two to four years with a 50 year asphalt composition roofing shingle and new underlayments. This project or a portion thereof was previously recommended in the FCA report dated 8/22/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2008. | CONTROL ROOM | 9984 | Correct | SCC |  | Carson City | 1994 | 1875 | 2008-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18750
2008INT3 | INTERIOR FINISHES | 2008 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | MULTI-USE BUILDING | 9984 | Correct | SCC |  | Carson City | 1994 | 7000 | 2008-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35000
2008EXT2 | EXTERIOR FINISHES | 2008 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | MULTI-USE BUILDING | 9984 | Correct | SCC |  | Carson City | 1994 | 7000 | 2008-04-29 | Four to Ten Years | Long-Term Needs | 3 | 70000
2013EXT1 | REPLACE ROOF | 2013 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. The extreme temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next two to four years with a 50 year asphalt composition roofing shingle and new underlayments. This project or a portion thereof was previously recommended in the FCA report dated 8/22/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2008. | HOUSING UNIT 03 | 9984 | Correct | SCC |  | Carson City | 1994 | 3920 | 2008-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 39200
2015HVA1 | EVAPORATIVE COOLER REPLACEMENT | 2015 | This building is cooled by three roof mounted evaporative coolers. This equipment will reach the end of its expected life in the next 5 to 6 years and should be scheduled for replacement in that time frame. The estimate includes removal and disposal of the existing equipment. | HOUSING UNIT 05 | 9984 | Correct | SCC |  | Carson City | 1994 | 3920 | 2008-04-29 | Four to Ten Years | Long-Term Needs | 3 | 12000
2008SFT1 | REPLACE STAIR HANDRAILS | 2008 | There is a set of stairs which lead to an upper level storage area in the NDF portion of the building. The existing wood framed handrails at the stairs do not meet the requirements of the 2006 IBC. This project would provide for the installation of handrails in accordance with the 2006 IBC Chapter 10, Section 1012. | MULTI-USE BUILDING | 9984 | Correct | SCC |  | Carson City | 1994 | 7000 | 2008-04-29 | Immediate to Two Years | Currently Critical | 1 | 1200
2015ADA1 | REMOVE WATER FOUNTAIN | 2015 | This building has a water fountain which is not ADA accessible, damaged and is very rarely used. This project recommends permanently removing the water fountain. | HOUSING UNIT 05 | 9984 | Correct | SCC |  | Carson City | 1994 | 3920 | 2008-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
2015ADA2 | RESTROOM REMODEL | 2015 | The restroom and shower room are in overall poor condition. The countertops in each room show signs of wear and deterioration. Extensive use, combined with repetitive water being spilled, has caused the laminate top to separate from the wooden underlayment and should be replaced. The tile on the floors and walls of the bathrooms are damaged and worn and should be replaced. This project provides for a complete remodel of the restroom and shower room which should include an ADA compliant toilet stall, shower and sink with all ADA complaint fixtures. The existing exhaust fans are undersized and should be replaced with commercial grade exhaust fans. The removal and disposal of the old fixtures and finishes is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 8/22/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2008. | HOUSING UNIT 05 | 9984 | Correct | SCC |  | Carson City | 1994 | 3920 | 2008-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 275000
2015INT4 | INTERIOR FINISHES | 2015 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HOUSING UNIT 05 | 9984 | Correct | SCC |  | Carson City | 1994 | 3920 | 2008-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19600
2015EXT2 | EXTERIOR FINISHES | 2015 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | HOUSING UNIT 05 | 9984 | Correct | SCC |  | Carson City | 1994 | 3920 | 2008-04-29 | Four to Ten Years | Long-Term Needs | 3 | 39200
2013HVA1 | EVAPORATIVE COOLER REPLACEMENT | 2013 | This building is cooled by three roof mounted evaporative coolers. This equipment will reach the end of its expected life in the next 5 to 6 years and should be scheduled for replacement in that time frame. The estimate includes removal and disposal of the existing equipment. | HOUSING UNIT 03 | 9984 | Correct | SCC |  | Carson City | 1994 | 3920 | 2008-04-29 | Four to Ten Years | Long-Term Needs | 3 | 12000
2015EXT1 | REPLACE ROOF | 2015 | The asphalt composition shingle roof on this building was in fair condition at the time of the survey. The extreme temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next two to four years with a 50 year asphalt composition roofing shingle and new underlayments. This project or a portion thereof was previously recommended in the FCA report dated 8/22/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2008. | HOUSING UNIT 05 | 9984 | Correct | SCC |  | Carson City | 1994 | 3920 | 2008-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 39200
2014ADA1 | RESTROOM REMODEL | 2014 | The restroom and shower room are in overall poor condition. The countertops in each room show signs of wear and deterioration. Extensive use, combined with repetitive water being spilled, has caused the laminate top to separate from the wooden underlayment and should be replaced. The tile on the floors and walls of the bathrooms are damaged and worn and should be replaced. This project provides for a complete remodel of the restroom and shower room which should include an ADA compliant toilet stall, shower and sink with all ADA complaint fixtures. The existing exhaust fans are undersized and should be replaced with commercial grade exhaust fans. The removal and disposal of the old fixtures and finishes is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 8/22/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2008. | HOUSING UNIT 04 | 9984 | Correct | SCC |  | Carson City | 1994 | 3920 | 2008-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 275000
2014EXT2 | EXTERIOR FINISHES | 2014 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | HOUSING UNIT 04 | 9984 | Correct | SCC |  | Carson City | 1994 | 3920 | 2008-04-29 | Four to Ten Years | Long-Term Needs | 3 | 39200
2014INT3 | INTERIOR FINISHES | 2014 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HOUSING UNIT 04 | 9984 | Correct | SCC |  | Carson City | 1994 | 3920 | 2008-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19600
2014HVA1 | EVAPORATIVE COOLER REPLACEMENT | 2014 | This building is cooled by three roof mounted evaporative coolers. This equipment will reach the end of its expected life in the next 5 to 6 years and should be scheduled for replacement in that time frame. The estimate includes removal and disposal of the existing equipment. | HOUSING UNIT 04 | 9984 | Correct | SCC |  | Carson City | 1994 | 3920 | 2008-04-29 | Four to Ten Years | Long-Term Needs | 3 | 12000
2014EXT1 | REPLACE ROOF | 2014 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. The extreme temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next two to four years with a 50 year asphalt composition roofing shingle and new underlayments. This project or a portion thereof was previously recommended in the FCA report dated 8/22/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2008. | HOUSING UNIT 04 | 9984 | Correct | SCC |  | Carson City | 1994 | 3920 | 2008-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 39200
2013EXT2 | EXTERIOR FINISHES | 2013 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | HOUSING UNIT 03 | 9984 | Correct | SCC |  | Carson City | 1994 | 3920 | 2008-04-29 | Four to Ten Years | Long-Term Needs | 3 | 39200
2013ADA1 | RESTROOM REMODEL | 2013 | The restroom and shower room are in overall poor condition. The countertops in each room show signs of wear and deterioration. Extensive use, combined with repetitive water being spilled, has caused the laminate top to separate from the wooden underlayment and should be replaced. The tile on the floors and walls of the bathrooms are damaged and worn and should be replaced. This project provides for a complete remodel of the restroom and shower room which should include an ADA compliant toilet stall, shower and sink with all ADA complaint fixtures. The existing exhaust fans are undersized and should be replaced with commercial grade exhaust fans. The removal and disposal of the old fixtures and finishes is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 8/22/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2008. | HOUSING UNIT 03 | 9984 | Correct | SCC |  | Carson City | 1994 | 3920 | 2008-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 275000
2013INT3 | INTERIOR FINISHES | 2013 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HOUSING UNIT 03 | 9984 | Correct | SCC |  | Carson City | 1994 | 3920 | 2008-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19600
2834EXT1 | EXTERIOR FINISHES | 2834 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 2 to 3 years and is recommended on a cyclical basis based on environmental conditions. | PHONE RAMADA | 9984 | Correct | SCC |  | Carson City | 2000 | 170 | 2008-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 340
9984SFT3 | FIRE ALARM INSPECTION | 9984 | The fire alarm system was not operating at the time of the survey. The reason for the malfunction was not known at the time of the survey and the maintenance staff explained that there is no funding to repair the system. This project would provide funding for an inspection of the system by a certified fire alarm equipment inspector to determine the cause of the problem. Any future projects would come from report recommendations. | STEWART CONSERVATION CAMP SITE | 9984 | Correct | SCC |  | Carson City | 1994 | 0 | 2008-04-29 | Immediate to Two Years | Currently Critical | 1 | 2000
9984SFT1 | FIRE SPRINKLER SUPPLY LINE REPLACEMENT | 9984 | The main fire sprinkler supply line servicing the campus has rusted and is due for replacement. Staff reported that they recently replaced a portion of the buried piping and visual inspection revealed that the entire line is beginning to fail. This project would provide funds to remove the existing piping and replace it with a new line. The estimate includes disposal of the existing materials, excavation, backfill, etc.. Backflow prevention replacement is included in this estimate. | STEWART CONSERVATION CAMP SITE | 9984 | Correct | SCC |  | Carson City | 1994 | 0 | 2008-04-29 | Immediate to Two Years | Currently Critical | 1 | 225000
9984SIT2 | LANDSCAPE IMPROVEMENTS | 9984 | A large portion of the site is not covered by vegetation or rock and is a constant maintenance problem. The wind and water causes the dirt to erode which then must be replaced once a year in order to maintain the grade and protect the buildings. This project recommends covering the dirt areas with grass including an irrigation system. Another alternative could include planting of shrubs as a wind break. Xeriscaping may be another method but due to security concerns, having cobblestone or other objects in the landscaping may pose a risk to inmates and staff. | STEWART CONSERVATION CAMP SITE | 9984 | Correct | SCC |  | Carson City | 1994 | 0 | 2008-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
9984SIT1 | SLURRY SEAL ASPHALT PAVING | 9984 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site wide including access roads and parking areas. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 80,000 square feet of asphalt area was used to generate this estimate. This project or a portion thereof was previously recommended in the FCA report dated 8/22/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2008. | STEWART CONSERVATION CAMP SITE | 9984 | Correct | SCC |  | Carson City | 1994 | 0 | 2008-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 48000
9984HVA1 | UPDATE WATER TREATMENT SYSTEM | 9984 | The chemical water treatment and water softener systems throughout the camp are in good condition, but some were not operating and others did not receive regular maintenance. This project would provide for a chemical treatment program including an updated chemicals control system, service and employee training provided by a qualified water treatment vendor. The annual maintenance fee charged by the water treatment vendor would be determined after an investigation of the water system is complete. These annual costs are not included in this project cost. For budgeting purposes, a $15,000 fee is suggested. | STEWART CONSERVATION CAMP SITE | 9984 | Correct | SCC |  | Carson City | 1994 | 0 | 2008-04-29 | Immediate to Two Years | Currently Critical | 1 | 15000
1446EXT2 | EXTERIOR DOOR REPLACEMENT | 1446 | The existing exterior wood doors on the carpenter shop portion appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement of the wood doors with two new metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | EQUIPMENT SHED | 9982 | Correct | Farm |  | Carson City | 1916 | 5103 | 2008-09-02 | Four to Ten Years | Long-Term Needs | 3 | 1000
1446STR1 | STRUCTURAL ASSESSMEMT | 1446 | The building was constructed in 1916 out of unreinforced sandstone masonry. The walls are showing signs of failure including cracking, settling and crumbling. This project would provide for an investigation and assessment to be done by a licensed Structural Engineer to identify possible deficiencies and problems in the building and provide a report outlining issues and resolutions. Future projects may result from this report and are not included in this estimate. | EQUIPMENT SHED | 9982 | Correct | Farm |  | Carson City | 1916 | 5103 | 2008-09-02 | Immediate to Two Years | Currently Critical | 1 | 5000
1446EXT1 | EXTERIOR FINISHES | 1446 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, sealing or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 2 to 3 years and is recommended on a cyclical basis based on environmental conditions. | EQUIPMENT SHED | 9982 | Correct | Farm |  | Carson City | 1916 | 5103 | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25515
1444EXT1 | EXTERIOR FINISHES | 1444 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, sealing or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 2 to 3 years and is recommended on a cyclical basis based on environmental conditions. | OLD DAIRY BARN/HAY STORAGE | 9982 | Correct | Farm |  | Carson City | 1916 | 5125 | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25625
1444EXT2 | ROOF REPLACEMENT | 1444 | The corrugated metal roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next two to three years with a new standing seam metal roofing system. This estimate includes removal and disposal of the old roofing. This project should coincide with any projects that may be recommended by the structural assessment report project. | OLD DAIRY BARN/HAY STORAGE | 9982 | Correct | Farm |  | Carson City | 1916 | 5125 | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 76875
1443EXT1 | EXTERIOR FINISHES | 1443 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, sealing or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 2 to 3 years and is recommended on a cyclical basis based on environmental conditions. | DAIRY BARN | 9982 | Correct | Farm |  | Carson City | 1970 | 2666 | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 26660
1448STR1 | STRUCTURAL ASSESSMEMT | 1448 | The building was constructed in 1916 out of unreinforced masonry. The walls are showing signs of failure including cracking, settling and crumbling. This project would provide for an investigation and assessment to be done by a licensed Structural Engineer to identify possible deficiencies and problems in the building and provide a report outlining issues and resolutions. Future projects may result from this report and are not included in this estimate. This project should coincide with the preservation project. | RANCH HOUSE | 9982 | Correct | Farm |  | Carson City | 1916 | 3000 | 2008-09-02 | Immediate to Two Years | Currently Critical | 1 | 5000
1448EXT2 | ROOF REPLACEMENT | 1448 | The wood shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next two to three years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. | RANCH HOUSE | 9982 | Correct | Farm |  | Carson City | 1916 | 3000 | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 45000
1447EXT1 | EXTERIOR FINISHES | 1447 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, sealing or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 2 to 3 years and is recommended on a cyclical basis based on environmental conditions. | CALVING BARN | 9982 | Correct | Farm |  | Carson City | 1998 | 1200 | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3600
1443HVA1 | EVAPORATIVE COOLER REPLACEMENT | 1443 | There are 2 existing wall mounted evaporative coolers that service this building. The units are not energy efficient and are approaching the end of their expected life. This project would provide for the removal of the existing coolers and replacement with one central roof top evaporative cooling unit including connections to utilities and existing duct work. | DAIRY BARN | 9982 | Correct | Farm |  | Carson City | 1970 | 2666 | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
1448EXT1 | EXTERIOR FINISHES | 1448 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, sealing or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 2 to 3 years and is recommended on a cyclical basis based on environmental conditions. | RANCH HOUSE | 9982 | Correct | Farm |  | Carson City | 1916 | 3000 | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
1446EXT4 | ROOF REPLACEMENT | 1446 | The corrugated metal roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next two to three years with a new standing seam metal roofing system. This estimate includes removal and disposal of the old roofing. | EQUIPMENT SHED | 9982 | Correct | Farm |  | Carson City | 1916 | 5103 | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 76545
1443INT3 | FLOORING REPLACEMENT - LAB | 1443 | The VCT (vinyl composite tile) flooring in the lab room is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the existing VCT and installation of new 12x12 VCT with a 6" base. | DAIRY BARN | 9982 | Correct | Farm |  | Carson City | 1970 | 2666 | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2700
1443INT2 | CEILING SYSTEM UPGRADE - PROCESSING ROOM | 1443 | The processing room in this building has a suspended acoustical tile ceiling system. The t-bar framing is bent and rusted in many areas and a number of the ceiling tiles are damaged and stained. This project would provide for the replacement of the suspended acoustical tile ceiling system. Removal and disposal of the existing ceiling system is included in this estimate. | DAIRY BARN | 9982 | Correct | Farm |  | Carson City | 1970 | 2666 | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10500
1443EXT4 | EXTERIOR DOOR REPLACEMENT | 1443 | The building has 3 exterior metal doors and 6 exterior wood doors that have reached the end of their expected life. They are damaged from age and general wear and tear. This project would provide for the replacement and installation of 9 new metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | DAIRY BARN | 9982 | Correct | Farm |  | Carson City | 1970 | 2666 | 2008-09-02 | Four to Ten Years | Long-Term Needs | 3 | 22500
1442EXT1 | DEMOLISH STRUCTURE | 1442 | The Chicken House is an unused wood framed structure that is in poor shape. This project would provide for the demolition of the structure including debris removal. | CHICKEN HOUSE | 9982 | Correct | Farm |  | Carson City |  | 144 | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 400
1443EXT3 | WINDOW REPLACEMENT | 1443 | The windows are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 18 units. | DAIRY BARN | 9982 | Correct | Farm |  | Carson City | 1970 | 2666 | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18000
1444STR1 | STRUCTURAL ASSESSMEMT | 1444 | The building was constructed in 1916 out of unreinforced masonry. The walls are showing signs of failure including cracking, settling and crumbling. This project would provide for an investigation and assessment to be done by a licensed Structural Engineer to identify possible deficiencies and problems in the building and provide a report outlining issues and resolutions. Future projects may result from this report and are not included in this estimate. | OLD DAIRY BARN/HAY STORAGE | 9982 | Correct | Farm |  | Carson City | 1916 | 5125 | 2008-09-02 | Immediate to Two Years | Currently Critical | 1 | 5000
1443SFT1 | FIRE ALARM INSTALLATION | 1443 | This building is not equipped with an automatic fire detection and alarm system. It is recommended that an automatic fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements. | DAIRY BARN | 9982 | Correct | Farm |  | Carson City | 1970 | 2666 | 2008-09-02 | Immediate to Two Years | Currently Critical | 1 | 7998
1443INT1 | INTERIOR FINISHES | 1443 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | DAIRY BARN | 9982 | Correct | Farm |  | Carson City | 1970 | 2666 | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 13330
1443EXT2 | ROOF REPLACEMENT | 1443 | The single-ply roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next two to three years with a new single-ply roofing system. The small pop-outs around the building are covered by asphalt composition roofing shingles. These areas should be replaced as well. This estimate includes removal and disposal of the old roofing. | DAIRY BARN | 9982 | Correct | Farm |  | Carson City | 1970 | 2666 | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 39990
1440STR1 | STRUCTURAL ASSESSMEMT | 1440 | The building was constructed in 1916 out of unreinforced sandstone masonry. The walls are showing signs of failure including cracking, settling and crumbling. This project would provide for an investigation and assessment to be done by a licensed Structural Engineer to identify possible deficiencies and problems in the building and provide a report outlining issues and resolutions. Future projects may result from this report and are not included in this estimate. | BULL BARN | 9982 | Correct | Farm |  | Carson City | 1930 | 1050 | 2008-09-02 | Immediate to Two Years | Currently Critical | 1 | 5000
1440EXT1 | EXTERIOR FINISHES | 1440 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, sealing or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 2 to 3 years and is recommended on a cyclical basis based on environmental conditions. | BULL BARN | 9982 | Correct | Farm |  | Carson City | 1930 | 1050 | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5250
1443EXT5 | CONCRETE APRON REPLACEMENT | 1443 | The exterior concrete apron outside of the processing room has extensive cracking and is due for replacement. This project would provide for the installation of a new 120 square foot 4" thick concrete slab-on-grade apron. Removal and disposal of the existing concrete is included in this estimate. | DAIRY BARN | 9982 | Correct | Farm |  | Carson City | 1970 | 2666 | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1200
1443ENR1 | LIGHTING UPGRADE | 1443 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts to current standards, resulting in increased efficiency and reduced costs associated with illumination. Any electrical wiring upgrades are not included in this estimate. | DAIRY BARN | 9982 | Correct | Farm |  | Carson City | 1970 | 2666 | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7998
1450EXT2 | WINDOW REPLACEMENT | 1450 | The windows are original, single pane construction in a metal frame. These older windows are drafty, not energy efficient and one is broken. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 3 units. | YARD OFFICE | 9982 | Correct | Farm |  | Carson City | 1970 | 100 | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
1450EXT3 | EXTERIOR DOOR REPLACEMENT | 1450 | The existing exterior wood door appears to be original to the building. It is damaged from age and general wear and tear. This project would provide for the replacement of the wood door with a new metal door, frame and hardware. Removal and disposal of the existing door and painting of the new door is included in this estimate. | YARD OFFICE | 9982 | Correct | Farm |  | Carson City | 1970 | 100 | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
1450EXT1 | EXTERIOR FINISHES | 1450 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, sealing or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 2 to 3 years and is recommended on a cyclical basis based on environmental conditions. | YARD OFFICE | 9982 | Correct | Farm |  | Carson City | 1970 | 100 | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
1450INT1 | INTERIOR FINISHES | 1450 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | YARD OFFICE | 9982 | Correct | Farm |  | Carson City | 1970 | 100 | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
1446EXT3 | WINDOW REPLACEMENT | 1446 | The windows are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 4 units. | EQUIPMENT SHED | 9982 | Correct | Farm |  | Carson City | 1916 | 5103 | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
1448SEC1 | CONSERVE AND PROTECT BUILDING | 1448 | The building was constructed in 1916 out of unreinforced sandstone masonry. It is currently used for incidental storage and has been vandalized. The broken windows in the buildings have allowed pigeons, bats and other pests access to the building, with related health hazards and permitted rain to enter the building. The second floor is unusable due to instability of the floor/ ceiling assembly. In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U.S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to providing drainage away from the buildings to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. Roofing is addressed in a separate project. | RANCH HOUSE | 9982 | Correct | Farm |  | Carson City | 1916 | 3000 | 2008-09-02 | Immediate to Two Years | Currently Critical | 1 | 30000
2915INT1 | INTERIOR FINISHES | 2915 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4 to 5 years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | MAINTENANCE SHOP | 9982 | Correct | Farm |  | Carson City | 2004 | 3600 | 2008-09-02 | Four to Ten Years | Long-Term Needs | 3 | 3600
2919ENR1 | LIGHTING UPGRADE | 2919 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts to current standards, resulting in increased efficiency and reduced costs associated with illumination. Any electrical wiring upgrades are not included in this estimate. | WILD HORSE OFFICE | 9982 | Correct | Farm |  | Carson City | 0 | 480 | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 960
2919EXT1 | EXTERIOR FINISHES | 2919 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, sealing or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 2 to 3 years and is recommended on a cyclical basis based on environmental conditions. | WILD HORSE OFFICE | 9982 | Correct | Farm |  | Carson City | 0 | 480 | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2400
2918ENR1 | LIGHTING UPGRADE | 2918 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts to current standards, resulting in increased efficiency and reduced costs associated with illumination. Any electrical wiring upgrades are not included in this estimate. | WILD HORSE ARENA | 9982 | Correct | Farm |  | Carson City | 0 | 10000 | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
2918INT1 | INTERIOR FINISHES | 2918 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4 to 5 years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | WILD HORSE ARENA | 9982 | Correct | Farm |  | Carson City | 0 | 10000 | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
2918EXT1 | EXTERIOR FINISHES | 2918 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, sealing or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 2 to 3 years and is recommended on a cyclical basis based on environmental conditions. | WILD HORSE ARENA | 9982 | Correct | Farm |  | Carson City | 0 | 10000 | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
2917EXT1 | EXTERIOR FINISHES | 2917 | It is important to maintain the finish, weather resistance and appearance of the steel structure. This project would provide for painting of the steel structure and should be done on a cyclical basis based on environmental conditions. | FREE STALL BARN | 9982 | Correct | Farm |  | Carson City | 2005 | 12000 | 2008-09-02 | Four to Ten Years | Long-Term Needs | 3 | 12000
2915EXT1 | EXTERIOR FINISHES | 2915 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, sealing or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | MAINTENANCE SHOP | 9982 | Correct | Farm |  | Carson City | 2004 | 3600 | 2008-09-02 | Four to Ten Years | Long-Term Needs | 3 | 10800
2915SFT1 | FIRE SUPPRESSION SYSTEM INSTALLATION | 2915 | Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.910 states, that every new building owned by the State that is intended for occupancy must be equipped with an automatic fire suppression system. This project would provide funding for the installation of an automatic fire suppression system and backflow prevention. | MAINTENANCE SHOP | 9982 | Correct | Farm |  | Carson City | 2004 | 3600 | 2008-09-02 | Immediate to Two Years | Currently Critical | 1 | 50400
2915SFT3 | FIRE ALARM INSTALLATION | 2915 | This building is not equipped with an automatic fire detection and alarm system. It is recommended that an automatic fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements. | MAINTENANCE SHOP | 9982 | Correct | Farm |  | Carson City | 2004 | 3600 | 2008-09-02 | Immediate to Two Years | Currently Critical | 1 | 10800
2915SFT2 | INSTALL EXIT SIGNS AND EGRESS LIGHTING | 2915 | The building does not have any emergency lighting and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency exit lighting to provide illumination along the egress route. IBC - 2006 Chapter 10 was referenced for this project. | MAINTENANCE SHOP | 9982 | Correct | Farm |  | Carson City | 2004 | 3600 | 2008-09-02 | Immediate to Two Years | Currently Critical | 1 | 1500
2919INT1 | INTERIOR FINISHES | 2919 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4 to 5 years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | WILD HORSE OFFICE | 9982 | Correct | Farm |  | Carson City | 0 | 480 | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2400
2916EXT1 | EXTERIOR FINISHES | 2916 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, sealing or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | A. I. BUILDING | 9982 | Correct | Farm |  | Carson City | 0 | 400 | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
9982SIT2 | WELL EVALUATION AND ABANDONMENT | 9982 | There are wells on this site that are no longer in use. The Division of Water Resources (DRW) requires that these wells be plugged as not to allow a conduit for ground water contamination. The costs to plug the wells depend on the depth of the wells and the casing size. Preliminary estimates run around $45.00 per foot to plug the wells estimating that it around 200 feet deep. NAC 534.427 was referenced for this project. Three wells with 8" casings were used to generate this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/02/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/02/2008. | NORTHERN NEVADA DAIRY FARM SITE | 9982 | Correct | Farm |  | Carson City |  |  | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 27000
9982ELE1 | ELECTRICAL DISTRIBUTION SYSTEM UPGRADE | 9982 | The electrical service was adequate for the original buildings for the site. With additional buildings and anticipated needs, the service is approaching available capacity. This project recommends upgrading the system, providing separate services and disconnects for each of the buildings, replacing the switchgear and providing additional capacity for future growth. This project or a portion thereof was previously recommended in the FCA report dated 09/02/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/02/2008. | NORTHERN NEVADA DAIRY FARM SITE | 9982 | Correct | Farm |  | Carson City |  |  | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 150000
0293ENR1 | LIGHTING UPGRADE | 0293 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts to current standards, resulting in increased efficiency and reduced costs associated with illumination. Any electrical wiring upgrades are not included in this estimate. | BREAK ROOM | 9982 | Correct | Farm |  | Carson City | 1970 | 168 | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 336
0288EXT1 | EXTERIOR FINISHES | 0288 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, including painting, staining, sealing or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. This building including the roof is in poor shape and should be weather sealed and caulked to prevent further damage. It is recommended that this project be done within the next two years. | PUMP HOUSE | 9982 | Correct | Farm |  | Carson City | 1965 | 120 | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 360
0293EXT3 | EXTERIOR DOOR REPLACEMENT | 0293 | The existing exterior wood doors appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement of the wood doors with two new metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | BREAK ROOM | 9982 | Correct | Farm |  | Carson City | 1970 | 168 | 2008-09-02 | Four to Ten Years | Long-Term Needs | 3 | 1000
0288EXT2 | EXTERIOR DOOR REPLACEMENT | 0288 | The existing exterior metal door appears to be original to the building. It is damaged from age and general wear and tear. This project would provide for the replacement and installation of one new metal door, frame and hardware. Removal and disposal of the existing door and painting of the new door is included in this estimate. | PUMP HOUSE | 9982 | Correct | Farm |  | Carson City | 1965 | 120 | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 750
0293EXT1 | EXTERIOR FINISHES | 0293 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, sealing or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 2 to 3 years and is recommended on a cyclical basis based on environmental conditions. | BREAK ROOM | 9982 | Correct | Farm |  | Carson City | 1970 | 168 | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 840
0293INT1 | INTERIOR FINISHES | 0293 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | BREAK ROOM | 9982 | Correct | Farm |  | Carson City | 1970 | 168 | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 840
0293EXT2 | ROOF REPLACEMENT | 0293 | The corrugated metal roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next two to three years with a standing seam metal roofing system. This estimate includes removal and disposal of the old roofing. | BREAK ROOM | 9982 | Correct | Farm |  | Carson City | 1970 | 168 | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2520
1404EXT5 | DEMOLISH STRUCTURE | 1404 | The Guard Tower #3 sways substantially during high winds and its structural integrity is suspect. The structure is also approaching 30 years of age and should be replaced. It is recommended that this structure be demolished and a new guard tower be built in its place. The cost estimate includes capping existing utilities and removal of possible asbestos containing materials. The "New Guard Tower" project should be implemented immediately following this project. | GUARD TOWER #3 NORTHEAST (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 144 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 15000
1408PLM1 | REMOVE AND REPLACE EXISTING WATER HEATER | 1408 | Two 100-gallon gas-fired water heaters supply domestic hot water. One has been replaced and the other is original to the building. The average life span of a typical gas/oil or electric water heater is eight to ten years. With the passage of time and constant use, the one unit is showing signs of wear. It is reaching the end of its expected life. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 13 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1988 | 11888 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 6500
1408INT1 | INTERIOR FINISHES | 1408 | The interior finishes are in fair to poor condition. It is recommended that the interior walls be painted in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 13 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1988 | 11888 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 59440
1408ELE1 | LIGHTING UPGRADE | 1408 | Existing building lighting fixtures in the rooms adjacent to the housing area use T-12 technology, and are older fluorescent types and are not energy efficient. The existing lighting in the housing areas are provided by high bay sodium type, large round fixtures. This project will upgrade the lighting fixtures in the area adjacent to the housing units with T-8 lamps and electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. It is also recommended that the sodium lights be replaced with new more energy efficient high-pressure sodium lights. These types of lights will provide better illumination and energy savings. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 13 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1988 | 11888 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 89160
1407EXT1 | DOG KENNEL DEMOLITION | 1407 | The Dog Kennel contains numerous code and safety issues including but not limited to rodent infestation, broken windows, broken or missing electrical fixtures, dry rot and possible structural damage due to the age. It has not been occupied for years. The building is dilapidated and deteriorating and has reached the end of its useful life. This project would provide funding for the demolition of the building. The existing stone was quarried on the prison site and it is suggested that the stone be salvaged for future use at the discretion of the Department of Corrections. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | DOG KENNEL (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 1200 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 12000
1406EXT5 | DEMOLISH STRUCTURE | 1406 | The Guard Tower #5 sways substantially during high winds and its structural integrity is suspect. The structure is also approaching 30 years of age and should be replaced. It is recommended that this structure be demolished and a new guard tower be built in its place. The cost estimate includes capping existing utilities and removal of possible asbestos containing materials. The "New Guard Tower" project should be implemented immediately following this project. | GUARD TOWER #5 SOUTHWEST (VACANT) | 9989 | Correct | NSP |  | Carson City | 1966 | 256 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 15000
1406EXT4 | NEW GUARD TOWER | 1406 | This project would provide for the construction of a new guard tower in place of the existing Guard Tower #3 Northeast. This project should be implemented immediately following the "Demolish Structure" project which will eliminate the existing guard tower. The cost estimate is based on the proposed Prison 8 Guard Tower design at Southern Desert Correctional Center. | GUARD TOWER #5 SOUTHWEST (VACANT) | 9989 | Correct | NSP |  | Carson City | 1966 | 256 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 560000
1405EXT4 | NEW GUARD TOWER | 1405 | This project would provide for the construction of a new guard tower in place of the existing Guard Tower #3 Northeast. This project should be implemented immediately following the "Demolish Structure" project which will eliminate the existing guard tower. The cost estimate is based on the proposed Prison 8 Guard Tower design at Indian Springs. | GUARD TOWER #4 SOUTHEAST (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 144 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 560000
1412EXT1 | EXTERIOR FINISHES | 1412 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding for the sealing of the exterior of the building. Included in the cost is sealing, caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | PUMP HOUSE (VACANT) | 9989 | Correct | NSP |  | Carson City | 1988 | 308 | 2009-02-10 | Four to Ten Years | Long-Term Needs | 3 | 1540
1404EXT4 | REPLACE GUARD TOWER | 1404 | This project would provide for the construction of a new guard tower in place of the existing Guard Tower #3 Northeast. This project should be implemented immediately following the "Demolish Structure" project which will eliminate the existing guard tower. The cost estimate is based on the proposed Prison 8 Guard Tower design at Indian Springs. | GUARD TOWER #3 NORTHEAST (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 144 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 560000
1408SFT1 | EXIT SIGN LIGHTING UPGRADE | 1408 | The existing exit signs in this building are older types and should be replaced with new self-illuminated or LED style signs with battery-backed internal systems. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 13 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1988 | 11888 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 2500
1403SEC1 | FIRE ALARM SYSTEM INSTALLATION | 1403 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2006 Section 7 and the 2006 International Fire Code. | GUARD TOWER #2 NORTH (VACANT) | 9989 | Correct | NSP |  | Carson City | 1963 | 624 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 4368
1405EXT5 | DEMOLISH STRUCTURE | 1405 | The Guard Tower #5 sways substantially during high winds and its structural integrity is suspect. The structure is also approaching 30 years of age and should be replaced. It is recommended that this structure be demolished and a new guard tower be built in its place. The cost estimate includes capping existing utilities and removal of possible asbestos containing materials. The "New Guard Tower" project should be implemented immediately following this project. | GUARD TOWER #4 SOUTHEAST (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 144 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 15000
1410ENR1 | LIGHTING UPGRADE | 1410 | Existing building lighting fixtures, T-12s, are older fluorescent types and not energy efficient. This project will upgrade lighting fixtures to T-8s with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. This project also includes the replacement of spot lights on the exterior of the structure. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | MAIN GATE/TOWER #1, NORTHWEST (VACANT) | 9989 | Correct | NSP |  | Carson City | 1963 | 450 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3375
1403EXT3 | EXTERIOR FINISHES | 1403 | It is important to maintain the finish, weather resistance and appearance of the building. The exterior finishes are faded and damaged to a point where the concrete is showing wear and deterioration. This project would provide funding for the exterior building envelope other than the roof, including painting, staining, or other applied finishes and caulking around windows, flashing, fixtures and other penetrations. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | GUARD TOWER #2 NORTH (VACANT) | 9989 | Correct | NSP |  | Carson City | 1963 | 624 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9360
1408EXT3 | EXTERIOR FINISHES | 1408 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding for the painting of the exterior of the building. Including in the cost is the sanding, priming, filling in the crack, caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT 13 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1988 | 11888 | 2009-02-10 | Four to Ten Years | Long-Term Needs | 3 | 59440
1411EXT3 | DISCONTINUE BUILDING USE | 1411 | The Old Electric Shop is dilapidated and deteriorating. It contains numerous code and safety issues including, but not limited to rodent infestation, broken or missing doors and windows, non code compliant entry stairs, possible asbestos contamination and broken or missing electrical fixtures. In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to providing drainage away from the buildings to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure The public/personnel should not be allowed to enter or use this building. | OLD ELECTRIC SHOP (VACANT) | 9989 | Correct | NSP |  | Carson City | 1900 | 1930 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 25000
1409SIT1 | EXTERIOR STAIRS | 1409 | The 2006 IBC Chapter 1009.5.1 requires the horizontal slope of stair treads in any direction not to exceed 2 percent. Chapter 1009.10 requires handrails be installed and a landing is required at the top and bottom of the stairs. There is an existing concrete stairway that provides access between the street and the building that is not within these required code parameters and is showing signs of settling and separation. This project would provide for the rebuilding of the concrete stairway to meet the 2006 IBC code requirements. Two handrails, one on each side of the stairway are included in this cost estimate. This project or a portion there of was previously recommended in the FCA report from July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | PROPERTY WAREHOUSE 1/OLD ARMORY(VACANT) | 9989 | Correct | NSP |  | Carson City | 1950 | 1800 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 7500
1409EXT2 | EXTERIOR FINISHES | 1409 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding for the painting of the exterior of the building. Included in the cost is sanding, priming, filling in the cracks, caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | PROPERTY WAREHOUSE 1/OLD ARMORY(VACANT) | 9989 | Correct | NSP |  | Carson City | 1950 | 1800 | 2009-02-10 | Four to Ten Years | Long-Term Needs | 3 | 18000
1410INT1 | INTERIOR FINISHES | 1410 | The interior wall, floor and ceiling finishes are in poor condition. The interior finishes are faded and damaged to a point where the concrete walls and floors are showing wear and deterioration. This project would provide funding for the interior walls, floors and ceilings to be painted on the lower and upper levels. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | MAIN GATE/TOWER #1, NORTHWEST (VACANT) | 9989 | Correct | NSP |  | Carson City | 1963 | 450 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5400
1410SEC2 | INSTALL FIRE ALARM SYSTEM | 1410 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2006 Section 7 and the 2006 International Fire Code. | MAIN GATE/TOWER #1, NORTHWEST (VACANT) | 9989 | Correct | NSP |  | Carson City | 1963 | 450 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 3150
1410SEC1 | SURVEILANCE / SECURITY SYSTEM INSTALLATION | 1410 | There is inadequate security camera coverage and insufficient recording equipment in the Guard Tower. This is a safety issue for the public, staff and inmates as all areas cannot be seen by the security staff or recorded in case of an incident. This project would provide for the installation of additional surveillance cameras and a security system for the entire building and all required connections to existing utility systems. | MAIN GATE/TOWER #1, NORTHWEST (VACANT) | 9989 | Correct | NSP |  | Carson City | 1963 | 450 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 20000
1410EXT3 | EXTERIOR FINISHES | 1410 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding for the painting of the exterior of the building. Included in the cost is sanding, priming, filling in the cracks, caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | MAIN GATE/TOWER #1, NORTHWEST (VACANT) | 9989 | Correct | NSP |  | Carson City | 1963 | 450 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6750
1410HVA1 | HVAC UPGRADE/INSTALLATION | 1410 | The heating unit appears to be original to the building. The unit is a forced-air-gas-type. The building is cooled by an evaporator cooler which is severely scared and has reached its normal life cycle. This project would provide for a complete HVAC system to be installed in the building including air handlers, duct work, connections to existing utilities, seismic bracing and an energy managements system. Design of the system is not included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | MAIN GATE/TOWER #1, NORTHWEST (VACANT) | 9989 | Correct | NSP |  | Carson City | 1963 | 450 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 27000
1410PLM1 | REPLACE PLUMBING SYSTEM AND INSTALL WATER HEATER | 1410 | The building's sanitary wastewater system is showing signs of deterioration. It was noted that the drains operate slowly. Deposits within the pipes will cause them to be restricted, which will slow the flow of water. It is recommended the wastewater system be replaced. The building's domestic water that is supplied to the facility has a high mineral content. This has a detrimental effect on the system. Pipe deterioration is accelerated. Deposits within these pipes restrict water flow as well. It is recommended this system be replaced concurrently with the drain system. The water closet and lavatory are reaching the end of their useful life. It is recommended these fixtures be replaced. For sanitation purposes, it is recommended a water heater be installed in this guard tower. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | MAIN GATE/TOWER #1, NORTHWEST (VACANT) | 9989 | Correct | NSP |  | Carson City | 1963 | 450 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35000
1408SEC1 | SURVEILANCE / SECURITY SYSTEM INSTALLATION | 1408 | There is no security system for this building except for a few isolated cameras. This is a safety issue for staff and inmates as all areas cannot be seen by the security staff or recorded in case of an incident. This project would provide for the installation of surveillance cameras and security system for the entire building and all required connections to existing utility systems. | HOUSING UNIT 13 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1988 | 11888 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 75000
1401SEC5 | REPLACE CELL DOORS | 1401 | Housing Unit No. 6 was constructed in 1981. The cell doors are original construction. They are damaged from inmate abuse and constant use and could become a security concern for staff and inmates. This project would provide for the replacement of the cell doors. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 11 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 192000
1401SFT3 | INSTALL FIRE ALARM SYSTEM | 1401 | The Housing unit has a smoke detector located in the bottom portion of the existing HVAC ducting system at each duct chase which provides the only fire protection system in the structure. There is no fire alarm or sprinkler system. This project would provide for the installation of a fully monitored fire alarm system in the housing unit. When completed, the new system will provide visual, as well as audible notification. | HOUSING UNIT 11 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 54607
1401SEC1 | REPLACE SECURITY GLAZING | 1401 | This housing unit is a tiered structure. It house inmates on two floors. One entrance door accesses the building. To enter the cellblock, inmates pass through a central assembly area. Four sets of double security doors are used to access the inmate rooms. The glazing in these doors gets broken and damaged frequently and should be replaced with security glazing. Security glazing is also located in the partition wall between the sally port and the guard station. These windows also experience damage and should be replaced with safety glazing. This project would provide funding for the purchase and installation of safety glazing. It is recommended that this project be implemented in the next two years. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 11 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 32000
1403ELE1 | LIGHTING UPGRADE | 1403 | Existing building lighting fixtures, T-12s, are older fluorescent types and not energy efficient. This project will upgrade lighting fixtures to T-8 lamps with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. This project also includes the replacement of spot lights on the exterior of the structure. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | GUARD TOWER #2 NORTH (VACANT) | 9989 | Correct | NSP |  | Carson City | 1963 | 624 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4680
1414EXT1 | DEMOLISH MAINTENANCE WAREHOUSE 2 | 1414 | The maintenance warehouse 2 contains numerous code and safety issues including but not limited to rodent infestation, broken windows, broken or missing electrical fixtures, dry rot and possible structural damage due to the age. The building is dilapidated and deteriorating and has reached the end of its useful life. This project would provide funding for the demolition of the building. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | MAINTENANCE WAREHOUSE 2 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1950 | 1288 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 15000
1401ELE1 | LIGHTING UPGRADE | 1401 | Existing building lighting fixtures, T-12s, are older fluorescent types and not energy efficient. This project will upgrade lighting fixtures to T-8s with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 11 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 58507
1401EXT1 | EXTERIOR FINISHES | 1401 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding for the painting of the exterior of the building. Including in the cost is the sanding, priming, filling in the crack, caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure.. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 11 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Four to Ten Years | Long-Term Needs | 3 | 78010
1401SEC4 | WINDOW REPLACEMENT | 1401 | The existing operable windows in the housing unit cells are original and have been damaged by inmate abuse and are no longer working as intended. This project would provide for the removal and replacement of the windows in the housing unit cells. | HOUSING UNIT 11 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 84000
1401INT2 | INTERIOR FINISHES | 1401 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HOUSING UNIT 11 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Four to Ten Years | Long-Term Needs | 3 | 39005
1401SFT2 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 1401 | The exit signs in this building are older types or painted on the walls. Illuminated exit signs shall be marked per 2003 IBC Section 1011.1. This project would provide funding to install self-illuminating or LED models with internal battery backups along all of the required exit pathways. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 11 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 5100
1401SEC2 | EXTERIOR DOOR REPLACEMENT | 1401 | The existing exterior doors to the housing unit are original to the building. They are showing signs of wear and deterioration from constant use and inmate abuse. Due to security concerns and the condition of the door, replacement is recommended. This project would provide for the removal and disposal of the existing doors and frames and replacement with new exterior security doors including door frames, hardware, security glazing, painting and connections to the security system as required. A total of 6 doors were used to generate this estimate. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 11 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 39000
1401SFT1 | FIRE SUPPRESSION SYSTEM INSTALLATION | 1401 | This building does not have an automatic fire suppression system. The 2006 IBC Chapter 903.2.5 states that "An automatic sprinkler system shall be provided throughout buildings with a Group I fire area". This building is an I-3 occupancy with sleeping quarters. It should be retrofitted with fire sprinklers during the next remodel or addition. This project would provide funding for the installation of fire sprinklers including backflow prevention devices. NAC 477.917 states that: Existing buildings and structures: Additions, alterations and repairs. (NRS 477.030) 1. If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. 2. The State Fire Marshal will determine the value of the building or structure and the value of any additions, alterations and repairs. If the owner of the building disagrees with the value as determined by the State Fire Marshal, the owner of the building may engage a qualified and disinterested appraiser to ascertain the fair market value of the building or structure and the value of any additions, alterations and repairs. 3. As used in this section, “addition” means any extension or increase in the floor space or height of a building or structure. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 11 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 109214
1401EXT2 | REPLACE ROOF | 1401 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 15 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1995. It is recommended that this building be re-roofed in the next two years to be consistent with the roofing program and the end of the warranty period. This project or a portion there of was previously recommended in the FCA report dated 02/07/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2006. | HOUSING UNIT 11 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 156020
1402INT4 | SUSPENDED CEILING REPLACEMENT | 1402 | The building has a suspended acoustical tile ceiling system. The t-bar framing is bent and rusted in many areas and a number of the ceiling tiles are damaged and stained. This project would provide for the replacement of the suspended acoustical tile ceiling system. Removal and disposal of the existing ceiling system is included in this estimate. | COURTHOUSE (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 1475 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14750
1402SFT2 | FIRE SUPPRESSION SYSTEM INSTALLATION | 1402 | The building is a B occupancy per the 2006 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of fire sprinklers including backflow prevention devices. NAC 477.917 states that: Existing buildings and structures: Additions, alterations and repairs. (NRS 477.030) 1. If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. 2. The State Fire Marshal will determine the value of the building or structure and the value of any additions, alterations and repairs. If the owner of the building disagrees with the value as determined by the State Fire Marshal, the owner of the building may engage a qualified and disinterested appraiser to ascertain the fair market value of the building or structure and the value of any additions, alterations and repairs. 3. As used in this section, “addition” means any extension or increase in the floor space or height of a building or structure. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | COURTHOUSE (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 1475 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 20650
1402SFT1 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 1402 | The exit signs in this building are older types or painted on the walls. Illuminated exit signs shall be marked per 2006 IBC Section 1011.1. This project would provide funding to install self-illuminating or LED models with internal battery backups along all of the required exit pathways. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | COURTHOUSE (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 1475 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 1700
1403INT1 | INTERIOR FINISHES | 1403 | The interior finishes are in poor condition. The interior finishes are faded and damaged to a point where the concrete is showing wear and deterioration. This project would provide funding for the interior walls and ceiling to be painted. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | GUARD TOWER #2 NORTH (VACANT) | 9989 | Correct | NSP |  | Carson City | 1963 | 624 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3120
1402SFT3 | SEISMIC RETROFIT | 1402 | This building is constructed of sandstone masonry walls on the exterior and wood framed interior walls and roof. The structure requires seismic strengthening to meet current life safety codes. This portion of the structure was built in the early 1900's and should be retrofitted to meet today's seismic codes. This project would provide for a seismic upgrade and retrofit to this facility. | COURTHOUSE (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 1475 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 73750
1401HVA1 | REPLACE HVAC / VENTILATION SYSTEM | 1401 | The air handler, fan coils and related equipment are original to the building, 1981. The building does not have a cooling system and the equipment is has reached it's expected life span. This project recommends replacement of all the air handlers, fan coils, ventilation equipment, exhaust fans and installation of a cooling system. It is recommended that this project be implemented in the next two years to avoid possible failure and emergency funding for replacement. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 11 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 468060
1402EXT1 | EXTERIOR FINISHES | 1402 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding for the painting of the exterior of the building. Included in the cost is sanding, priming, filling in the cracks, caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | COURTHOUSE (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 1475 | 2009-02-10 | Four to Ten Years | Long-Term Needs | 3 | 14750
1402SEC1 | SURVEILANCE / SECURITY SYSTEM INSTALLATION | 1402 | There is no security camera or recording system in the Courthouse. This is a safety issue for the public, staff and inmates as all areas cannot be seen by the security staff or recorded in case of an incident. This project would provide for the installation of surveillance cameras and security system for the entire courthouse and all required connections to existing utility systems. | COURTHOUSE (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 1475 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 50000
1402ELE1 | LIGHTING UPGRADE | 1402 | Existing building lighting fixtures, T-12s, are older fluorescent types and not energy efficient. This project will upgrade lighting fixtures to T-8s with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | COURTHOUSE (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 1475 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11062
1402ADA1 | ADA PROJECTS | 1402 | The building is lacking ADA compliant entry access, signage and restrooms. The restroom adjacent to the courtroom is not accessible. Grab bars and proper paper dispensers are necessary to make it comply. Currently the mirror height in this restroom is 49" above the finished floor. ICC/ANSI A117.1 - 2003 Section 603.3 states: "Mirrors shall be mounted with the bottom edge of the reflecting surface 40 inches maximum above the floor or ground". The existing railing on the accessible ramp that leads to the front door of the courthouse does not have proper extensions and is too low at 29 1/2". ICCANSI A117.1 - 2003 Section 505.4 states: "Top of gripping surfaces of handrails shall be 34" minimum and 38" maximum vertically above stair nosing and ramp surfaces." The existing doors in this facility have locking knob-type door hardware. ICC/ANSI A117.2003 section 404.2.6 requires door handles to have a shape that is easy to grasp with one hand and does not require tight grasping, pinching or twisting of the wrist to operate. The exterior door and entrance used by the inmates is not ADA compliant. This project would provide for an ADA complaint inmate entrance including door and hardware and floor modifications. Americans with Disabilities Act (ADA) regulations pertaining to building access, route of travel and restrooms has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances, route of travel inside the building and restrooms. Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2003 was referenced for this project. This project would provide funding to bring the building into ADA compliance. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | COURTHOUSE (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 1475 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 60000
1402INT3 | INTERIOR FINISHES | 1402 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to three years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | COURTHOUSE (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 1475 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7375
1402INT2 | REPLACE CARPET | 1402 | The interior floor covering is mostly carpet and is showing signs of extreme wear. Several areas are worn out and tears are evident throughout the carpeted areas causing a tripping hazard. This project would replace the existing broad loom carpet with carpet tile. Carpet tile would allow for future replacement of only those sections of carpet that are worn or damaged without the need to remove the entire carpeted area. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | COURTHOUSE (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 1475 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 14750
1402SFT4 | INSTALL FIRE ALARM SYSTEM | 1402 | This building is lacking an automatic fire detection and alarm system. It is recommended that a fully monitored fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2002 Section 7. | COURTHOUSE (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 1475 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 10325
1402HVA1 | REPLACE HVAC SYSTEM | 1402 | The Courthouse has a roof top packaged HVAC unit which appears to be more than 20 years old. This project would provide for installation of a new roof mounted packaged HVAC unit to be installed. It is recommended that this project be implemented in the next two to three years to avoid possible failure and emergency funding for replacement. | COURTHOUSE (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 1475 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 36875
2573EXT1 | EXTERIOR FINISHES | 2573 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding for the painting of the exterior of the building. Included in the cost is sanding, priming, filling in the cracks, caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOBBY CRAFT STORE | 9989 | Correct | NSP |  | Carson City | 0 | 320 | 2009-02-10 | Four to Ten Years | Long-Term Needs | 3 | 3200
2171EXT2 | EXTERIOR FINISHES | 2171 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding for the maintenance of the exterior of the building. Including in the cost is the sealing and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MAINTENANCE SHOP | 9989 | Correct | NSP |  | Carson City | 2004 | 4000 | 2009-02-10 | Four to Ten Years | Long-Term Needs | 3 | 4000
2171SFT1 | SEISMIC GAS SHUT OFF VALVE | 2171 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | MAINTENANCE SHOP | 9989 | Correct | NSP |  | Carson City | 2004 | 4000 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 3500
2171SFT2 | JANITOR CLOSET WALL PROTECTION | 2171 | The mop sinks in the Janitor's Closets are mounted adjacent to gypsum board that is showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54 inches above the floor finish. This project includes FRP on both Janitor's Closets that currently do not have wall protection. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | MAINTENANCE SHOP | 9989 | Correct | NSP |  | Carson City | 2004 | 4000 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2800
2171SFT3 | HANDRAIL INSTALLATION | 2171 | The 2006 International Building Code 1009.11 requires handrails on each side of stairways. The building has a set of stairs to access the offices on the mezzanine above the cafeteria and restrooms. The stairway has only one handrail. This project would provide for the installation of another handrail on the stairway to match the existing handrail. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | MAINTENANCE SHOP | 9989 | Correct | NSP |  | Carson City | 2004 | 4000 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 2500
2545EXT1 | EXTERIOR FINISHES | 2545 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding for the painting of the exterior of the building. Included in the cost is sanding, priming, filling in the cracks, caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | MODULAR EDUCATION BUILDING (VACANT) | 9989 | Correct | NSP |  | Carson City | 2002 | 1680 | 2009-02-10 | Four to Ten Years | Long-Term Needs | 3 | 16800
2573INT1 | INTERIOR FINISHES | 2573 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HOBBY CRAFT STORE | 9989 | Correct | NSP |  | Carson City | 0 | 320 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1600
2545SEC1 | SURVEILANCE / SECURITY SYSTEM INSTALLATION | 2545 | There is no security camera or recording system in the Modular Education Building. This is a safety issue for the staff and inmates as all areas cannot be seen by the security staff or recorded in case of an incident. This project would provide for the installation of surveillance cameras and a security system for the entire building and all required connections to existing utility systems. | MODULAR EDUCATION BUILDING (VACANT) | 9989 | Correct | NSP |  | Carson City | 2002 | 1680 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 35000
2569EXT1 | EXTERIOR FINISHES | 2569 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding for the painting of the exterior of the building. Included in the cost is priming and painting as well as caulking flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BOILER ROOM STORAGE SHED (VACANT) | 9989 | Correct | NSP |  | Carson City | 0 | 80 | 2009-02-10 | Four to Ten Years | Long-Term Needs | 3 | 160
2568SFT1 | STAIRWAY / HANDRAIL REPAIRS | 2568 | The existing stairs on the east side are constructed of wood, which have deteriorated to point where they are unsafe to use and do not meet current building codes. Also, the hand rails do not meet the requirements in the 2012 IBC section 1009.11. This project would provide for the removal and disposal of the existing stairs and construction of a new wood framed set of stairs and handrails. The door swings outward, therefore, a three foot wide landing will be required at the top of the stairs and is included in this estimate. | CHEMICAL STORAGE BUILDING (VACANT) | 9989 | Correct | NSP |  | Carson City | 0 | 308 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 4500
2545INT1 | INTERIOR FINISHES | 2545 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | MODULAR EDUCATION BUILDING (VACANT) | 9989 | Correct | NSP |  | Carson City | 2002 | 1680 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8400
2545SFT1 | FIRE SUPPRESSION SYSTEM INSTALLATION | 2545 | The building is a B occupancy per the 2006 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | MODULAR EDUCATION BUILDING (VACANT) | 9989 | Correct | NSP |  | Carson City | 2002 | 1680 | 2009-02-10 | Four to Ten Years | Long-Term Needs | 3 | 23520
2545SFT3 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 2545 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. Illuminated exit signs shall be marked per 2006 IBC Section 1011.1. This project would provide funding to install self-illuminating or LED models with internal battery backups as well as emergency egress lighting to provide illumination along the egress route. | MODULAR EDUCATION BUILDING (VACANT) | 9989 | Correct | NSP |  | Carson City | 2002 | 1680 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 1700
2545SFT2 | INSTALL FIRE ALARM SYSTEM | 2545 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2006 Section 7 and the 2006 International Fire Code. | MODULAR EDUCATION BUILDING (VACANT) | 9989 | Correct | NSP |  | Carson City | 2002 | 1680 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 11760
2171INT1 | INTERIOR FINISHES | 2171 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | MAINTENANCE SHOP | 9989 | Correct | NSP |  | Carson City | 2004 | 4000 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
9989SIT4 | REPLACE SALLY PORT GATES | 9989 | There are three 16’ high motorize gates used at the prison. One is located near the Main Gate / Tower #1 and two are located at Tower #2. The gates are problematic and are having difficulty opening and closing. When the gates are inoperable this creates security issues for the inmates and staff. This project would provide for the replacement of the three motorized gate assemblies. The gates will be required to meet UL Standard 325, per NRS 405.270. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | NEVADA STATE PRISON SITE | 9989 | Correct | NSP |  | Carson City | 1868 |  | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 45000
9989SIT1 | REPAVE DAMAGED ASPHALT AND RESEAL ROADWAY | 9989 | Asphalt walkways have been constructed to many of the facilities, including the guard towers; most of these walkways are in fair condition. Some of the driveways and parking areas throughout the site have damage. Numerous cracks, potholes, and general deterioration are present. Snow accumulations, frost and rain, etc. are contributing factors. This is typical wear over time. It was noted that under the main parking lot a geothermal area exists. This is the main cause of accelerated deterioration from heat rising through the road surface. The areas for replacement are all non-foot traffic areas. The asphalt leading to the housing units will only need to be sealed. 145,233 square feet was used to generate this estimate. An access road around the perimeter of the fence has been constructed. It is in good condition. For proper routine maintenance it is recommended the entire roadway be resealed. This type of application will extend the life of the asphalt. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | NEVADA STATE PRISON SITE | 9989 | Correct | NSP |  | Carson City | 1868 |  | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 480000
9989ELE2 | REPLACE ELECTRICAL SWITCH GEAR | 9989 | The main electrical switch gear for the site is located east of the Boiler Plant and is approximately 30 years old. The equipment has reached the end of its expected life and should be scheduled for replacement. This project would provide for removal and replacement of the existing switch gear and includes connection to the emergency generator. | NEVADA STATE PRISON SITE | 9989 | Correct | NSP |  | Carson City | 1868 |  | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 350000
9989SIT6 | SITE DRAINAGE STUDY | 9989 | The Nevada State Prison site has many areas with steep slopes, stone terraces, and paved areas that do not drain properly during a heavy precipitation event. There are no storm drains or designated channels for water to flow. This has caused areas of erosion around some of the structures and pavement. This project would provide for a site drainage study to be performed by a civil engineer to address the above mentioned items. Future projects may arise from the findings contained in the report which are not included in this estimate. | NEVADA STATE PRISON SITE | 9989 | Correct | NSP |  | Carson City | 1868 |  | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
9989ADA1 | ADA PROGRAM SITE ACCESSIBILITY | 9989 | The Nevada State Prison site currently does not have any ADA program accessibility for staff and inmates. There is also a visitation room at Housing Unit 12 in the north east area of the site. This project would provide for ADA program accessibility improvements to the prison site which may include a route of travel from the Administration / Visitation area to the Culinary / Dining facility, educational programs located in building 0094 Administration / Cell Blocks, the Gymnasium and Infirmary. This project includes new walks, ramps, stairs, handrails on existing and new stairs and other improvements which will provide ADA program accessibility and building code compliance in the lower yard and to Housing Unit 12. Also included is an ADA accessible walkway with a ramp and handrails for access into Housing Unit 12. This project should be done concurrent with the tenant improvement project in the Administration / Cell Block building which will relocate programs to the lower level of this building. | NEVADA STATE PRISON SITE | 9989 | Correct | NSP |  | Carson City | 1868 |  | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 1500000
9989SIT5 | REPLACE DAMAGED SEWER WASTE LINE | 9989 | The existing sewer waste line from the Culinary building to just west of the Courthouse has had numerous failures and is in need of replacement. This project would provide for the replacement of about 200 lineal feet of 4" sewer waste line. Excavation, backfill and boring under the existing structure is included in this estimate. A lump sum of $5,000 was used for the boring portion of this estimate. This project should be done concurrently with the sewer grinder installation project for the Culinary / Dining facility. | NEVADA STATE PRISON SITE | 9989 | Correct | NSP |  | Carson City | 1868 |  | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 18000
9989SIT7 | TELECOMMUNICATION / SECURITY SYSTEM INFRASTRUCTURE | 9989 | There are projects proposed for adding a fully monitored fire alarm, security and telecommunications system for the entire institution. This project would provide for the underground infrastructure improvements site wide excluding the buildings including excavation, conduit installation, backfill, and pull boxes as required for the systems. | NEVADA STATE PRISON SITE | 9989 | Correct | NSP |  | Carson City | 1868 |  | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 975000
9989SIT3 | REPLACE STAIRS TO CULINARY | 9989 | The exterior stairs that lead to the main entrance and culinary appears to be part of the original construction. Deterioration, spalling and cracking has occurred, mainly from exposure to the weather and freeze / thaw conditions. This project would provide funding for the removal and disposal of the old concrete and the installation of new concrete steps including handrails. This project should be done concurrently with ADA accessible route improvement project proposed for the lower yard. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | NEVADA STATE PRISON SITE | 9989 | Correct | NSP |  | Carson City | 1868 |  | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35000
0103HVA1 | REPLACE HVAC / VENTILATION SYSTEM | 0103 | The two rooftop packaged HVAC units, two evaporative coolers, two make-up air units and the exhaust fans appear to be more than 20 years old and are reaching the end of their useful life. This project recommends replacement of HVAC and make-up air equipment. It is recommended that this project be implemented in the next two years to avoid possible failure and emergency funding for replacement. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | CULINARY/DINING HALL (VACANT) | 9989 | Correct | NSP |  | Carson City | 1966 | 11334 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 340020
0105HVA1 | REPLACE HVAC SYSTEM | 0105 | The HVAC system consists of a boiler, air handler and a condenser. It is original equipment and should be scheduled for replacement in the next two to four years to mitigate possible emergency funding due to failure. | HOUSING UNIT 12 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1982 | 7931 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 237930
0106SFT2 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0106 | The exit signs in this building are older types or painted on the walls. Illuminated exit signs shall be marked per 2003 IBC Section 1011.1. This project would provide funding to install self-illuminating or LED models with internal battery backups along all of the required exit pathways. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 06 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 5100
0106HVA1 | REPLACE HVAC / VENTILATION SYSTEM | 0106 | The air handler, fan coils and related equipment are original to the building, 1981. The building does not have a cooling system and the equipment is has reached it's expected life span. This project recommends replacement of all the air handlers, fan coils, ventilation equipment, exhaust fans and installation of a cooling system. It is recommended that this project be implemented in the next two years to avoid possible failure and emergency funding for replacement. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 06 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 468060
0106SFT1 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0106 | This building does not have an automatic fire suppression system. The 2006 IBC Chapter 903.2.5 states that "An automatic sprinkler system shall be provided throughout buildings with a Group I fire area". This building is an I-3 occupancy with sleeping quarters. It should be retrofitted with fire sprinklers during the next remodel or addition. This project would provide funding for the installation of fire sprinklers including backflow prevention devices. NAC 477.917 states that: Existing buildings and structures: Additions, alterations and repairs. (NRS 477.030) 1. If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. 2. The State Fire Marshal will determine the value of the building or structure and the value of any additions, alterations and repairs. If the owner of the building disagrees with the value as determined by the State Fire Marshal, the owner of the building may engage a qualified and disinterested appraiser to ascertain the fair market value of the building or structure and the value of any additions, alterations and repairs. 3. As used in this section, “addition” means any extension or increase in the floor space or height of a building or structure. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 06 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 109214
0106EXT1 | EXTERIOR FINISHES | 0106 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding for the painting of the exterior of the building. Including in the cost is the sanding, priming, filling in the crack, caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure.. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 06 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Four to Ten Years | Long-Term Needs | 3 | 78010
0106SEC1 | REPLACE SECURITY GLAZING | 0106 | This housing unit is a tiered structure. It house inmates on two floors. One entrance door accesses the building. To enter the cellblock, inmates pass through a central assembly area. Four sets of double security doors are used to access the inmate rooms. The glazing in these doors gets broken and damaged frequently and should be replaced with security glazing. Security glazing is also located in the partition wall between the sally port and the guard station. These windows also experience damage and should be replaced with safety glazing. This project would provide funding for the purchase and installation of safety glazing. It is recommended that this project be implemented in the next two years. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 06 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 32000
0105EXT2 | EXTERIOR FINISHES | 0105 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide for the painting of the exterior of the building. Included in the cost estimate is the sanding, priming, filling in the cracks, caulking of the windows, flashing, fixtures and all other penetrations that may be required. This building should be painted within the next five to seven years. This project or a portion there of was previously recommended in the FCA report dated July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 12 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1982 | 7931 | 2009-02-10 | Four to Ten Years | Long-Term Needs | 3 | 79310
0105SFT2 | INSTALL FIRE ALARM SYSTEM | 0105 | The fire alarm system is original to the building and is due for an upgrade. This project would provide for the installation of a fully monitored fire alarm system in the housing unit. When completed, the new system will provide visual, as well as audible notification. | HOUSING UNIT 12 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1982 | 7931 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 55517
0105SEC2 | SURVEILANCE / SECURITY SYSTEM INSTALLATION | 0105 | There is no security system for this building except for a few isolated cameras which are new according to staff. This is a safety issue for staff and inmates as all areas cannot be seen by the security staff or recorded in case of an incident. This project would provide for the installation of surveillance cameras and security system for the entire building and all required connections to existing utility systems. | HOUSING UNIT 12 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1982 | 7931 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 75000
0109SEC5 | WINDOW REPLACEMENT | 0109 | The existing operable windows in the housing unit cells are original and have been damaged by inmate abuse and are no longer working as intended. This project would provide for the removal and replacement of the windows in the housing unit cells. | HOUSING UNIT 09 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 84000
0105SFT1 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0105 | The exit signs in this building are older types or painted on the walls. Illuminated exit signs shall be marked per 2006 IBC Section 1011.1. This project would provide funding to install self-illuminating or LED models with internal battery backups along all of the required exit pathways. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 12 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1982 | 7931 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 5100
0105ADA1 | ADA PROJECTS / RESTROOM REMODEL | 0105 | A separate public and inmate visitation restroom is present in this building. They does not meet the Americans with Disabilities Act (ADA) regulations. A retrofit is necessary to comply with ICC/ANSI A117.1-2002 Sections 603 - 604 and 2006 IBC Chapter 11. Given the current configuration of the restrooms, the work will include the installation of a new water closet, a urinal, sink, and stall; grab bars, faucets, mirrors, dispensers and hardware. Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with these criteria. It is recommended that applicable signage be replaced and/or relocated to comply with ADA requirements. This housing unit is a lockdown unit which does not have ADA compliant cells and shower. This project also includes funding for retrofitting 2 cells into ADA compliant cells and remodeling one shower unit into an ADA compliant shower unit. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 12 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1982 | 7931 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 80000
0105ELE1 | LIGHTING UPGRADE | 0105 | Existing building lighting fixtures, T-12s, are older fluorescent types and not energy efficient. This project will upgrade lighting fixtures to T-8s with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. Existing building lighting fixtures, T-12s, are older fluorescent types and not energy efficient. This project will upgrade lighting fixtures to T-8s with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 12 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1982 | 7931 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 59482
0105INT1 | INTERIOR FINISHES | 0105 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next four to six years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 12 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1982 | 7931 | 2009-02-10 | Four to Ten Years | Long-Term Needs | 3 | 39655
0103INT4 | RESURFACE KITCHEN FLOOR | 0103 | The painted concrete floor in the kitchen is worn and damaged and should be resurfaced. This project would provide for the installation of an epoxy based floor covering suitable for food preparation areas and health department specifications. 5,000 square feet of floor area was used to generate this estimate. | CULINARY/DINING HALL (VACANT) | 9989 | Correct | NSP |  | Carson City | 1966 | 11334 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 75000
0103EXT2 | REPLACE ROOF | 0103 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 15 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1999. It is recommended that this building be re-roofed in the next five years to be consistent with the roofing program and the end of the warranty period. | CULINARY/DINING HALL (VACANT) | 9989 | Correct | NSP |  | Carson City | 1966 | 11334 | 2009-02-10 | Four to Ten Years | Long-Term Needs | 3 | 226680
0106SEC2 | EXTERIOR DOOR REPLACEMENT | 0106 | The existing exterior doors to the housing unit are original to the building. They are showing signs of wear and deterioration from constant use and inmate abuse. Due to security concerns and the condition of the door, replacement is recommended. This project would provide for the removal and disposal of the existing doors and frames and replacement with new exterior security doors including door frames, hardware, security glazing, painting and connections to the security system as required. A total of 6 doors were used to generate this estimate. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 06 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 39000
0106SEC3 | REPLACE CELL DOORS | 0106 | Housing Unit No. 6 was constructed in 1981. The cell doors are original construction. They are damaged from inmate abuse and constant use and could become a security concern for staff and inmates. This project would provide for the replacement of the cell doors. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 06 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 192000
0106PLM3 | REPLACE WATERCLOSETS AND LAVATORIES | 0106 | The existing lavatories and water closets in this housing unit are made of vitreous china. These types of fixtures are damaged and broken frequently; weapons can be made from the broken pieces, which creates a security risk. Stainless steel units are more durable and are recommended to be installed. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 06 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 144000
0106INT1 | INTERIOR FINISHES | 0106 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HOUSING UNIT 06 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 39005
0106ENR1 | LIGHTING UPGRADE | 0106 | Existing building lighting fixtures, T-12s, are older fluorescent types and not energy efficient. This project will upgrade lighting fixtures to T-8s with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 06 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 58507
0106SEC5 | WINDOW REPLACEMENT | 0106 | The existing operable windows in the housing unit cells are original and have been damaged by inmate abuse and are no longer working as intended. This project would provide for the removal and replacement of the windows in the housing unit cells. | HOUSING UNIT 06 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 84000
0103PLM1 | INSTALL SEWAGE GRINDER | 0103 | The grease interceptor to the west of the building is not currently operating correctly. The sewage pipes down the line from the interceptor have been clogged with grease and other waste from the kitchen. It is recommended that a sewage grinder be installed between the kitchen sewage lines and the grease interceptor to remedy this problem. This project would provide for the purchase and installation of a sewage grinder and connection to existing sewer system in the Culinary. | CULINARY/DINING HALL (VACANT) | 9989 | Correct | NSP |  | Carson City | 1966 | 11334 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 25000
0109SEC1 | REPLACE SECURITY GLAZING | 0109 | This housing unit is a tiered structure. It house inmates on two floors. One entrance door accesses the building. To enter the cellblock, inmates pass through a central assembly area. Four sets of double security doors are used to access the inmate rooms. The glazing in these doors gets broken and damaged frequently and should be replaced with security glazing. Security glazing is also located in the partition wall between the sally port and the guard station. These windows also experience damage and should be replaced with safety glazing. This project would provide funding for the purchase and installation of safety glazing. It is recommended that this project be implemented in the next two years. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 09 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 32000
0107SEC1 | REPLACE SECURITY GLAZING | 0107 | This housing unit is a tiered structure. It house inmates on two floors. One entrance door accesses the building. To enter the cellblock, inmates pass through a central assembly area. Four sets of double security doors are used to access the inmate rooms. The glazing in these doors gets broken and damaged frequently and should be replaced with security glazing. Security glazing is also located in the partition wall between the sally port and the guard station. These windows also experience damage and should be replaced with safety glazing. This project would provide funding for the purchase and installation of safety glazing. It is recommended that this project be implemented in the next two years. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 07 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 32000
0107SFT2 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0107 | The exit signs in this building are older types or painted on the walls. Illuminated exit signs shall be marked per 2003 IBC Section 1011.1. This project would provide funding to install self-illuminating or LED models with internal battery backups along all of the required exit pathways. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 07 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 5100
0107HVA1 | REPLACE HVAC / VENTILATION SYSTEM | 0107 | The air handler, fan coils and related equipment are original to the building, 1981. The building does not have a cooling system and the equipment is has reached it's expected life span. This project recommends replacement of all the air handlers, fan coils, ventilation equipment, exhaust fans and installation of a cooling system. It is recommended that this project be implemented in the next two years to avoid possible failure and emergency funding for replacement. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 07 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 468060
0107PLM3 | REPLACE WATERCLOSETS AND LAVATORIES | 0107 | The existing lavatories and water closets in this housing unit are made of vitreous china. These types of fixtures are damaged and broken frequently; weapons can be made from the broken pieces, which creates a security risk. Stainless steel units are more durable and are recommended to be installed. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 07 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 144000
0107INT1 | INTERIOR FINISHES | 0107 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HOUSING UNIT 07 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 39005
0107EXT1 | EXTERIOR FINISHES | 0107 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding for the painting of the exterior of the building. Including in the cost is the sanding, priming, filling in the crack, caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure.. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 07 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Four to Ten Years | Long-Term Needs | 3 | 78010
0109SEC2 | EXTERIOR DOOR REPLACEMENT | 0109 | The existing exterior doors to the housing unit are original to the building. They are showing signs of wear and deterioration from constant use and inmate abuse. Due to security concerns and the condition of the door, replacement is recommended. This project would provide for the removal and disposal of the existing doors and frames and replacement with new exterior security doors including door frames, hardware, security glazing, painting and connections to the security system as required. A total of 6 doors were used to generate this estimate. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 09 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 39000
0109INT1 | INTERIOR FINISHES | 0109 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HOUSING UNIT 09 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 39005
0107SEC5 | WINDOW REPLACEMENT | 0107 | The existing operable windows in the housing unit cells are original and have been damaged by inmate abuse and are no longer working as intended. This project would provide for the removal and replacement of the windows in the housing unit cells. | HOUSING UNIT 07 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 84000
0109PLM3 | REPLACE WATERCLOSETS AND LAVATORIES | 0109 | The existing lavatories and water closets in this housing unit are made of vitreous china. These types of fixtures are damaged and broken frequently; weapons can be made from the broken pieces, which creates a security risk. Stainless steel units are more durable and are recommended to be installed. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 09 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 144000
0109SFT1 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0109 | This building does not have an automatic fire suppression system. The 2006 IBC Chapter 903.2.5 states that "An automatic sprinkler system shall be provided throughout buildings with a Group I fire area". This building is an I-3 occupancy with sleeping quarters. It should be retrofitted with fire sprinklers during the next remodel or addition. This project would provide funding for the installation of fire sprinklers including backflow prevention devices. NAC 477.917 states that: Existing buildings and structures: Additions, alterations and repairs. (NRS 477.030) 1. If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. 2. The State Fire Marshal will determine the value of the building or structure and the value of any additions, alterations and repairs. If the owner of the building disagrees with the value as determined by the State Fire Marshal, the owner of the building may engage a qualified and disinterested appraiser to ascertain the fair market value of the building or structure and the value of any additions, alterations and repairs. 3. As used in this section, “addition” means any extension or increase in the floor space or height of a building or structure. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 09 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 109214
0098ELE1 | LIGHTING UPGRADE | 0098 | Existing building lighting fixtures, T-12s, are older fluorescent types and not energy efficient. This project will upgrade lighting fixtures to T-8s with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | BOOK BINDERY (VACANT) | 9989 | Correct | NSP |  | Carson City | 1976 | 4137 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 31027
0109EXT2 | REPLACE ROOF | 0109 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 15 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1995. It is recommended that this building be re-roofed in the next two years to be consistent with the roofing program and the end of the warranty period. This project or a portion there of was previously recommended in the FCA report dated 02/07/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2006. | HOUSING UNIT 09 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 156020
0103SEC1 | SURVEILANCE / SECURITY SYSTEM INSTALLATION | 0103 | There is no security camera or recording system in the Culinary/ Dining Hall. This is a safety issue for the staff and inmates as all areas cannot be seen by the security staff or recorded in case of an incident. This project would provide for the installation of surveillance cameras and a security system for the entire building and all required connections to existing utility systems. | CULINARY/DINING HALL (VACANT) | 9989 | Correct | NSP |  | Carson City | 1966 | 11334 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 50000
0109SFT3 | INSTALL FIRE ALARM SYSTEM | 0109 | The Housing unit has a smoke detector located in the bottom portion of the existing HVAC ducting system at each duct chase which provides the only fire protection system in the structure. There is no fire alarm or sprinkler system. This project would provide for the installation of a fully monitored fire alarm system in the housing unit. When completed, the new system will provide visual, as well as audible notification. | HOUSING UNIT 09 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 54607
0107SEC3 | REPLACE CELL DOORS | 0107 | Housing Unit No. 7 was constructed in 1981. The cell doors are original construction. They are damaged from inmate abuse and constant use and could become a security concern for staff and inmates. This project would provide for the replacement of the cell doors. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 07 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 192000
0108ENR1 | LIGHTING UPGRADE | 0108 | Existing building lighting fixtures, T-12s, are older fluorescent types and not energy efficient. This project will upgrade lighting fixtures to T-8s with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 08 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 58507
0109EXT1 | EXTERIOR FINISHES | 0109 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding for the painting of the exterior of the building. Including in the cost is the sanding, priming, filling in the crack, caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure.. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 09 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Four to Ten Years | Long-Term Needs | 3 | 78010
0108EXT2 | REPLACE ROOF | 0108 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 15 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1995. It is recommended that this building be re-roofed in the next two years to be consistent with the roofing program and the end of the warranty period. This project or a portion there of was previously recommended in the FCA report dated 02/07/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2006. | HOUSING UNIT 08 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 156020
0108SEC5 | WINDOW REPLACEMENT | 0108 | The existing operable windows in the housing unit cells are original and have been damaged by inmate abuse and are no longer working as intended. This project would provide for the removal and replacement of the windows in the housing unit cells. | HOUSING UNIT 08 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 84000
0108SFT3 | INSTALL FIRE ALARM SYSTEM | 0108 | The Housing unit has a smoke detector located in the bottom portion of the existing HVAC ducting system at each duct chase which provides the only fire protection system in the structure. There is no fire alarm or sprinkler system. This project would provide for the installation of a fully monitored fire alarm system in the housing unit. When completed, the new system will provide visual, as well as audible notification. | HOUSING UNIT 08 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 54607
0108HVA1 | REPLACE HVAC / VENTILATION SYSTEM | 0108 | The air handler, fan coils and related equipment are original to the building, 1981. The building does not have a cooling system and the equipment is has reached it's expected life span. This project recommends replacement of all the air handlers, fan coils, ventilation equipment, exhaust fans and installation of a cooling system. It is recommended that this project be implemented in the next two years to avoid possible failure and emergency funding for replacement. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 08 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 468060
0108SFT1 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0108 | This building does not have an automatic fire suppression system. The 2006 IBC Chapter 903.2.5 states that "An automatic sprinkler system shall be provided throughout buildings with a Group I fire area". This building is an I-3 occupancy with sleeping quarters. It should be retrofitted with fire sprinklers during the next remodel or addition. This project would provide funding for the installation of fire sprinklers including backflow prevention devices. NAC 477.917 states that: Existing buildings and structures: Additions, alterations and repairs. (NRS 477.030) 1. If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. 2. The State Fire Marshal will determine the value of the building or structure and the value of any additions, alterations and repairs. If the owner of the building disagrees with the value as determined by the State Fire Marshal, the owner of the building may engage a qualified and disinterested appraiser to ascertain the fair market value of the building or structure and the value of any additions, alterations and repairs. 3. As used in this section, “addition” means any extension or increase in the floor space or height of a building or structure. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 08 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 109214
0107ENR1 | LIGHTING UPGRADE | 0107 | Existing building lighting fixtures, T-12s, are older fluorescent types and not energy efficient. This project will upgrade lighting fixtures to T-8s with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 07 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 58507
0108INT1 | INTERIOR FINISHES | 0108 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HOUSING UNIT 08 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 39005
0107SFT3 | INSTALL FIRE ALARM SYSTEM | 0107 | The Housing unit has a smoke detector located in the bottom portion of the existing HVAC ducting system at each duct chase which provides the only fire protection system in the structure. There is no fire alarm or sprinkler system. This project would provide for the installation of a fully monitored fire alarm system in the housing unit. When completed, the new system will provide visual, as well as audible notification. | HOUSING UNIT 07 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 54607
0108SEC3 | REPLACE CELL DOORS | 0108 | Housing Unit No. 8 was constructed in 1981. The cell doors are original construction. They are damaged from inmate abuse and constant use and could become a security concern for staff and inmates. This project would provide for the replacement of the cell doors. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 08 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 192000
0108PLM3 | REPLACE WATERCLOSETS AND LAVATORIES | 0108 | The existing lavatories and water closets in this housing unit are made of vitreous china. These types of fixtures are damaged and broken frequently; weapons can be made from the broken pieces, which creates a security risk. Stainless steel units are more durable and are recommended to be installed. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 08 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 144000
0108SEC2 | EXTERIOR DOOR REPLACEMENT | 0108 | The existing exterior doors to the housing unit are original to the building. They are showing signs of wear and deterioration from constant use and inmate abuse. Due to security concerns and the condition of the door, replacement is recommended. This project would provide for the removal and disposal of the existing doors and frames and replacement with new exterior security doors including door frames, hardware, security glazing, painting and connections to the security system as required. A total of 6 doors were used to generate this estimate. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 08 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 39000
0108EXT1 | EXTERIOR FINISHES | 0108 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding for the painting of the exterior of the building. Including in the cost is the sanding, priming, filling in the crack, caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure.. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 08 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Four to Ten Years | Long-Term Needs | 3 | 78010
0108SEC1 | REPLACE SECURITY GLAZING | 0108 | This housing unit is a tiered structure. It house inmates on two floors. One entrance door accesses the building. To enter the cellblock, inmates pass through a central assembly area. Four sets of double security doors are used to access the inmate rooms. The glazing in these doors gets broken and damaged frequently and should be replaced with security glazing. Security glazing is also located in the partition wall between the sally port and the guard station. These windows also experience damage and should be replaced with safety glazing. This project would provide funding for the purchase and installation of safety glazing. It is recommended that this project be implemented in the next two years. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 08 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 32000
0107EXT2 | REPLACE ROOF | 0107 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 15 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1995. It is recommended that this building be re-roofed in the next two years to be consistent with the roofing program and the end of the warranty period. This project or a portion there of was previously recommended in the FCA report dated 02/07/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2006. | HOUSING UNIT 07 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 156020
0110SFT1 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0110 | This building does not have an automatic fire suppression system. The 2006 IBC Chapter 903.2.5 states that "An automatic sprinkler system shall be provided throughout buildings with a Group I fire area". This building is an I-3 occupancy with sleeping quarters. It should be retrofitted with fire sprinklers during the next remodel or addition. This project would provide funding for the installation of fire sprinklers including backflow prevention devices. NAC 477.917 states that: Existing buildings and structures: Additions, alterations and repairs. (NRS 477.030) 1. If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. 2. The State Fire Marshal will determine the value of the building or structure and the value of any additions, alterations and repairs. If the owner of the building disagrees with the value as determined by the State Fire Marshal, the owner of the building may engage a qualified and disinterested appraiser to ascertain the fair market value of the building or structure and the value of any additions, alterations and repairs. 3. As used in this section, “addition” means any extension or increase in the floor space or height of a building or structure. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 10/GUN POST #5 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 109214
0108SFT2 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0108 | The exit signs in this building are older types or painted on the walls. Illuminated exit signs shall be marked per 2003 IBC Section 1011.1. This project would provide funding to install self-illuminating or LED models with internal battery backups along all of the required exit pathways. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 08 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 5100
0114ELE2 | ELECTRICAL UPGRADE | 0114 | This building was constructed before the high demand for new types of electrical devices were needed. As time progressed the buildings electrical demand has changed. It is utilized to its current maximum potential. The electrical panels and receptacles are at their limit. It is recommended the entire system be upgraded to meet the evolving needs of the building. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/19/2006. | STORAGE & MAINTENANCE OFFICE (VACANT) | 9989 | Correct | NSP |  | Carson City | 1952 | 2190 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 77500
0109SFT2 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0109 | The exit signs in this building are older types or painted on the walls. Illuminated exit signs shall be marked per 2003 IBC Section 1011.1. This project would provide funding to install self-illuminating or LED models with internal battery backups along all of the required exit pathways. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 09 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 5100
0114SFT4 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0114 | This building does not have an automatic fire suppression system. We are recommending installation of fire sprinklers in critical need buildings within the prison enclosure. This project will include a backflow prevention device as required by state law. State law regulates connections between public water systems and sources of contaminants which can enter the system by back pressure or siphonage. Public water systems include supplies, systems for pumping, storage and treatment and distribution systems. The NAC 477.915 requires a fire sprinkler system to be installed: (c) If the building: (1) Is designated as a B occupancy; (2) Regardless of occupancy designation, has a floor area which exceeds 12,000 square feet on any floor or 24,000 square feet on all floors, including any mezzanines; or (3) Is an R-1 or R-2 occupancy, be scheduled for installation of an automatic fire suppression system during the next remodeling of or addition to the building. This building contains a B occupancy. Water purveyors require service backflow prevention immediately after the meter, which isolates the customer's water system from the distribution system. If fire water or irrigation systems tap directly into the public system, backflow devices would be necessary on both domestic, irrigation and fire water services. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/19/2006. | STORAGE & MAINTENANCE OFFICE (VACANT) | 9989 | Correct | NSP |  | Carson City | 1952 | 2190 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 54750
0114ELE1 | LIGHTING UPGRADE | 0114 | Existing building lighting fixtures, T-12s, are older fluorescent types and not energy efficient. This project will upgrade lighting fixtures to T-8s with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/19/2006. | STORAGE & MAINTENANCE OFFICE (VACANT) | 9989 | Correct | NSP |  | Carson City | 1952 | 2190 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8760
0114SFT1 | FIRE ALARM SYSTEM INSTALLATION | 0114 | This building is equipped with an automatic fire detection and alarm system, but the system is antiquated. It is recommended that the fire detection and alarm system be upgraded. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 1998 Section 7. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/19/2006. | STORAGE & MAINTENANCE OFFICE (VACANT) | 9989 | Correct | NSP |  | Carson City | 1952 | 2190 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 6570
0114SFT3 | CONSTRUCT OCCUPANCY SEPARATION WALLS | 0114 | The building has low hazard storage adjacent to the welding shop. The low hazard storage areas are S-2 occupancy. The welding shop is H-4 occupancy. The 2003 IBC table 302.3.2 states that where these occupancies are adjacent to each other a 1-hour occupancy separation wall is required. This project would provide for the construction of a 1-hour occupancy separation walls be constructed on either side of the welding shop. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/19/2006. | STORAGE & MAINTENANCE OFFICE (VACANT) | 9989 | Correct | NSP |  | Carson City | 1952 | 2190 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 20000
0114HVA1 | REPLACE AIR CONDITIONERS WITH EVAPORATIVE COOLERS | 0114 | Each separate section is cooled by window-mounted air-conditioners. The units are reaching the end of useful live. With the use and/or occupancy of the each section either being storage, welding or small repairs, an evaporative cooler would operate more efficient. This project would provide funding for the purchase and installation of three evaporative coolers including all required connections to utilities. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/19/2006. | STORAGE & MAINTENANCE OFFICE (VACANT) | 9989 | Correct | NSP |  | Carson City | 1952 | 2190 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
0112INT1 | REPLACE VINYL/ ASBESTOS TILE FLOOR | 0112 | The existing building is used as an armory. The floor tiles contain asbestos and have reached the end of their useful life. When cabinets or files are moved around, asbestos fiber becomes air-borne, this is harmful to anyone inside the building. This project would provide funding for the removal and disposal of the asbestos tile and the installation of vinyl floor tiles to be installed. This project or a portion there of was previously recommended in the FCA report from July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | COTTAGE #1 (NSP) LOCATED AT WSCC(VACANT) | 9989 | Correct | NSP |  | Carson City | 1957 | 850 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 29750
0114PLM1 | REPLACE DOMESTIC AND WASTE WATER SYSTEMS | 0114 | The sanitary wastewater system is showing signs of deterioration. It was noted that the drains operate adequately. Because of the deterioration, the system is not working to its full potential. Some of the lines are original to the building and are in fair condition. The passage of time and constant heavy use is a contributing factor to problems that arise. Deposits within the pipes will cause them to be restricted, which will slow the flow of water. It is recommended the entire wastewater system be replaced. The domestic water that is supplied to the facility has a high mineral content. This has a detrimental effect on the system. Pipe deterioration is accelerated. Deposits within these pipes restrict water flow as well. It is recommended this system be replaced concurrently with the drain system. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/19/2006. | STORAGE & MAINTENANCE OFFICE (VACANT) | 9989 | Correct | NSP |  | Carson City | 1952 | 2190 | 2009-02-10 | Four to Ten Years | Long-Term Needs | 3 | 46000
0112HVA1 | REPLACE HEATER, INSTALL EVAPORATIVE COOLER | 0112 | The building is currently used for storage files. It is important to maintain temperature. The heater appears to be original to the building. It is not energy efficient and has reached the end of its useful life. There is no air-conditioning or ways of cooling the building. This project would provide funding for the design, purchase and installation of a new HVAC system. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | COTTAGE #1 (NSP) LOCATED AT WSCC(VACANT) | 9989 | Correct | NSP |  | Carson City | 1957 | 850 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 25500
0114EXT1 | STONE RE-POINTING | 0114 | The existing building exterior is unreinforced natural stone that was quarried directly from the correctional facility site. Some portions of this structure are over 50 years old. There are numerous areas where the mortar is failing, missing and not sealed properly due the age, settling and exposure to the weather. This project would provide for the cleaning, repair and re-pointing of the exterior stone work. | STORAGE & MAINTENANCE OFFICE (VACANT) | 9989 | Correct | NSP |  | Carson City | 1952 | 2190 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 21900
0114SFT2 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0114 | The exit signs in this building are older types. Illuminated exit signs shall be marked per 2003 IBC Section 1011.1. This project would provide funding to install self-illuminating or LED models with internal battery backups along all of the required exit pathways. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/19/2006. | STORAGE & MAINTENANCE OFFICE (VACANT) | 9989 | Correct | NSP |  | Carson City | 1952 | 2190 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 4000
0120SFT2 | SEISMIC GAS SHUT OFF | 0120 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion there of was previously recommended in the FCA report from July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | COTTAGE #3 (NSP) LOCATED AT WSCC(VACANT) | 9989 | Correct | NSP |  | Carson City | 1953 | 930 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 3500
0120HVA1 | HVAC INSTALLATION | 0120 | The building is currently used as an Armory. It is important to maintain temperature and humidity. The heater appears to be original to the building. It is not energy efficient and has reached the end of its useful life. There is no air-conditioning or way of controlling humidity. This project would provide funding for the purchase and installation of a new HVAC and humidity control unit. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | COTTAGE #3 (NSP) LOCATED AT WSCC(VACANT) | 9989 | Correct | NSP |  | Carson City | 1953 | 930 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 27900
0107SFT1 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0107 | This building does not have an automatic fire suppression system. The 2006 IBC Chapter 903.2.5 states that "An automatic sprinkler system shall be provided throughout buildings with a Group I fire area". This building is an I-3 occupancy with sleeping quarters. It should be retrofitted with fire sprinklers during the next remodel or addition. This project would provide funding for the installation of fire sprinklers including backflow prevention devices. NAC 477.917 states that: Existing buildings and structures: Additions, alterations and repairs. (NRS 477.030) 1. If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. 2. The State Fire Marshal will determine the value of the building or structure and the value of any additions, alterations and repairs. If the owner of the building disagrees with the value as determined by the State Fire Marshal, the owner of the building may engage a qualified and disinterested appraiser to ascertain the fair market value of the building or structure and the value of any additions, alterations and repairs. 3. As used in this section, “addition” means any extension or increase in the floor space or height of a building or structure. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 07 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 109214
0107SEC2 | EXTERIOR DOOR REPLACEMENT | 0107 | The existing exterior doors to the housing unit are original to the building. They are showing signs of wear and deterioration from constant use and inmate abuse. Due to security concerns and the condition of the door, replacement is recommended. This project would provide for the removal and disposal of the existing doors and frames and replacement with new exterior security doors including door frames, hardware, security glazing, painting and connections to the security system as required. A total of 6 doors were used to generate this estimate. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 07 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 39000
0106EXT2 | REPLACE ROOF | 0106 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 15 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1995. It is recommended that this building be re-roofed in the next two years to be consistent with the roofing program and the end of the warranty period. This project or a portion there of was previously recommended in the FCA report dated 02/07/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2006. | HOUSING UNIT 06 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 156020
0114PLM2 | INSTALL 40 GALLON GAS WATER HEATERS | 0114 | The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear. It is recommended that a new gas-fired water heater be installed for more efficient use of energy. This estimate includes: 100 feet of gas pipe, fittings, couplers, and labor for installation. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/19/2006. | STORAGE & MAINTENANCE OFFICE (VACANT) | 9989 | Correct | NSP |  | Carson City | 1952 | 2190 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 3750
0110INT1 | REPLACE FLOORING IN GUN POST #5 | 0110 | Attached to the roof of this housing unit is Gun Post #5. The flooring is vinyl composition tile (VCT) and has deteriorated from constant use, weather and the passage of time. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 10/GUN POST #5 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
0106SFT3 | INSTALL FIRE ALARM SYSTEM | 0106 | The Housing unit has a smoke detector located in the bottom portion of the existing HVAC ducting system at each duct chase which provides the only fire protection system in the structure. There is no fire alarm or sprinkler system. This project would provide for the installation of a fully monitored fire alarm system in the housing unit. When completed, the new system will provide visual, as well as audible notification. | HOUSING UNIT 06 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 54607
0110EXT2 | EXTERIOR FINISHES | 0110 | It is important to maintain the finish, weather resistance and appearance of the building. The exterior paint is peeling and the caulking around the windows, flashing, fixtures and other penetrations is failing. This project would provide for the painting of the exterior of the building. Included in the cost estimate is the sanding, priming, filling in the cracks, caulking of the windows, flashing, fixtures and all other penetrations that may be required. This building should be painted within the next two years. This project or a portion there of was previously recommended in the FCA report dated 09/17/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/19/2006. | HOUSING UNIT 10/GUN POST #5 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 78010
0110HVA1 | REPLACE HVAC / VENTILATION SYSTEM | 0110 | The air handler, fan coils and related equipment are original to the building, 1981. The building does not have a cooling system and the equipment is has reached it's expected life span. This project recommends replacement of all the air handlers, fan coils, ventilation equipment, exhaust fans and installation of a cooling system. It is recommended that this project be implemented in the next two years to avoid possible failure and emergency funding for replacement. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 10/GUN POST #5 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 468060
0110SFT2 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0110 | The exit signs in this building are older types or painted on the walls. Illuminated exit signs shall be marked per 2003 IBC Section 1011.1. This project would provide funding to install self-illuminating or LED models with internal battery backups along all of the required exit pathways. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 10/GUN POST #5 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 5100
0110SEC3 | REPLACE CELL DOORS | 0110 | Housing Unit No. 10 was constructed in 1981. The cell doors are original construction. They are damaged from inmate abuse and constant use and could become a security concern for staff and inmates. This project would provide for the replacement of the cell doors. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 10/GUN POST #5 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 192000
0110SEC2 | EXTERIOR DOOR REPLACEMENT | 0110 | The existing exterior doors to the housing unit are original to the building. They are showing signs of wear and deterioration from constant use and inmate abuse. Due to security concerns and the condition of the door, replacement is recommended. This project would provide for the removal and disposal of the existing doors and frames and replacement with new exterior security doors including door frames, hardware, security glazing, painting and connections to the security system as required. A total of 6 doors were used to generate this estimate. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 10/GUN POST #5 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 39000
0113EXT2 | DISCONTINUE BUILDING USE | 0113 | The existing Warden’s House is dilapidated and deteriorating. It contains numerous code and safety issues including, but not limited to an upper level exterior door without a deck or stairway, rodent infestation, broken or missing doors and windows, possible asbestos contamination and broken or missing electrical fixtures. In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to providing drainage away from the buildings to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure The public/personnel should not be allowed to enter or use this building. This project or a portion there of was previously recommended in the FCA report dated July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | INVESTIGATION/OLD WARDENS HOUSE (VACANT) | 9989 | Correct | NSP |  | Carson City | 1957 | 2880 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 25000
0110ENR1 | LIGHTING UPGRADE | 0110 | Existing building lighting fixtures, T-12s, are older fluorescent types and not energy efficient. This project will upgrade lighting fixtures to T-8s with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 10/GUN POST #5 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 58507
0109ENR1 | LIGHTING UPGRADE | 0109 | Existing building lighting fixtures, T-12s, are older fluorescent types and not energy efficient. This project will upgrade lighting fixtures to T-8s with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 09 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 58507
0110SFT3 | INSTALL FIRE ALARM SYSTEM | 0110 | The Housing unit has a smoke detector located in the bottom portion of the existing HVAC ducting system at each duct chase which provides the only fire protection system in the structure. There is no fire alarm or sprinkler system. This project would provide for the installation of a fully monitored fire alarm system in the housing unit. When completed, the new system will provide visual, as well as audible notification. | HOUSING UNIT 10/GUN POST #5 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 54607
0110SEC5 | WINDOW REPLACEMENT | 0110 | The existing operable windows in the housing unit cells are original and have been damaged by inmate abuse and are no longer working as intended. This project would provide for the removal and replacement of the windows in the housing unit cells. | HOUSING UNIT 10/GUN POST #5 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 84000
0110EXT1 | REPLACE WINDOWS AND DOORS IN GUN POST 5 | 0110 | The gun post contains two doors and four windows. The seals are broken on several of the windows. Because of the broken seals, condensation occurs and the windows become fogged between the panes of glass. It is difficult to see through this fogging. This is a structure that observes inmates, so it is important that the officer has a clear line of site. A high probability exists that this situation will occur with the remaining windows also. This project would provide funding for the purchase and installation of new security/safety glazed windows. The two doors are also showing signs of wear and deterioration. The hardware on one door is damaged from constant use. This project would provide funding for the purchase and installation of new doors and associated hardware. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 10/GUN POST #5 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18000
0110SEC1 | REPLACE SECURITY GLAZING | 0110 | This housing unit is a tiered structure. It house inmates on two floors. One entrance door accesses the building. To enter the cellblock, inmates pass through a central assembly area. Four sets of double security doors are used to access the inmate rooms. The glazing in these doors gets broken and damaged frequently and should be replaced with security glazing. Security glazing is also located in the partition wall between the sally port and the guard station. These windows also experience damage and should be replaced with safety glazing. This project would provide funding for the purchase and installation of safety glazing. It is recommended that this project be implemented in the next two years. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 10/GUN POST #5 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 32000
0110EXT3 | REPLACE ROOF | 0110 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 15 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1995. It is recommended that this building be re-roofed in the next two years to be consistent with the roofing program and the end of the warranty period. This project or a portion there of was previously recommended in the FCA report dated 02/07/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2006. | HOUSING UNIT 10/GUN POST #5 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 156020
0112SFT1 | SEISMIC GAS SHUT OFF | 0112 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion there of was previously recommended in the FCA report from July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | COTTAGE #1 (NSP) LOCATED AT WSCC(VACANT) | 9989 | Correct | NSP |  | Carson City | 1957 | 850 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 3500
0112ELE1 | LIGHTING UPGRADE | 0112 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts to current standards, resulting in increased efficiency and reduced costs associated with illumination. Any electrical wiring upgrades are not included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | COTTAGE #1 (NSP) LOCATED AT WSCC(VACANT) | 9989 | Correct | NSP |  | Carson City | 1957 | 850 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2975
0110INT2 | INTERIOR FINISHES | 0110 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HOUSING UNIT 10/GUN POST #5 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 39005
0094SEC1 | REPLACE CELL BLOCK DOOR CONTROL PANELS AND MOTORS | 0094 | Problems exist with the door control panel and cell door motor systems in the cell blocks. It is believed the systems are original equipment. Repairs to the control systems and motors are difficult because replacement parts are not being manufactured for the units. It was noted that at one time, some of the controls were operated by an electric motor however most of them have become defective. Some of the systems are now operated manually. This type of operation is more difficult and could create a possible security risk. It is recommended that the door control and cell door motor systems be replaced in the cell blocks. This estimate is for 5 door control systems and 300 cell door motors. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | ADMINISTRATION/CELL BLOCKS (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 106251 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 2250000
0094ADA2 | SIGNAGE FOR ADA COMPLIANCE | 0094 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with these criteria. It is recommended that applicable signage be installed where required. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | ADMINISTRATION/CELL BLOCKS (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 106251 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 10000
0094EXT3 | REPLACE WINDOWS | 0094 | Some of the existing windows open inward which protrudes into the walkways and are original to the building. Some of the units are cracked or damaged, seals are broken, are difficult to operate and they have reached the end of their useful life. This project would provide funding to replace the window units with new security window units. A total of 352 units was used to generate this estimate. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | ADMINISTRATION/CELL BLOCKS (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 106251 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1056000
0094SFT3 | FIRE ALARM SYSTEM UPGRADE | 0094 | This building is equipped with an automatic fire detection and alarm system, but the system is old, does not meet current code requirements and is missing in some locations. It is recommended that the fire detection and alarm system be upgraded to a fully monitored. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements and building codes. This project should be coordinated with the fire sprinkler upgrade project. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | ADMINISTRATION/CELL BLOCKS (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 106251 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 743757
0094SFT4 | INSTALL SECOND MEANS OF EGRESS IN VISITORS CENTER | 0094 | The visitor center has only one means of egress. The maximum posted occupancy of this room is 76. The 2006 International Building Code (IBC), table 1018.1 requires the occupant load 1-500 to have a minimum of 2 exits. This project would provide for the labor and material necessary to install a second means of egress. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | ADMINISTRATION/CELL BLOCKS (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 106251 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 35000
0094EXT2 | REPLACE EXISTING ROOF | 0094 | The roof on this building was in fair condition at the time of the survey. The single-ply system is spongy along the walkways, and is especially noticeable at the bottom of the stairs from the third story to the fourth story and there is an old built-up roofing system with concrete pavers on top which should be replaced. It appears that a roof coating has been applied on the unit 3 section of the building. One portion of the roof was redone in 1989. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next two years to be consistent with the roofing program. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | ADMINISTRATION/CELL BLOCKS (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 106251 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 840000
0094ELE2 | LIGHTING REPLACEMENT / UPGRADE | 0094 | Existing building lighting fixtures, T-12s, are older fluorescent types and not energy efficient. The majority of the light fixtures are not the security type fixtures with the enclosed housing. This project would provide funding for the purchase of new security type fixtures with T-8 lamps and electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. Security lighting fixtures shall be installed in inmate areas. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. This project should be done concurrently with the other electrical related projects which may help reduce the costs. | ADMINISTRATION/CELL BLOCKS (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 106251 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 796882
0094HVA3 | REPLACE HVAC SYSTEM | 0094 | The building is heated by low pressure steam. The steam pipes are deteriorating, leaking under the concrete has occurred, and other areas of the steam piping system has had leaks. There is a steam leak currently in unit 5. The Administration portion of the building is cooled by a central air-conditioning system. This section also requires evaporative coolers and windows air-conditioners to supplement the cooling. The cell block areas have roof and wall mounted evaporative coolers which are old and inefficient. The air distribution system in this facility is reaching the end of its useful life or is non-existent. The exhaust system in the chase ways no longer operates properly. There is not adequate fresh air supply in the cell areas as required in the IMC table 403.3. These systems appear to be over 25 years old and no longer energy efficient and some do not function. This project would provide funding for the design and engineering of a total renovation of the heating, air-conditioning and ventilation system. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | ADMINISTRATION/CELL BLOCKS (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 106251 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 4781295
0094SFT6 | INSTALL HANDRAILS AT ALL INTERIOR STAIRWAYS | 0094 | All of the existing stairways in the interior of the building do not meet current building codes. Some are missing and they do not have proper extensions or are not at proper heights. This project would provide for the installation of new tube steel handrails at all interior stairways including the housing units. | ADMINISTRATION/CELL BLOCKS (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 106251 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 50000
0094SFT1 | FIRE SPRINKLER INSTALLATION UPGRADE | 0094 | The administration offices, visiting area, education, laundry, infirmary, mattress factory, housing units, and canteen are located in this building. Most of the building does not have fire sprinklers. The 2006 IBC Chapter 903.2.5 states that "An automatic sprinkler system shall be provided throughout buildings with a Group I fire area". This building is an I-3 occupancy with sleeping quarters. It should be retrofitted with fire sprinklers during the next remodel or addition. This project would provide funding for the installation of fire sprinklers including backflow prevention devices. NAC 477.917 states that: Existing buildings and structures: Additions, alterations and repairs. (NRS 477.030) 1. If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. 2. The State Fire Marshal will determine the value of the building or structure and the value of any additions, alterations and repairs. If the owner of the building disagrees with the value as determined by the State Fire Marshal, the owner of the building may engage a qualified and disinterested appraiser to ascertain the fair market value of the building or structure and the value of any additions, alterations and repairs. 3. As used in this section, “addition” means any extension or increase in the floor space or height of a building or structure. Also, NAC 477.915 Existing buildings owned by State: Requirements; reporting of fires; smoke detectors; penalty for violation of section. (NRS 477.030) 1. Every existing building owned by the State of Nevada must: (a) Comply with the provisions of NRS 477.100 to 477.170, inclusive; (b) Meet the requirements of the building code in effect when the building was constructed; (c) If the building: (1) Is designated as a B occupancy; (2) Regardless of occupancy designation, has a floor area which exceeds 12,000 square feet on any floor or 24,000 square feet on all floors, including any mezzanines; or (3) Is an R-1 or R-2 occupancy, be scheduled for installation of an automatic fire suppression system during the next remodeling of or addition to the building; This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | ADMINISTRATION/CELL BLOCKS (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 106251 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 1487514
0099SFT3 | INSTALL FIRE ALARM SYSTEM | 0099 | This building is lacking an automatic fire detection and alarm system. It is recommended that a fully monitored fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2002 Section 7. | BOILER PLANT (VACANT) | 9989 | Correct | NSP |  | Carson City | 1958 | 2688 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 18816
0094ADA1 | ADA RESTROOM REMODEL | 0094 | The Administration Offices do not have an accessible restroom. The existing bathroom does not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | ADMINISTRATION/CELL BLOCKS (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 106251 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 30000
0094INT3 | REPLACE FLOORING ADMINISTRATION / VISITATION | 0094 | The floor coverings in this building are in generally poor condition and have reached the end of their serviceable life. The carpeted areas are showing signs of traffic wear and the 12"x12" VCT is loose and separating from the substrate creating a potential tripping hazard. This project would provide funding for the replacement of these floor coverings in the administration and visitation areas. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | ADMINISTRATION/CELL BLOCKS (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 106251 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 100000
0094PLM3 | REPLACE DOMESTIC WATER DISTRIBUTION SYSTEM | 0094 | The majority of the domestic water supply lines in the building are over 50 years old. At the time of the 2009 survey, all of unit 5 and some of unit 3 were having problems and the system was not 100 percent operational. Some of the pipe, hangers, connectors and couplers are deteriorating and water leaks are developing. Dielectric corrosion is occurring between different types of pipe metals, internal corrosion is occurring on the 4" pipe and compression clamps are located in areas where leaks have occurred. Other small repairs have been done over time as needed to keep system operational. A break in the pipe has the potential to short out the power supply, alarm system, flood the lowest levels of the building and presents a safety hazard. This project would provide funding for the removal and installation a new domestic water supply piping system, check and mixing valves and isolation valves. 8,000 lineal feet of steel piping was used in this estimate. If copper pipe is used, the price could double. Removal and/or abandonment of the existing system is included in this estimate. A project for replacing the utilities in the "Sagebrush" basement area was completed in 2001. This project number was 95-M27. This project or a portion there of was previously recommended in the FCA report dated July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | ADMINISTRATION/CELL BLOCKS (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 106251 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 800000
0094PLM2 | REPLACE SEWER / WASTE WATER LINES | 0094 | The sewer / waste water infrastructure in the building is over 50 years old except for some small areas that have been repaired or replaced over the years as needed. Some of the sanitary sewer pipe, hangers, connectors and couplers have or are deteriorating to a point where raw sewage may be leaking in some areas. The waste vents in the cell block chases are too close to the exhaust vents on the roof and in unit 5, some have been damaged and to not vent properly. The waste lines in unit 2 have failed. This may be a potential health hazard. This project would provide for the removal and installation a new sewer / waste water infrastructure in the building including all connections, supports, anchoring. Some of the waste lines have been upgraded in the Sagebrush basement area in a past Capital Improvement Project. 8,000 lineal feet of cast iron pipe was used to generate this estimate. This project or a portion there of was previously recommended in the FCA report dated July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | ADMINISTRATION/CELL BLOCKS (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 106251 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 800000
0094STR1 | SEISMIC RETROFIT AND TENANT IMPROVEMENT | 0094 | This building is constructed of sandstone masonry walls on the exterior and poured in place concrete columns, floors and roof deck which are keyed into the stone except for Housing Unit 5 and the third level which contains the third level addition known as Unit 2. The majority of this structure was constructed around 1925. This project would provide for a seismic retrofit of a portion of the structure. Included in this estimate is a cost for tenant improvements to relocate and or remodel offices, restrooms, control room, entrance lobby, and associated programs to provide ADA accessibility and efficient use of space mainly at the first floor of the building. Final design and scope of this project may impact the cost of this project. 45,000 square feet of floor area was used to generate this cost estimate. | ADMINISTRATION/CELL BLOCKS (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 106251 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 5297500
0095HVA1 | REPLACE EVAPORATIVE COOLERS | 0095 | There are currently four evaporative coolers mounted on the side of the building. They are severely scaled and have reached the end of their serviceable life. This project would provide for four new evaporative coolers to be installed. Project includes removal and disposal of the old coolers and utility connections to the new units. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | INDUSTRIAL/LICENSE PLATE FACTORY(VACANT) | 9989 | Correct | NSP |  | Carson City | 1962 | 7462 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
0095SFT1 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0095 | The exit signs in this building are older types or painted on the walls. Illuminated exit signs shall be marked per 2006 IBC Section 1011.1. This project would provide funding to install self-illuminating or LED models with internal battery backups along all of the required exit pathways. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | INDUSTRIAL/LICENSE PLATE FACTORY(VACANT) | 9989 | Correct | NSP |  | Carson City | 1962 | 7462 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 2550
0095HVA2 | REPLACE EXHAUST FANS IN SCREENING ROOM | 0095 | There are two exhaust fans in the silk screening room to remove fumes. The fans are noisy and have reached the end of their expected service life. This project would provide funding for the replacement of the exhaust fans. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | INDUSTRIAL/LICENSE PLATE FACTORY(VACANT) | 9989 | Correct | NSP |  | Carson City | 1962 | 7462 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 1500
0095INT1 | INTERIOR FINISHES | 0095 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | INDUSTRIAL/LICENSE PLATE FACTORY(VACANT) | 9989 | Correct | NSP |  | Carson City | 1962 | 7462 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 37310
0095SFT2 | INSTALL FIRE ALARM SYSTEM | 0095 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2006 Section 7 and the 2006 International Fire Code. | INDUSTRIAL/LICENSE PLATE FACTORY(VACANT) | 9989 | Correct | NSP |  | Carson City | 1962 | 7462 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 52234
0095PLM1 | REPLACE WATER HEATER | 0095 | The water heater tank is showing signs of wear and deterioration and is not seismic anchored. It appears this appliance is original to the building. This project would provide funding for the purchase and installation of a new natural gas unit and seismic anchoring. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | INDUSTRIAL/LICENSE PLATE FACTORY(VACANT) | 9989 | Correct | NSP |  | Carson City | 1962 | 7462 | 2009-02-10 | Four to Ten Years | Long-Term Needs | 3 | 3500
0094SFT5 | INSTALL STAIRS / HANDRAILS AT ADMINISTRATION | 0094 | The existing concrete stairs are showing signs of wear and deterioration. The handrails do not meet current building codes for ADA accessibility and handrail extensions and configurations. This project would provide for the removal and replacement of the concrete stairs and handrails. | ADMINISTRATION/CELL BLOCKS (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 106251 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 6500
0029EXT2 | EXTERIOR FINISHES | 0029 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding for the painting of the exterior of the building. Included in the cost is repairing any cracks and sealing the stone masonry as well as caulking the windows and other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion there of was previously recommended in the FCA report dated July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | OLD PUMPHOUSE (VACANT) | 9989 | Correct | NSP |  | Carson City | 1868 | 64 | 2009-02-10 | Four to Ten Years | Long-Term Needs | 3 | 320
0022ADA1 | INSTALL LEVER ACTION DOOR HARDWARE | 0022 | The existing doors in this facility have locking knob-type door hardware and do not meet the requirements for ADA accessibility. ICC/ANSI A117.1-1998 section 404.2.7 requires door handles to have a shape that is easy to grasp with one hand and does not require tight grasping, pinching or twisting of the wrist to operate. This project would provide for the purchase and installation of lever action hardware to be placed on all the interior doors. This project or a portion there of was previously recommended in the FCA report dated July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | CHAPEL/SIX POST (VACANT) | 9989 | Correct | NSP |  | Carson City | 1971 | 2968 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 6750
0022SFT1 | FIRE ALARM SYSTEM INSTALLATION | 0022 | This building is lacking an automatic fire detection and alarm system. It is recommended that a fully monitored fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2002 Section 7. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | CHAPEL/SIX POST (VACANT) | 9989 | Correct | NSP |  | Carson City | 1971 | 2968 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 20776
0022INT1 | INTERIOR FINISHES | 0022 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA report dated July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | CHAPEL/SIX POST (VACANT) | 9989 | Correct | NSP |  | Carson City | 1971 | 2968 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14840
0022SFT2 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0022 | This building does not have an automatic fire suppression system. It should be retrofitted with fire sprinklers during the next remodel or addition. This project would provide funding for the installation of fire sprinklers including backflow prevention devices. NAC 477.917 states that: Existing buildings and structures: Additions, alterations and repairs. (NRS 477.030) 1. If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. 2. The State Fire Marshal will determine the value of the building or structure and the value of any additions, alterations and repairs. If the owner of the building disagrees with the value as determined by the State Fire Marshal, the owner of the building may engage a qualified and disinterested appraiser to ascertain the fair market value of the building or structure and the value of any additions, alterations and repairs. 3. As used in this section, “addition” means any extension or increase in the floor space or height of a building or structure. | CHAPEL/SIX POST (VACANT) | 9989 | Correct | NSP |  | Carson City | 1971 | 2968 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 41552
0022SFT3 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0022 | The exit signs in this building are older types or painted on the walls. Illuminated exit signs shall be marked per 2006 IBC Section 1011.1. This project would provide funding to install self-illuminating or LED models with internal battery backups along all of the required exit pathways. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | CHAPEL/SIX POST (VACANT) | 9989 | Correct | NSP |  | Carson City | 1971 | 2968 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 2250
0022EXT1 | EXTERIOR FINISHES | 0022 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion there of was previously recommended in the FCA report dated July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | CHAPEL/SIX POST (VACANT) | 9989 | Correct | NSP |  | Carson City | 1971 | 2968 | 2009-02-10 | Four to Ten Years | Long-Term Needs | 3 | 29680
0022INT2 | REPLACE EXISTING FLOORING | 0022 | The floor coverings in this building are in generally poor condition and have reached the end of their serviceable life. The carpeted areas are showing signs of traffic wear and the 12"x12" vinyl composition tile (VCT) is loose and separating from the substrate creating a potential tripping hazard. In April of 1989 an asbestos survey was conducted. It was reported that in some areas of the buildings asbestos was present. This project would provide for the replacement of these floor coverings with new VCT. This project includes removal and disposal of the asbestos. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | CHAPEL/SIX POST (VACANT) | 9989 | Correct | NSP |  | Carson City | 1971 | 2968 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 29680
0022HVA1 | REPLACE HVAC SYSTEM | 0022 | The Chapel / Six Post currently has only ducted heat and evaporative cooling which is in need of replacement. This project would provide for a cooling system to be installed in the building. This project or a portion there of was previously recommended in the FCA report dated July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | CHAPEL/SIX POST (VACANT) | 9989 | Correct | NSP |  | Carson City | 1971 | 2968 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 89040
0022ADA2 | ADA RESTROOM REMODEL | 0022 | The existing restroom is not ADA compliant. This project would provide for the remodeling of the restroom into a unisex ADA compliant facility including a sink, toilet, grab bars, mirror, plumbing jacket and signage as indicated in the 2006 IBC Chapter 11, Section 1109.2.1. Minor plumbing modifications and room reconfiguration may be required and this cost estimate includes funds for minor modifications including new vinyl composition flooring, and a new 3'-0" wide door with lever action door handles. | CHAPEL/SIX POST (VACANT) | 9989 | Correct | NSP |  | Carson City | 1971 | 2968 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 30000
0094SFT2 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0094 | The exit signs in this building are older types or painted on the walls. Illuminated exit signs shall be marked per 2006 IBC Section 1011.1. This project would provide funding to install self-illuminating or LED models with internal battery backups along all of the required exit pathways throughout the building. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | ADMINISTRATION/CELL BLOCKS (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 106251 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 25000
0022ELE1 | LIGHTING UPGRADE | 0022 | Existing building lighting fixtures, T-12s, are older fluorescent types and not energy efficient. This project will upgrade lighting fixtures to T-8s with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | CHAPEL/SIX POST (VACANT) | 9989 | Correct | NSP |  | Carson City | 1971 | 2968 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 22260
0094INT2 | INTERIOR FINISHES | 0094 | The interior walls, ceilings and cells of this building should have a new application of paint in the next two to four years for proper upkeep and maintenance. Prior to painting, all surfaces should be repaired, and additional funds have been included to address the extensive wall repairs. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA report dated July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | ADMINISTRATION/CELL BLOCKS (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 106251 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 743757
0041EXT2 | EXTERIOR FINISHES | 0041 | It is important to maintain the finish, weather resistance and appearance of the building. The exterior paint is peeling; the caulking around the windows, flashing, fixtures and other penetrations is failing. This project would provide funding for the painting of the exterior of the building. Including in the cost is the sanding, priming, filling in the crack, caulking of the windows, flashing, fixtures and all other penetrations. This project should be completed in the next two years. This project or a portion there of was previously recommended in the FCA report dated July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | OLD 5TH STREET TOWER (VACANT) | 9989 | Correct | NSP |  | Carson City | 1868 | 100 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 1500
0041INT1 | INTERIOR FINISHES | 0041 | The interior finishes are in fair to poor condition. It is recommended that the interior walls be painted at least once in the next two years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA report dated July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | OLD 5TH STREET TOWER (VACANT) | 9989 | Correct | NSP |  | Carson City | 1868 | 100 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 1000
0094INT4 | REFURBISH GUN POSTS | 0094 | Disney Films constructed the gun post at this building while making a movie at the prison. It is constructed of wood, sitting atop a non-combustible building. It needs complete refurbishing including flooring, windows, doors and electrical. The soffits and walls are peeling and deteriorating. The gun post is not heated or cooled. The other two gun posts also will need to be refurbished. They are constructed of concrete. Only one of the gun posts has a restroom. They use radiator-heating units, which are inadequate in colder weather. Gun post three has a window-mounted air conditioning unit and an electric resistance-heating unit. The windows are tilt-out metal frame and should be replaced. The roof-mounted spotlights will need to be replaced also. The escape hatches located in the floor, are too small and need to be enlarged. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | ADMINISTRATION/CELL BLOCKS (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 106251 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 200000
0094ENV1 | ENVIRONMENTAL HAZARDS SURVEY | 0094 | An inspection was performed on this building in 1989 for asbestos containing materials (ACM). Not included in the previous testing was lead paint and other possible environmental hazards. This project would provide funding to complete a building survey of potential environmental hazards located inside the building and on the roofing system. Future projects and their associated costs that may arise from the results of the survey are not included in this estimate. This project or a portion there of was previously recommended in the FCA report dated July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | ADMINISTRATION/CELL BLOCKS (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 106251 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 15000
0094ELE1 | UPGRADE ELECTRICAL SYSTEM | 0094 | This building was constructed before the high demand for electrical services were needed for computers and other electrical devices. As time progressed the building's electrical demand and system has been changed. It is utilized to its current maximum potential. The electrical panels and receptacles are older types and are at their limit. It is recommended the entire system be upgraded to meet the evolving needs of the building including switchgear, main panels and subpanels located in the utility chases and basement areas. Electrical fixtures are addressed in another project. This project or a portion there of was previously recommended in the FCA report dated July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | ADMINISTRATION/CELL BLOCKS (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 106251 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1912518
0094EXT4 | STONE MASONRY RE-POINTING | 0094 | The existing building exterior is natural sandstone that was quarried directly from the correctional facility site. Some portions of this structure are over 100 years old. There are numerous areas where the mortar is failing, missing and not sealed properly due the age and exposure to the weather. This project would provide for the cleaning, repair and re-pointing of the exterior stone work. Due to the vertical nature of the building, scaffolding will be required to accomplish this project and is included in this estimate. This project does not include the exterior stairway on the southwest side of the building. This project or a portion there of was previously recommended in the FCA report dated July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | ADMINISTRATION/CELL BLOCKS (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 106251 | 2009-02-10 | Four to Ten Years | Long-Term Needs | 3 | 531255
0094INT1 | REPLACE ADMINISTRATION OFFICE DOORS | 0094 | The front office doors in the administration portion of the building are showing signs of heavy use. The bottom of the doors have become warped and damaged over the years. this project would provide funding for the purchase and installation of new hollow metal offices doors, frames, lever action door handles, hardware and painting of doors and frames. Removal and disposal of existing damaged doors and frames is included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009.. This estimate is for the removal and replacement of 15 doors. | ADMINISTRATION/CELL BLOCKS (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 106251 | 2009-02-10 | Four to Ten Years | Long-Term Needs | 3 | 52500
0094ELE3 | CELL BLOCK LIGHTING CONTROL SYSTEM | 0094 | The lights for cell block units' 3 and 5 are controlled in the hallway by switches. The maintenance staff has installed lock boxes to protect them from inmate abuse. However the inmates have broken all of the lighting controls. This is a safety issue as the correctional officers need to be able to control the lighting. This project would provide for the design, purchase and installation of a lighting control unit to be located in the correctional offices room. This project should be coordinated with the electrical system upgrade project which may reduce the cost estimate if done simultaneously. This project or a portion there of was previously recommended in the FCA report dated July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | ADMINISTRATION/CELL BLOCKS (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 106251 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 50000
0094SEC2 | SURVEILANCE / SECURITY SYSTEM INSTALLATION | 0094 | There is no security camera or recording system for this building except for a few isolated areas like the visitation area. This is a safety issue for staff and inmates as all areas cannot be seen by the security staff or recorded in case of an incident. This project would provide for the installation of surveillance cameras and security system for the entire building and all required connections to existing utility systems. This project or a portion there of was previously recommended in the FCA report dated July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | ADMINISTRATION/CELL BLOCKS (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 106251 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 1500000
0096EXT1 | REPLACE ROOF | 0096 | The standing seam metal roof on this building was in poor condition at the time of the survey and had active leaks. It is recommended that this building be re-roofed in the next one to two years with a new single-ply roofing system to be installed over the existing metal roofing system. | GYMNASIUM (VACANT) | 9989 | Correct | NSP |  | Carson City | 1976 | 7980 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 159600
0022SEC1 | SURVEILANCE / SECURITY SYSTEM INSTALLATION | 0022 | There is no security camera or recording system in the Chapel/ Six Post. This is a safety issue for the staff and inmates as all areas cannot be seen by the security staff or recorded in case of an incident. This project would provide for the installation of surveillance cameras and a security system for the entire building and all required connections to existing utility systems. | CHAPEL/SIX POST (VACANT) | 9989 | Correct | NSP |  | Carson City | 1971 | 2968 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 50000
0101EXT2 | DEMOLISH WATER TANK | 0101 | The existing water tank is not used for water storage, but it is used for maintenance storage. This was a quick remedy for needed storage space. This building contains numerous code and safety issues including but limit to rodent infestation and improper ventilation. The tank is dilapidated and deteriorating and has reached the end of its useful like. This project would provide funding for the demolition of the water tank. This project or a portion there of was previously recommended in the FCA report dated July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | WATER TANK STORAGE (VACANT) | 9989 | Correct | NSP |  | Carson City | 1969 | 2375 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 23750
0095ELE1 | LIGHTING UPGRADE | 0095 | Existing building lighting fixtures, T-12s, are older fluorescent types and not energy efficient. This project will upgrade lighting fixtures to T-8s with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | INDUSTRIAL/LICENSE PLATE FACTORY(VACANT) | 9989 | Correct | NSP |  | Carson City | 1962 | 7462 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 55965
0098INT1 | INTERIOR FINISHES | 0098 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | BOOK BINDERY (VACANT) | 9989 | Correct | NSP |  | Carson City | 1976 | 4137 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20685
0099PLM1 | BOILER MAINTENANCE | 0099 | The three steam boilers are functioning well and it is important to maintain the equipment including replacing worn parts. The maintenance staff indicated several specific parts that will be due for replacement in the next 2-3 years in order to ensure the equipment is functioning to its maximum potential. These parts include a valve for the Deaerator tank and a fan motor for Boiler #1. This project would provide for the purchase and installation of these parts and includes extra funds for other necessary maintenance. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | BOILER PLANT (VACANT) | 9989 | Correct | NSP |  | Carson City | 1958 | 2688 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0109HVA1 | REPLACE HVAC / VENTILATION SYSTEM | 0109 | The air handler, fan coils and related equipment are original to the building, 1981. The building does not have a cooling system and the equipment is has reached it's expected life span. This project recommends replacement of all the air handlers, fan coils, ventilation equipment, exhaust fans and installation of a cooling system. It is recommended that this project be implemented in the next two years to avoid possible failure and emergency funding for replacement. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 09 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 468060
0099HVA1 | HVAC UPGRADE | 0099 | The air handler, fan coils and related equipment have reached the end of their expected life. The building does not have a cooling system. This project recommends replacement of all the air handlers, fan coils, ventilation equipment, exhaust fans and installation of a cooling system. It is recommended that this project be implemented in the next two years to avoid possible failure and emergency funding for replacement. | BOILER PLANT (VACANT) | 9989 | Correct | NSP |  | Carson City | 1958 | 2688 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 80640
0099ELE1 | LIGHTING UPGRADE | 0099 | Existing building lighting fixtures, T-12s, are older fluorescent types and not energy efficient. This project will upgrade lighting fixtures to T-8s with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | BOILER PLANT (VACANT) | 9989 | Correct | NSP |  | Carson City | 1958 | 2688 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20160
0099EXT3 | REPLACE CONCRETE STEPS | 0099 | The IBC 2006 section 1008.1.5 requires landings shall have a width not less than the width of the stairway or the door, which is the greater. The landing and stairs have been saw cut and partially removed. This situation could create a slip and fall hazard. This project would provide funding for the removal of the existing concrete and the installation of a concrete landing, stairs and handrail as required. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | BOILER PLANT (VACANT) | 9989 | Correct | NSP |  | Carson City | 1958 | 2688 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 5000
0099SFT4 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0099 | This building does not have an automatic fire suppression system. It should be retrofitted with fire sprinklers during the next remodel or addition. This project would provide funding for the installation of fire sprinklers including backflow prevention devices. NAC 477.917 states that: Existing buildings and structures: Additions, alterations and repairs. (NRS 477.030) 1. If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. 2. The State Fire Marshal will determine the value of the building or structure and the value of any additions, alterations and repairs. If the owner of the building disagrees with the value as determined by the State Fire Marshal, the owner of the building may engage a qualified and disinterested appraiser to ascertain the fair market value of the building or structure and the value of any additions, alterations and repairs. 3. As used in this section, “addition” means any extension or increase in the floor space or height of a building or structure. | BOILER PLANT (VACANT) | 9989 | Correct | NSP |  | Carson City | 1958 | 2688 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 37632
0099SFT1 | EXIT SIGN & EGRESS LIGHTING INSTALLATION | 0099 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. Illuminated exit signs shall be marked per 2006 IBC Section 1011.1. This project would provide funding to install self-illuminating or LED models with internal battery backups along all of the required exit pathways. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | BOILER PLANT (VACANT) | 9989 | Correct | NSP |  | Carson City | 1958 | 2688 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 1700
0098ADA2 | ADA RESTROOM PROJECT | 0098 | The restroom does not meet the Americans with Disabilities Act (ADA) regulations. A retrofit is necessary to comply with 2006 IBC Chapter 11, ICC/ANSI A117.1-1998 Sections 603 - 604 and the Americans with Disabilities Act Accessibility Guidelines (ADAAG). Given the current configuration of the restrooms, the work will include the installation of a new toilet, sink, grab bars, faucet, mirror, dispensers and hardware. Some minor design work will be required and may impact the final cost estimate. This estimate is for one ADA restroom facility. The removal and disposal of the old restroom fixtures is included in this estimate. | BOOK BINDERY (VACANT) | 9989 | Correct | NSP |  | Carson City | 1976 | 4137 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 25000
0099INT1 | INTERIOR FINISHES | 0099 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next four to six years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | BOILER PLANT (VACANT) | 9989 | Correct | NSP |  | Carson City | 1958 | 2688 | 2009-02-10 | Four to Ten Years | Long-Term Needs | 3 | 13440
0098INT2 | STRUCTURAL ASSESSMEMT | 0098 | An upper level storage mezzanine has been constructed inside of the Bindery Building. The 2006 IBC has a minimum requirement of 125p.s.f. for light storage in non-residential spaces. There is no record of a CIP project or structural plans for this construction and could be a potential safety issue due to collapse. This project recommends that a licensed engineer perform a structural investigation to assess the load carrying capacity of this area. Future projects would be based on this report. This project was listed as "BEAM INSTALLATION" in the FCA report dated 09/15/1999 and was previously recommended in the FCA report dated July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | BOOK BINDERY (VACANT) | 9989 | Correct | NSP |  | Carson City | 1976 | 4137 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 3500
0102EXT2 | DEMOLISH OLD BUTCHERS SHOP | 0102 | The Old Butchers Shop contains numerous code and safety issues including but not limited to rodent infestation, missing windows and doors, and possible structural deficiencies. Also, the building is located outside of the secure area of the prison and could be accessed by the public. The building is dilapidated and deteriorating and has reached the end of its useful life. This project would provide funding for the demolition of the building. The sandstone masonry has historic value and should be salvaged for future renovations. This project or a portion there of was previously recommended in the FCA report dated July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | OLD BUTCHERS SHOP (VACANT) | 9989 | Correct | NSP |  | Carson City | 1868 | 300 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 3000
0103ADA1 | ADA ACCESSIBILITY PROJECTS | 0103 | The Culinary / Dining facility is lacking ADA compliant facilities. There is a restroom present inside which also does not meet ADA requirements. This project would provide for ADA improvements which include at a minimum remodeling the existing restroom into a new ADA compliant restroom, lever action door hardware, an ADA compliant dining table with proper clearances and adding an ADA accessible food service counter. The ADA accessible route into the building is addressed in the site portion of this report. | CULINARY/DINING HALL (VACANT) | 9989 | Correct | NSP |  | Carson City | 1966 | 11334 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 35000
0103INT1 | INTERIOR FINISHES | 0103 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | CULINARY/DINING HALL (VACANT) | 9989 | Correct | NSP |  | Carson City | 1966 | 11334 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 56670
0103EXT3 | EXTERIOR DOOR REPLACEMENT | 0103 | The existing exterior doors to the Culinary / Dining Hall are original to the building. They are showing signs of wear and deterioration from constant use and inmate abuse. Due to security concerns and the condition of the door, replacement is recommended. This project would provide for the removal and disposal of the existing doors and frames and replacement with new exterior security doors including door frames, hardware, security glazing, painting and connections to the security system as required. A total of 4 doors were used to generate this estimate. | CULINARY/DINING HALL (VACANT) | 9989 | Correct | NSP |  | Carson City | 1966 | 11334 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 26000
0103ELE1 | LIGHTING UPGRADE | 0103 | Existing building lighting fixtures, T-12s, are older fluorescent types and not energy efficient. This project will upgrade lighting fixtures to T-8s with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | CULINARY/DINING HALL (VACANT) | 9989 | Correct | NSP |  | Carson City | 1966 | 11334 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 85005
0103INT3 | REPAIR WALLS IN DISHWASHING AREA | 0103 | The dishwashing area has a large room where carts and other large items are washed. The walls are CMU and the ceiling is gypsum board. This room is severely damage and deteriorating from moisture and water overspray. This project would provide for the installation of fiberglass reinforced panels (FRP) on the walls, and an epoxy based paint on the ceiling. Prior to painting all damaged surfaces should be repaired and prepped for paint as required. This project or a portion there of was previously recommended in the FCA report dated July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | CULINARY/DINING HALL (VACANT) | 9989 | Correct | NSP |  | Carson City | 1966 | 11334 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 9000
0103SFT1 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0103 | The exit signs in this building are older types or painted on the walls. Illuminated exit signs shall be marked per 2006 IBC Section 1011.1. This project would provide funding to install self-illuminating or LED models with internal battery backups along all of the required exit pathways. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | CULINARY/DINING HALL (VACANT) | 9989 | Correct | NSP |  | Carson City | 1966 | 11334 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 3400
0103EXT1 | EXTERIOR FINISHES | 0103 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding for the painting of the exterior of the building. Included in the cost is the sanding, priming, filling in the cracks, caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | CULINARY/DINING HALL (VACANT) | 9989 | Correct | NSP |  | Carson City | 1966 | 11334 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 113340
0103SFT0 | UPGRADE FIRE ALARM SYSTEM | 0103 | This building has an automatic fire detection and alarm system but it appears to be original to the facility. It is recommended that a fully monitored fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2002 Section 7. | CULINARY/DINING HALL (VACANT) | 9989 | Correct | NSP |  | Carson City | 1966 | 11334 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 79338
0099EXT1 | EXTERIOR FINISHES | 0099 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding for the painting of the exterior of the building. Included in the cost is the sanding, priming, filling in the crack, caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | BOILER PLANT (VACANT) | 9989 | Correct | NSP |  | Carson City | 1958 | 2688 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 26880
0096SFT2 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0096 | This building does not have an automatic fire suppression system. It should be retrofitted with fire sprinklers during the next remodel or addition. This project would provide funding for the installation of fire sprinklers including backflow prevention devices. NAC 477.917 states that: Existing buildings and structures: Additions, alterations and repairs. (NRS 477.030) 1. If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. 2. The State Fire Marshal will determine the value of the building or structure and the value of any additions, alterations and repairs. If the owner of the building disagrees with the value as determined by the State Fire Marshal, the owner of the building may engage a qualified and disinterested appraiser to ascertain the fair market value of the building or structure and the value of any additions, alterations and repairs. 3. As used in this section, “addition” means any extension or increase in the floor space or height of a building or structure. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | GYMNASIUM (VACANT) | 9989 | Correct | NSP |  | Carson City | 1976 | 7980 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 111720
0103INT2 | REPAIR FLOORING IN DINING ROOM | 0103 | The painted floor in the dining area needs to be repaired and resealed. A significant amount of foot traffic goes though this building daily and deterioration is occurring. It is showing signs of wear from constant use. This project would provide for the floor to be repaired, patched and resealed with an epoxy floor covering for ongoing upkeep and maintenance. This estimate includes two 5 foot by 5 foot concrete areas to be saw cut removed and replaced at areas that are the most damaged.. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | CULINARY/DINING HALL (VACANT) | 9989 | Correct | NSP |  | Carson City | 1966 | 11334 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 45900
0096INT2 | RESEAL FLOORING | 0096 | The flooring system in the weight and shower area needs to be resealed. A significant amount of foot traffic goes though this building daily and deterioration is occurring. It is showing signs of wear from constant use and abuse. This project would provide for the existing floor to be ground, patched and resealed with an epoxy resin for ongoing upkeep and maintenance. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | GYMNASIUM (VACANT) | 9989 | Correct | NSP |  | Carson City | 1976 | 7980 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14700
0096SEC1 | SURVEILANCE / SECURITY SYSTEM INSTALLATION | 0096 | There is no security camera or recording system in the Gymnasium. This is a safety issue for the staff and inmates as all areas cannot be seen by the security staff or recorded in case of an incident. This project would provide for the installation of surveillance cameras and a security system for the entire building and all required connections to existing utility systems. | GYMNASIUM (VACANT) | 9989 | Correct | NSP |  | Carson City | 1976 | 7980 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 95000
0096SFT1 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0096 | The exit signs in this building are older types or are missing. Illuminated exit signs shall be marked per 2003 IBC Section 1011.1. This project would provide funding to install self-illuminating or LED models with internal battery backups along all of the required exit pathways. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | GYMNASIUM (VACANT) | 9989 | Correct | NSP |  | Carson City | 1976 | 7980 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 7650
0096SFT4 | FIRE ALARM SYSTEM UPGRADE | 0096 | This building is equipped with an automatic fire detection and alarm system, but the system is old, does not meet current code requirements and is missing in some locations. It is recommended that the fire detection and alarm system be upgraded to a fully monitored. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements and building codes. This project should be coordinated with the fire sprinkler install project. | GYMNASIUM (VACANT) | 9989 | Correct | NSP |  | Carson City | 1976 | 7980 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 55860
0096ELE1 | LIGHTING UPGRADE | 0096 | Existing building lighting fixtures in the rooms adjacent to the gymnasium are T-12s, and are older fluorescent types and are not energy efficient. The existing lighting in the gymnasium is provided by high bay metal halide type fixtures. This project will upgrade the lighting fixtures in the area adjacent to the gymnasium to T-8s with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. It is recommended that the metal-halide lights be replaced with high pressure sodium lights. These types of lights will provide better illumination as well as energy savings. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | GYMNASIUM (VACANT) | 9989 | Correct | NSP |  | Carson City | 1976 | 7980 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 59850
0096HVA1 | REPLACE HVAC / VENTILATION SYSTEM | 0096 | The air handler, fan coils and related equipment are original to the building, 1976. The building does not have a cooling system and the equipment has reached it's expected life span. This project recommends replacement of all the air handlers, fan coils, ventilation equipment, exhaust fans and installation of a cooling system. It is recommended that this project be implemented in the next two years to avoid possible failure and emergency funding for replacement. | GYMNASIUM (VACANT) | 9989 | Correct | NSP |  | Carson City | 1976 | 7980 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 239400
0096ADA2 | ACCESSIBLE ENTRANCE RAMP | 0096 | The gymnasium is lacking an accessible entrance into the building. The building is used to allow inmates to play basketball, table tennis and lift weights. This building is required to have an accessible entrance per the Americans with Disabilities Act (ADA) regulations. This project would provide for an accessible ramp to access the building. IBC - 2006, ICC/ANSI A117.1 - 2003 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2003 were referenced for this project. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | GYMNASIUM (VACANT) | 9989 | Correct | NSP |  | Carson City | 1976 | 7980 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 35000
0096EXT2 | EXTERIOR FINISHES | 0096 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding for the protection of the exterior of the building. Included in the cost is sealing and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the project be completed in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | GYMNASIUM (VACANT) | 9989 | Correct | NSP |  | Carson City | 1976 | 7980 | 2009-02-10 | Four to Ten Years | Long-Term Needs | 3 | 15960
0096SFT3 | STAIRWAY HANDRAIL INSTALLATION | 0096 | The existing concrete exterior stairs at the entry are lacking handrails as required in the 2006 IBC Chapter 10, Section 1012. This project would provide for tubular steel framed handrails to be installed. Painting is included in this estimate. This project should be coordinated with the ADA ramp project. | GYMNASIUM (VACANT) | 9989 | Correct | NSP |  | Carson City | 1976 | 7980 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 5000
0098SEC1 | SURVEILANCE / SECURITY SYSTEM INSTALLATION | 0098 | There is no security camera or recording system in the Book Bindery. This is a safety issue for the staff and inmates as all areas cannot be seen by the security staff or recorded in case of an incident. This project would provide for the installation of surveillance cameras and a security system for the entire building and all required connections to existing utility systems. | BOOK BINDERY (VACANT) | 9989 | Correct | NSP |  | Carson City | 1976 | 4137 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 75000
0096ADA1 | ADA RESTROOM PROJECT | 0096 | The restroom does not meet the Americans with Disabilities Act (ADA) regulations. A retrofit is necessary to comply with 2006 IBC Chapter 11, ICC/ANSI A117.1-1998 Sections 603 - 604 and the Americans with Disabilities Act Accessibility Guidelines (ADAAG). Given the current configuration of the restrooms, the work will include the installation of a new shower stall, toilet, sink, shower, grab bars, faucet, mirror, dispensers and hardware. Some minor design work will be required and may impact the final cost estimate. This estimate is for one ADA restroom facility. The removal and disposal of the old restroom fixtures is included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | GYMNASIUM (VACANT) | 9989 | Correct | NSP |  | Carson City | 1976 | 7980 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 30000
0095EXT3 | REPLACE WINDOWS | 0095 | The windows are single pane, open inward which protrudes into the isles and are original to the building. Some of the units have several cracks, seals are broken, are difficult to operate and they have reached the end of their useful life. This project would provide funding to replace the window units with new double pane energy efficient units. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | INDUSTRIAL/LICENSE PLATE FACTORY(VACANT) | 9989 | Correct | NSP |  | Carson City | 1962 | 7462 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30250
0098HVA1 | REPLACE HVAC / VENTILATION SYSTEM | 0098 | The air handler, fan coils and related equipment are original to the building, 1976. The building does not have a cooling system and the equipment is has reached it's expected life span. This project recommends replacement of all the air handlers, fan coils, ventilation equipment, exhaust fans and installation of a cooling system. It is recommended that this project be implemented in the next two years to avoid possible failure and emergency funding for replacement. | BOOK BINDERY (VACANT) | 9989 | Correct | NSP |  | Carson City | 1976 | 4137 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 124110
0098SFT1 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0098 | This building does not have an automatic fire suppression system. It should be retrofitted with fire sprinklers during the next remodel or addition. This project would provide funding for the installation of fire sprinklers including backflow prevention devices. NAC 477.917 states that: Existing buildings and structures: Additions, alterations and repairs. (NRS 477.030) 1. If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. 2. The State Fire Marshal will determine the value of the building or structure and the value of any additions, alterations and repairs. If the owner of the building disagrees with the value as determined by the State Fire Marshal, the owner of the building may engage a qualified and disinterested appraiser to ascertain the fair market value of the building or structure and the value of any additions, alterations and repairs. 3. As used in this section, “addition” means any extension or increase in the floor space or height of a building or structure. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | BOOK BINDERY (VACANT) | 9989 | Correct | NSP |  | Carson City | 1976 | 4137 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 57918
0098ADA1 | INSTALL LEVER ACTION DOOR HARDWARE | 0098 | The existing doors in this facility have locking knob-type door hardware and do not meet the requirements for ADA accessibility. ICC/ANSI A117.1-1998 section 404.2.7 requires door handles to have a shape that is easy to grasp with one hand and does not require tight grasping, pinching or twisting of the wrist to operate. This project would provide for the purchase and installation of lever action door hardware to be placed on all the interior doors. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | BOOK BINDERY (VACANT) | 9989 | Correct | NSP |  | Carson City | 1976 | 4137 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 7500
0098EXT2 | REPLACE ROOF | 0098 | The standing seam metal roof on this building was in poor condition at the time of the survey and had active leaks. It is recommended that this building be re-roofed in the next one to two years with a new single-ply roofing system to be installed over the existing metal roofing system. | BOOK BINDERY (VACANT) | 9989 | Correct | NSP |  | Carson City | 1976 | 4137 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 82740
0098SFT2 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0098 | The exit signs in this building are older types or painted on the walls. Illuminated exit signs shall be marked per 2003 IBC Section 1011.1. This project would provide funding to install self-illuminating or LED models with internal battery backups along all of the required exit pathways. This project or a portion there of was previously recommended in the FCA report dated 09/15/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/19/2006. | BOOK BINDERY (VACANT) | 9989 | Correct | NSP |  | Carson City | 1976 | 4137 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 3400
0120ELE1 | LIGHTING UPGRADE | 0120 | The existing building lighting fixtures are older luminescent type and are not energy efficient. If this building would be used for anything other than storage, it is recommended a lighting upgrade be done. This project will upgrade lighting fixtures to T-8 lamps with electronic ballasts resulting in increased efficiency and reduced costs associated with illumination. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | COTTAGE #3 (NSP) LOCATED AT WSCC(VACANT) | 9989 | Correct | NSP |  | Carson City | 1953 | 930 | 2009-02-10 | Four to Ten Years | Long-Term Needs | 3 | 3255
0120SFT1 | REPLACE VINYL/ ASBESTOS TILE FLOOR | 0120 | The existing building is used as an armory. The floor tiles contain asbestos and have reached the end of their useful life. When cabinets or files are moved around, asbestos fiber becomes air-borne, this is harmful to anyone inside the building. This project would provide funding for the removal and disposal of the asbestos tile and the installation of vinyl floor tiles to be installed. This project or a portion there of was previously recommended in the FCA report from July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | COTTAGE #3 (NSP) LOCATED AT WSCC(VACANT) | 9989 | Correct | NSP |  | Carson City | 1953 | 930 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 31605
0098SFT3 | FIRE ALARM SYSTEM INSTALLATION | 0098 | This building is equipped with an automatic fire detection and alarm system that no longer complies with current requirements. It is recommended that the fire detection and alarm system be upgraded. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 1998 Section 7. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | BOOK BINDERY (VACANT) | 9989 | Correct | NSP |  | Carson City | 1976 | 4137 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 28959
0098EXT1 | EXTERIOR FINISHES | 0098 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding for the protection of the exterior of the building. Included in the cost is sealing and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the project be completed in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BOOK BINDERY (VACANT) | 9989 | Correct | NSP |  | Carson City | 1976 | 4137 | 2009-02-10 | Four to Ten Years | Long-Term Needs | 3 | 8274
0096INT1 | INTERIOR FINISHES | 0096 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | GYMNASIUM (VACANT) | 9989 | Correct | NSP |  | Carson City | 1976 | 7980 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 39900
0763EXT1 | EXTERIOR FINISHES | 0763 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding for the protection of the exterior of the building. Included in the cost is sealing and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the project be completed in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | GENERATOR BUILDING | 9989 | Correct | NSP |  | Carson City | 1999 | 900 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1800
1706EXT2 | EXTERIOR FINISHES | 1706 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is painting of the handrails and guardrails and caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted, caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | TOWER 3 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4800
1706EXT1 | ROOF REPLACEMENT | 1706 | The standing seam metal roof on this building was in fair to poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new single-ply roofing system which will be installed directly over the existing metal roof. This will allow the roof to qualify for the statewide roofing program warranty and preventative maintenance agreement. This project or a portion thereof was previously recommended in the FCA report dated 7/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 3/9/2010. | TOWER 3 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4800
1706SEC1 | ACTIVATE ELECTRONIC LOCK SYSTEM | 1706 | The tower controls included an electronic control for the door lock at grade. The system was never made operational and requires tower staff to physically transfer a key from the tower to personnel below. This system is time consuming and rough on the keys and locks. This project recommends running conduit and power to activate the system, permitting tower personnel to remotely actuate the door locks. This project or a portion thereof was previously recommended in the FCA report dated 7/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 3/9/2010. | TOWER 3 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
1705INT2 | VCT FLOORING REPLACEMENT | 1705 | The VCT (vinyl composite tile) flooring on the Intermediate Platform and the Observation Platform is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. | TOWER 2 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4050
1705ENR2 | EXTERIOR WALL INSULATION | 1705 | This building has no insulation in the exterior walls of the stairwell area. The temperature extremes make it impossible to properly condition the guard station above creating an uncomfortable work environment. This project will install batt insulation in the walls to help moderate temperature fluctuations. It may be possible to use a foamed-in system to fill the cavities where applicable; costs are similar to the batt insulation provided for in this project. | TOWER 2 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8750
1705SEC1 | ACTIVATE ELECTRONIC LOCK SYSTEM | 1705 | The tower controls included an electronic control for the door lock at grade. The system was never made operational and requires tower staff to physically transfer a key from the tower to personnel below. This system is time consuming and rough on the keys and locks. This project recommends running conduit and power to activate the system, permitting tower personnel to remotely actuate the door locks. This project or a portion thereof was previously recommended in the FCA report dated 7/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 3/9/2010. | TOWER 2 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
1705ENR3 | HVAC EQUIPMENT UPGRADE | 1705 | The wall mounted air conditioner/ heater is not energy efficient and has reached the end of its expected and useful life. There is also a window mounted evaporative cooler that is no longer operational. This project would provide for the purchase and installation of a new wall mounted air conditioner/ heater. The cost includes removal and disposal of the existing HVAC units and all required connections to utilities. | TOWER 2 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
1705SEC2 | SPOTLIGHT REPAIRS | 1705 | The electrical cords on the spotlights are frayed and will eventually cause the lights to malfunction. It is important to replace the cords to prevent a short as well as to protect the staff from electrical shock. This project would provide for replacing the cords in the next 2-3 years. | TOWER 2 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
1705PLM1 | WATER HEATER REPLACEMENT | 1705 | There is an 8 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | TOWER 2 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
1705EXT3 | SLIDING GLASS DOOR REPLACEMENT | 1705 | The sliding glass door has reached the end of its expected life. It is damaged from age and general wear and tear and is missing the screen door. This project would provide for the replacement of the sliding glass door assembly with a new door, frame and hardware. Removal and disposal of the existing door is included in this estimate. | TOWER 2 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
1705EXT1 | ROOF REPLACEMENT | 1705 | The standing seam metal roof on this building was in fair to poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new single-ply roofing system which will be installed directly over the existing metal roof. This will allow the roof to qualify for the statewide roofing program warranty and preventative maintenance agreement. This project or a portion thereof was previously recommended in the FCA report dated 7/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 3/9/2010. | TOWER 2 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4800
1705EXT2 | EXTERIOR FINISHES | 1705 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is painting of the handrails and guardrails and caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted, caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | TOWER 2 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4800
1705INT1 | INTERIOR FINISHES | 1705 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings of the observation platform be painted at least once in the next 2-4 years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | TOWER 2 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2010
1707SEC2 | SPOTLIGHT REPAIRS | 1707 | The electrical cords on the spotlights are frayed and will eventually cause the lights to malfunction. It is important to replace the cords to prevent a short as well as to protect the staff from electrical shock. This project would provide for replacing the cords in the next 2-3 years. | TOWER 4 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
1706INT1 | INTERIOR FINISHES | 1706 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings of the observation platform be painted at least once in the next 2-4 years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | TOWER 3 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2010
1705SFT1 | EXIT SIGN INSTALLATION | 1705 | The building does not have any exit signs. This project would provide for the purchase and installation of a self-illuminated or LED style exit sign with battery-backed internal system at the entry/ exit door. IBC - 2006 Chapter 10 was referenced for this project. | TOWER 2 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Immediate to Two Years | Currently Critical | 1 | 500
1707EXT1 | ROOF REPLACEMENT | 1707 | The standing seam metal roof on this building was in fair to poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new single-ply roofing system which will be installed directly over the existing metal roof. This will allow the roof to qualify for the statewide roofing program warranty and preventative maintenance agreement. This project or a portion thereof was previously recommended in the FCA report dated 7/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 3/9/2010. | TOWER 4 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4800
1700HVA1 | BOILER REPLACEMENT | 1700 | There are three hot water boilers in the plant that service a majority of the HVAC needs throughout the facility. The system is designed to utilize two boilers at full capacity with the third being a reserve or back-up unit. This project recommends replacing the reserve boiler, or Boiler #3. It has had continuous problems with the fire tubes and tube sheets due to stress cracks and is due for replacement. The estimate includes removal and disposal of the existing equipment and connections to all utilities. This project or a portion thereof was previously recommended in the FCA report dated 7/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 3/9/2010. | BLDG. 07-CENTRAL PLANT | 9962 | Correct | LCC |  | Lovelock | 1993 | 7400 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 250000
1704SFT1 | EXTERIOR STAIR HANDRAIL INSTALLATION | 1704 | The concrete exterior stairs near the entry gate are lacking a handrail as required in the 2006 IBC Chapter 10, Section 1012. This project would provide for a tubular steel framed handrail to be installed at the two steps along the walkway. | TOWER 1 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Immediate to Two Years | Currently Critical | 1 | 1500
1707ENR2 | EXTERIOR WALL INSULATION | 1707 | This building has no insulation in the exterior walls of the stairwell area. The temperature extremes make it impossible to properly condition the guard station above creating an uncomfortable work environment. This project will install batt insulation in the walls to help moderate temperature fluctuations. It may be possible to use a foamed-in system to fill the cavities where applicable; costs are similar to the batt insulation provided for in this project. | TOWER 4 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4200
1707PLM1 | WATER HEATER REPLACEMENT | 1707 | There is an 8 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | TOWER 4 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
1707EXT3 | SLIDING GLASS DOOR REPLACEMENT | 1707 | The sliding glass door has reached the end of its expected life. It is damaged from age and general wear and tear and is missing the screen door. This project would provide for the replacement of the sliding glass door assembly with a new door, frame and hardware. Removal and disposal of the existing door is included in this estimate. | TOWER 4 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
1707SFT1 | EXIT SIGN INSTALLATION | 1707 | The building does not have any exit signs. This project would provide for the purchase and installation of a self-illuminated or LED style exit sign with battery-backed internal system at the entry/ exit door. IBC - 2006 Chapter 10 was referenced for this project. | TOWER 4 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Immediate to Two Years | Currently Critical | 1 | 500
1707INT1 | INTERIOR FINISHES | 1707 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings of the observation platform be painted at least once in the next 2-4 years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | TOWER 4 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2010
1707INT2 | VCT FLOORING REPLACEMENT | 1707 | The VCT (vinyl composite tile) flooring on the Intermediate Platform and the Observation Platform is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. | TOWER 4 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4050
1707EXT2 | EXTERIOR FINISHES | 1707 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is painting of the handrails and guardrails and caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted, caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | TOWER 4 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
1706PLM1 | WATER HEATER REPLACEMENT | 1706 | There is an 8 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | TOWER 3 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
1707SEC1 | ACTIVATE ELECTRONIC LOCK SYSTEM | 1707 | The tower controls included an electronic control for the door lock at grade. The system was never made operational and requires tower staff to physically transfer a key from the tower to personnel below. This system is time consuming and rough on the keys and locks. This project recommends running conduit and power to activate the system, permitting tower personnel to remotely actuate the door locks. This project or a portion thereof was previously recommended in the FCA report dated 7/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 3/9/2010. | TOWER 4 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
1706ENR2 | EXTERIOR WALL INSULATION | 1706 | This building has no insulation in the exterior walls of the stairwell area. The temperature extremes make it impossible to properly condition the guard station above creating an uncomfortable work environment. This project will install batt insulation in the walls to help moderate temperature fluctuations. It may be possible to use a foamed-in system to fill the cavities where applicable; costs are similar to the batt insulation provided for in this project. | TOWER 3 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8750
1706EXT3 | SLIDING GLASS DOOR REPLACEMENT | 1706 | The sliding glass door has reached the end of its expected life. It is damaged from age and general wear and tear and is missing the screen door. This project would provide for the replacement of the sliding glass door assembly with a new door, frame and hardware. Removal and disposal of the existing door is included in this estimate. | TOWER 3 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
1706ENR3 | HVAC EQUIPMENT UPGRADE | 1706 | The wall mounted air conditioner/ heater is not energy efficient and has reached the end of its expected and useful life. There is also a window mounted evaporative cooler that is no longer operational. This project would provide for the purchase and installation of a new wall mounted air conditioner/ heater. The cost includes removal and disposal of the existing HVAC units and all required connections to utilities. | TOWER 3 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
1706SFT1 | EXIT SIGN INSTALLATION | 1706 | The building does not have any exit signs. This project would provide for the purchase and installation of a self-illuminated or LED style exit sign with battery-backed internal system at the entry/ exit door. IBC - 2006 Chapter 10 was referenced for this project. | TOWER 3 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Immediate to Two Years | Currently Critical | 1 | 500
1706INT2 | VCT FLOORING REPLACEMENT | 1706 | The VCT (vinyl composite tile) flooring on the Intermediate Platform and the Observation Platform is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. | TOWER 3 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4050
1706SEC2 | SPOTLIGHT REPAIRS | 1706 | The electrical cords on the spotlights are frayed and will eventually cause the lights to malfunction. It is important to replace the cords to prevent a short as well as to protect the staff from electrical shock. This project would provide for replacing the cords in the next 2-3 years. | TOWER 3 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
1707ENR3 | HVAC EQUIPMENT UPGRADE | 1707 | The wall mounted air conditioner/ heater is not energy efficient and has reached the end of its expected and useful life. There is also a window mounted evaporative cooler that is no longer operational. This project would provide for the purchase and installation of a new wall mounted air conditioner/ heater. The cost includes removal and disposal of the existing HVAC units and all required connections to utilities. | TOWER 4 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
1699INT1 | INTERIOR FINISHES | 1699 | The interior finishes are in fair condition. This project would provide funding to maintain the interior of the building. Included in the cost is painting the walls and ceilings, sealing the exposed masonry, repairing cracks in the masonry and replacing grout and caulk as needed. An epoxy-based paint should be utilized in wet areas for durability. It is recommended that the interior of the building be painted, sealed and repaired in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BLDG. 06-WAREHOUSE/MAINTENANCE | 9962 | Correct | LCC |  | Lovelock | 1993 | 23000 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 115000
1700EXT2 | EXTERIOR FINISHES | 1700 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the concrete masonry walls, painting the flashing and caulking the flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BLDG. 07-CENTRAL PLANT | 9962 | Correct | LCC |  | Lovelock | 1993 | 7400 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 37000
1701EXT2 | EXTERIOR FINISHES | 1701 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the concrete masonry walls, painting the window frames and flashing and caulking the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BLDG. 08-TRUSTEE DORMITORY | 9962 | Correct | LCC |  | Lovelock | 1993 | 3700 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18500
1700INT1 | INTERIOR FINISHES | 1700 | The interior finishes are in fair condition. This project would provide funding to maintain the interior of the building. Included in the cost is painting the walls and ceilings, sealing the exposed masonry, repairing cracks in the masonry and replacing grout and caulk as needed. An epoxy-based paint should be utilized in wet areas for durability. It is recommended that the interior of the building be painted, sealed and repaired in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BLDG. 07-CENTRAL PLANT | 9962 | Correct | LCC |  | Lovelock | 1993 | 7400 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 37000
1700INT2 | RESTROOM FLOOR REPLACEMENT | 1700 | The epoxy floor covering in the restroom is damaged and reaching the end of its useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of a new poured epoxy flooring in the next 2-3 years. | BLDG. 07-CENTRAL PLANT | 9962 | Correct | LCC |  | Lovelock | 1993 | 7400 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
1700HVA2 | CHEMICAL FREE WATER FILTER | 1700 | The cooling tower was installed without a proper filtering system. The original design called for a Dolphin system, but funding was insufficient. The maintenance staff suggested that a Dolphin or similar chemical free system would be ideal. This project would provide for removal and disposal of the existing sock filter and installation of a chemical free filtering system. | BLDG. 07-CENTRAL PLANT | 9962 | Correct | LCC |  | Lovelock | 1993 | 7400 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
1700ENV1 | PROVIDE HAZARDOUS MATERIALS CONTAINMENT | 1700 | There are many different paints, stains, oils and other hazardous or flammable products on open shelves throughout the building. This does not meet OSHA standards for hazardous materials containment. This project would provide 5 hazardous materials storage cabinets in the building and install placards on the building exterior in accordance with OSHA 1910.106 (d). | BLDG. 07-CENTRAL PLANT | 9962 | Correct | LCC |  | Lovelock | 1993 | 7400 | 2010-03-09 | Immediate to Two Years | Currently Critical | 1 | 25000
1700EXT1 | ROOF REPLACEMENT | 1700 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1993. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 7/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 3/9/2010. | BLDG. 07-CENTRAL PLANT | 9962 | Correct | LCC |  | Lovelock | 1993 | 7400 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 103500
1701INT1 | INTERIOR FINISHES | 1701 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-4 years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | BLDG. 08-TRUSTEE DORMITORY | 9962 | Correct | LCC |  | Lovelock | 1993 | 3700 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18500
1699ENV1 | DUST COLLECTION SYSTEM INSTALLATIONS | 1699 | The building has a carpentry shop and a welding shop which do not have complete dust collection systems. There is a fan and motor in the carpentry shop, but no ducting to the tables or equipment. In order to reduce the possibility of damage or injury, each piece of equipment should have complete collection capability. It is assumed that the existing equipment in the carpentry shop does not work or will need to be replaced in the near future. This project recommends installing a complete new dust collection system in each shop. | BLDG. 06-WAREHOUSE/MAINTENANCE | 9962 | Correct | LCC |  | Lovelock | 1993 | 23000 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 40000
1701INT2 | JANITORS CLOSET REPAIRS | 1701 | The mop sink in the Janitors Closet is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | BLDG. 08-TRUSTEE DORMITORY | 9962 | Correct | LCC |  | Lovelock | 1993 | 3700 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
1699EXT2 | EXTERIOR FINISHES | 1699 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the concrete masonry walls, painting the window frames and flashing and caulking the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BLDG. 06-WAREHOUSE/MAINTENANCE | 9962 | Correct | LCC |  | Lovelock | 1993 | 23000 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 115000
1699EXT1 | ROOF REPLACEMENT | 1699 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1993. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 7/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 3/9/2010. | BLDG. 06-WAREHOUSE/MAINTENANCE | 9962 | Correct | LCC |  | Lovelock | 1993 | 23000 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 345000
1902EXT2 | EXTERIOR FINISHES | 1902 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the concrete walls, painting the window frames and flashing and caulking the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT 6 | 9962 | Correct | LCC |  | Lovelock | 1997 | 23000 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 115000
1902EXT1 | ROOF REPLACEMENT | 1902 | The roof on this building was in fair to poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1997. It is recommended that this building be re-roofed in the next 2-4 years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 7/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 3/9/2010. | HOUSING UNIT 6 | 9962 | Correct | LCC |  | Lovelock | 1997 | 23000 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 172500
1902INT2 | SHOWER FLOOR REPLACEMENT | 1902 | The epoxy floor covering in the two shower areas is damaged and reaching the end of its useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of a new poured epoxy flooring in the next 2-3 years. | HOUSING UNIT 6 | 9962 | Correct | LCC |  | Lovelock | 1997 | 23000 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
1902PLM2 | WATER HEATER REPLACEMENT | 1902 | There are two 100 gallon natural gas-fired water heaters in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, these units are showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that two new natural gas-fired water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. | HOUSING UNIT 6 | 9962 | Correct | LCC |  | Lovelock | 1997 | 23000 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
1902INT1 | INTERIOR FINISHES | 1902 | The interior finishes are in fair condition. This project would provide funding to maintain the interior of the building. Included in the cost is painting the walls and ceilings, sealing the exposed masonry, repairing cracks in the masonry and replacing grout and caulk as needed. An epoxy-based paint should be utilized in wet areas for durability. It is recommended that the interior of the building be painted, sealed and repaired in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT 6 | 9962 | Correct | LCC |  | Lovelock | 1997 | 23000 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 115000
1902PLM1 | WATER SOFTENER SYSTEM INSTALLATION | 1902 | There is no water softening/ treatment systems in the building to serve the mechanical equipment. Water that has not been treated causes wear and tear on the domestic water supply lines, plumbing fixtures and HVAC equipment. This project would provide for the purchase and installation of water softener system including all required connections to plumbing and electrical systems. | HOUSING UNIT 6 | 9962 | Correct | LCC |  | Lovelock | 1997 | 23000 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
1699PLM1 | WATER HEATER REPLACEMENT | 1699 | There is a 50 gallon natural gas-fired water heater in the basement. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new natural gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | BLDG. 06-WAREHOUSE/MAINTENANCE | 9962 | Correct | LCC |  | Lovelock | 1993 | 23000 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
1704EXT2 | EXTERIOR FINISHES | 1704 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is painting of the handrails and guardrails and caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted, caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | TOWER 1 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3600
1704ENR2 | EXTERIOR WALL INSULATION | 1704 | This building has no insulation in the exterior walls of the stairwell area. The temperature extremes make it impossible to properly condition the guard station above creating an uncomfortable work environment. This project will install batt insulation in the walls to help moderate temperature fluctuations. It may be possible to use a foamed-in system to fill the cavities where applicable; costs are similar to the batt insulation provided for in this project. | TOWER 1 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4200
1704INT2 | VCT FLOORING REPLACEMENT | 1704 | The VCT (vinyl composite tile) flooring on the Intermediate Platform and the Observation Platform is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. | TOWER 1 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4050
1704INT1 | INTERIOR FINISHES | 1704 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings of the observation platform be painted at least once in the next 2-4 years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | TOWER 1 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2010
1704SEC2 | SPOTLIGHT REPAIRS | 1704 | The electrical cords on the spotlights are frayed and will eventually cause the lights to malfunction. It is important to replace the cords to prevent a short as well as to protect the staff from electrical shock. This project would provide for replacing the cords in the next 2-3 years. | TOWER 1 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
1704SFT2 | EXIT SIGN INSTALLATION | 1704 | The building does not have any exit signs. This project would provide for the purchase and installation of a self-illuminated or LED style exit sign with battery-backed internal system at the entry/ exit door. IBC - 2006 Chapter 10 was referenced for this project. | TOWER 1 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Immediate to Two Years | Currently Critical | 1 | 500
1704ENR3 | HVAC EQUIPMENT UPGRADE | 1704 | The wall mounted air conditioner/ heater is not energy efficient and has reached the end of its expected and useful life. There is also a window mounted evaporative cooler that is no longer operational. This project would provide for the purchase and installation of a new wall mounted air conditioner/ heater. The cost includes removal and disposal of the existing HVAC units and all required connections to utilities. | TOWER 1 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
1704PLM1 | WATER HEATER REPLACEMENT | 1704 | There is an 8 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | TOWER 1 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
1701EXT1 | ROOF REPLACEMENT | 1701 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1993. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 7/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 3/9/2010. | BLDG. 08-TRUSTEE DORMITORY | 9962 | Correct | LCC |  | Lovelock | 1993 | 3700 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 55500
1704SEC1 | ACTIVATE ELECTRONIC LOCK SYSTEM | 1704 | The tower controls included an electronic control for the door lock at grade. The system was never made operational and requires tower staff to physically transfer a key from the tower to personnel below. This system is time consuming and rough on the keys and locks. This project recommends running conduit and power to activate the system, permitting tower personnel to remotely actuate the door locks. This project or a portion thereof was previously recommended in the FCA report dated 7/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 3/9/2010. | TOWER 1 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
1704EXT3 | SLIDING GLASS DOOR REPLACEMENT | 1704 | The sliding glass door has reached the end of its expected life. It is damaged from age and general wear and tear and is missing the screen door. This project would provide for the replacement of the sliding glass door assembly with a new door, frame and hardware. Removal and disposal of the existing door is included in this estimate. | TOWER 1 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
1703ADA1 | ADA RESTROOM UPGRADES | 1703 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. There are several minor adjustments that must be made to the restrooms in order to comply with the ADA. These include new signs, mounting the signs on the wall adjacent to the doors instead of on the doors and altering the locations and orientations of some of the restroom fixtures. The 2006 IBC, ICC/ANSI A117.1 - 2003 and the most current version of the Americans With Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | BLDG. 10-ENTRY | 9962 | Correct | LCC |  | Lovelock | 1993 | 1515 | 2010-03-09 | Immediate to Two Years | Currently Critical | 1 | 2500
1703INT1 | INTERIOR FINISHES | 1703 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-4 years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | BLDG. 10-ENTRY | 9962 | Correct | LCC |  | Lovelock | 1993 | 1515 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7575
1703EXT1 | ROOF REPLACEMENT | 1703 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1993. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 7/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 3/9/2010. | BLDG. 10-ENTRY | 9962 | Correct | LCC |  | Lovelock | 1993 | 1515 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 22725
1703EXT2 | EXTERIOR FINISHES | 1703 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the concrete masonry walls, painting the window frames and flashing and caulking the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BLDG. 10-ENTRY | 9962 | Correct | LCC |  | Lovelock | 1993 | 1515 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7575
1702PLM1 | WATER HEATER REPLACEMENT | 1702 | There is a 30 gallon natural gas-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new natural gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | BLDG. 09-ARMORY | 9962 | Correct | LCC |  | Lovelock | 1993 | 1275 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
1702INT1 | INTERIOR FINISHES | 1702 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-4 years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | BLDG. 09-ARMORY | 9962 | Correct | LCC |  | Lovelock | 1993 | 1275 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6375
1702EXT2 | EXTERIOR FINISHES | 1702 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the concrete masonry walls, painting the flashing and caulking the flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BLDG. 09-ARMORY | 9962 | Correct | LCC |  | Lovelock | 1993 | 1275 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6375
1702EXT1 | ROOF REPLACEMENT | 1702 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1993. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 7/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 3/9/2010. | BLDG. 09-ARMORY | 9962 | Correct | LCC |  | Lovelock | 1993 | 1275 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19125
1704EXT1 | ROOF REPLACEMENT | 1704 | The standing seam metal roof on this building was in fair to poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new single-ply roofing system which will be installed directly over the existing metal roof. This will allow the roof to qualify for the statewide roofing program warranty and preventative maintenance agreement. This project or a portion thereof was previously recommended in the FCA report dated 7/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 3/9/2010. | TOWER 1 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4800
9962ELE1 | HIGH MAST LAMP REPLACEMENT | 9962 | There are 13 high mast security light poles throughout the facility that have 10 security lamps each. A lot of these lamps were burned out at the time of the survey and should be scheduled for replacement. This project provides for the purchase and installation of 130 security lamps for the high mast light poles. The cost includes removal and disposal of the existing lamps. | LOVELOCK CORRECTIONAL CENTER SITE | 9962 | Correct | LCC |  | Lovelock | 0 |  | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 65000
9962ENR2 | AIR HANDLER REPLACEMENT | 9962 | The HVAC roof top units throughout the site were installed in 1993 and 1997. They are not energy efficient and are reaching the end of their expected life. This project would provide for installation of new HVAC packaged units and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. There are approximately 56 units at the site. This project or a portion thereof was previously recommended in the FCA report dated 7/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 3/9/2010. | LOVELOCK CORRECTIONAL CENTER SITE | 9962 | Correct | LCC |  | Lovelock | 0 |  | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6800000
9962SEC2 | VIDEO SECURITY SYSTEM UPGRADE | 9962 | The site video security system is outdated and should be scheduled for replacement. The cameras have been removed or do not function on several of the buildings and there are blind spots in the coverage that should be addressed. This project addresses replacement of the cameras and controls at the site with all digital equipment as well as sufficient storage capacity. This project or a portion thereof was previously recommended in the FCA report dated 7/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 3/9/2010. | LOVELOCK CORRECTIONAL CENTER SITE | 9962 | Correct | LCC |  | Lovelock | 0 |  | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500000
9962PLM3 | BACKFLOW PREVENTION | 9962 | State Health Law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of back siphonage or backpressure. This project allows for the installation of double check valves or reduced pressure principle backflow preventers on the main connection to city water. Costs include an above ground vault and allowance for 200 feet of 1" conduit to provide power for freeze protection. | LOVELOCK CORRECTIONAL CENTER SITE | 9962 | Correct | LCC |  | Lovelock | 0 |  | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
9962ENR1 | EXTERIOR SOLAR SITE LIGHTING INSTALLATION | 9962 | The pole lights for the parking lot and entry access road were installed in 1993 and are due for an upgrade. The existing lamps are not energy efficient and require excessive labor time to replace. This project would provide for replacing the lamp heads with solar powered LED exterior light fixtures. This installation will eliminate electricity costs and the longer lifetime of the LED lamps will lower labor time for replacements. The estimate is based on the removal and replacement of 13 light fixtures. | LOVELOCK CORRECTIONAL CENTER SITE | 9962 | Correct | LCC |  | Lovelock | 0 |  | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 84500
3040EXT1 | EXTERIOR FINISHES | 3040 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is the caulking and sealing of the flashing, fixtures, and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | FIRE PUMP HOUSE | 9962 | Correct | LCC |  | Lovelock | 1993 | 192 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 576
3041EXT1 | EXTERIOR FINISHES | 3041 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the flashing, fixtures, and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SEWAGE GRINDER SHELTER | 9962 | Correct | LCC |  | Lovelock | 0 | 160 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 800
3042EXT1 | EXTERIOR FINISHES | 3042 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding, priming, painting, and caulking of the flashing, fixtures, and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | STORAGE BUILDING | 9962 | Correct | LCC |  | Lovelock | 2007 | 676 | 2010-03-09 | Four to Ten Years | Long-Term Needs | 3 | 3380
9962SFT1 | FIRE ALARM SYSTEM UPGRADE | 9962 | This site is equipped with an automatic fire detection and alarm system that no longer complies with current requirements. It has given the maintenance staff continuous problems and replacement parts are becoming more difficult to find. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 "If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure". When completed, the new system will provide visual, as well as audible notification, in accordance with the 2006 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. This project or a portion thereof was previously recommended in the FCA report dated 7/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 3/9/2010. | LOVELOCK CORRECTIONAL CENTER SITE | 9962 | Correct | LCC |  | Lovelock | 0 |  | 2010-03-09 | Immediate to Two Years | Currently Critical | 1 | 2000000
9962SIT3 | SLURRY SEAL ASPHALT PAVING | 9962 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site wide including access roads, parking areas, the maintenance yard, and the basketball court at Building #8. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 350,000 square feet of asphalt area was used to generate this estimate. | LOVELOCK CORRECTIONAL CENTER SITE | 9962 | Correct | LCC |  | Lovelock | 0 |  | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 262500
1692INT1 | INTERIOR FINISHES | 1692 | The interior finishes are in fair condition. This project would provide funding to maintain the interior of the building. Included in the cost is painting the walls and ceilings, sealing the exposed masonry, repairing cracks in the masonry and replacing grout and caulk as needed. An epoxy-based paint should be utilized in wet areas for durability. It is recommended that the interior of the building be painted, sealed and repaired in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT 3 | 9962 | Correct | LCC |  | Lovelock | 1997 | 44500 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 222500
1691EXT2 | EXTERIOR FINISHES | 1691 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the concrete walls, painting the window frames and flashing and caulking the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT 2 | 9962 | Correct | LCC |  | Lovelock | 1993 | 44500 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 222500
1692EXT1 | ROOF REPLACEMENT | 1692 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1997. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 7/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 3/17/2010. | HOUSING UNIT 3 | 9962 | Correct | LCC |  | Lovelock | 1997 | 44500 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 345000
1694EXT1 | ROOF REPLACEMENT | 1694 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1993. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 7/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 3/17/2010. | BLDG. 02-INFIRMARY & EDUCATION | 9962 | Correct | LCC |  | Lovelock | 1993 | 27000 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 405000
1693INT2 | SHOWER FLOOR REPLACEMENT | 1693 | The epoxy floor covering in the two shower areas is damaged and reaching the end of its useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of a new poured epoxy flooring in the next 2-3 years. | HOUSING UNIT 4 | 9962 | Correct | LCC |  | Lovelock | 1997 | 44500 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
1693EXT1 | ROOF REPLACEMENT | 1693 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1997. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 7/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 3/17/2010. | HOUSING UNIT 4 | 9962 | Correct | LCC |  | Lovelock | 1997 | 44500 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 345000
1693INT1 | INTERIOR FINISHES | 1693 | The interior finishes are in fair condition. This project would provide funding to maintain the interior of the building. Included in the cost is painting the walls and ceilings, sealing the exposed masonry, repairing cracks in the masonry and replacing grout and caulk as needed. An epoxy-based paint should be utilized in wet areas for durability. It is recommended that the interior of the building be painted, sealed and repaired in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT 4 | 9962 | Correct | LCC |  | Lovelock | 1997 | 44500 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 222500
1693EXT2 | EXTERIOR FINISHES | 1693 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the concrete walls, painting the window frames and flashing and caulking the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT 4 | 9962 | Correct | LCC |  | Lovelock | 1997 | 44500 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 222500
1692INT2 | SHOWER FLOOR REPLACEMENT | 1692 | The epoxy floor covering in the two shower areas is damaged and reaching the end of its useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of a new poured epoxy flooring in the next 2-3 years. | HOUSING UNIT 3 | 9962 | Correct | LCC |  | Lovelock | 1997 | 44500 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
1692EXT2 | EXTERIOR FINISHES | 1692 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the concrete walls, painting the window frames and flashing and caulking the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT 3 | 9962 | Correct | LCC |  | Lovelock | 1997 | 44500 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 222500
1691INT2 | SHOWER FLOOR REPLACEMENT | 1691 | The epoxy floor covering in the two shower areas is damaged and reaching the end of its useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of a new poured epoxy flooring in the next 2-3 years. | HOUSING UNIT 2 | 9962 | Correct | LCC |  | Lovelock | 1993 | 44500 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
1694EXT2 | EXTERIOR FINISHES | 1694 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the concrete masonry walls, painting the window frames and flashing and caulking the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BLDG. 02-INFIRMARY & EDUCATION | 9962 | Correct | LCC |  | Lovelock | 1993 | 27000 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 135000
1691EXT1 | ROOF REPLACEMENT | 1691 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1993. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 7/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 3/17/2010. | HOUSING UNIT 2 | 9962 | Correct | LCC |  | Lovelock | 1993 | 44500 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 345000
1694INT2 | INTERIOR FINISHES | 1694 | The interior finishes are in fair condition. This project would provide funding to maintain the interior of the building. Included in the cost is painting the walls and ceilings, sealing the exposed masonry, repairing cracks in the masonry and replacing grout and caulk as needed. An epoxy-based paint should be utilized in wet areas for durability. It is recommended that the interior of the building be painted, sealed and repaired in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BLDG. 02-INFIRMARY & EDUCATION | 9962 | Correct | LCC |  | Lovelock | 1993 | 27000 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 135000
1679INT2 | SHOWER FLOOR REPLACEMENT | 1679 | The epoxy floor covering in the two shower areas is damaged and reaching the end of its useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of a new poured epoxy flooring in the next 2-3 years. | HOUSING UNIT 1 | 9962 | Correct | LCC |  | Lovelock | 1993 | 44500 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
1679INT1 | INTERIOR FINISHES | 1679 | The interior finishes are in fair condition. This project would provide funding to maintain the interior of the building. Included in the cost is painting the walls and ceilings, sealing the exposed masonry, repairing cracks in the masonry and replacing grout and caulk as needed. An epoxy-based paint should be utilized in wet areas for durability. It is recommended that the interior of the building be painted, sealed and repaired in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT 1 | 9962 | Correct | LCC |  | Lovelock | 1993 | 44500 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 222500
1679EXT2 | EXTERIOR FINISHES | 1679 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the concrete walls, painting the window frames and flashing and caulking the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT 1 | 9962 | Correct | LCC |  | Lovelock | 1993 | 44500 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 222500
1679EXT1 | ROOF REPLACEMENT | 1679 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1993. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 7/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 3/17/2010. | HOUSING UNIT 1 | 9962 | Correct | LCC |  | Lovelock | 1993 | 44500 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 345000
2018EXT1 | ROOF REPLACEMENT | 2018 | The roof on this building was in fair to poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1997. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 7/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 3/17/2010. | HOUSING UNIT 5 | 9962 | Correct | LCC |  | Lovelock | 1997 | 23000 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 172500
2018EXT2 | EXTERIOR FINISHES | 2018 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the concrete walls, painting the window frames and flashing, and caulking the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT 5 | 9962 | Correct | LCC |  | Lovelock | 1997 | 23000 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 115000
2018INT2 | SHOWER FLOOR REPLACEMENT | 2018 | The epoxy floor covering in the two shower areas is damaged and reaching the end of its useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of a new poured epoxy flooring in the next 2-3 years. | HOUSING UNIT 5 | 9962 | Correct | LCC |  | Lovelock | 1997 | 23000 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
2018INT1 | INTERIOR FINISHES | 2018 | The interior finishes are in fair condition. This project would provide funding to maintain the interior of the building. Included in the cost is painting the walls and ceilings, sealing the exposed masonry, repairing cracks in the masonry and replacing grout and caulk as needed. An epoxy-based paint should be utilized in wet areas for durability. It is recommended that the interior of the building be painted, sealed and repaired in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT 5 | 9962 | Correct | LCC |  | Lovelock | 1997 | 23000 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 115000
2018PLM2 | WATER HEATER REPLACEMENT | 2018 | There are two 100 gallon natural gas-fired water heaters in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, these units are showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that two new natural gas-fired water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. | HOUSING UNIT 5 | 9962 | Correct | LCC |  | Lovelock | 1997 | 23000 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
2018PLM1 | WATER SOFTENER SYSTEM INSTALLATION | 2018 | There is no water softening/ treatment systems in the building to serve the mechanical equipment. Water that has not been treated causes wear and tear on the domestic water supply lines, plumbing fixtures and HVAC equipment. This project would provide for the purchase and installation of water softener system including all required connections to plumbing and electrical systems. | HOUSING UNIT 5 | 9962 | Correct | LCC |  | Lovelock | 1997 | 23000 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
1691INT1 | INTERIOR FINISHES | 1691 | The interior finishes are in fair condition. This project would provide funding to maintain the interior of the building. Included in the cost is painting the walls and ceilings, sealing the exposed masonry, repairing cracks in the masonry and replacing grout and caulk as needed. An epoxy-based paint should be utilized in wet areas for durability. It is recommended that the interior of the building be painted, sealed and repaired in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT 2 | 9962 | Correct | LCC |  | Lovelock | 1993 | 44500 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 222500
1695ADA3 | ADA RESTROOM / SIGNAGE | 1695 | The restrooms and signage in the visitation area are not fully ADA compliant. This project would provide for proper signage to be installed on the walls adjacent to the restroom and also provide for minor restroom fixture adjustments including relocating the flush valve on the toilet. The 2006 IBC, ICC/ANSI A117.1 - 2003, NRS 338.180 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) was used as a reference for this project. | BLDG. 01-ADMINISTRATION & VISITING | 9962 | Correct | LCC |  | Lovelock | 1993 | 30700 | 2010-03-17 | Immediate to Two Years | Currently Critical | 1 | 2000
1697EXT1 | ROOF REPLACEMENT | 1697 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1993. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 7/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 3/17/2010. | BLDG. 04-LAUNDRY/PRISON INDUSTRY | 9962 | Correct | LCC |  | Lovelock | 1993 | 27000 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 405000
1696INT2 | FLOORING REPAIRS | 1696 | The ceramic tile flooring in the Bakery is damaged and is reaching the end of its useful life. There are also numerous places throughout the buildings interior where the tile base is damaged or missing. It is recommended that the flooring and wall base be replaced as needed. This project would provide for removal and disposal of the existing flooring and installation of new 6x6 ceramic tiles and ceramic base in the next 2-3 years. | BLDG. 03-GYM/CULINARY/DINING | 9962 | Correct | LCC |  | Lovelock | 1993 | 32000 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18000
1696INT1 | INTERIOR FINISHES | 1696 | The interior finishes are in fair condition. This project would provide funding to maintain the interior of the building. Included in the cost is painting the walls and ceilings, sealing the exposed masonry, repairing cracks in the masonry and replacing grout and caulk as needed. An epoxy-based paint should be utilized in wet areas for durability. It is recommended that the interior of the building be painted, sealed and repaired in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BLDG. 03-GYM/CULINARY/DINING | 9962 | Correct | LCC |  | Lovelock | 1993 | 32000 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 160000
1697PLM1 | TEST VALVE INSTALLATION | 1697 | The water softening system for the laundry room boiler is in Bldg. 5. Testing the water then becomes difficult because the test valve is in the other building. There are strict guidelines for the water supply to the washing machines. This project provides for the installation of a test valve in the Laundry area. | BLDG. 04-LAUNDRY/PRISON INDUSTRY | 9962 | Correct | LCC |  | Lovelock | 1993 | 27000 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
1697INT1 | INTERIOR FINISHES | 1697 | The interior finishes are in fair condition. This project would provide funding to maintain the interior of the building. Included in the cost is painting the walls and ceilings, sealing the exposed masonry, repairing cracks in the masonry and replacing grout and caulk as needed. An epoxy-based paint should be utilized in wet areas for durability. It is recommended that the interior of the building be painted, sealed and repaired in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BLDG. 04-LAUNDRY/PRISON INDUSTRY | 9962 | Correct | LCC |  | Lovelock | 1993 | 27000 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 135000
1694INT1 | CARPET REPLACEMENT | 1694 | Approximately 2,500 square feet of the building is covered by carpet. It is showing signs of extreme wear and should be scheduled for replacement. It is recommended that the carpet be replaced with heavy duty commercial grade carpet in the next 2-3 years. This project or a portion thereof was previously recommended in the FCA report dated 7/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 3/17/2010. | BLDG. 02-INFIRMARY & EDUCATION | 9962 | Correct | LCC |  | Lovelock | 1993 | 27000 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 17500
1698EXT1 | ROOF REPLACEMENT | 1698 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1993. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 7/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 3/17/2010. | BLDG. 05-CANTEEN/PRISON INDUSTRY | 9962 | Correct | LCC |  | Lovelock | 1993 | 24700 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 370500
1698INT1 | INTERIOR FINISHES | 1698 | The interior finishes are in fair condition. This project would provide funding to maintain the interior of the building. Included in the cost is painting the walls and ceilings, sealing the exposed masonry, repairing cracks in the masonry and replacing grout and caulk as needed. An epoxy-based paint should be utilized in wet areas for durability. It is recommended that the interior of the building be painted, sealed and repaired in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BLDG. 05-CANTEEN/PRISON INDUSTRY | 9962 | Correct | LCC |  | Lovelock | 1993 | 24700 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 123500
1697EXT2 | EXTERIOR FINISHES | 1697 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the concrete masonry walls, painting the window frames and flashing and caulking the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BLDG. 04-LAUNDRY/PRISON INDUSTRY | 9962 | Correct | LCC |  | Lovelock | 1993 | 27000 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 135000
1698EXT2 | EXTERIOR FINISHES | 1698 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the concrete masonry walls, painting the window frames and flashing and caulking the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BLDG. 05-CANTEEN/PRISON INDUSTRY | 9962 | Correct | LCC |  | Lovelock | 1993 | 24700 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 123500
1696EXT2 | EXTERIOR FINISHES | 1696 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the concrete masonry walls, painting the window frames and flashing and caulking the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BLDG. 03-GYM/CULINARY/DINING | 9962 | Correct | LCC |  | Lovelock | 1993 | 32000 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 160000
1695EXT3 | WINDOW REPLACEMENT | 1695 | There are two windows in this building that are damaged and should be scheduled for replacement. The seals have broken allowing moisture to accumulate between the panes. This project would provide for the replacement of the windows with new dual pane security rated window systems. Removal and disposal of the existing windows is included in this estimate. | BLDG. 01-ADMINISTRATION & VISITING | 9962 | Correct | LCC |  | Lovelock | 1993 | 30700 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2400
1695PLM1 | WATER HEATER REPLACEMENT | 1695 | There is a 30 gallon natural gas-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new natural gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | BLDG. 01-ADMINISTRATION & VISITING | 9962 | Correct | LCC |  | Lovelock | 1993 | 30700 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
1695ADA1 | TDD INSTALLATION | 1695 | The visitation area is not equipped with a telecommunications device for the deaf (TDD). In order to comply with ADA requirements it is recommended to install a TDD system in the non-contact visitation area. The 2006 IBC, ICC/ANSI A117.1 - 2003, NRS 338.180 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) was used as a reference for this project. | BLDG. 01-ADMINISTRATION & VISITING | 9962 | Correct | LCC |  | Lovelock | 1993 | 30700 | 2010-03-17 | Immediate to Two Years | Currently Critical | 1 | 20000
1695ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 1695 | The visiting area has a water fountain which was not operational at the time of the survey and should be scheduled for replacement. The 2006 IBC Section 1109.5 states where a water fountain is provided, at least half should be accessible. This project would provide funding for the purchase and installation of a new accessible fixed high/ low ADA drinking fountain. The 2006 IBC, ICC/ANSI A117.1 - 2003, NRS 338.180 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) was used as a reference for this project. | BLDG. 01-ADMINISTRATION & VISITING | 9962 | Correct | LCC |  | Lovelock | 1993 | 30700 | 2010-03-17 | Immediate to Two Years | Currently Critical | 1 | 4000
1695INT2 | INTERIOR FINISHES | 1695 | The interior finishes are in fair condition. This project would provide funding to maintain the interior of the building. Included in the cost is painting the walls and ceilings, sealing the exposed masonry, repairing cracks in the masonry and replacing grout and caulk as needed. An epoxy-based paint should be utilized in wet areas for durability. It is recommended that the interior of the building be painted, sealed and repaired in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BLDG. 01-ADMINISTRATION & VISITING | 9962 | Correct | LCC |  | Lovelock | 1993 | 30700 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 153500
1695EXT1 | ROOF REPLACEMENT | 1695 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1993. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 7/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 3/17/2010. | BLDG. 01-ADMINISTRATION & VISITING | 9962 | Correct | LCC |  | Lovelock | 1993 | 30700 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 460500
1695EXT2 | EXTERIOR FINISHES | 1695 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the concrete masonry walls, painting the window frames and flashing and caulking the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BLDG. 01-ADMINISTRATION & VISITING | 9962 | Correct | LCC |  | Lovelock | 1993 | 30700 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 153500
1695INT1 | FLOORING REPLACEMENT | 1695 | The VCT (vinyl composite tile), sheet vinyl and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base, heavy duty sheet vinyl and heavy duty commercial grade carpet in the next 2-3 years. This project or a portion thereof was previously recommended in the FCA report dated 7/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 3/17/2010. | BLDG. 01-ADMINISTRATION & VISITING | 9962 | Correct | LCC |  | Lovelock | 1993 | 30700 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 224000
1696EXT1 | ROOF REPLACEMENT | 1696 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1993. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 7/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 3/17/2010. | BLDG. 03-GYM/CULINARY/DINING | 9962 | Correct | LCC |  | Lovelock | 1993 | 32000 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 480000
1897EXT1 | EXTERIOR FINISHES | 1897 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units, painting the doors, window frames and other painted metal surfaces and caulking of the control joints, windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/03/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/03/2011. | HOUSING UNIT 3 | 9892 | Correct | JCC |  | Jean | 2000 | 3932 | 2011-11-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19660
1897PLM1 | WATER TREATMENT SYSTEM REPLACEMENT | 1897 | The existing water softening/ treatment systems in the building are currently not operational. They are original to the building and approaching the end of their lifecycles. Failure of the equipment causes wear and tear on the domestic water supply lines, plumbing fixtures and HVAC equipment. This project would provide for the replacement of the existing water softeners/ treatment systems with new equipment. This project would also provide for a chemical treatment program including an updated chemicals control system, service and employee training provided by a qualified water treatment vendor. The annual maintenance fee charged by the water treatment vendor would be determined after an investigation of the water system is complete. These annual costs are not included in this project cost. For budgeting purposes, a $12,000 fee is suggested. This project or a portion thereof was previously recommended in the FCA report dated 05/03/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/03/2011. | HOUSING UNIT 3 | 9892 | Correct | JCC |  | Jean | 2000 | 3932 | 2011-11-03 | Immediate to Two Years | Currently Critical | 1 | 20000
1897EXT2 | ROOF REPLACEMENT | 1897 | The single-ply roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. It is recommended that this building be re-roofed within ten years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 05/03/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/03/2011. | HOUSING UNIT 3 | 9892 | Correct | JCC |  | Jean | 2000 | 3932 | 2011-11-03 | Four to Ten Years | Long-Term Needs | 3 | 9600
1897PLM2 | WATER HEATER REPLACEMENT | 1897 | There are two 80 gallon propane-fired water heaters in the closet. The average life span of a water heater is eight to ten years. With the passage of time and constant use, these units are showing signs of wear and should be scheduled for replacement in the next 3-4 years. It is recommended that new propane-fired water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. | HOUSING UNIT 3 | 9892 | Correct | JCC |  | Jean | 2000 | 3932 | 2011-11-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
1897SEC1 | EXTERIOR DOOR REPLACEMENT | 1897 | The existing exterior metal doors and frames appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement and installation of two new hollow metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | HOUSING UNIT 3 | 9892 | Correct | JCC |  | Jean | 2000 | 3932 | 2011-11-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
1986INT2 | INTERIOR FINISHES | 1986 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HOUSING UNIT 4 | 9892 | Correct | JCC |  | Jean | 2000 | 3932 | 2011-11-03 | Four to Ten Years | Long-Term Needs | 3 | 19660
1986EXT1 | EXTERIOR FINISHES | 1986 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units, painting the doors, window frames and other painted metal surfaces and caulking of the control joints, windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/03/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/03/2011. | HOUSING UNIT 4 | 9892 | Correct | JCC |  | Jean | 2000 | 3932 | 2011-11-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19660
1986SEC1 | EXTERIOR DOOR REPLACEMENT | 1986 | The existing exterior metal doors and frames appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement and installation of two new hollow metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | HOUSING UNIT 4 | 9892 | Correct | JCC |  | Jean | 2000 | 3932 | 2011-11-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
1986PLM1 | WATER TREATMENT SYSTEM REPLACEMENT | 1986 | The existing water softening/ treatment systems in the building are currently not operational. They are original to the building and approaching the end of their lifecycles. Failure of the equipment causes wear and tear on the domestic water supply lines, plumbing fixtures and HVAC equipment. This project would provide for the replacement of the existing water softeners/ treatment systems with new equipment. This project would also provide for a chemical treatment program including an updated chemicals control system, service and employee training provided by a qualified water treatment vendor. The annual maintenance fee charged by the water treatment vendor would be determined after an investigation of the water system is complete. These annual costs are not included in this project cost. This project or a portion thereof was previously recommended in the FCA report dated 05/03/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/03/2011. | HOUSING UNIT 4 | 9892 | Correct | JCC |  | Jean | 2000 | 3932 | 2011-11-03 | Immediate to Two Years | Currently Critical | 1 | 20000
1986PLM2 | WATER HEATER REPLACEMENT | 1986 | There are two 80 gallon propane-fired water heaters in the closet. The average life span of a water heater is eight to ten years. With the passage of time and constant use, these units are showing signs of wear and should be scheduled for replacement in the next 3-4 years. It is recommended that new propane-fired water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. | HOUSING UNIT 4 | 9892 | Correct | JCC |  | Jean | 2000 | 3932 | 2011-11-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
1987PLM4 | WATER HEATER REPLACEMENT | 1987 | There are two 80 gallon propane-fired water heaters in the closet. The average life span of a water heater is eight to ten years. With the passage of time and constant use, these units are showing signs of wear and should be scheduled for replacement in the next 3-4 years. It is recommended that new propane-fired water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. | HOUSING UNIT 5 | 9892 | Correct | JCC |  | Jean | 2000 | 3932 | 2011-11-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
1987PLM1 | WATER TREATMENT SYSTEM REPLACEMENT | 1987 | The existing water softening/ treatment systems in the building are currently not operational. They are original to the building and approaching the end of their lifecycles. Failure of the equipment causes wear and tear on the domestic water supply lines, plumbing fixtures and HVAC equipment. This project would provide for the replacement of the existing water softeners/ treatment systems with new equipment. This project would also provide for a chemical treatment program including an updated chemicals control system, service and employee training provided by a qualified water treatment vendor. The annual maintenance fee charged by the water treatment vendor would be determined after an investigation of the water system is complete. These annual costs are not included in this project cost. This project or a portion thereof was previously recommended in the FCA report dated 05/03/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/03/2011. | HOUSING UNIT 5 | 9892 | Correct | JCC |  | Jean | 2000 | 3932 | 2011-11-03 | Immediate to Two Years | Currently Critical | 1 | 20000
1987EXT1 | EXTERIOR FINISHES | 1987 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units, painting the doors, window frames and other painted metal surfaces and caulking of the control joints, windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/03/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/03/2011. | HOUSING UNIT 5 | 9892 | Correct | JCC |  | Jean | 2000 | 3932 | 2011-11-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19660
1987SEC1 | EXTERIOR DOOR REPLACEMENT | 1987 | The existing exterior metal doors and frames appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement and installation of two new hollow metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | HOUSING UNIT 5 | 9892 | Correct | JCC |  | Jean | 2000 | 3932 | 2011-11-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
1987INT2 | INTERIOR FINISHES | 1987 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HOUSING UNIT 5 | 9892 | Correct | JCC |  | Jean | 2000 | 3932 | 2011-11-03 | Four to Ten Years | Long-Term Needs | 3 | 19660
1987EXT2 | ROOF REPLACEMENT | 1987 | The single-ply roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. It is recommended that this building be re-roofed within ten years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 05/03/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/03/2011. | HOUSING UNIT 5 | 9892 | Correct | JCC |  | Jean | 2000 | 3932 | 2011-11-03 | Four to Ten Years | Long-Term Needs | 3 | 9600
1897INT3 | INTERIOR FINISHES | 1897 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HOUSING UNIT 3 | 9892 | Correct | JCC |  | Jean | 2000 | 3932 | 2011-11-03 | Four to Ten Years | Long-Term Needs | 3 | 19660
2125EXT1 | EXTERIOR FINISHES | 2125 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units, painting the doors, window frames and other painted metal surfaces and caulking of the control joints, windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/03/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/03/2011. | CULINARY/CANTEEN/DINING HALL | 9892 | Correct | JCC |  | Jean | 2000 | 5680 | 2011-11-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 28400
2125PLM1 | WATER HEATER REPLACEMENT | 2125 | There are two 100 gallon propane-fired water heaters in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, these units are showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that two new propane-fired water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. | CULINARY/CANTEEN/DINING HALL | 9892 | Correct | JCC |  | Jean | 2000 | 5680 | 2011-11-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
2125INT1 | INTERIOR FINISHES | 2125 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 05/03/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/03/2011. | CULINARY/CANTEEN/DINING HALL | 9892 | Correct | JCC |  | Jean | 2000 | 5680 | 2011-11-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 28400
2125ADA1 | ADA RESTROOM UPGRADE | 2125 | The designated ADA restroom does not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | CULINARY/CANTEEN/DINING HALL | 9892 | Correct | JCC |  | Jean | 2000 | 5680 | 2011-11-03 | Immediate to Two Years | Currently Critical | 1 | 10000
2125CUL1 | CULINARY EQUIPMENT REPLACEMENT | 2125 | The culinary cooking equipment is original to the building and has reached the end of its lifetime. It is recommended that the equipment be scheduled for replacement in the next two to three years, including ovens and hoods, skittles, kettles, sinks, the icemaker, refrigerator and freezer cooling units and dishwasher. This project provides for the removal and disposal of the existing equipment and replacement with new equipment. | CULINARY/CANTEEN/DINING HALL | 9892 | Correct | JCC |  | Jean | 2000 | 5680 | 2011-11-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 150000
2125EXT2 | EXTERIOR DOOR REPLACEMENT | 2125 | The existing exterior metal doors and frames appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the purchase and installation of eight new hollow metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | CULINARY/CANTEEN/DINING HALL | 9892 | Correct | JCC |  | Jean | 2000 | 5680 | 2011-11-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 32000
2125LGT1 | ROOF REPLACEMENT | 2125 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. It is recommended that this building be re-roofed within ten years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 05/03/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/03/2011. | CULINARY/CANTEEN/DINING HALL | 9892 | Correct | JCC |  | Jean | 2000 | 5680 | 2011-11-03 | Four to Ten Years | Long-Term Needs | 3 | 56800
0632SEC1 | EXTERIOR DOOR REPLACEMENT | 0632 | The existing exterior metal doors and frames appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement and installation of two new hollow metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | HOUSING UNIT 1 | 9892 | Correct | JCC |  | Jean | 2000 | 3932 | 2011-11-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
0632INT3 | INTERIOR FINISHES | 0632 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HOUSING UNIT 1 | 9892 | Correct | JCC |  | Jean | 2000 | 3932 | 2011-11-03 | Four to Ten Years | Long-Term Needs | 3 | 19660
0632PLM1 | WATER TREATMENT SYSTEM REPLACEMENT | 0632 | The existing water softening/ treatment systems in the building are currently not operational. They are original to the building and approaching the end of their lifecycles. Failure of the equipment causes wear and tear on the domestic water supply lines, plumbing fixtures and HVAC equipment. This project would provide for the replacement of the existing water softeners/ treatment systems with new equipment. This project would also provide for a chemical treatment program including an updated chemicals control system, service and employee training provided by a qualified water treatment vendor. The annual maintenance fee charged by the water treatment vendor would be determined after an investigation of the water system is complete. These annual costs are not included in this project cost. For budgeting purposes, a $12,000 fee is suggested. This project or a portion thereof was previously recommended in the FCA report dated 05/03/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/03/2011. | HOUSING UNIT 1 | 9892 | Correct | JCC |  | Jean | 2000 | 3932 | 2011-11-03 | Immediate to Two Years | Currently Critical | 1 | 20000
0883EXT2 | DEMOLISH STRUCTURE | 0883 | The building is an old Guard Tower that is no longer in use. The building is dilapidated and deteriorating and has reached the end of its useful life. This project would provide funding for the demolition of the Guard Tower. | JCC GUARD TOWER | 9892 | Correct | JCC |  | Jean | 0 | 288 | 2011-11-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0663HVA1 | HVAC SYSTEM INSTALLATION | 0663 | The Intake area and the Medical area do not currently have any cooling equipment and are uncomfortably hot in the summer. The electric heaters are not energy efficient and have reached the end of their expected life. It is recommended to install HVAC equipment in these occupied areas to ensure a comfortable work environment. This project would provide for the purchase and installation of roof mounted HVAC units including all required connections to existing utilities. | ADMINISTRATION OFFICE/MEDICAL | 9892 | Correct | JCC |  | Jean | 1987 | 3934 | 2011-11-03 | Immediate to Two Years | Currently Critical | 1 | 36000
0663SFT1 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0663 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 05/03/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/03/2011. | ADMINISTRATION OFFICE/MEDICAL | 9892 | Correct | JCC |  | Jean | 1987 | 3934 | 2011-11-03 | Immediate to Two Years | Currently Critical | 1 | 4000
0663ADA1 | ADA SIGNAGE | 0663 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | ADMINISTRATION OFFICE/MEDICAL | 9892 | Correct | JCC |  | Jean | 1987 | 3934 | 2011-11-03 | Immediate to Two Years | Currently Critical | 1 | 1500
0632EXT2 | ROOF REPLACEMENT | 0632 | The single-ply roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. It is recommended that this building be re-roofed within ten years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 05/03/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/03/2011. | HOUSING UNIT 1 | 9892 | Correct | JCC |  | Jean | 2000 | 3932 | 2011-11-03 | Four to Ten Years | Long-Term Needs | 3 | 9600
0663EXT2 | EXTERIOR FINISHES | 0663 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units, painting the doors, window frames and other painted metal surfaces and caulking of the control joints, windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/03/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/03/2011. | ADMINISTRATION OFFICE/MEDICAL | 9892 | Correct | JCC |  | Jean | 1987 | 3934 | 2011-11-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11802
0663INT1 | INTERIOR FINISHES | 0663 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | ADMINISTRATION OFFICE/MEDICAL | 9892 | Correct | JCC |  | Jean | 1987 | 3934 | 2011-11-03 | Four to Ten Years | Long-Term Needs | 3 | 19670
0663INT4 | DOOR REPLACEMENT | 0663 | The existing metal door assemblies are in poor shape from age and wear and tear. This project would provide for the replacement of 11 metal door assemblies including all hardware and painting. Removal and disposal of the old door assemblies is included in this estimate. | ADMINISTRATION OFFICE/MEDICAL | 9892 | Correct | JCC |  | Jean | 1987 | 3934 | 2011-11-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 27500
0663ADA2 | ADA RESTROOM UPGRADES | 0663 | The ADA restroom does not entirely meet the current accessibility requirements. There is no under sink protection and the clear space required under the sink is blocked by the water heater. This project provides for installing under sink protection and relocating the water heater. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2003 were referenced for this project. | ADMINISTRATION OFFICE/MEDICAL | 9892 | Correct | JCC |  | Jean | 1987 | 3934 | 2011-11-03 | Immediate to Two Years | Currently Critical | 1 | 500
0663INT2 | FLOORING REPLACEMENT | 0663 | The VCT (vinyl composite tile), carpet and painted concrete floors in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base, heavy duty commercial grade carpet and applying a new paint or sealant to the concrete in the next 2-3 years. | ADMINISTRATION OFFICE/MEDICAL | 9892 | Correct | JCC |  | Jean | 1987 | 3934 | 2011-11-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19670
0662EXT1 | EXTERIOR FINISHES | 0662 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units, painting the doors, window frames and other painted metal surfaces and caulking of the control joints, windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/03/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/03/2011. | HOUSING UNIT 2 | 9892 | Correct | JCC |  | Jean | 2000 | 3932 | 2011-11-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19660
0662SEC1 | EXTERIOR DOOR REPLACEMENT | 0662 | The existing exterior metal doors and frames appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement and installation of two new hollow metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | HOUSING UNIT 2 | 9892 | Correct | JCC |  | Jean | 2000 | 3932 | 2011-11-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
0662PLM2 | WATER HEATER REPLACEMENT | 0662 | There are two 80 gallon propane-fired water heaters in the closet. The average life span of a water heater is eight to ten years. With the passage of time and constant use, these units are showing signs of wear and should be scheduled for replacement in the next 3-4 years. It is recommended that new propane-fired water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. | HOUSING UNIT 2 | 9892 | Correct | JCC |  | Jean | 2000 | 3932 | 2011-11-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
0662PLM1 | WATER TREATMENT SYSTEM REPLACEMENT | 0662 | The existing water softening/ treatment systems in the building are currently not operational. They are original to the building and approaching the end of their lifecycles. Failure of the equipment causes wear and tear on the domestic water supply lines, plumbing fixtures and HVAC equipment. This project would provide for the replacement of the existing water softeners/ treatment systems with new equipment. This project would also provide for a chemical treatment program including an updated chemicals control system, service and employee training provided by a qualified water treatment vendor. The annual maintenance fee charged by the water treatment vendor would be determined after an investigation of the water system is complete. These annual costs are not included in this project cost. For budgeting purposes, a $12,000 fee is suggested. This project or a portion thereof was previously recommended in the FCA report dated 05/03/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/03/2011. | HOUSING UNIT 2 | 9892 | Correct | JCC |  | Jean | 2000 | 3932 | 2011-11-03 | Immediate to Two Years | Currently Critical | 1 | 20000
0632PLM2 | WATER HEATER REPLACEMENT | 0632 | There are two 80 gallon propane-fired water heaters in the closet. The average life span of a water heater is eight to ten years. With the passage of time and constant use, these units are showing signs of wear and should be scheduled for replacement in the next 3-4 years. It is recommended that new propane-fired water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. | HOUSING UNIT 1 | 9892 | Correct | JCC |  | Jean | 2000 | 3932 | 2011-11-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
0662INT3 | INTERIOR FINISHES | 0662 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HOUSING UNIT 2 | 9892 | Correct | JCC |  | Jean | 2000 | 3932 | 2011-11-03 | Four to Ten Years | Long-Term Needs | 3 | 19660
0632EXT1 | EXTERIOR FINISHES | 0632 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units, painting the doors, window frames and other painted metal surfaces and caulking of the control joints, windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/03/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/03/2011. | HOUSING UNIT 1 | 9892 | Correct | JCC |  | Jean | 2000 | 3932 | 2011-11-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19660
0663PLM1 | WATER HEATER REPLACEMENT | 0663 | There is a 15 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit will be showing signs of wear and should be scheduled for replacement in the next 6-7 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | ADMINISTRATION OFFICE/MEDICAL | 9892 | Correct | JCC |  | Jean | 1987 | 3934 | 2011-11-03 | Four to Ten Years | Long-Term Needs | 3 | 1000
3090INT1 | INTERIOR FINISHES | 3090 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | INMATE SERVICES B | 9967 | Correct | TLVCC |  | Indian Springs | 2010 | 23866 | 2013-05-01 | Four to Ten Years | Long-Term Needs | 3 | 119330
3093EXT1 | EXTERIOR FINISHES | 3093 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NDF OFFICE/SHOP E | 9967 | Correct | Forestry |  | Indian Springs | 2010 | 14685 | 2013-05-01 | Four to Ten Years | Long-Term Needs | 3 | 73425
3091EXT1 | EXTERIOR FINISHES | 3091 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NDOC/NDF ADMINISTRATION C | 9967 | Correct | TLVCC |  | Indian Springs | 2010 | 16386 | 2013-05-01 | Four to Ten Years | Long-Term Needs | 3 | 81930
3091INT1 | INTERIOR FINISHES | 3091 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | NDOC/NDF ADMINISTRATION C | 9967 | Correct | TLVCC |  | Indian Springs | 2010 | 16386 | 2013-05-01 | Four to Ten Years | Long-Term Needs | 3 | 81930
3090EXT1 | EXTERIOR FINISHES | 3090 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | INMATE SERVICES B | 9967 | Correct | TLVCC |  | Indian Springs | 2010 | 23866 | 2013-05-01 | Four to Ten Years | Long-Term Needs | 3 | 119330
3092EXT1 | EXTERIOR FINISHES | 3092 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | INMATE PROGRAMS D | 9967 | Correct | TLVCC |  | Indian Springs | 2010 | 10838 | 2013-05-01 | Four to Ten Years | Long-Term Needs | 3 | 54190
3089EXT1 | EXTERIOR FINISHES | 3089 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT A2 | 9967 | Correct | TLVCC |  | Indian Springs | 2010 | 26767 | 2013-05-01 | Four to Ten Years | Long-Term Needs | 3 | 133835
9967SIT2 | CRACK FILL & SEAL ASPHALT PAVING | 9967 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the paving site wide including access roads, parking areas and the maintenance yard. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 415,000 square feet of asphalt area was used to generate this estimate. | THREE LAKES VALLEY CONSERVATION CAMP | 9967 | Correct | TLVCC |  | Indian Springs |  |  | 2013-05-01 | Four to Ten Years | Long-Term Needs | 3 | 249000
3088INT1 | INTERIOR FINISHES | 3088 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HOUSING UNIT A1 | 9967 | Correct | TLVCC |  | Indian Springs | 2010 | 26767 | 2013-05-01 | Four to Ten Years | Long-Term Needs | 3 | 133835
3089INT1 | INTERIOR FINISHES | 3089 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HOUSING UNIT A2 | 9967 | Correct | TLVCC |  | Indian Springs | 2010 | 26767 | 2013-05-01 | Four to Ten Years | Long-Term Needs | 3 | 133835
3088EXT1 | EXTERIOR FINISHES | 3088 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT A1 | 9967 | Correct | TLVCC |  | Indian Springs | 2010 | 26767 | 2013-05-01 | Four to Ten Years | Long-Term Needs | 3 | 133835
3092INT1 | INTERIOR FINISHES | 3092 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | INMATE PROGRAMS D | 9967 | Correct | TLVCC |  | Indian Springs | 2010 | 10838 | 2013-05-01 | Four to Ten Years | Long-Term Needs | 3 | 54190
3093INT1 | INTERIOR FINISHES | 3093 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | NDF OFFICE/SHOP E | 9967 | Correct | Forestry |  | Indian Springs | 2010 | 14685 | 2013-05-01 | Four to Ten Years | Long-Term Needs | 3 | 73425
2560INT1 | INTERIOR FINISHES | 2560 | The interior finishes are in fair condition. It is recommended that the interior walls, ceilings, doors, frames, steel stairs and exposed steel framing be painted at least once in the next two to three years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | RESIDENTIAL BUILDING B | 9875 | Correct |  |  | Las Vegas | 2005 | 30484 | 2013-05-02 | Four to Ten Years | Long-Term Needs | 3 | 132540
2559PLM1 | INSTALL WATER HEATERS | 2559 | There are two gas fired water heaters that are approaching the end of their useful life and should be scheduled for replacement. This project would provide for the purchase and installation of two gas fired water heaters including required connections to existing utilities. Removal and disposal of the existing equipment is included in this estimate. | ADMINISTRATION BUILDING A | 9875 | Correct |  |  | Las Vegas | 2005 | 26598 | 2013-05-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5200
2559CUL1 | REPLACE STEAM KETTLE | 2559 | The existing steam kettle in the culinary is no longer in service. The unit has failed and is in need of replacement. This project would provide for a new gas fired tilting steam kettle to be purchased and installed. | ADMINISTRATION BUILDING A | 9875 | Correct |  |  | Las Vegas | 2005 | 26598 | 2013-05-02 | Immediate to Two Years | Currently Critical | 1 | 16000
2559INT1 | INTERIOR FINISHES | 2559 | The interior finishes are in fair condition. It is recommended that the interior walls, ceilings, doors, frames, steel stairs and exposed steel framing be painted at least once in the next two to three years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | ADMINISTRATION BUILDING A | 9875 | Correct |  |  | Las Vegas | 2005 | 26598 | 2013-05-02 | Four to Ten Years | Long-Term Needs | 3 | 143965
2560ADA1 | ADA MODIFICATIONS | 2560 | The restrooms in the building are not 100% ADA compliant. This project would provide for improvements including but not limited to flush valve relocation and ADA compliant shower seat and fixture installation in the restrooms. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | RESIDENTIAL BUILDING B | 9875 | Correct |  |  | Las Vegas | 2005 | 30484 | 2013-05-02 | Immediate to Two Years | Currently Critical | 1 | 1500
2561EXT1 | EXTERIOR FINISHES | 2561 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | RESIDENTIAL BUILDING C | 9875 | Correct |  |  | Las Vegas | 2005 | 30484 | 2013-05-02 | Four to Ten Years | Long-Term Needs | 3 | 132540
2561PLM1 | INSTALL WATER HEATERS | 2561 | There are two gas fired water heaters that are approaching the end of their useful life and should be scheduled for replacement. This project would provide for the purchase and installation of two gas fired water heaters including required connections to existing utilities. Removal and disposal of the existing equipment is included in this estimate. | RESIDENTIAL BUILDING C | 9875 | Correct |  |  | Las Vegas | 2005 | 30484 | 2013-05-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5200
2561INT1 | INTERIOR FINISHES | 2561 | The interior finishes are in fair condition. It is recommended that the interior walls, ceilings, doors, frames, steel stairs and exposed steel framing be painted at least once in the next two to three years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | RESIDENTIAL BUILDING C | 9875 | Correct |  |  | Las Vegas | 2005 | 30484 | 2013-05-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 132540
2559EXT1 | EXTERIOR FINISHES | 2559 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | ADMINISTRATION BUILDING A | 9875 | Correct |  |  | Las Vegas | 2005 | 26598 | 2013-05-02 | Four to Ten Years | Long-Term Needs | 3 | 143965
2561ADA1 | ADA MODIFICATIONS | 2561 | The restrooms in the building are not 100% ADA compliant. This project would provide for improvements including but not limited to flush valve relocation and ADA compliant shower seat and fixture installation in the restrooms. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | RESIDENTIAL BUILDING C | 9875 | Correct |  |  | Las Vegas | 2005 | 30484 | 2013-05-02 | Immediate to Two Years | Currently Critical | 1 | 1500
2560PLM1 | INSTALL WATER HEATERS | 2560 | There are two gas fired water heaters that are approaching the end of their useful life and should be scheduled for replacement. This project would provide for the purchase and installation of two gas fired water heaters including required connections to existing utilities. Removal and disposal of the existing equipment is included in this estimate. | RESIDENTIAL BUILDING B | 9875 | Correct |  |  | Las Vegas | 2005 | 30484 | 2013-05-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5200
2560EXT1 | EXTERIOR FINISHES | 2560 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | RESIDENTIAL BUILDING B | 9875 | Correct |  |  | Las Vegas | 2005 | 30484 | 2013-05-02 | Four to Ten Years | Long-Term Needs | 3 | 132540
9875SIT1 | CRACK FILL / SEAL ASPHALT PAVING | 9875 | The existing asphalt concrete paving on site is in good condition. This project would provide for crack filling as needed and sealing and striping the pavement in the next three to four years including striping all loading zones and ADA accessible parking spaces and route of travel. This project should be completed on a cyclical basis based on environmental conditions and use. | CASA GRANDE TRANSITIONAL CENTER SITE | 9875 | Correct |  |  | Las Vegas | 2005 |  | 2013-05-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 58242
9875ADA2 | ADA ROUTE OF TRAVEL | 9875 | The ADA accessible route of travel at the west parking area ADA parking spaces has a non compliant step or change in elevation from the paving to the sidewalk. This project would provide for necessary repairs to be made to eliminate the step. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | CASA GRANDE TRANSITIONAL CENTER SITE | 9875 | Correct |  |  | Las Vegas | 2005 |  | 2013-05-02 | Immediate to Two Years | Currently Critical | 1 | 500
9875ADA1 | ADA PARKING SIGNAGE | 9875 | The existing ADA accessible parking signage is not up to current standards. This project would provide for new stickers reflecting the most current maximum fine information to be installed on the existing signs. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | CASA GRANDE TRANSITIONAL CENTER SITE | 9875 | Correct |  |  | Las Vegas | 2005 |  | 2013-05-02 | Immediate to Two Years | Currently Critical | 1 | 450
1580ELE1 | LIGHTING UPGRADE | 1580 | Existing building lighting fixtures, T-12s, are older fluorescent types and not energy efficient. This project will upgrade lighting fixtures to T-8 lamps with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. This project or a portion there of was previously recommended in the FCA report dated 09/19/2000 and 9/29/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date 09/17/2013. | CCC MULTI-PURPOSE BUILDING | 9973 | Correct | CCC |  | Carlin | 1990 | 7000 | 2013-09-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10500
1580EXT2 | EXTERIOR FINISHES | 1580 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, metal siding repairs, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | CCC MULTI-PURPOSE BUILDING | 9973 | Correct | CCC |  | Carlin | 1990 | 7000 | 2013-09-17 | Four to Ten Years | Long-Term Needs | 3 | 7000
1580SFT1 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 1580 | The existing exit signs in this building are non-illuminated or the older type style and should be replaced with new self-illuminated or LED style signs with a battery-backup. Emergency exit lighting should be installed and/or replaced to provide illumination along the egress route. This project would provide for 3 emergency lights and three exit signs including required electrical connections and installation. This project or a portion there of was previously recommended in the FCA report dated 09/19/2000 and 9/29/2005. It has been amended accordingly to reflect conditions observed during the recent survey date of 9/17/2013. | CCC MULTI-PURPOSE BUILDING | 9973 | Correct | CCC |  | Carlin | 1990 | 7000 | 2013-09-17 | Immediate to Two Years | Currently Critical | 1 | 1600
1580SEC1 | EXTERIOR DOOR REPLACEMENT | 1580 | The two existing exterior doors, frames and locks appear to be original to the building. They are showing signs of wear and deterioration from constant use and abuse. The frames are damaged as well as the hinges. Because of security concerns and the condition of the doors, this project would provide funding to replace the doors, frames, locks and hardware including paint. This project or a portion there of was previously recommended in the FCA report dated 09/19/2000 and 9/29/2005. It has been amended accordingly to reflect conditions observed during the recent survey date of 9/17/2013. | CCC MULTI-PURPOSE BUILDING | 9973 | Correct | CCC |  | Carlin | 1990 | 7000 | 2013-09-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7000
1580ENR2 | WINDOW REPLACEMENT | 1580 | There are three small old single pane window units that should be scheduled for replacement. This project would provide for the installation of three new insulated window units. Removal and disposal of the old units is included in this estimate. | CCC MULTI-PURPOSE BUILDING | 9973 | Correct | CCC |  | Carlin | 1990 | 7000 | 2013-09-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2400
1580ADA2 | SIGNAGE FOR ADA COMPLIANCE | 1580 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. This project would provide funding for the purchase and installation of new signage to meet the criteria for ADA. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 09/19/2000 and 9/29/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 9/17/2013. | CCC MULTI-PURPOSE BUILDING | 9973 | Correct | CCC |  | Carlin | 1990 | 7000 | 2013-09-17 | Immediate to Two Years | Currently Critical | 1 | 3750
1580ADA1 | ADA RESTROOM REMODEL | 1580 | Two restrooms are present in this building. They do not meet the Americans with Disabilities Act (ADA) regulations. This project would provide funding for remodeling one of the restrooms into a unisex restroom for ADA compliance. These items may include new sinks, toilets, urinals, partitions, hardware, mirrors, fixtures, accessible showers, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 09/19/2000 and 9/29/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 9/17/2013. | CCC MULTI-PURPOSE BUILDING | 9973 | Correct | CCC |  | Carlin | 1990 | 7000 | 2013-09-17 | Immediate to Two Years | Currently Critical | 1 | 15000
1580STR1 | STRUCTURAL ASSESSMENT | 1580 | An upper level storage mezzanine has been constructed inside of the multi-purpose building. The 2012 IBC has a minimum requirement of 125 p.s.f. for light storage in non-residential spaces. There is no record of a CIP project or structural plans for this construction and could be a potential safety issue due to collapse. This project recommends that a licensed engineer perform a structural investigation to assess the load carrying capacity of this area. Future projects would be based on this report. This project or a portion there of was previously recommended in the FCA report dated 9/29/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 9/17/2013. | CCC MULTI-PURPOSE BUILDING | 9973 | Correct | CCC |  | Carlin | 1990 | 7000 | 2013-09-17 | Immediate to Two Years | Currently Critical | 1 | 2500
1580HVA1 | EVAPORATIVE COOLER REPLACEMENT | 1580 | The building has a side discharge evaporative cooler. The cooler is beginning to rust and alkaline has scaled the unit to the point of plugging up the fins. This project would provide funding for the purchase and installation of a new side discharge evaporative cooler. This project or a portion there of was previously recommended in the FCA report dated 9/29/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 9/17/2013. | CCC MULTI-PURPOSE BUILDING | 9973 | Correct | CCC |  | Carlin | 1990 | 7000 | 2013-09-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
1580ELE2 | MINOR ELECTRICAL REPAIRS | 1580 | The building has numerous electrical outlets and switches which are missing covers or broken, have extension cords being used to supply electrical power, and no GFCI outlets. This project would provide for repairs and/or replacement by a licensed contractor to repair and/or replace the damaged electrical outlets, switches, covers and conduit. This project or a portion there of was previously recommended in the FCA report dated 9/29/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date 09/17/2013. | CCC MULTI-PURPOSE BUILDING | 9973 | Correct | CCC |  | Carlin | 1990 | 7000 | 2013-09-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
1580INT2 | INTERIOR FINISHES | 1580 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | CCC MULTI-PURPOSE BUILDING | 9973 | Correct | CCC |  | Carlin | 1990 | 7000 | 2013-09-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 28000
1580EXT1 | OVERHEAD DOOR REPLACEMENT | 1580 | The existing 10’x16’ sectional overhead door is damaged from abuse and is original to the building. It has holes, bent panels, and no longer operates properly. This project would provide funding for removal and disposal of the old overhead door and the purchase and installation of a new insulated sectional overhead door with a motor, including connections to utilities as required. This project or a portion there of was previously recommended in the FCA report dated 09/19/2000 and 9/29/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date 09/17/2013. | CCC MULTI-PURPOSE BUILDING | 9973 | Correct | CCC |  | Carlin | 1990 | 7000 | 2013-09-17 | Immediate to Two Years | Currently Critical | 1 | 15500
2144EXT1 | EXTERIOR FINISHES | 2144 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | CCC WELL PUMP HOUSE | 9973 | Correct | CCC |  | Carlin | 1988 | 98 | 2013-09-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
2146EXT1 | EXTERIOR FINISHES | 2146 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | CCC STORAGE SHED | 9973 | Correct | CCC |  | Carlin | 1988 | 100 | 2013-09-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
2145EXT2 | EXTERIOR FINISHES | 2145 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | CCC GATEHOUSE | 9973 | Correct | CCC |  | Carlin | 1988 | 48 | 2013-09-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
9973SFT1 | PORTABLE FIRE EXTINGUISHERS | 9973 | Several of the buildings do not have fire extinguishers. Portable fire extinguishers shall be provided for employee use and selected and distributed based on the classes of anticipated workplace fires and on the size and degree of hazard which would affect their use. On Class A fires, the placement of extinguishers shall be located so that the travel distance for employees to any extinguisher is 75 feet or less and on Class B fires, placement of extinguishers shall be located so that the travel distance for employees to any extinguisher is 50 feet or less. Reference OSHA 1910.157(d). This project would provide funding for the purchase of 10 fire extinguishers, cabinets, and the hardware necessary to install them. This project or a portion there of was previously recommended in the FCA report dated 09/19/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/17/2013. | CARLIN CONSERVATION CAMP SITE | 9973 | Correct | CCC |  | Carlin | 1988 |  | 2013-09-17 | Immediate to Two Years | Currently Critical | 1 | 5000
9973SIT2 | BUILDING SIGNAGE | 9973 | The site contains several different buildings with no signage to identify the contents or use. Some of the buildings contain paint, propane tanks and other possible flammable items. In case of an emergency the buildings should be labeled. This project would provide funding for signage to be installed on all the buildings. This project or a portion there of was previously recommended in the FCA report dated 09/19/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/17/2013. | CARLIN CONSERVATION CAMP SITE | 9973 | Correct | CCC |  | Carlin | 1988 |  | 2013-09-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
9973SEC1 | INSTALL POLE LIGHTING AROUND PARKING LOT | 9973 | The entrance road and parking area have insufficient lighting. Considering the environment of the site, this area needs to be well lighted. This project would provide funding for purchase and installation of 12 additional 30 foot tall light poles including 30" diameter raised concrete bases, electrical trenching, conduit, wiring and connections to existing utilities. LED Light fixtures should be considered for energy savings. The poles should match the existing light poles surrounding the site. This project or a portion there of was previously recommended in the FCA report dated 09/19/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/17/2013. | CARLIN CONSERVATION CAMP SITE | 9973 | Correct | CCC |  | Carlin | 1988 |  | 2013-09-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 108000
9973SIT4 | CRACK FILL AND SEAL ASPHALT PAVING | 9973 | The existing paved area around the site is in fair condition. This project recommends filling in the minor cracks, applying a slurry seal and re-striping the parking area and entrance road in the next two to three years. This project or a portion there of was previously recommended in the FCA report dated 09/29/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/17/2013. | CARLIN CONSERVATION CAMP SITE | 9973 | Correct | CCC |  | Carlin | 1988 |  | 2013-09-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0697EXT4 | EXTERIOR FINISHES | 0697 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | CCC HOUSING UNIT | 9973 | Correct | CCC |  | Carlin | 1988 | 13477 | 2013-09-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 67385
0697HVA4 | BOILER REPLACEMENT | 0697 | There are two gas fired boilers that are original to the housing unit and are reaching the end of their expected life. This project would provide for 2 new gas fired boilers to be installed. Removal of the old boilers and connection to existing utilities is also included in this estimate. | CCC HOUSING UNIT | 9973 | Correct | CCC |  | Carlin | 1988 | 13477 | 2013-09-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16000
0697SFT3 | HANDRAIL INSTALLATION | 0697 | There are two exterior sets of stairs which are lacking handrails. The 2012 IBC Chapter 10, Section 1012 outlines the requirements for handrails. This project would provide for the installation of handrails on each side of the exterior stairs an two locations. | CCC HOUSING UNIT | 9973 | Correct | CCC |  | Carlin | 1988 | 13477 | 2013-09-17 | Immediate to Two Years | Currently Critical | 1 | 1100
0697SEC1 | EXTERIOR DOOR REPLACEMENT | 0697 | The existing exterior doors and locks appear to be original to the building. They are showing signs of wear and deterioration from constant use and abuse. The frames are damaged as well as the hinges. Because of security concerns and the door's condition, this project would provide funding to replace the door, frame, locks and hardware, typical of 8. This project or a portion there of was previously recommended in the FCA report dated 09/19/2000 and 9/29/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/17/2013. | CCC HOUSING UNIT | 9973 | Correct | CCC |  | Carlin | 1988 | 13477 | 2013-09-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 32000
0697SFT1 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0697 | This building does not have an automatic fire suppression system. This building has more than 12,000 square feet on the first floor. NAC 477.917 indicates every existing building owned by the State of Nevada must: (a) Comply with the provisions of NRS 477.100 to 477.170, inclusive; (b) Meet the requirements of the building code in effect when the building was constructed; (c) If the building: (1) Is designated as a B occupancy; (2) Regardless of occupancy designation, has a floor area which exceeds 12,000 square feet on any floor or 24,000 square feet on all floors, including any mezzanines; or (3) Is an R-1, R-2 or R-4 occupancy be scheduled for installation of an automatic fire suppression system during the next remodeling of or addition to the building; This project or a portion there of was previously recommended in the FCA report dated 09/19/2000 and 9/29/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/17/2013. | CCC HOUSING UNIT | 9973 | Correct | CCC |  | Carlin | 1988 | 13477 | 2013-09-17 | Immediate to Two Years | Currently Critical | 1 | 94339
0697HVA3 | SHOWER EXHAUST FAN REPLACEMENT | 0697 | Many of the exhaust fans in the restrooms and shower area were damaged, missing covers and inoperative. This project would provide for the removal of the existing exhaust fan assembly and the purchase and installation of 6 exhaust fan assemblies including ducting and connections to utilities. Due to excessive humidity concerns, high volume commercial units should be installed. This project there of was previously recommended in the FAC report dated 09/19/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/17/2013. | CCC HOUSING UNIT | 9973 | Correct | CCC |  | Carlin | 1988 | 13477 | 2013-09-17 | Four to Ten Years | Long-Term Needs | 3 | 4800
0697HVA1 | ROOF-MOUNTED EVAPORATIVE COOLER REPLACEMENT | 0697 | There are 7 evaporative coolers installed on the roof of this building. It appears that they have reached the end of their useful life. It is recommended that the evaporative coolers be replaced. Connection to the existing utilities is included in this estimate This project or a portion there of was previously recommended in the FCA report dated 09/19/2000 and 9/29/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/17/2013. | CCC HOUSING UNIT | 9973 | Correct | CCC |  | Carlin | 1988 | 13477 | 2013-09-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 21000
0697INT2 | INTERIOR FINISHES | 0697 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | CCC HOUSING UNIT | 9973 | Correct | CCC |  | Carlin | 1988 | 13477 | 2013-09-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 67385
0697ADA2 | SIGNAGE FOR ADA COMPLIANCE | 0697 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with these criteria. This project would provide funding for the purchase and installation of new signage to meet the criteria for ADA. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 09/19/2000 and 9/29/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 9/17/2013. | CCC HOUSING UNIT | 9973 | Correct | CCC |  | Carlin | 1988 | 13477 | 2013-09-17 | Immediate to Two Years | Currently Critical | 1 | 3500
0697ADA1 | ADA RESTROOM REMODEL | 0697 | Restrooms are present in this building. They do not meet the Americans with Disabilities Act (ADA) regulations. This project would provide funding for remodeling one of the restrooms for ADA compliance. These items may include new sinks, toilets, urinals, partitions, hardware, mirrors, fixtures, accessible showers, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 09/19/2000 and 9/29/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 9/17/2013. | CCC HOUSING UNIT | 9973 | Correct | CCC |  | Carlin | 1988 | 13477 | 2013-09-17 | Immediate to Two Years | Currently Critical | 1 | 40000
0697INT1 | REPLACE FLOORING | 0697 | The flooring in this building consists of carpet in the living and office areas, VCT (vinyl composite tile) in the corridors and bathrooms, and ceramic tile in the culinary area. These floor finishes are reaching the end of their useful life. The tile in the culinary has numerous areas missing tiles It is recommended that the flooring in the building be replaced. This project or a portion there of was previously recommended in the FAC report dated 09/19/2000 and 9/29/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/17/2013. | CCC HOUSING UNIT | 9973 | Correct | CCC |  | Carlin | 1988 | 13477 | 2013-09-17 | Immediate to Two Years | Currently Critical | 1 | 161724
1898SFT3 | STAIR REPLACEMENT | 1898 | The three sets of stairs and handrails between the first floor and the second floor do not meet the requirements in the 2012 International Building Code sections 1009 and 1012. The stairs do not have the correct rise and run, one stairway is less than 44" wide and they are either missing handrails altogether or have handrails that do not meet code. This project would provide funding to remove and replace the stairways and handrails. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | MPR/VISITATION/NDF SHOP | 9892 | Correct | JCC | Forestry | Jean | 1987 | 9100 | 2014-01-30 | Immediate to Two Years | Currently Critical | 1 | 15000
1898PLM1 | WATER HEATER REPLACEMENT | 1898 | There is a 40 gallon propane-fired water heater in the MPR and a 15 gallon electric water heater in the NDF Shop. The average life span of a water heater is eight to ten years. With the passage of time and constant use, these units are showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that two new water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | MPR/VISITATION/NDF SHOP | 9892 | Correct | JCC | Forestry | Jean | 1987 | 9100 | 2014-01-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
1898HVA2 | HVAC EQUIPMENT REPLACEMENT | 1898 | Some of the HVAC equipment servicing the building has recently been upgraded. This project addresses the remaining work to be done. The chapel, restrooms and second floor education rooms are heated by electric baseboard heaters and cooled by window mounted evaporative coolers. The NDF shops have older ceiling mounted heaters and roof mounted evaporative coolers. They are not energy efficient and have reached the end of their expected and useful life. The new equipment shall be designed to significantly reduce electrical and natural gas usage in order to comply with the 2009 IECC and ASHRAE 90.1 and to reduce utility costs. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | MPR/VISITATION/NDF SHOP | 9892 | Correct | JCC | Forestry | Jean | 1987 | 9100 | 2014-01-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35000
1898EXT4 | WINDOW REPLACEMENT | 1898 | The windows are original, dual pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 8 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | MPR/VISITATION/NDF SHOP | 9892 | Correct | JCC | Forestry | Jean | 1987 | 9100 | 2014-01-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
1898ADA3 | ADA SIGNAGE | 1898 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | MPR/VISITATION/NDF SHOP | 9892 | Correct | JCC | Forestry | Jean | 1987 | 9100 | 2014-01-30 | Immediate to Two Years | Currently Critical | 1 | 750
1898EXT5 | EXTERIOR DOOR REPLACEMENT | 1898 | The exterior metal doors are damaged from age, abuse and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the 5 exterior metal man-doors, frames and hardware. Removal and disposal of the existing doors is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | MPR/VISITATION/NDF SHOP | 9892 | Correct | JCC | Forestry | Jean | 1987 | 9100 | 2014-01-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
1898EXT3 | EXTERIOR FINISHES | 1898 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is replacing damaged metal panels and caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be repaired in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. It is recommended that the earth to metal siding contact be mitigated to prevent further damage to the metal siding panels. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | MPR/VISITATION/NDF SHOP | 9892 | Correct | JCC | Forestry | Jean | 1987 | 9100 | 2014-01-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 45500
1898ADA2 | ADA RESTROOM UPGRADE | 1898 | The building does not have an accessible restroom. The existing restrooms in the NDF shop, Visitation and Gymnasium do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit of 3 restrooms is necessary. This project would provide funding for construction of three unisex accessible restrooms. These items may include a new sink, toilet, shower, hardware, mirrors, fixtures, flooring and paint in each restroom. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | MPR/VISITATION/NDF SHOP | 9892 | Correct | JCC | Forestry | Jean | 1987 | 9100 | 2014-01-30 | Immediate to Two Years | Currently Critical | 1 | 45000
1898INT2 | FLOORING REPLACEMENT | 1898 | The VCT (vinyl composite tile), sheet vinyl and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the next 2-3 years. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | MPR/VISITATION/NDF SHOP | 9892 | Correct | JCC | Forestry | Jean | 1987 | 9100 | 2014-01-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16000
1898SFT2 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 1898 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | MPR/VISITATION/NDF SHOP | 9892 | Correct | JCC | Forestry | Jean | 1987 | 9100 | 2014-01-30 | Immediate to Two Years | Currently Critical | 1 | 4500
1898INT1 | INTERIOR FINISHES | 1898 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | MPR/VISITATION/NDF SHOP | 9892 | Correct | JCC | Forestry | Jean | 1987 | 9100 | 2014-01-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 45500
1898EXT6 | OVERHEAD DOOR REPLACEMENT | 1898 | There are two 10'x14' overhead coiling doors for the building. One has recently been replaced, the other does not function properly. Exposure and wind have caused the door to bend, crack and lose its finish. It is original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead coiling door and replacement with a new manually operated overhead coiling door. | MPR/VISITATION/NDF SHOP | 9892 | Correct | JCC | Forestry | Jean | 1987 | 9100 | 2014-01-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
1898ELE2 | ELECTRICAL UPGRADE | 1898 | There are numerous instances of broken, outdated and non-code compliant electrical elements in the building. These include exposed wiring on a water heater, broken or missing outlet covers, broken receptacles, and wiring not in proper conduit. Also, this building was constructed before the high demand for electrical services were needed for computers, vehicle repair equipment and other electrical devices. As time has progressed, the buildings electrical demand and system has changed. It is utilized to its current maximum potential. It is recommended the entire system be upgraded for safety and code compliance and to meet the evolving needs of the building including three-phase power. | MPR/VISITATION/NDF SHOP | 9892 | Correct | JCC | Forestry | Jean | 1987 | 9100 | 2014-01-30 | Immediate to Two Years | Currently Critical | 1 | 91000
9892SFT1 | EXTERIOR STAIR / HANDRAIL INSTALLATION | 9892 | The concrete exterior stairs leading from the Visitors parking area to the MPR/ Visitation Building are lacking handrails as required in the 2012 IBC Chapter 10, Section 1012. There is also a stairway constructed with railroad ties which is lacking handrails and is not compliant with current building codes. This project would provide for a tubular steel framed handrail to be installed on both sets of stairs. This project recommends reconstructing the railroad tie stairs to meet current building codes or eliminating them. The construction cost includes handrails and new stairs. This project or a portion thereof was previously recommended in the FCA reports dated 05/03/2005 and 11/03/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | JEAN CONSERVATION CAMP SITE | 9892 | Correct | JCC |  | Jean | 2000 |  | 2014-01-30 | Immediate to Two Years | Currently Critical | 1 | 10000
2004EXT2 | EXTERIOR FINISHES | 2004 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is scraping, priming and painting the painted concrete and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | CENTRAL WAREHOUSE | 9990 | Correct | NNCC |  | Carson City | 1972 | 25298 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 63900
1673INT4 | CABINET AND BREAK ROOM UPGRADES | 1673 | The cabinets and countertops in the building are showing signs of wear and tear and the break rooms are not ADA compliant. The countertops are delaminating and failing particularly at the Formica edges and corners. This condition is prevalent throughout the building including staff desks and 3 staff break rooms. This project recommends the replacement of the existing damaged laminate on the counters and cabinets with heavy duty, quality finishes. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards For Accessible Design should be incorporated into the design such as providing accessible sinks. This project would provide funding for the removal and replacement of the existing materials. This project or a portion thereof was previously recommended in the FCA report dated 04/21/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | REGIONAL MEDICAL FACILITY UNIT 8 | 9990 | Correct | NNCC |  | Carson City | 1993 | 61138 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
1673ENV1 | PEST CONTROL | 1673 | The roof, roof cap flashing, and exterior lights have become a roosting place for birds. The roof and exterior lights are covered in bird droppings. This project would provide for the removal and cleaning of the bird droppings from the above mentioned areas. | REGIONAL MEDICAL FACILITY UNIT 8 | 9990 | Correct | NNCC |  | Carson City | 1993 | 61138 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
2004INT3 | JANITORS CLOSET REPAIRS | 2004 | The mop sink in the Janitors Closet is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | CENTRAL WAREHOUSE | 9990 | Correct | NNCC |  | Carson City | 1972 | 25298 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
2004SFT3 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 2004 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | CENTRAL WAREHOUSE | 9990 | Correct | NNCC |  | Carson City | 1972 | 25298 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 6000
1673INT3 | ACOUSTICAL CEILING TILE REPLACEMENT | 1673 | The existing ceiling is covered by 12"x 12" interlocking acoustical tiles. They do not appear to be a hospital-grade product and many of the tiles are damaged and stained and need to be replaced. There is also a need for a tamper-proof tile in the inmate areas and access panels for HVAC equipment servicing. This project would provide for the replacement of the damaged, staining and missing ceiling tiles and installation of six 12"x12" one- hour rated access panels at HVAC equipment locations. This project or a portion thereof was previously recommended in the FCA report dated 04/21/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | REGIONAL MEDICAL FACILITY UNIT 8 | 9990 | Correct | NNCC |  | Carson City | 1993 | 61138 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35000
2004ELE1 | SERVICE OUTLET INSTALLATION | 2004 | The NEC 2011 Section 210.63 requires a 125-volt, single-phase, 15 or 20 ampere-rated receptacle outlet to be located on the same level and within 25' of an HVAC unit. The rooftop HVAC units do not have a receptacle located near them and neither does the emergency generator. This project would provide funding to install two 125 volt receptacles, one for the HVAC units and the other for the emergency generator. This estimate includes an allowance for 100 feet of conduit and electrical wire. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | CENTRAL WAREHOUSE | 9990 | Correct | NNCC |  | Carson City | 1972 | 25298 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
1673EXT2 | EXTERIOR FINISHES | 1673 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete walls, painting the doors and trim and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/21/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | REGIONAL MEDICAL FACILITY UNIT 8 | 9990 | Correct | NNCC |  | Carson City | 1993 | 61138 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 305690
1673SEC1 | CELL DOOR LOCK REPLACEMENT | 1673 | The existing cell door locks are original to the building. The control panel, paracentric and mogul electric door cylinders are warn, have reached the end of their expected life and have become a security and safety concern for correctional officers. This project would provide for a new electric door control system including cylinders, keys, control panel and all required electrical connections. | REGIONAL MEDICAL FACILITY UNIT 8 | 9990 | Correct | NNCC |  | Carson City | 1993 | 61138 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1300000
2004EXT3 | ROOF REPLACEMENT | 2004 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in the 1980's. It is recommended that the single-ply roof on the older half of the structure of this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. | CENTRAL WAREHOUSE | 9990 | Correct | NNCC |  | Carson City | 1972 | 25298 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 120000
2004ENR1 | LIGHTING UPGRADE | 2004 | The existing lighting fixtures in the refrigerators and freezers are not performing well in the cold temperatures. The T-8 lamps are slow to start, work intermittently and burn out prematurely. This project will upgrade the T-8 lamps to LED's or another fixture appropriate for the cold temperatures. Any electrical wiring upgrades are not included in this estimate. | CENTRAL WAREHOUSE | 9990 | Correct | NNCC |  | Carson City | 1972 | 25298 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
1673HVA1 | BOILER REPLACEMENT | 1673 | The hot water boilers servicing the building were installed more than 20 years ago and should be scheduled for replacement. The life expectancy of these units is 20 to 25 years with proper maintenance and water treatment programs. Replacement parts for performing routine and emergency maintenance are hard to find for this older equipment. The controls and mixing valves should be replaced for the same reasons. This project would provide for the removal and disposal of the existing boilers, controls and mixing valves and replacement with new equipment including all required connections to utilities and equipment. The estimate is based on two 1,145 MBH maximum output hot water boilers and associated equipment. The existing chemical water treatment system will need to be tested and adjusted once equipment is operational. $2,000 is included in this estimate for testing of the chemical water treatment system. | REGIONAL MEDICAL FACILITY UNIT 8 | 9990 | Correct | NNCC |  | Carson City | 1993 | 61138 | 2014-05-01 | Four to Ten Years | Long-Term Needs | 3 | 300000
2005LGT1 | ROOF REPLACEMENT | 2005 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | INMATE CLOTHING STORE | 9990 | Correct | NNCC |  | Carson City |  | 400 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4800
2004SFT1 | INTERIOR STAIRWAY REPLACEMENT | 2004 | The wood stairs and handrails in the north side of the original warehouse do not meet the requirements in the 2012 International Building Code sections 1009 and 1012. The landing at the top is not large enough and the handrails are not structurally adequate. This project would provide funding to remove and replace the stairway and handrail. | CENTRAL WAREHOUSE | 9990 | Correct | NNCC |  | Carson City | 1972 | 25298 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 5000
1673INT1 | INTERIOR FINISHES | 1673 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 04/21/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | REGIONAL MEDICAL FACILITY UNIT 8 | 9990 | Correct | NNCC |  | Carson City | 1993 | 61138 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 305690
2004INT2 | INTERIOR FINISHES | 2004 | The interior finishes are in fair condition. Approximately 1/3 of the interior walls are painted. It is recommended to paint the interior walls at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | CENTRAL WAREHOUSE | 9990 | Correct | NNCC |  | Carson City | 1972 | 25298 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 32500
1648INT3 | INTERIOR FINISHES | 1648 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | HOUSING UNIT 7 | 9990 | Correct | NNCC |  | Carson City | 1990 | 44500 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 222500
1648SFT3 | GLAZING REPLACEMENT | 1648 | The 2 control rooms are located on the upper level of each wing. The flooring in these rooms contains structural glass block vision panels of which two are damaged and many are scratched and cloudy. This project would provide for the removal and replacement of 74 8"x8" structural glass blocks to ensure that the guards have clear vision below them. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | HOUSING UNIT 7 | 9990 | Correct | NNCC |  | Carson City | 1990 | 44500 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 37000
1648ADA1 | ADA PROJECTS | 1648 | The existing accessible cells do not meet the Americans with Disabilities Act (ADA) requirements. The sinks have inadequate underside clearances and the mirrors are mounted too high. This project proposes providing new sinks and relocating the mirrors in each of the ADA accessible cells. The bank of phones does not have an accessible installation and is not equipped with hearing assisted equipment. This project provides an adaptive phone on each side of the housing unit. ADA requirements states that a threshold at an entrance door will not exceed 1/2 inch in height. The thresholds at the entrances to this building are about 1-1/4 inches high. It is recommended that a new accessible threshold and a door shoe be installed. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards For Accessible Design This project or a portion there of was previously recommended in the FCA report dated 03/30/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | HOUSING UNIT 7 | 9990 | Correct | NNCC |  | Carson City | 1990 | 44500 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 50000
1648SFT2 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 1648 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | HOUSING UNIT 7 | 9990 | Correct | NNCC |  | Carson City | 1990 | 44500 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 6000
1648PLM1 | PLUMBING UPGRADES | 1648 | This building has a hose bib in each of the plumbing chases serving a pair of toilets on each floor. None of these hose bibs are equipped with a backflow prevention device. Additionally, every other plumbing chase has a floor drain in case the inmates clog the toilets and flood the cells. The existing drip-type trap primers have been extremely problematic, requiring frequent service and replacement. Without a functioning primer, the trap seal can dry out, permitting sewer gases to back into the building. This project addresses the installation of backflow prevention devices for each of the hose bibs and a flush-action trap primer for each of the floor drains. The flush action primers are activated each time the toilets are flushed. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | HOUSING UNIT 7 | 9990 | Correct | NNCC |  | Carson City | 1990 | 44500 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
1648HVA1 | HVAC EQUIPMENT REPLACEMENT | 1648 | The existing HVAC system consists of 4 unit heaters and window mounted evaporative coolers. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of 4 new HVAC units, ductwork and piping modifications, chemical treatment, temperature control modifications, testing, balancing and commissioning. This project is recommended under CIP 13-M17. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | HOUSING UNIT 7 | 9990 | Correct | NNCC |  | Carson City | 1990 | 44500 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 450000
2005INT2 | INTERIOR FINISHES | 2005 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 4-5 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. | INMATE CLOTHING STORE | 9990 | Correct | NNCC |  | Carson City |  | 400 | 2014-05-01 | Four to Ten Years | Long-Term Needs | 3 | 2000
2004PLM1 | WATER HEATER REPLACEMENT | 2004 | There is a 20 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed for more efficient use of energy. This estimate includes: 100 feet of gas pipe, fittings, couplers, and labor for installation. Removal and disposal of the existing equipment is included in this estimate. | CENTRAL WAREHOUSE | 9990 | Correct | NNCC |  | Carson City | 1972 | 25298 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3750
2005EXT2 | EXTERIOR FINISHES | 2005 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | INMATE CLOTHING STORE | 9990 | Correct | NNCC |  | Carson City |  | 400 | 2014-05-01 | Four to Ten Years | Long-Term Needs | 3 | 2000
2006EXT2 | ROOF REPLACEMENT | 2006 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. | BIKE STORAGE BUILDING | 9990 | Correct | NNCC |  | Carson City | 1963 | 384 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4608
2006EXT1 | EXTERIOR FINISHES | 2006 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | BIKE STORAGE BUILDING | 9990 | Correct | NNCC |  | Carson City | 1963 | 384 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1920
2005EXT3 | WINDOW REPLACEMENT | 2005 | The windows are original, single pane construction in a wooden frame. These older windows are drafty, not energy efficient and the wooden frames have deteriorated significantly. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 2 units including wooden frames. Removal and disposal of the existing windows is included in this estimate. | INMATE CLOTHING STORE | 9990 | Correct | NNCC |  | Carson City |  | 400 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
2005EXT4 | EXTERIOR DOOR REPLACEMENT | 2005 | The 2 exterior wood man doors appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement of the wood doors with new metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | INMATE CLOTHING STORE | 9990 | Correct | NNCC |  | Carson City |  | 400 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
2004HVA1 | HVAC EQUIPMENT REPLACEMENT | 2004 | The existing HVAC system consists of 2 roof mounted evaporative coolers and an original oil fired boiler. They are not energy efficient and have reached the end of their expected and useful life. The cooling is insufficient and does not provide a comfortable work environment in the summer. This project would provide for installation of new HVAC packaged units and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | CENTRAL WAREHOUSE | 9990 | Correct | NNCC |  | Carson City | 1972 | 25298 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 127800
2004EXT4 | OVERHEAD DOOR REPLACEMENT | 2004 | There are two 10'x10' overhead coiling doors in the original portion of the warehouse. One of them has been replaced, the other has not and is damaged and does not function properly. Exposure and wind have caused the door to bend, crack and lose its finish. It is original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the motorized overhead coiling door and replacement with a new motorized overhead coiling door including remote operation, safety controls and connection to existing utilities. | CENTRAL WAREHOUSE | 9990 | Correct | NNCC |  | Carson City | 1972 | 25298 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
1648EXT3 | EXTERIOR FINISHES | 1648 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete walls, painting the doors and trim and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | HOUSING UNIT 7 | 9990 | Correct | NNCC |  | Carson City | 1990 | 44500 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 89000
1436EXT3 | ROOF REPLACEMENT | 1436 | The roof on this building was in fair to poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The current roofing system was installed in 1993 and is now 21 years old. The roof warranty for this roof expired on 9-27-2009. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program. | EDUCATION | 9990 | Correct | NNCC |  | Carson City | 1963 | 7670 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 95640
1436HVA1 | HVAC EQUIPMENT REPLACEMENT | 1436 | The existing HVAC system consists of 8 rooftop evaporative coolers and several air handlers connected to the sitewide hot water loop. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of new HVAC units, ductwork and piping modifications, chemical treatment, temperature control modifications, testing, balancing and commissioning. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | EDUCATION | 9990 | Correct | NNCC |  | Carson City | 1963 | 7670 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 115050
1436ELE2 | ELECTRICAL UPGRADE | 1436 | This building was constructed before the high demand for electrical services were needed for maintenance equipment, computers and other electrical devices. As time has progressed, the buildings electrical demand and system has changed. It is utilized to its current maximum potential. The electrical panels and receptacles are at their limit. It is recommended the entire system be upgraded to meet the evolving needs of the building including three-phase power. | EDUCATION | 9990 | Correct | NNCC |  | Carson City | 1963 | 7670 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 115050
1436INT4 | INTERIOR FINISHES | 1436 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | EDUCATION | 9990 | Correct | NNCC |  | Carson City | 1963 | 7670 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 38350
1436ADA1 | ADA RESTROOM UPGRADE | 1436 | The building does not have an accessible restroom. The existing restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for remodeling the staff restroom and the inmate restroom into ADA compliant restrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | EDUCATION | 9990 | Correct | NNCC |  | Carson City | 1963 | 7670 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 50000
1436EXT2 | EXTERIOR FINISHES | 1436 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the stucco and concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 5-6 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | EDUCATION | 9990 | Correct | NNCC |  | Carson City | 1963 | 7670 | 2014-05-01 | Four to Ten Years | Long-Term Needs | 3 | 38350
1436INT1 | CEILING TILE REPLACEMENT | 1436 | The ceiling in the building is covered with acoustical ceiling tiles. The ceiling tiles are damaged and stained and some are coming loose from the substrate. This project would provide for the replacement of the ceiling tiles. Removal and disposal of the existing tiles is included in this estimate. Additional costs would be required if there is asbestos in the tiles or adhesive. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | EDUCATION | 9990 | Correct | NNCC |  | Carson City | 1963 | 7670 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 38350
1436ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 1436 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | EDUCATION | 9990 | Correct | NNCC |  | Carson City | 1963 | 7670 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 4000
1436INT2 | FLOORING REPLACEMENT | 1436 | The VCT (vinyl composite tile) and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the next 2-3 years. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | EDUCATION | 9990 | Correct | NNCC |  | Carson City | 1963 | 7670 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 61360
2784EXT1 | EXTERIOR FINISHES | 2784 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | NNCC BIOMASS PLANT | 9990 | Correct | NNCC |  | Carson City | 2006 | 6853 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6853
2785EXT1 | EXTERIOR FINISHES | 2785 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT #10 | 9990 | Correct | NNCC |  | Carson City | 2008 | 23780 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 118900
2785INT1 | INTERIOR FINISHES | 2785 | The interior finishes are in fair condition. About 10% of the interior walls are covered by painted gypsum board. It is recommended to paint the interior walls at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HOUSING UNIT #10 | 9990 | Correct | NNCC |  | Carson City | 2008 | 23780 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12500
2557EXT1 | EXTERIOR FINISHES | 2557 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | MAINTENANCE STORAGE | 9990 | Correct | NNCC |  | Carson City | 2004 | 3000 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
9990ADA2 | ADA PATH OF TRAVEL | 9990 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. A concrete path of travel to the recreation yards and religious group area are necessary to comply with ADA accessibility requirements. This project would provide for concrete walkways from the housing units to the recreation and religious areas to the north. This will require regrading, placement of P.C. concrete, signage and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. 4,000 square feet of concrete was used for this estimate. | NORTHERN NEVADA CORRECTIONAL CENTER SITE | 9990 | Correct | NNCC |  | Carson City | 1963 |  | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 40000
9990ENR1 | HIGH MAST LIGHTING UPGRADE | 9990 | There are 15 high mast security light poles throughout the facility that have 9 security lamps each. The current lamps are an older, less efficient style and should be replaced with LED lamps. This project provides for the purchase and installation of 135 LED lamps for the high mast light poles. The cost includes removal and disposal of the existing lamps. | NORTHERN NEVADA CORRECTIONAL CENTER SITE | 9990 | Correct | NNCC |  | Carson City | 1963 |  | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 270000
9990SIT2 | CRACK FILL & SEAL ASPHALT PAVING | 9990 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the paving site wide including access roads, parking areas, loading docks, exercise yards and the perimeter road. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 600,000 square feet of asphalt area was used to generate this estimate. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | NORTHERN NEVADA CORRECTIONAL CENTER SITE | 9990 | Correct | NNCC |  | Carson City | 1963 |  | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 300000
9990SIT5 | CONCRETE CURB REPLACEMENT | 9990 | The concrete curbing in the parking lot has been damaged and is failing in many areas. There is extensive cracking, crumbling and failure due to vehicles colliding with the curbs. Due to the high traffic volume and high percentage of large commercial vehicles in this parking lot, it is recommended to replace the curbs with a system with a longer lifespan. This project would provide for the installation of concrete curbing with a deeper footing throughout and a high strength concrete mix to ensure a longer life cycle of the new curbing. Removal and disposal of the existing curbing is included in this estimate. This project should be implemented concurrently with the Crack Fill and Seal Asphalt Paving project. | NORTHERN NEVADA CORRECTIONAL CENTER SITE | 9990 | Correct | NNCC |  | Carson City | 1963 |  | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 100000
9990HVA1 | BOILER PLANT AND DISTRIBUTION SYSTEM UPGRADE | 9990 | The hot water and steam boilers and hot water distribution piping has reached the end of its useful life and is due for replacement. The boilers were installed in 1978 and 1982 and are over 30 years old. The life expectancy of these units is 20 to 25 years with proper maintenance and water treatment programs. Replacement parts for performing routine and emergency maintenance are hard to find for this old equipment. This project would provide for the removal and disposal of the existing boilers, controls, piping and valves and replacement with new equipment including all required connections to utilities and equipment. The estimate is based on (4) 5,000 MBH hot water boilers, (2) 100 hp steam boilers, heat exchangers, pumps, 12,500 linear feet of pre-insulated piping and temperature controls. The existing chemical water treatment system will need to be tested and adjusted once equipment is operational. $2,000 is included in this estimate for testing of the chemical water treatment system. Planning for this project is recommended under CIP 15-5289. | NORTHERN NEVADA CORRECTIONAL CENTER SITE | 9990 | Correct | NNCC |  | Carson City | 1963 |  | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5500000
9990SIT6 | DRAINAGE IMPROVEMENTS | 9990 | The site has several areas with inadequate drainage due to deteriorated asphalt, clogged drains or insufficient sloping. The standing water causes premature deterioration of the paving and other site improvements. The grade does not slope properly near the entrance to the Maintenance Building. The drain at the Sally Port cannot handle the large volume of water coming from the parking lot which results in standing water around the Sally Port and Education building. This project would create positive flow away from the Maintenance Building, Education Building and Sally Port by regrading, paving, installing additional drainage swales or storm drains as needed. | NORTHERN NEVADA CORRECTIONAL CENTER SITE | 9990 | Correct | NNCC |  | Carson City | 1963 |  | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
9990PLM1 | ISOLATION VALVE INSTALLATION | 9990 | There are no isolation valves for the individual building's water lines. The main water line that serves each of the buildings on the site is in need of an isolation valve. This will allow the maintenance staff to do repairs and maintenance to the plumbing without shutting down the whole site. More importantly, a leak in the building can be shut down quickly minimizing damage in an emergency. This estimate provides for a 2-1/2" gate valve to be installed at each of 20 separate buildings. | NORTHERN NEVADA CORRECTIONAL CENTER SITE | 9990 | Correct | NNCC |  | Carson City | 1963 |  | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
9990SIT3 | ASPHALT PAVING INSTALLATION | 9990 | The Prison Industries buildings do not have paved access roads around them and the drainage in this area is problematic. The unpaved areas make it difficult to transport materials and supplies between the buildings especially during and after inclement weather. The dirt areas do not provide proper drainage and graded areas are easily damaged by rain, snow and ice which exacerbates the problem. This project would provide asphalt cement paving for a 20' wide access road between and around the Prison Industries buildings. The estimate includes grading, 6" base, compaction and installation of 4" thick asphalt cement paving. | NORTHERN NEVADA CORRECTIONAL CENTER SITE | 9990 | Correct | NNCC |  | Carson City | 1963 |  | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 250000
9990ADA1 | ADA SITE UPGRADES | 9990 | The Command Post/ Operations/ Education building and the Education building are lacking an accessible entrance into the buildings from the yard. The buildings are used by the inmates and staff on a daily basis and are required to have an accessible entrance per the Americans with Disabilities Act (ADA) regulations. This project would provide for an accessible ramp to access the buildings. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | NORTHERN NEVADA CORRECTIONAL CENTER SITE | 9990 | Correct | NNCC |  | Carson City | 1963 |  | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 70000
0137ADA1 | ADA RESTROOM UPGRADE | 0137 | The building does not have an accessible restroom. The existing restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for remodeling the restrooms in the gym and in the classroom hallway into ADA compliant restrooms. These items may include sinks, toilets, showers, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | MULTI-PURPOSE/GYM/CHAPEL | 9990 | Correct | NNCC |  | Carson City | 1968 | 16306 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 90000
0138SEC1 | CELL DOOR LOCK REPLACEMENT | 0138 | The existing cell door locks are original to the building. The control panel, paracentric and mogul electric door cylinders are warn, have reached the end of their expected life and have become a security and safety concern for correctional officers. This project would provide for a new electric door control system including cylinders, keys, control panel and all required electrical connections. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | HOUSING UNIT 1 | 9990 | Correct | NNCC |  | Carson City | 1963 | 21586 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 287500
0138SFT2 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0138 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | HOUSING UNIT 1 | 9990 | Correct | NNCC |  | Carson City | 1963 | 21586 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 10793
0138EXT4 | EXTERIOR FINISHES | 0138 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the stucco and concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 5-6 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT 1 | 9990 | Correct | NNCC |  | Carson City | 1963 | 21586 | 2014-05-01 | Four to Ten Years | Long-Term Needs | 3 | 107930
0138INT2 | INTERIOR FINISHES | 0138 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 4-5 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HOUSING UNIT 1 | 9990 | Correct | NNCC |  | Carson City | 1963 | 21586 | 2014-05-01 | Four to Ten Years | Long-Term Needs | 3 | 107930
0138ENV1 | ROOF CLEANUP | 0138 | The roof on this building was in fair condition at the time of the survey but pigeon debris had built up significantly in certain areas. Pigeon droppings, nests and dead pigeons have built up around the HVAC equipment and roof drains. Due to the potential risk of disease and damage to the building, this project provides for treatment and clean up of the pigeon debris by a licensed pest control business using cleaning materials approved by the roofing manufacturer. Using the proper cleaning agents per the roofing manufacturer should not void the warranty. The roof should be cleaned as soon as possible. | HOUSING UNIT 1 | 9990 | Correct | NNCC |  | Carson City | 1963 | 21586 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 4500
0138EXT5 | ROOF REPLACEMENT | 0138 | The roof on this building was in fair to poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The current roofing system was installed in 1991 and is now 23 years old. The roof warranty for this roof expired on 7-16-2008. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program. | HOUSING UNIT 1 | 9990 | Correct | NNCC |  | Carson City | 1963 | 21586 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 259032
0145STR1 | STRUCTURAL ASSESSMENT | 0145 | The Guard Tower #2 sways substantially during high winds. This project recommends that a licensed engineer perform a structural investigation to assess the swaying of the metal guard tower. Future projects would be based on this report. | GUARD TOWER 2 | 9990 | Correct | NNCC |  | Carson City | 1974 | 75 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 2500
0137ADA3 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0137 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | MULTI-PURPOSE/GYM/CHAPEL | 9990 | Correct | NNCC |  | Carson City | 1968 | 16306 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 4000
0139INT2 | INTERIOR FINISHES | 0139 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 4-5 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HOUSING UNIT 2 | 9990 | Correct | NNCC |  | Carson City | 1963 | 21586 | 2014-05-01 | Four to Ten Years | Long-Term Needs | 3 | 107930
0137INT1 | CEILING TILE REPLACEMENT | 0137 | The ceiling in the Gym portion of this building is covered with acoustical ceiling tiles. The ceiling tiles are damaged and stained and many have fallen off of the substrate. This project would provide for the replacement of the ceiling tiles. Removal and disposal of the existing tiles is included in this estimate. Additional costs would be required if there is asbestos in the tiles or adhesive. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | MULTI-PURPOSE/GYM/CHAPEL | 9990 | Correct | NNCC |  | Carson City | 1968 | 16306 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 50000
0137INT4 | INTERIOR FINISHES | 0137 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 3-4 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | MULTI-PURPOSE/GYM/CHAPEL | 9990 | Correct | NNCC |  | Carson City | 1968 | 16306 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 81530
0137ELE2 | ELECTRICAL UPGRADE | 0137 | This building was constructed before the high demand for electrical services were needed for equipment, computers and other electrical devices. As time has progressed, the buildings electrical demand and system has changed. It is utilized to its current maximum potential. The electrical panels and receptacles are at their limit. It is recommended the entire system be upgraded to meet the evolving needs of the building including three-phase power. | MULTI-PURPOSE/GYM/CHAPEL | 9990 | Correct | NNCC |  | Carson City | 1968 | 16306 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 163060
0137EXT3 | EXTERIOR DOOR REPLACEMENT | 0137 | The existing exterior metal doors and frames appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement and installation of 9 new security grade metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | MULTI-PURPOSE/GYM/CHAPEL | 9990 | Correct | NNCC |  | Carson City | 1968 | 16306 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 36000
0137INT5 | INTERIOR DOOR REPLACEMENT | 0137 | The interior doors are original to the building. Many are damaged, difficult to lock and operate and do not have lever action handles. This project would provide for the removal of the existing doors and the purchase and installation of new metal security grade doors and frames. All hardware and painting is included in this estimate. Hardware to include security keys and fusible locks. This estimate is for 12 doors. | MULTI-PURPOSE/GYM/CHAPEL | 9990 | Correct | NNCC |  | Carson City | 1968 | 16306 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 48000
0137EXT4 | ROOF REPLACEMENT | 0137 | The roof on this building was in fair to poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The current roofing system was installed in 2001 and is now 13 years old. The roof warranty for this roof expired on 2-27-2019. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next 7-8 years to be consistent with the roofing program. | MULTI-PURPOSE/GYM/CHAPEL | 9990 | Correct | NNCC |  | Carson City | 1968 | 16306 | 2014-05-01 | Four to Ten Years | Long-Term Needs | 3 | 195672
0150INT3 | JANITORS CLOSET REPAIRS | 0150 | The mop sink in the Janitors Closet is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | AUTO SHOP | 9990 | Correct | NNCC |  | Carson City | 1974 | 3325 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
0137EXT2 | EXTERIOR FINISHES | 0137 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the stucco and concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 5-6 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | MULTI-PURPOSE/GYM/CHAPEL | 9990 | Correct | NNCC |  | Carson City | 1968 | 16306 | 2014-05-01 | Four to Ten Years | Long-Term Needs | 3 | 81530
0140ENV1 | ROOF CLEANUP | 0140 | The roof on this building was in fair condition at the time of the survey but pigeon debris had built up significantly in certain areas. Pigeon droppings, nests and dead pigeons have built up around the HVAC equipment and roof drains. Due to the potential risk of disease and damage to the building, this project provides for treatment and clean up of the pigeon debris by a licensed pest control business using cleaning materials approved by the roofing manufacturer. Using the proper cleaning agents per the roofing manufacturer should not void the warranty. The roof should be cleaned as soon as possible. | HOUSING UNIT 3 | 9990 | Correct | NNCC |  | Carson City | 1963 | 21586 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 4500
0141SEC1 | CELL DOOR LOCK REPLACEMENT | 0141 | The existing cell door locks are original to the building. The control panel, paracentric and mogul electric door cylinders are warn, have reached the end of their expected life and have become a security and safety concern for correctional officers. This project would provide for a new electric door control system including cylinders, keys, control panel and all required electrical connections. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | HOUSING UNIT 4 | 9990 | Correct | NNCC |  | Carson City | 1974 | 13641 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 287500
0141INT2 | INTERIOR FINISHES | 0141 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 4-5 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HOUSING UNIT 4 | 9990 | Correct | NNCC |  | Carson City | 1974 | 13641 | 2014-05-01 | Four to Ten Years | Long-Term Needs | 3 | 81705
0141SFT2 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0141 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | HOUSING UNIT 4 | 9990 | Correct | NNCC |  | Carson City | 1974 | 13641 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 6821
0141EXT4 | EXTERIOR FINISHES | 0141 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the stucco and concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 5-6 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT 4 | 9990 | Correct | NNCC |  | Carson City | 1974 | 13641 | 2014-05-01 | Four to Ten Years | Long-Term Needs | 3 | 68205
0141EXT3 | EXTERIOR DOOR REPLACEMENT | 0141 | The existing exterior metal doors and frames appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement and installation of 9 new security grade metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | HOUSING UNIT 4 | 9990 | Correct | NNCC |  | Carson City | 1974 | 13641 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 36000
0141EXT2 | WINDOW REPLACEMENT | 0141 | The existing exterior window units are original to the building and are damaged or broken and are not energy efficient. They present a safety and security issue due to their condition. This project would provide for the removal and replacement of the existing exterior window units with new institutional grade safety glazed window units. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | HOUSING UNIT 4 | 9990 | Correct | NNCC |  | Carson City | 1974 | 13641 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 110400
0141ENV1 | ROOF CLEANUP | 0141 | The roof on this building was in fair condition at the time of the survey but pigeon debris had built up significantly in certain areas. Pigeon droppings, nests and dead pigeons have built up around the HVAC equipment and roof drains. Due to the potential risk of disease and damage to the building, this project provides for treatment and clean up of the pigeon debris by a licensed pest control business using cleaning materials approved by the roofing manufacturer. Using the proper cleaning agents per the roofing manufacturer should not void the warranty. The roof should be cleaned as soon as possible. | HOUSING UNIT 4 | 9990 | Correct | NNCC |  | Carson City | 1974 | 13641 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 4500
0139EXT4 | EXTERIOR FINISHES | 0139 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the stucco and concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 5-6 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT 2 | 9990 | Correct | NNCC |  | Carson City | 1963 | 21586 | 2014-05-01 | Four to Ten Years | Long-Term Needs | 3 | 107930
0140EXT4 | EXTERIOR FINISHES | 0140 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the stucco and concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 5-6 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT 3 | 9990 | Correct | NNCC |  | Carson City | 1963 | 21586 | 2014-05-01 | Four to Ten Years | Long-Term Needs | 3 | 107930
0139EXT5 | ROOF REPLACEMENT | 0139 | The roof on this building was in fair to poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The current roofing system was installed in 1991 and is now 23 years old. The roof warranty for this roof expired on 7-16-2008. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program. | HOUSING UNIT 2 | 9990 | Correct | NNCC |  | Carson City | 1963 | 21586 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 259032
0140INT3 | JANITORS CLOSET REPAIRS | 0140 | The ceramic mop sink in the Janitors Closet is cracked and the paint on the CMU surround has peeled off. This project would provide for a new mop sink to be installed and applying an epoxy based paint to the surrounding CMU walls. The epoxy paint shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | HOUSING UNIT 3 | 9990 | Correct | NNCC |  | Carson City | 1963 | 21586 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0140SEC1 | CELL DOOR LOCK REPLACEMENT | 0140 | The existing cell door locks are original to the building. The control panel, paracentric and mogul electric door cylinders are warn, have reached the end of their expected life and have become a security and safety concern for correctional officers. This project would provide for a new electric door control system including cylinders, keys, control panel and all required electrical connections. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | HOUSING UNIT 3 | 9990 | Correct | NNCC |  | Carson City | 1963 | 21586 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 287500
0140INT2 | INTERIOR FINISHES | 0140 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 4-5 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HOUSING UNIT 3 | 9990 | Correct | NNCC |  | Carson City | 1963 | 21586 | 2014-05-01 | Four to Ten Years | Long-Term Needs | 3 | 107930
0139ENV1 | ROOF CLEANUP | 0139 | The roof on this building was in fair condition at the time of the survey but pigeon debris had built up significantly in certain areas. Pigeon droppings, nests and dead pigeons have built up around the HVAC equipment and roof drains. Due to the potential risk of disease and damage to the building, this project provides for treatment and clean up of the pigeon debris by a licensed pest control business using cleaning materials approved by the roofing manufacturer. Using the proper cleaning agents per the roofing manufacturer should not void the warranty. The roof should be cleaned as soon as possible. | HOUSING UNIT 2 | 9990 | Correct | NNCC |  | Carson City | 1963 | 21586 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 4500
0139SEC1 | CELL DOOR LOCK REPLACEMENT | 0139 | The existing cell door locks are original to the building. The control panel, paracentric and mogul electric door cylinders are warn, have reached the end of their expected life and have become a security and safety concern for correctional officers. This project would provide for a new electric door control system including cylinders, keys, control panel and all required electrical connections. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | HOUSING UNIT 2 | 9990 | Correct | NNCC |  | Carson City | 1963 | 21586 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 287500
0139SFT2 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0139 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | HOUSING UNIT 2 | 9990 | Correct | NNCC |  | Carson City | 1963 | 21586 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 10793
0137INT6 | FLOORING REPLACEMENT | 0137 | The various flooring materials in the building are damaged and reaching the end of their useful life. In the Law Library and corridor, the sheet vinyl is due for replacement as well as the carpeted Storage Rooms. The gymnasium floor is due for sanding and refinishing with a polyurethane or similar coating. It is recommended that the sheet vinyl and carpet be replaced and the gymnasium floor refinished. This project would provide for removal and disposal of the sheet vinyl, installation of new 12x12 VCT with a 6" base in its place and refinishing the gymnasium floor in the next 2-3 years. | MULTI-PURPOSE/GYM/CHAPEL | 9990 | Correct | NNCC |  | Carson City | 1968 | 16306 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 130448
0140SFT2 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0140 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | HOUSING UNIT 3 | 9990 | Correct | NNCC |  | Carson City | 1963 | 21586 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 10793
0133INT2 | INTERIOR FINISHES | 0133 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | PRISON INDUSTRY/CANTEEN BUILDING A | 9990 | Correct | NNCC |  | Carson City | 1967 | 17995 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 89975
0137SFT4 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0137 | The building has a floor area greater than 12,000 square feet. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 or R-2 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. | MULTI-PURPOSE/GYM/CHAPEL | 9990 | Correct | NNCC |  | Carson City | 1968 | 16306 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 228284
0133INT3 | JANITORS CLOSET REPAIRS | 0133 | The mop sink in the Janitors Closet is mounted adjacent to gypsum board and are showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | PRISON INDUSTRY/CANTEEN BUILDING A | 9990 | Correct | NNCC |  | Carson City | 1967 | 17995 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
0133ENV1 | DUST COLLECTION SYSTEM REPLACEMENT | 0133 | The existing wood working equipment has partial dust collection capacity. In order to reduce the possibility of damage or injury, each piece of equipment should have complete collection capability. This project will provide for the replacement of several existing systems and installation of additional systems to minimize explosion hazard and disruption to production schedules. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | PRISON INDUSTRY/CANTEEN BUILDING A | 9990 | Correct | NNCC |  | Carson City | 1967 | 17995 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
0133EXT2 | EXTERIOR FINISHES | 0133 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the stucco and concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | PRISON INDUSTRY/CANTEEN BUILDING A | 9990 | Correct | NNCC |  | Carson City | 1967 | 17995 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 89975
0133INT4 | RESTROOM REMODEL | 0133 | The restroom in the Property Room was in overall poor condition at the time of the survey. It was not designed according to the building code. For example, the water closet seat is 34" above the finish floor and the walls and partitions do not fully enclose the restroom. This project would provide for a complete remodel of the restroom fixtures, hardware, doors, walls, floor and wall finishes. The removal and disposal of the existing fixtures and finishes is included in this estimate. | PRISON INDUSTRY/CANTEEN BUILDING A | 9990 | Correct | NNCC |  | Carson City | 1967 | 17995 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 15000
0133EXT5 | ROOF REPLACEMENT | 0133 | The roof on this building was in fair to poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The current roofing system was installed in 1991 and is now 23 years old. The roof warranty for this roof expired on 7-16-2008. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program. | PRISON INDUSTRY/CANTEEN BUILDING A | 9990 | Correct | NNCC |  | Carson City | 1967 | 17995 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 215940
0133EXT4 | EXTERIOR DOOR REPLACEMENT | 0133 | The existing exterior metal doors and frames appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement and installation of 14 new security grade metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | PRISON INDUSTRY/CANTEEN BUILDING A | 9990 | Correct | NNCC |  | Carson City | 1967 | 17995 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 56000
0135SFT1 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0135 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | VISITORS CENTER II | 9990 | Correct | NNCC |  | Carson City | 1974 | 4768 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2300
0133ELE2 | ELECTRICAL UPGRADE | 0133 | This building was constructed before the high demand for electrical services were needed for equipment, computers and other electrical devices. As time has progressed, the buildings electrical demand and system has changed. It is utilized to its current maximum potential. The electrical panels and receptacles are at their limit. It is recommended the entire system be upgraded to meet the evolving needs of the building including three-phase power. | PRISON INDUSTRY/CANTEEN BUILDING A | 9990 | Correct | NNCC |  | Carson City | 1967 | 17995 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 269925
0135INT3 | INTERIOR FINISHES | 0135 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | VISITORS CENTER II | 9990 | Correct | NNCC |  | Carson City | 1974 | 4768 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 23840
0133HVA1 | HVAC EQUIPMENT REPLACEMENT | 0133 | The existing HVAC system consists of 2 large air handlers in the penthouse. They are not energy efficient, insufficient for the spaces and have reached the end of their expected and useful life. This project would provide for installation of new HVAC units, ductwork and piping modifications, chemical treatment, temperature control modifications, testing, balancing and commissioning. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | PRISON INDUSTRY/CANTEEN BUILDING A | 9990 | Correct | NNCC |  | Carson City | 1967 | 17995 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 269925
0133PLM1 | WATER HEATER REPLACEMENT | 0133 | There is a 40 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed for more efficient use of energy. This estimate includes: 100 feet of gas pipe, fittings, couplers, and labor for installation. Removal and disposal of the existing equipment is included in this estimate. | PRISON INDUSTRY/CANTEEN BUILDING A | 9990 | Correct | NNCC |  | Carson City | 1967 | 17995 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3750
0132EXT4 | ROOF REPLACEMENT | 0132 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. | TV DISTRIBUTION BUILDING | 9990 | Correct | NNCC |  | Carson City |  | 196 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2352
0132EXT2 | EXTERIOR FINISHES | 0132 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | TV DISTRIBUTION BUILDING | 9990 | Correct | NNCC |  | Carson City |  | 196 | 2014-05-01 | Four to Ten Years | Long-Term Needs | 3 | 980
0132EXT3 | EXTERIOR DOOR REPLACEMENT | 0132 | The existing exterior metal doors and frames appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement and installation of 2 new security grade metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | TV DISTRIBUTION BUILDING | 9990 | Correct | NNCC |  | Carson City |  | 196 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
0132INT2 | INTERIOR FINISHES | 0132 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 4-5 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | TV DISTRIBUTION BUILDING | 9990 | Correct | NNCC |  | Carson City |  | 196 | 2014-05-01 | Four to Ten Years | Long-Term Needs | 3 | 980
0131EXT5 | EXTERIOR DOOR REPLACEMENT | 0131 | The existing exterior metal doors and frames appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement and installation of 8 new security grade metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | PRISON INDUSTRY BUILDING C | 9990 | Correct | NNCC |  | Carson City | 1974 | 10560 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 32000
0133EXT3 | WINDOWS REPLACEMENT | 0133 | The existing windows in this building are of single pane wire mesh construction. Many are broken and all are not energy efficient. This project would provide for the removal and replacement of the windows with new dual pane security rated window systems. | PRISON INDUSTRY/CANTEEN BUILDING A | 9990 | Correct | NNCC |  | Carson City | 1967 | 17995 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 26400
0136SIT2 | SIDEWALK REPLACEMENT | 0136 | The sidewalks serving the building between the parking lot and the entrances are deteriorated and failing. It is spalling and cracking in all areas and should be scheduled for replacement. This project addresses removal and replacement of existing sidewalks as needed. 1,500 SF of 4" thick concrete sidewalk was used for this estimate. | ADMINISTRATION/VISITING I | 9990 | Correct | NNCC |  | Carson City | 1974 | 9304 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0142EXT4 | ROOF REPLACEMENT | 0142 | The roof on this building was in fair to poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The current roofing system was installed in 1991 and is now 23 years old. The roof warranty for this roof expired on 7-16-2008. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program. | HOUSING UNIT 5 | 9990 | Correct | NNCC |  | Carson City | 1977 | 13641 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 163692
0136EXT4 | WINDOW WALL SYSTEM REPLACEMENT | 0136 | There are six exterior aluminum window wall systems around the building that appear to be original to the building. They are damaged from age and general wear and tear and are a constant maintenance problem. The windows are single pane construction and the metal frames are rusted and damaged. This project would provide for the replacement of 203 linear feet of exterior aluminum window walls including dual pane, thermally broke windows, ADA compliant doors and hardware. Removal and disposal of the existing walls is included in this estimate. | ADMINISTRATION/VISITING I | 9990 | Correct | NNCC |  | Carson City | 1974 | 9304 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 203000
0136INT1 | CEILING SYSTEM REPLACEMENT | 0136 | The majority of the building has a suspended acoustical tile ceiling system. The t-bar framing is old, bent and rusted in many areas and many ceiling tiles are damaged and stained. This project would provide for the replacement of the suspended acoustical tile ceiling system including the framing, acoustical tile and seismic bracing assemblies. Removal and disposal of the existing ceiling system is included in this estimate. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | ADMINISTRATION/VISITING I | 9990 | Correct | NNCC |  | Carson City | 1974 | 9304 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 93040
0136EXT3 | ROOF REPLACEMENT | 0136 | The roof on this building was in fair to poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The current roofing system was installed in 1993 and is now 21 years old. The roof warranty for this roof expired on 9-27-2009. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program. | ADMINISTRATION/VISITING I | 9990 | Correct | NNCC |  | Carson City | 1974 | 9304 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 111648
0136EXT2 | EXTERIOR FINISHES | 0136 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the stucco and concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 5-6 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | ADMINISTRATION/VISITING I | 9990 | Correct | NNCC |  | Carson City | 1974 | 9304 | 2014-05-01 | Four to Ten Years | Long-Term Needs | 3 | 46520
0136INT3 | INTERIOR FINISHES | 0136 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | ADMINISTRATION/VISITING I | 9990 | Correct | NNCC |  | Carson City | 1974 | 9304 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 46520
0136INT4 | CARPET REPLACEMENT | 0136 | The carpet in the Conference Room is showing signs of extreme wear and should be scheduled for replacement. It is recommended that the carpet be replaced with heavy duty commercial grade carpet in the next 2-3 years. | ADMINISTRATION/VISITING I | 9990 | Correct | NNCC |  | Carson City | 1974 | 9304 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2800
0133SFT2 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0133 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | PRISON INDUSTRY/CANTEEN BUILDING A | 9990 | Correct | NNCC |  | Carson City | 1967 | 17995 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 5500
0136INT5 | JANITORS CLOSET REPAIRS | 0136 | The mop sink in the Janitors Closet is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | ADMINISTRATION/VISITING I | 9990 | Correct | NNCC |  | Carson City | 1974 | 9304 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 1400
0150ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0150 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | AUTO SHOP | 9990 | Correct | NNCC |  | Carson City | 1974 | 3325 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 4000
0136ADA3 | BREAK ROOM REMODEL | 0136 | The kitchenette and associated cabinets in the employee break room are original to the building. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and countertops are delaminating and failing. This project recommends the replacement of the existing kitchen countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards For Accessible Design should be incorporated into the design such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. | ADMINISTRATION/VISITING I | 9990 | Correct | NNCC |  | Carson City | 1974 | 9304 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 15000
0135EXT6 | ROOF REPLACEMENT | 0135 | The roof on this building was in fair to poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The current roofing system was installed in 1993 and is now 21 years old. The roof warranty for this roof expired on 9-27-2009. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program. | VISITORS CENTER II | 9990 | Correct | NNCC |  | Carson City | 1974 | 4768 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 57216
0135EXT3 | EXTERIOR FINISHES | 0135 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and storefront systems and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 3-4 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | VISITORS CENTER II | 9990 | Correct | NNCC |  | Carson City | 1974 | 4768 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 23840
0135PLM1 | WATER HEATER REPLACEMENT | 0135 | There is a 20 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed for more efficient use of energy. This estimate includes: 100 feet of gas pipe, fittings, couplers, and labor for installation. Removal and disposal of the existing equipment is included in this estimate. | VISITORS CENTER II | 9990 | Correct | NNCC |  | Carson City | 1974 | 4768 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0135ELE2 | ELECTRICAL UPGRADE | 0135 | This building was constructed before the high demand for electrical services were needed for equipment, computers and other electrical devices. As time has progressed, the buildings electrical demand and system has changed. It is utilized to its current maximum potential. The electrical panels and receptacles are at their limit. It is recommended the entire system be upgraded to meet the evolving needs of the building including three-phase power. | VISITORS CENTER II | 9990 | Correct | NNCC |  | Carson City | 1974 | 4768 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 71520
0135EXT5 | EXTERIOR DOOR REPLACEMENT | 0135 | The existing exterior metal doors and frames appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement and installation of 4 new security grade metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | VISITORS CENTER II | 9990 | Correct | NNCC |  | Carson City | 1974 | 4768 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16000
0135EXT4 | WINDOW WALL SYSTEM REPLACEMENT | 0135 | There are two exterior window wall systems on the north and west exteriors of the building that appear to be original to the building. They are damaged from age and general wear and tear and are a constant maintenance problem. The windows are single pane construction and the metal frames are rusted and damaged. This project would provide for the replacement of 104 linear feet of exterior aluminum window walls including dual pane, thermally broke windows, ADA compliant doors and hardware. Removal and disposal of the existing walls is included in this estimate. | VISITORS CENTER II | 9990 | Correct | NNCC |  | Carson City | 1974 | 4768 | 2014-05-01 | Four to Ten Years | Long-Term Needs | 3 | 104000
0136ELE2 | ELECTRICAL UPGRADE | 0136 | This building was constructed before the high demand for electrical services were needed for equipment, computers and other electrical devices. As time has progressed, the buildings electrical demand and system has changed. It is utilized to its current maximum potential. The electrical panels and receptacles are at their limit. It is recommended the entire system be upgraded to meet the evolving needs of the building including three-phase power. | ADMINISTRATION/VISITING I | 9990 | Correct | NNCC |  | Carson City | 1974 | 9304 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 139560
0146EXT1 | EXTERIOR FINISHES | 0146 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the metal panels, windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | GUARD TOWER 3 | 9990 | Correct | NNCC |  | Carson City | 1990 | 864 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0150EXT4 | EXTERIOR DOOR REPLACEMENT | 0150 | The existing exterior metal doors and frames appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement and installation of 5 new security grade metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | AUTO SHOP | 9990 | Correct | NNCC |  | Carson City | 1974 | 3325 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0147EXT4 | ROOF REPLACEMENT | 0147 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. | GUARD TOWER 4 | 9990 | Correct | NNCC |  | Carson City | 1979 | 75 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 900
0147INT1 | INTERIOR FINISHES | 0147 | The interior finishes are in fair to poor condition. It is recommended to paint the interior walls and ceiling at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | GUARD TOWER 4 | 9990 | Correct | NNCC |  | Carson City | 1979 | 75 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 750
0146INT2 | INTERIOR FINISHES | 0146 | The interior finishes are in fair to poor condition. It is recommended to paint the interior walls and ceiling at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | GUARD TOWER 3 | 9990 | Correct | NNCC |  | Carson City | 1990 | 864 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8640
0146EXT2 | WINDOW REPLACEMENT | 0146 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 7 units. Removal and disposal of the existing windows is included in this estimate. The estimate includes additional costs due to the difficulty of the installation. | GUARD TOWER 3 | 9990 | Correct | NNCC |  | Carson City | 1990 | 864 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14000
0146PLM1 | PLUMBING SYSTEM UPGRADE | 0146 | The water supply and waste system is original to the building and in poor condition. There is not enough heating or insulation to prevent the pipes from freezing and repairs have been made frequently. This project recommends replacing all of the water and sewer lines in the building including sufficient insulation and heating to prevent freezing. This estimate includes removal and disposal of the existing system as required. | GUARD TOWER 3 | 9990 | Correct | NNCC |  | Carson City | 1990 | 864 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0146PLM3 | WATER HEATER REPLACEMENT | 0146 | There is a 15 gallon electric water heater in the tower. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new on-demand water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | GUARD TOWER 3 | 9990 | Correct | NNCC |  | Carson City | 1990 | 864 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0147EXT2 | WINDOW REPLACEMENT | 0147 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 16 units. Removal and disposal of the existing windows is included in this estimate. The estimate includes additional costs due to the difficulty of the installation. | GUARD TOWER 4 | 9990 | Correct | NNCC |  | Carson City | 1979 | 75 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 32000
0146EXT4 | ROOF REPLACEMENT | 0146 | The standing seam metal roof on this building was in poor condition at the time of the survey and had active leaks. It is recommended that this building be re-roofed in the next 1-2 years with a new single-ply roofing system which will be installed directly over the existing metal roof. This will allow the roof to qualify for the statewide roofing program warranty and preventative maintenance agreement. | GUARD TOWER 3 | 9990 | Correct | NNCC |  | Carson City | 1990 | 864 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10368
0147EXT3 | EXTERIOR DOOR REPLACEMENT | 0147 | The existing exterior metal door and frame appears to be original to the building. It is damaged from age and general wear and tear. This project would provide for the replacement and installation of one new security grade metal door, frame and hardware. Removal and disposal of the existing door and painting of the new door is included in this estimate. | GUARD TOWER 4 | 9990 | Correct | NNCC |  | Carson City | 1979 | 75 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0146INT3 | FLOORING REPLACEMENT | 0146 | The VCT (vinyl composite tile) flooring is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. The estimate includes additional costs due to the difficulty of the installation. | GUARD TOWER 3 | 9990 | Correct | NNCC |  | Carson City | 1990 | 864 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 17280
0146PLM2 | RESTROOM FIXTURE UPGRADE | 0146 | The existing restroom fixtures are original to the building. They are worn and damaged from many years of use and should be scheduled for replacement. This project recommends the replacement of the existing fixtures including the water closet, lavatory and faucet. | GUARD TOWER 3 | 9990 | Correct | NNCC |  | Carson City | 1990 | 864 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0145EXT4 | ROOF REPLACEMENT | 0145 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. | GUARD TOWER 2 | 9990 | Correct | NNCC |  | Carson City | 1974 | 75 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0149EXT4 | EXTERIOR FINISHES | 0149 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | HOUSING UNIT 6 | 9990 | Correct | NNCC |  | Carson City | 1981 | 10634 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 53170
0149HVA1 | HVAC SYSTEM REPLACEMENT | 0149 | The existing HVAC system consists of older air handling units and hot water coils and a cooling tower that is 8 years old. The air handlers and coils are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of 2 new air handling units and hot water coils, ductwork and piping modifications, chemical treatment, temperature control modifications, testing, balancing and commissioning. This project is recommended under CIP 13-M17. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | HOUSING UNIT 6 | 9990 | Correct | NNCC |  | Carson City | 1981 | 10634 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 159510
0149ADA2 | ADA RESTROOM UPGRADE | 0149 | The building does not have an accessible restroom. The existing restrooms in the staff area do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | HOUSING UNIT 6 | 9990 | Correct | NNCC |  | Carson City | 1981 | 10634 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 25000
0142SEC3 | EXTERIOR DOOR REPLACEMENT | 0142 | The existing exterior metal doors and frames appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement and installation of 12 new security grade double metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | HOUSING UNIT 5 | 9990 | Correct | NNCC |  | Carson City | 1977 | 13641 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 84000
0146EXT3 | SLIDING GLASS DOOR REPLACEMENT | 0146 | The sliding glass door is damaged from age and general wear and tear and has reached the end of its expected life. This project would provide for the replacement of the sliding glass door assembly with a new door, frame and hardware. Removal and disposal of the existing door is included in this estimate. | GUARD TOWER 3 | 9990 | Correct | NNCC |  | Carson City | 1990 | 864 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0148INT1 | INTERIOR FINISHES | 0148 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | GUARD TOWER 5 | 9990 | Correct | NNCC |  | Carson City | 1979 | 267 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2670
0149ADA3 | RESTROOM REMODEL | 0149 | The building does not have an accessible staff restroom. The existing staff restrooms have some accessible upgrades but they do not fully meet the Americans with Disabilities Act (ADA) requirements. A partial retrofit is necessary. This project would provide funding to bring the restrooms into full ADA compliance. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | HOUSING UNIT 6 | 9990 | Correct | NNCC |  | Carson City | 1981 | 10634 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 25000
0149EXT5 | ROOF REPLACEMENT | 0149 | The roof on this building was in fair to poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The current roofing system was installed in 1991 and is now 23 years old. The roof warranty for this roof expired on 7-16-2008. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program. | HOUSING UNIT 6 | 9990 | Correct | NNCC |  | Carson City | 1981 | 10634 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 127608
0149EXT2 | WINDOW REPLACEMENT | 0149 | The existing exterior window units are original to the building and are damaged or broken and are not energy efficient. They present a safety and security issue due to their condition. This project would provide for the removal and replacement of the existing exterior window units with new institutional grade safety glazed window units. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | HOUSING UNIT 6 | 9990 | Correct | NNCC |  | Carson City | 1981 | 10634 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 66000
0149EXT3 | EXTERIOR DOOR REPLACEMENT | 0149 | The existing exterior metal doors and frames appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement and installation of 8 new security grade metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | HOUSING UNIT 6 | 9990 | Correct | NNCC |  | Carson City | 1981 | 10634 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 32000
0149SFT2 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0149 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | HOUSING UNIT 6 | 9990 | Correct | NNCC |  | Carson City | 1981 | 10634 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 2500
0149INT2 | INTERIOR FINISHES | 0149 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | HOUSING UNIT 6 | 9990 | Correct | NNCC |  | Carson City | 1981 | 10634 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 53170
0149ADA1 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0149 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | HOUSING UNIT 6 | 9990 | Correct | NNCC |  | Carson City | 1981 | 10634 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 4000
0147EXT1 | EXTERIOR FINISHES | 0147 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting the metal panels, structural posts and stairs and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended to paint the building in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | GUARD TOWER 4 | 9990 | Correct | NNCC |  | Carson City | 1979 | 75 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0148EXT1 | EXTERIOR FINISHES | 0148 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. The estimate includes additional costs due to the difficulty of the work. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | GUARD TOWER 5 | 9990 | Correct | NNCC |  | Carson City | 1979 | 267 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0150EXT3 | WINDOW REPLACEMENT | 0150 | The existing exterior window units are original to the building and are damaged or broken and are not energy efficient. They present a safety and security issue due to their condition. This project would provide for the removal and replacement of the existing exterior window units with new institutional grade safety glazed window units. | AUTO SHOP | 9990 | Correct | NNCC |  | Carson City | 1974 | 3325 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4800
0148PLM2 | WATER HEATER REPLACEMENT | 0148 | There is a 15 gallon electric water heater in the tower. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new on-demand water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | GUARD TOWER 5 | 9990 | Correct | NNCC |  | Carson City | 1979 | 267 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0148PLM1 | RESTROOM FIXTURE REPLACEMENT | 0148 | The existing restroom fixtures are original to the building. They are worn and damaged from many years of use and should be scheduled for replacement. This project recommends the replacement of the existing fixtures including the water closet, lavatory and faucet. | GUARD TOWER 5 | 9990 | Correct | NNCC |  | Carson City | 1979 | 267 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0148INT2 | FLOORING REPLACEMENT | 0148 | The VCT (vinyl composite tile) flooring is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. The estimate includes additional costs due to the difficulty of the installation. | GUARD TOWER 5 | 9990 | Correct | NNCC |  | Carson City | 1979 | 267 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5340
0148EXT2 | WINDOW REPLACEMENT | 0148 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 7 units. Removal and disposal of the existing windows is included in this estimate. The estimate includes additional costs due to the difficulty of the installation. | GUARD TOWER 5 | 9990 | Correct | NNCC |  | Carson City | 1979 | 267 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14000
0147PLM2 | WATER HEATER REPLACEMENT | 0147 | There is an on-demand water heater in the tower. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new on-demand water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | GUARD TOWER 4 | 9990 | Correct | NNCC |  | Carson City | 1979 | 75 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0147PLM1 | RESTROOM FIXTURE REPLACEMENT | 0147 | The existing restroom fixtures are original to the building. They are worn and damaged from many years of use and should be scheduled for replacement. This project recommends the replacement of the existing fixtures including the water closet, lavatory and faucet. | GUARD TOWER 4 | 9990 | Correct | NNCC |  | Carson City | 1979 | 75 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0147INT2 | FLOORING REPLACEMENT | 0147 | The VCT (vinyl composite tile) flooring is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. The estimate includes additional costs due to the difficulty of the installation. | GUARD TOWER 4 | 9990 | Correct | NNCC |  | Carson City | 1979 | 75 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0148EXT3 | EXTERIOR DOOR REPLACEMENT | 0148 | The existing exterior metal door and frame appears to be original to the building. It is damaged from age and general wear and tear. This project would provide for the replacement and installation of one new security grade metal door, frame and hardware. Removal and disposal of the existing door and painting of the new door is included in this estimate. | GUARD TOWER 5 | 9990 | Correct | NNCC |  | Carson City | 1979 | 267 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0143EXT2 | EXTERIOR FINISHES | 0143 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the stucco and concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | GENERATOR/ SWITCH GEAR ROOM | 9990 | Correct | NNCC |  | Carson City | 1974 | 550 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2750
0150SFT2 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0150 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | AUTO SHOP | 9990 | Correct | NNCC |  | Carson City | 1974 | 3325 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 1700
0144EXT1 | EXTERIOR FINISHES | 0144 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting the metal panels, structural posts and stairs and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended to paint the building in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | GUARD TOWER 1 | 9990 | Correct | NNCC |  | Carson City | 1963 | 75 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
0144EXT2 | EXTERIOR DOOR REPLACEMENT | 0144 | The existing exterior metal door and frame appears to be original to the building. It is damaged from age and general wear and tear. This project would provide for the replacement and installation of one new security grade metal door, frame and hardware. Removal and disposal of the existing door and painting of the new door is included in this estimate. | GUARD TOWER 1 | 9990 | Correct | NNCC |  | Carson City | 1963 | 75 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0144EXT3 | ROOF REPLACEMENT | 0144 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. | GUARD TOWER 1 | 9990 | Correct | NNCC |  | Carson City | 1963 | 75 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 900
0144ENR1 | WINDOW REPLACEMENT | 0144 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 16 units. Removal and disposal of the existing windows is included in this estimate. The estimate includes additional costs due to the difficulty of the installation. | GUARD TOWER 1 | 9990 | Correct | NNCC |  | Carson City | 1963 | 75 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 32000
0144INT2 | FLOORING REPLACEMENT | 0144 | The VCT (vinyl composite tile) flooring is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. The estimate includes additional costs due to the difficulty of the installation. | GUARD TOWER 1 | 9990 | Correct | NNCC |  | Carson City | 1963 | 75 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0143INT2 | INTERIOR FINISHES | 0143 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | GENERATOR/ SWITCH GEAR ROOM | 9990 | Correct | NNCC |  | Carson City | 1974 | 550 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2750
0144PLM1 | RESTROOM FIXTURE REPLACEMENT | 0144 | The existing restroom fixtures are original to the building. They are worn and damaged from many years of use and should be scheduled for replacement. This project recommends the replacement of the existing fixtures including the water closet, lavatory and faucet. | GUARD TOWER 1 | 9990 | Correct | NNCC |  | Carson City | 1963 | 75 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0143EXT5 | ROOF REPLACEMENT | 0143 | The roof on this building was in fair to poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The current roofing system was installed in 2001 and is now 13 years old. The roof warranty for this roof expires on 2-27-2019. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next 6-7 years to be consistent with the roofing program. | GENERATOR/ SWITCH GEAR ROOM | 9990 | Correct | NNCC |  | Carson City | 1974 | 550 | 2014-05-01 | Four to Ten Years | Long-Term Needs | 3 | 6600
0150PLM1 | WATER HEATER REPLACEMENT | 0150 | There is a 19 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new on-demand water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | AUTO SHOP | 9990 | Correct | NNCC |  | Carson City | 1974 | 3325 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0143ELE1 | LIGHTING UPGRADE | 0143 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | GENERATOR/ SWITCH GEAR ROOM | 9990 | Correct | NNCC |  | Carson City | 1974 | 550 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 825
0143EXT3 | EXTERIOR DOOR REPLACEMENT | 0143 | The exterior metal doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the louvered double metal door assembly and the 2 single metal man door assemblies with new metal doors, frames and hardware. Removal and disposal of the existing doors is included in this estimate. | GENERATOR/ SWITCH GEAR ROOM | 9990 | Correct | NNCC |  | Carson City | 1974 | 550 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
0142EXT3 | EXTERIOR FINISHES | 0142 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the stucco and concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 5-6 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT 5 | 9990 | Correct | NNCC |  | Carson City | 1977 | 13641 | 2014-05-01 | Four to Ten Years | Long-Term Needs | 3 | 68205
0142SEC1 | CELL DOOR LOCK REPLACEMENT | 0142 | The existing cell door locks are original to the building. The control panel, paracentric and mogul electric door cylinders are warn, have reached the end of their expected life and have become a security and safety concern for correctional officers. This project would provide for a new electric door control system including cylinders, keys, control panel and all required electrical connections. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | HOUSING UNIT 5 | 9990 | Correct | NNCC |  | Carson City | 1977 | 13641 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 287500
0142SFT2 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0142 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | HOUSING UNIT 5 | 9990 | Correct | NNCC |  | Carson City | 1977 | 13641 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 6821
0142INT2 | INTERIOR FINISHES | 0142 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 4-5 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HOUSING UNIT 5 | 9990 | Correct | NNCC |  | Carson City | 1977 | 13641 | 2014-05-01 | Four to Ten Years | Long-Term Needs | 3 | 81705
0149SEC1 | CELL DOOR LOCK REPLACEMENT | 0149 | The existing cell door locks are original to the building. The control panel, paracentric and mogul electric door cylinders are warn, have reached the end of their expected life and have become a security and safety concern for correctional officers. This project would provide for a new electric door control system including cylinders, keys, control panel and all required electrical connections. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | HOUSING UNIT 6 | 9990 | Correct | NNCC |  | Carson City | 1981 | 10634 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 250000
0143EXT4 | COILING DOOR REPLACEMENT | 0143 | There is an 8'x8' coiling door on the west side of the building which is damaged and does not function properly. It is original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated coiling door and replacement with a new manually operated coiling door. Removal and disposal of the existing door is included in this estimate. | GENERATOR/ SWITCH GEAR ROOM | 9990 | Correct | NNCC |  | Carson City | 1974 | 550 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0145INT2 | INTERIOR FINISHES | 0145 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceiling at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | GUARD TOWER 2 | 9990 | Correct | NNCC |  | Carson City | 1974 | 75 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 750
0150INT2 | INTERIOR FINISHES | 0150 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | AUTO SHOP | 9990 | Correct | NNCC |  | Carson City | 1974 | 3325 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16625
0150EXT2 | EXTERIOR FINISHES | 0150 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 5-7 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | AUTO SHOP | 9990 | Correct | NNCC |  | Carson City | 1974 | 3325 | 2014-05-01 | Four to Ten Years | Long-Term Needs | 3 | 16625
0150EXT5 | OVERHEAD DOOR REPLACEMENT | 0150 | There are three 16'x14' overhead coiling doors which are damaged and do not function properly. They are original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead coiling doors and replacement with three new motorized doors. | AUTO SHOP | 9990 | Correct | NNCC |  | Carson City | 1974 | 3325 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18000
0150EXT6 | ROOF REPLACEMENT | 0150 | The roof on this building was in fair to poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The current roofing system was installed in 1997 and is now 17 years old. The roof warranty for this roof expired on 12-15-2013. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program. | AUTO SHOP | 9990 | Correct | NNCC |  | Carson City | 1974 | 3325 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 39900
0150SIT1 | SAND/ OIL INTERCEPTOR | 0150 | There is no sand/ oil interceptor for the repair garage. It is recommended that a sand/ oil interceptor be installed and connected to the sewer drain to prevent oils and solids from entering the city sewer lines. This project would provide funding for the purchase and installation of a 50 GPM sand/ oil interceptor with a high oil alarm. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | AUTO SHOP | 9990 | Correct | NNCC |  | Carson City | 1974 | 3325 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0137SFT2 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0137 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | MULTI-PURPOSE/GYM/CHAPEL | 9990 | Correct | NNCC |  | Carson City | 1968 | 16306 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 5000
0150ELE2 | ELECTRICAL UPGRADE | 0150 | This building was constructed before the high demand for electrical services were needed for equipment, computers and other electrical devices. As time has progressed, the buildings electrical demand and system has changed. It is utilized to its current maximum potential. The electrical panels and receptacles are at their limit. It is recommended the entire system be upgraded to meet the evolving needs of the building including three-phase power. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | AUTO SHOP | 9990 | Correct | NNCC |  | Carson City | 1974 | 3325 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 49875
0144PLM2 | WATER HEATER REPLACEMENT | 0144 | There is an on-demand water heater in the tower. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new on-demand water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | GUARD TOWER 1 | 9990 | Correct | NNCC |  | Carson City | 1963 | 75 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0145EXT1 | EXTERIOR FINISHES | 0145 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting the metal panels, structural posts and stairs and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended to paint the building in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | GUARD TOWER 2 | 9990 | Correct | NNCC |  | Carson City | 1974 | 75 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
0142EXT2 | WINDOW REPLACEMENT | 0142 | The existing exterior window units are original to the building and are damaged or broken and are not energy efficient. They present a safety and security issue due to their condition. This project would provide for the removal and replacement of the existing exterior window units with new institutional grade safety glazed window units. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | HOUSING UNIT 5 | 9990 | Correct | NNCC |  | Carson City | 1977 | 13641 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 110400
0145PLM1 | RESTROOM FIXTURE REPLACEMENT | 0145 | The existing restroom fixtures are original to the building. They are worn and damaged from many years of use and should be scheduled for replacement. This project recommends the replacement of the existing fixtures including the water closet, lavatory and faucet. | GUARD TOWER 2 | 9990 | Correct | NNCC |  | Carson City | 1974 | 75 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0145EXT2 | WINDOW REPLACEMENT | 0145 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 16 units. Removal and disposal of the existing windows is included in this estimate. The estimate includes additional costs due to the difficulty of the installation. | GUARD TOWER 2 | 9990 | Correct | NNCC |  | Carson City | 1974 | 75 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 32000
0145EXT3 | EXTERIOR DOOR REPLACEMENT | 0145 | The existing exterior metal door and frame appears to be original to the building. It is damaged from age and general wear and tear. This project would provide for the replacement and installation of one new security grade metal door, frame and hardware. Removal and disposal of the existing door and painting of the new door is included in this estimate. | GUARD TOWER 2 | 9990 | Correct | NNCC |  | Carson City | 1974 | 75 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0145INT3 | FLOORING REPLACEMENT | 0145 | The VCT (vinyl composite tile) flooring is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. The estimate includes additional costs due to the difficulty of the installation. | GUARD TOWER 2 | 9990 | Correct | NNCC |  | Carson City | 1974 | 75 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0145PLM2 | WATER HEATER REPLACEMENT | 0145 | There is a 15 gallon electric water heater in the tower. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new on-demand water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | GUARD TOWER 2 | 9990 | Correct | NNCC |  | Carson City | 1974 | 75 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0144INT1 | INTERIOR FINISHES | 0144 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceiling at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | GUARD TOWER 1 | 9990 | Correct | NNCC |  | Carson City | 1963 | 75 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 750
0150HVA1 | HVAC EQUIPMENT REPLACEMENT | 0150 | The existing HVAC system consists of hydronic unit heaters and evaporative coolers. They are not energy efficient, insufficient for the spaces and have reached the end of their expected and useful life. This project would provide for installation of new HVAC units, ductwork and piping modifications, chemical treatment, temperature control modifications, testing, balancing and commissioning. This project includes the removal and disposal of approximately 50 asbestos mudded elbows on the hot water piping. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | AUTO SHOP | 9990 | Correct | NNCC |  | Carson City | 1974 | 3325 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 66500
0131EXT6 | ROOF REPLACEMENT | 0131 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. | PRISON INDUSTRY BUILDING C | 9990 | Correct | NNCC |  | Carson City | 1974 | 10560 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 126720
0126INT6 | JANITORS CLOSET REPAIRS | 0126 | The mop sink in the Janitors Closet is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | MAINTENANCE BUILDING | 9990 | Correct | NNCC |  | Carson City | 1969 | 3584 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
0127EXT4 | OVERHEAD DOOR REPLACEMENT | 0127 | There are seven 8'x10' overhead coiling doors which are damaged and do not function properly. Exposure and wind have caused the doors to bend, crack and lose their finish. They are original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead coiling doors and replacement with new manually operated overhead coiling doors. | PRISON INDUSTRY BUILDING B | 9990 | Correct | NNCC |  | Carson City | 1967 | 10560 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35000
0125INT5 | JANITORS CLOSET REPAIRS | 0125 | The mop sink in the Janitors Closets is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | COMMAND POST/OPERATIONS/EDUCATION | 9990 | Correct | NNCC |  | Carson City | 1976 | 9215 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
0125INT1 | FLOORING REPLACEMENT | 0125 | The VCT (vinyl composite tile) and carpet in the building are damaged and reaching the end of their useful life. There is asbestos in the floor tile mastic that will need to be abated by a licensed abatement professional. It is recommended that the VCT and carpet be replaced. Additional monies are included in this project for asbestos removal and disposal. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the next 2-3 years. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | COMMAND POST/OPERATIONS/EDUCATION | 9990 | Correct | NNCC |  | Carson City | 1976 | 9215 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 92150
0125PLM1 | WATER HEATER REPLACEMENT | 0125 | There is a 120 gallon natural gas-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is missing proper seismic bracing and an expansion tank. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | COMMAND POST/OPERATIONS/EDUCATION | 9990 | Correct | NNCC |  | Carson City | 1976 | 9215 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0126SFT4 | SAFETY CABINETS | 0126 | The Maintenance Building contains many different paints, stains, pesticides and other hazardous products on open shelves and on the floor. This does not meet OSHA standards for hazardous materials containment. This project would provide two hazardous storage containers in the building and install placards on the building exterior in accordance with OSHA 1910.106 (d). This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | MAINTENANCE BUILDING | 9990 | Correct | NNCC |  | Carson City | 1969 | 3584 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 10000
0126PLM2 | WATER HEATER REPLACEMENT | 0126 | There is a 120 gallon gas-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 1-2 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | MAINTENANCE BUILDING | 9990 | Correct | NNCC |  | Carson City | 1969 | 3584 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 5000
0126ELE1 | ELECTRICAL UPGRADE | 0126 | This building was constructed before the high demand for electrical services were needed for maintenance equipment, computers and other electrical devices. As time has progressed, the buildings electrical demand and system has changed. It is utilized to its current maximum potential. The electrical panels and receptacles are at their limit. It is recommended the entire system be upgraded to meet the evolving needs of the building including three-phase power. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | MAINTENANCE BUILDING | 9990 | Correct | NNCC |  | Carson City | 1969 | 3584 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 53760
0126INT1 | VCT FLOORING REPLACEMENT | 0126 | The VCT (vinyl composite tile) in the building is damaged and reaching the end of their useful life. There is asbestos in the floor tile mastic that will need to be abated by a licensed abatement professional. It is recommended that the VCT be replaced. Additional monies are included in this project for asbestos removal and disposal. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base in the next 2-3 years. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | MAINTENANCE BUILDING | 9990 | Correct | NNCC |  | Carson City | 1969 | 3584 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35840
0126EXT5 | ROOF REPLACEMENT | 0126 | The roof on this building was in fair to poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. | MAINTENANCE BUILDING | 9990 | Correct | NNCC |  | Carson City | 1969 | 3584 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 43008
0125EXT3 | EXTERIOR FINISHES | 0125 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 5-7 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | COMMAND POST/OPERATIONS/EDUCATION | 9990 | Correct | NNCC |  | Carson City | 1976 | 9215 | 2014-05-01 | Four to Ten Years | Long-Term Needs | 3 | 46075
0126SFT3 | WELDING VENTILATION INSTALLATION | 0126 | The building has insufficient ventilation for welding under OSHA Chapter 1926.353. If welding operations continue in this building, either general mechanical ventilation or local exhaust ventilation shall be provided. This project would provide for the installation of a mechanical ventilation system for the safety of the employees. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | MAINTENANCE BUILDING | 9990 | Correct | NNCC |  | Carson City | 1969 | 3584 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 15000
0125INT4 | INTERIOR DOOR REPLACEMENT | 0125 | The interior doors are original to the building. Many are damaged, difficult to lock and operate and do not have lever action handles. This project would provide for the removal of the existing doors and the purchase and installation of new metal security grade doors and frames. All hardware and painting is included in this estimate. Hardware to include security keys and fusible locks. This estimate is for 75 doors. | COMMAND POST/OPERATIONS/EDUCATION | 9990 | Correct | NNCC |  | Carson City | 1976 | 9215 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 150000
0126INT5 | INTERIOR DOOR REPLACEMENT | 0126 | The interior doors are original to the building. Many are damaged, difficult to lock and operate and do not have lever action handles. This project would provide for the removal of the existing doors and the purchase and installation of new metal security grade doors and frames. All hardware and painting is included in this estimate. Hardware to include security keys and fusible locks. This estimate is for 8 doors. | MAINTENANCE BUILDING | 9990 | Correct | NNCC |  | Carson City | 1969 | 3584 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16000
0126SFT1 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0126 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | MAINTENANCE BUILDING | 9990 | Correct | NNCC |  | Carson City | 1969 | 3584 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 1500
0126INT4 | CEILING SYSTEM REPLACEMENT | 0126 | The office side of the building has a suspended acoustical tile ceiling system. The t-bar framing is old, bent and rusted in many areas and many ceiling tiles are damaged and stained. This project would provide for the replacement of the suspended acoustical tile ceiling system including the framing, acoustical tile and seismic bracing assemblies. Removal and disposal of the existing ceiling system is included in this estimate. | MAINTENANCE BUILDING | 9990 | Correct | NNCC |  | Carson City | 1969 | 3584 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0126EXT2 | EXTERIOR FINISHES | 0126 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 5-7 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | MAINTENANCE BUILDING | 9990 | Correct | NNCC |  | Carson City | 1969 | 3584 | 2014-05-01 | Four to Ten Years | Long-Term Needs | 3 | 17920
0126INT3 | INTERIOR FINISHES | 0126 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 5-6 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | MAINTENANCE BUILDING | 9990 | Correct | NNCC |  | Carson City | 1969 | 3584 | 2014-05-01 | Four to Ten Years | Long-Term Needs | 3 | 17920
0126ADA2 | ADA DOOR & THRESHOLD REPLACEMENT | 0126 | The existing exterior entrance door and threshold to the building is not accessible. It is missing a lever action door handle and the threshold is too tall. This project would provide for a new accessible door and threshold assembly including removal of the existing door assembly and installation of the new accessible door assembly. ADA compliant signage is also included in this project. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | MAINTENANCE BUILDING | 9990 | Correct | NNCC |  | Carson City | 1969 | 3584 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 4500
0126EXT3 | WINDOW REPLACEMENT | 0126 | The existing windows in this building are of single pane wire mesh construction. Some are broken and all are not energy efficient. This project would provide for the removal and replacement of the windows with new dual pane security rated window systems. | MAINTENANCE BUILDING | 9990 | Correct | NNCC |  | Carson City | 1969 | 3584 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16200
0126HVA1 | HVAC EQUIPMENT REPLACEMENT | 0126 | The existing HVAC system consists of 2 four-ton condensing units and 2 original Fedderer furnaces. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of new HVAC units, ductwork and piping modifications, chemical treatment, temperature control modifications, testing, balancing and commissioning. This project is recommended under CIP 13-M17. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | MAINTENANCE BUILDING | 9990 | Correct | NNCC |  | Carson City | 1969 | 3584 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 53760
0127INT2 | INTERIOR FINISHES | 0127 | The interior finishes are in fair to poor condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | PRISON INDUSTRY BUILDING B | 9990 | Correct | NNCC |  | Carson City | 1967 | 10560 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 52800
0127EXT3 | EXTERIOR DOOR REPLACEMENT | 0127 | The existing exterior metal doors and frames appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement and installation of 2 new security grade metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | PRISON INDUSTRY BUILDING B | 9990 | Correct | NNCC |  | Carson City | 1967 | 10560 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
0126ADA1 | ADA RESTROOM UPGRADE | 0126 | The building does not have an accessible restroom. The existing restroom does not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | MAINTENANCE BUILDING | 9990 | Correct | NNCC |  | Carson City | 1969 | 3584 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 15000
0124ADA1 | ADA RESTROOM UPGRADE | 0124 | The building does not have an accessible restroom. The existing restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for remodeling the Men's and Women's restrooms into ADA compliant restrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | MAIN GATE HOUSE | 9990 | Correct | NNCC |  | Carson City | 1963 | 1440 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 30000
0131SFT4 | SAFETY CABINETS | 0131 | The building contains many different paints, stains, printing chemicals and other hazardous products on open shelves and on the floor. This does not meet OSHA standards for hazardous materials containment. This project would provide two hazardous storage containers in the building and install placards on the building exterior in accordance with OSHA 1910.106 (d). This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | PRISON INDUSTRY BUILDING C | 9990 | Correct | NNCC |  | Carson City | 1974 | 10560 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 10000
0137ADA2 | ADA SIGNAGE | 0137 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | MULTI-PURPOSE/GYM/CHAPEL | 9990 | Correct | NNCC |  | Carson City | 1968 | 16306 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 2500
0124EXT2 | WINDOW REPLACEMENT | 0124 | The existing windows in this building are of single pane wire mesh construction. Some are broken and all are not energy efficient. This project would provide for the removal and replacement of the windows with new dual pane security rated window systems. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | MAIN GATE HOUSE | 9990 | Correct | NNCC |  | Carson City | 1963 | 1440 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 42000
0124INT4 | INTERIOR FINISHES | 0124 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | MAIN GATE HOUSE | 9990 | Correct | NNCC |  | Carson City | 1963 | 1440 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11000
0124INT2 | VCT FLOORING REPLACEMENT | 0124 | The VCT (vinyl composite tile) flooring in the building is damaged and reaching the end of its useful life. There is asbestos in the floor tile mastic that will need to be abated by a licensed abatement professional. It is recommended that the VCT flooring be replaced. Additional monies are included in this project for asbestos removal and disposal. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | MAIN GATE HOUSE | 9990 | Correct | NNCC |  | Carson City | 1963 | 1440 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 22000
0124HVA1 | HVAC EQUIPMENT REPLACEMENT | 0124 | The existing HVAC system consists of 4 unit heaters and window mounted evaporative coolers. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of 4 new HVAC units, ductwork and piping modifications, chemical treatment, temperature control modifications, testing, balancing and commissioning. This project is recommended under CIP 13-M17. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | MAIN GATE HOUSE | 9990 | Correct | NNCC |  | Carson City | 1963 | 1440 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 33000
0124ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0124 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | MAIN GATE HOUSE | 9990 | Correct | NNCC |  | Carson City | 1963 | 1440 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 4000
0124EXT5 | ROOF REPLACEMENT | 0124 | The roof on this building was in fair to poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The current roofing system was installed in 1997 and is now 17 years old. The roof warranty for this roof expired on 12-15-2013. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program. | MAIN GATE HOUSE | 9990 | Correct | NNCC |  | Carson City | 1963 | 1440 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 17280
0124INT6 | JANITORS CLOSET REPAIRS | 0124 | The mop sink in the Janitors Closet is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | MAIN GATE HOUSE | 9990 | Correct | NNCC |  | Carson City | 1963 | 1440 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
0125EXT4 | EXTERIOR DOOR REPLACEMENT | 0125 | The existing exterior metal doors and frames appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement and installation of 17 new security grade metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | COMMAND POST/OPERATIONS/EDUCATION | 9990 | Correct | NNCC |  | Carson City | 1976 | 9215 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 68000
0124EXT3 | EXTERIOR FINISHES | 0124 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 5-7 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | MAIN GATE HOUSE | 9990 | Correct | NNCC |  | Carson City | 1963 | 1440 | 2014-05-01 | Four to Ten Years | Long-Term Needs | 3 | 11000
0126ADA3 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0126 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | MAINTENANCE BUILDING | 9990 | Correct | NNCC |  | Carson City | 1969 | 3584 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 4000
0124EXT4 | EXTERIOR DOOR REPLACEMENT | 0124 | The existing exterior metal doors and frames appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement and installation of 4 new security grade metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | MAIN GATE HOUSE | 9990 | Correct | NNCC |  | Carson City | 1963 | 1440 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16000
0124INT1 | CEILING TILE REPLACEMENT | 0124 | The ceiling in this building is covered with acoustical ceiling tiles. The ceiling tiles are damaged and stained and some are coming loose from the substrate. This project would provide for the replacement of the ceiling tiles. Removal and disposal of the existing tiles is included in this estimate. Additional costs would be required if there is asbestos in the tiles or adhesive. Given the location of HVAC equipment in the ceiling, this work could be performed concurrent with proposed HVAC equipment replacement. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | MAIN GATE HOUSE | 9990 | Correct | NNCC |  | Carson City | 1963 | 1440 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 22000
0124SFT1 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0124 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | MAIN GATE HOUSE | 9990 | Correct | NNCC |  | Carson City | 1963 | 1440 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 1000
0125HVA1 | HVAC EQUIPMENT REPLACEMENT | 0125 | The existing HVAC system consists of 4 air handling units connected to the central boiler, a chiller, 2 split system air conditioners and window mounted evaporative coolers. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of new HVAC units, ductwork and piping modifications, chemical treatment, temperature control modifications, testing, balancing and commissioning. This project is recommended under CIP 13-M17. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | COMMAND POST/OPERATIONS/EDUCATION | 9990 | Correct | NNCC |  | Carson City | 1976 | 9215 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 138225
0125EXT5 | ROOF REPLACEMENT | 0125 | The roof on this building was in fair to poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. | COMMAND POST/OPERATIONS/EDUCATION | 9990 | Correct | NNCC |  | Carson City | 1976 | 9215 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 110580
0125EXT1 | WINDOW REPLACEMENT | 0125 | The existing windows in this building are of single pane wire mesh construction. Some are broken and all are not energy efficient. This project would provide for the removal and replacement of the windows with new dual pane security rated window systems. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | COMMAND POST/OPERATIONS/EDUCATION | 9990 | Correct | NNCC |  | Carson City | 1976 | 9215 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 66600
0125ADA1 | ADA RESTROOM UPGRADE | 0125 | There are 9 restrooms in the building. None of these restrooms meet Americans with Disabilities Act (ADA) requirements. A complete retrofit of 3 of the restrooms is necessary. This project would provide funding for construction of a Men's and Women's restroom for staff and one restroom for inmates. These items may include demolition of several walls, new sinks, water closets, grab bars, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | COMMAND POST/OPERATIONS/EDUCATION | 9990 | Correct | NNCC |  | Carson City | 1976 | 9215 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 45000
0125ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0125 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | COMMAND POST/OPERATIONS/EDUCATION | 9990 | Correct | NNCC |  | Carson City | 1976 | 9215 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 4000
0125SFT3 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0125 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | COMMAND POST/OPERATIONS/EDUCATION | 9990 | Correct | NNCC |  | Carson City | 1976 | 9215 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 4000
0125INT3 | INTERIOR FINISHES | 0125 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 5-6 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | COMMAND POST/OPERATIONS/EDUCATION | 9990 | Correct | NNCC |  | Carson City | 1976 | 9215 | 2014-05-01 | Four to Ten Years | Long-Term Needs | 3 | 46075
0124INT5 | INTERIOR DOOR REPLACEMENT | 0124 | The interior doors are original to the building. Many are damaged, difficult to lock and operate and do not have lever action handles. This project would provide for the removal of the existing doors and the purchase and installation of new metal security grade doors and frames. All hardware and painting is included in this estimate. Hardware to include security keys and fusible locks. This estimate is for 10 doors. | MAIN GATE HOUSE | 9990 | Correct | NNCC |  | Carson City | 1963 | 1440 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0130HVA1 | HVAC EQUIPMENT REPLACEMENT | 0130 | The existing HVAC system consists of a rooftop air handler. It is not energy efficient, insufficient for the spaces and has reached the end of its expected and useful life. This project would provide for installation of a new HVAC unit, ductwork and piping modifications, chemical treatment, temperature control modifications, testing, balancing and commissioning. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | PRISON INDUSTRY BUILDING D | 9990 | Correct | NNCC |  | Carson City | 1965 | 10560 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 158400
0129INT5 | INTERIOR DOOR REPLACEMENT | 0129 | The interior doors are original to the building. Many are damaged, difficult to lock and operate and do not have lever action handles. This project would provide for the removal of the existing doors and the purchase and installation of new metal security grade doors and frames. All hardware and painting is included in this estimate. Hardware to include security keys and fusible locks. This estimate is for 28 doors. | CULINARY/DINING | 9990 | Correct | NNCC |  | Carson City | 1987 | 16354 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 112000
0129EXT4 | EXTERIOR DOOR REPLACEMENT | 0129 | The existing exterior metal doors and frames appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement and installation of 10 new security grade metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | CULINARY/DINING | 9990 | Correct | NNCC |  | Carson City | 1987 | 16354 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 40000
0129EXT3 | WINDOW REPLACEMENT | 0129 | The existing windows in this building are of single pane wire mesh construction. Some are broken and all are not energy efficient. This project would provide for the removal and replacement of the windows with new dual pane security rated window systems. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | CULINARY/DINING | 9990 | Correct | NNCC |  | Carson City | 1987 | 16354 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 59400
0129ELE2 | ELECTRICAL UPGRADE | 0129 | This building was constructed before the high demand for electrical services were needed for equipment, computers and other electrical devices. As time has progressed, the buildings electrical demand and system has changed. It is utilized to its current maximum potential. The electrical panels and receptacles are at their limit. It is recommended the entire system be upgraded to meet the evolving needs of the building including three-phase power. | CULINARY/DINING | 9990 | Correct | NNCC |  | Carson City | 1987 | 16354 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 245310
0129EXT2 | EXTERIOR FINISHES | 0129 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the stucco and concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 5-6 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | CULINARY/DINING | 9990 | Correct | NNCC |  | Carson City | 1987 | 16354 | 2014-05-01 | Four to Ten Years | Long-Term Needs | 3 | 81770
0129INT1 | CEILING REPLACEMENT | 0129 | The ceiling areas in this building are either acoustical tile or gypsum board in poor condition. The ceiling tiles are damaged and stained and some are coming loose from the substrate. The painted gypsum board in the kitchen is soiled and damaged in many areas. Due to their age and continuing deterioration, these ceilings should be scheduled for replacement. The ceiling finishes in food preparation areas shall be rated for food service applications as required by the health department which include but are not limited to a smooth, cleanable surface that is moisture resistant. Additional costs would be required if there is asbestos in the tiles or adhesive. This project or a portion thereof was previously recommended in the FCA report dated 01/12/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | CULINARY/DINING | 9990 | Correct | NNCC |  | Carson City | 1987 | 16354 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 114478
0129SFT2 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0129 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | CULINARY/DINING | 9990 | Correct | NNCC |  | Carson City | 1987 | 16354 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 7500
0129INT3 | INTERIOR FINISHES | 0129 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 4-5 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | CULINARY/DINING | 9990 | Correct | NNCC |  | Carson City | 1987 | 16354 | 2014-05-01 | Four to Ten Years | Long-Term Needs | 3 | 81770
0129ADA1 | ADA RESTROOM REMODEL | 0129 | The building does not have an accessible restroom. The existing restroom does not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | CULINARY/DINING | 9990 | Correct | NNCC |  | Carson City | 1987 | 16354 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 15000
0127ELE1 | ELECTRICAL UPGRADE | 0127 | This building was constructed before the high demand for electrical services were needed for maintenance equipment, computers and other electrical devices. As time has progressed, the buildings electrical demand and system has changed. It is utilized to its current maximum potential. The electrical panels and receptacles are at their limit. It is recommended the entire system be upgraded to meet the evolving needs of the building including three-phase power. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | PRISON INDUSTRY BUILDING B | 9990 | Correct | NNCC |  | Carson City | 1967 | 10560 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 158400
0129EXT5 | ROOF REPLACEMENT | 0129 | The roof on this building was in fair to poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The current roofing system was installed in 1999 and is now 15 years old. The roof warranty for this roof expires on 8-8-2015. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program. | CULINARY/DINING | 9990 | Correct | NNCC |  | Carson City | 1987 | 16354 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 196248
0126EXT4 | EXTERIOR DOOR REPLACEMENT | 0126 | The existing exterior metal doors and frames appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement and installation of 5 new security grade metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | MAINTENANCE BUILDING | 9990 | Correct | NNCC |  | Carson City | 1969 | 3584 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0130ELE2 | ELECTRICAL UPGRADE | 0130 | This building was constructed before the high demand for electrical services were needed for equipment, computers and other electrical devices. As time has progressed, the buildings electrical demand and system has changed. It is utilized to its current maximum potential. The electrical panels and receptacles are at their limit. It is recommended the entire system be upgraded to meet the evolving needs of the building including three-phase power. | PRISON INDUSTRY BUILDING D | 9990 | Correct | NNCC |  | Carson City | 1965 | 10560 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 158400
0130SFT3 | WELDING VENTILATION INSTALLATION | 0130 | The building has insufficient ventilation for welding under OSHA Chapter 1926.353. If welding operations continue in this building, either general mechanical ventilation or local exhaust ventilation shall be provided. This project would provide for the installation of a mechanical ventilation system for the safety of the employees. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | PRISON INDUSTRY BUILDING D | 9990 | Correct | NNCC |  | Carson City | 1965 | 10560 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0130SFT1 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0130 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | PRISON INDUSTRY BUILDING D | 9990 | Correct | NNCC |  | Carson City | 1965 | 10560 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 3500
0130EXT3 | ROOF REPLACEMENT | 0130 | The roof on this building was in fair to poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The current roofing system was installed in 1999 and is now 15 years old. The roof warranty for this roof expires on 8-8-2015. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program. | PRISON INDUSTRY BUILDING D | 9990 | Correct | NNCC |  | Carson City | 1965 | 10560 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 126720
0131SFT1 | INTERIOR STAIRWAY REPLACEMENT | 0131 | The stairs and handrails between the main floor and the storage loft do not meet the requirements in the 2012 International Building Code sections 1009 and 1012. The stairs to the area have become unstable and unsafe from years of use. This project would provide funding to remove and replace the stairway and handrail. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | PRISON INDUSTRY BUILDING C | 9990 | Correct | NNCC |  | Carson City | 1974 | 10560 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 9000
0131ELE1 | ELECTRICAL UPGRADE | 0131 | This building was constructed before the high demand for electrical services were needed for equipment, computers and other electrical devices. As time has progressed, the buildings electrical demand and system has changed. It is utilized to its current maximum potential. The electrical panels and receptacles are at their limit. It is recommended the entire system be upgraded to meet the evolving needs of the building including three-phase power. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | PRISON INDUSTRY BUILDING C | 9990 | Correct | NNCC |  | Carson City | 1974 | 10560 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 158400
0131EXT2 | EXTERIOR FINISHES | 0131 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the stucco and concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | PRISON INDUSTRY BUILDING C | 9990 | Correct | NNCC |  | Carson City | 1974 | 10560 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 52800
0131HVA1 | HVAC EQUIPMENT REPLACEMENT | 0131 | The existing HVAC system consists of 2 convectors, 10 hydronic unit heaters and 1 evaporative cooler. They are not energy efficient, insufficient for the spaces and have reached the end of their expected and useful life. This project would provide for installation of new HVAC units, ductwork and piping modifications, chemical treatment, temperature control modifications, testing, balancing and commissioning. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | PRISON INDUSTRY BUILDING C | 9990 | Correct | NNCC |  | Carson City | 1974 | 10560 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 158400
0131SFT3 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0131 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | PRISON INDUSTRY BUILDING C | 9990 | Correct | NNCC |  | Carson City | 1974 | 10560 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 3800
0131INT2 | INTERIOR FINISHES | 0131 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | PRISON INDUSTRY BUILDING C | 9990 | Correct | NNCC |  | Carson City | 1974 | 10560 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 52800
0131EXT4 | OVERHEAD DOOR REPLACEMENT | 0131 | Two out of the seven 10'x14' overhead coiling doors are damaged and do not function properly. Exposure and wind have caused the doors to bend, crack and lose their finish. They are original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead coiling doors and replacement with new manually operated overhead coiling doors. | PRISON INDUSTRY BUILDING C | 9990 | Correct | NNCC |  | Carson City | 1974 | 10560 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
0130INT2 | INTERIOR FINISHES | 0130 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | PRISON INDUSTRY BUILDING D | 9990 | Correct | NNCC |  | Carson City | 1965 | 10560 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 52800
0127SFT4 | SPRAY FINISHING BOOTH UPGRADES | 0127 | There is a spray finishing booth in the building that does not meet the design and fire safety guidelines outlined in the International Fire Code (IFC) and the National Fire Protection Association (NFPA) standards. Section 2404 of the 2012 IFC includes design codes for spray finishing rooms including constructing the room with approved noncombustible materials, proper means of egress, installation of an approved automatic fire-extinguishing system, fire extinguishers and mechanical ventilation requirements. NFPA 33 outlines standards for spray application areas including electrical, ventilation and fire protection systems and rules for drying and curing processes, operations and maintenance. This project would provide for installation of a spray finishing room in the building that complies with the IFC and NFPA to ensure the safety of the occupants. | PRISON INDUSTRY BUILDING B | 9990 | Correct | NNCC |  | Carson City | 1967 | 10560 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 50000
0130EXT2 | EXTERIOR FINISHES | 0130 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the stucco and concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | PRISON INDUSTRY BUILDING D | 9990 | Correct | NNCC |  | Carson City | 1965 | 10560 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 52800
0127SFT1 | INTERIOR STAIRWAY REPLACEMENT | 0127 | The stairs and handrails between the main floor and the storage loft do not meet the requirements in the 2012 International Building Code sections 1009 and 1012. The stairs to the area have become unstable and unsafe from years of use. This project would provide funding to remove and replace the stairway and handrail. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | PRISON INDUSTRY BUILDING B | 9990 | Correct | NNCC |  | Carson City | 1967 | 10560 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 9000
0129HVA2 | FREEZER COMPRESSOR REPLACEMENT | 0129 | There are 2 compressors for the freezer that will need to be replaced in the near future. They utilize older R-22 refrigerant and are original to the building. This project covers the recovery of the existing refrigerant and changing out the compressors with high efficiency units. If the existing compressor suffers a burnout and contaminates the refrigerant it will be more costly to change the unit out. | CULINARY/DINING | 9990 | Correct | NNCC |  | Carson City | 1987 | 16354 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 40000
0127INT3 | INTERIOR DOOR REPLACEMENT | 0127 | The interior doors are original to the building. Many are damaged, difficult to lock and operate and do not have lever action handles. This project would provide for the removal of the existing doors and the purchase and installation of new metal security grade doors and frames. All hardware and painting is included in this estimate. Hardware to include security keys and fusible locks. This estimate is for 12 doors. | PRISON INDUSTRY BUILDING B | 9990 | Correct | NNCC |  | Carson City | 1967 | 10560 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24000
0127SFT3 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0127 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | PRISON INDUSTRY BUILDING B | 9990 | Correct | NNCC |  | Carson City | 1967 | 10560 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 3500
0127EXT5 | ROOF REPLACEMENT | 0127 | The roof on this building was in fair to poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The current roofing system was installed in 1997 and is now 17 years old. The roof warranty for this roof expired on 12-15-2013. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program. | PRISON INDUSTRY BUILDING B | 9990 | Correct | NNCC |  | Carson City | 1967 | 10560 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 126720
0127EXT2 | EXTERIOR FINISHES | 0127 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls, repairing and painting the stucco and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | PRISON INDUSTRY BUILDING B | 9990 | Correct | NNCC |  | Carson City | 1967 | 10560 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 52800
0127HVA1 | HVAC EQUIPMENT REPLACEMENT | 0127 | The existing HVAC system consists of fan coil units, hydronic heaters and evaporative coolers. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of new HVAC units, ductwork and piping modifications, chemical treatment, temperature control modifications, testing, balancing and commissioning. This project is recommended under CIP 13-M17. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | PRISON INDUSTRY BUILDING B | 9990 | Correct | NNCC |  | Carson City | 1967 | 10560 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 158400
0127ADA1 | ADA RESTROOM UPGRADE | 0127 | The building does not have an accessible restroom. The existing restroom does not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | PRISON INDUSTRY BUILDING B | 9990 | Correct | NNCC |  | Carson City | 1967 | 10560 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 15000
0128EXT1 | WINDOW REPLACEMENT | 0128 | The existing windows in this building are of single pane wire mesh construction. Some are broken and all are not energy efficient. This project would provide for the removal and replacement of the windows with new dual pane security rated window systems. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | LAUNDRY/CENTRAL PLANT | 9990 | Correct | NNCC |  | Carson City | 1968 | 7000 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 64800
0128INT3 | DRYER REPLACEMENT | 0128 | The commercial tumbler dryers in the laundry are original to the building and are troublesome and problematic to operate. Considering the age of the machines and the evolving needs of the facility it is recommended to replace them. This project provides for removal and disposal of the existing tumbler dryers and replacement with new units. A total of 7 dryers was used for this estimate. | LAUNDRY/CENTRAL PLANT | 9990 | Correct | NNCC |  | Carson City | 1968 | 7000 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 56000
0129INT4 | CULINARY FLOOR REPLACEMENT | 0129 | This project recommends replacing 3,525 sq. ft. of flooring in the kitchen. The ceramic tile and substrate are damaged and failing. There are broken tiles throughout and water has infiltrated the substrate. This project would provide for removal and disposal of the existing flooring and installation of new quartz flooring in the next 1-2 years. Removal and reinstallation of kitchen equipment is also included in this estimate. This project is in design under CIP 13-M44 and the estimate is based off of that project. | CULINARY/DINING | 9990 | Correct | NNCC |  | Carson City | 1987 | 16354 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 243225
0128EXT5 | ROOF REPLACEMENT | 0128 | The roof on this building was in fair to poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The current roofing system was installed in 1995 and is now 19 years old. The roof warranty for this roof expired on 5-8-2012. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program. | LAUNDRY/CENTRAL PLANT | 9990 | Correct | NNCC |  | Carson City | 1968 | 7000 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 84000
0129PLM3 | PLUMBING REPLACEMENT | 0129 | The cast iron waste and supply lines are older and in poor condition. Most of the system appears to be original to the building and should be scheduled for replacement. Excess moisture under the kitchen has contributed to the deterioration of the waste and supply piping. This project recommends replacing all of the water and sewer lines in the building. This estimate includes removal and disposal of the existing system as required. | CULINARY/DINING | 9990 | Correct | NNCC |  | Carson City | 1987 | 16354 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 60000
0129HVA1 | HVAC EQUIPMENT REPLACEMENT | 0129 | The existing HVAC system consists of a rooftop air handler, 2 Futera hot water boilers, fan coil units and evaporative coolers. They are not energy efficient, insufficient for the spaces and have reached the end of their expected and useful life. This project would provide for installation of new HVAC units, ductwork and piping modifications, chemical treatment, temperature control modifications, testing, balancing and commissioning. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | CULINARY/DINING | 9990 | Correct | NNCC |  | Carson City | 1987 | 16354 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 327080
0128SFT1 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0128 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | LAUNDRY/CENTRAL PLANT | 9990 | Correct | NNCC |  | Carson City | 1968 | 7000 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 2500
0128INT2 | INTERIOR FINISHES | 0128 | The interior finishes are in fair to poor condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | LAUNDRY/CENTRAL PLANT | 9990 | Correct | NNCC |  | Carson City | 1968 | 7000 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35000
0128EXT4 | EXTERIOR DOOR REPLACEMENT | 0128 | The existing exterior metal doors and frames appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement and installation of 11 new security grade metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | LAUNDRY/CENTRAL PLANT | 9990 | Correct | NNCC |  | Carson City | 1968 | 7000 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 44000
0128ELE1 | ELECTRICAL UPGRADE | 0128 | This building was constructed before the high demand for electrical services were needed for equipment, computers and other electrical devices. As time has progressed, the buildings electrical demand and system has changed. It is utilized to its current maximum potential. The electrical panels and receptacles are at their limit. It is recommended the entire system be upgraded to meet the evolving needs of the building including three-phase power. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | LAUNDRY/CENTRAL PLANT | 9990 | Correct | NNCC |  | Carson City | 1968 | 7000 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 105000
0128HVA1 | HVAC EQUIPMENT REPLACEMENT | 0128 | The existing HVAC system consists of 2 fan coil units and 1 evaporative cooler. They are not energy efficient, insufficient for the spaces and have reached the end of their expected and useful life. This project would provide for installation of new HVAC units, ductwork and piping modifications, chemical treatment, temperature control modifications, testing, balancing and commissioning. This project is recommended under CIP 13-M17. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | LAUNDRY/CENTRAL PLANT | 9990 | Correct | NNCC |  | Carson City | 1968 | 7000 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 105000
0128PLM2 | WATER STORAGE TANK REPLACEMENT | 0128 | There is a 860 gallon water storage tank in the building. The average life span of a water storage tank is forty to fifty years. The tank was installed in 1978. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 5-6 years. This project would provide for a new water storage tank to be installed including connections to existing utilities. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | LAUNDRY/CENTRAL PLANT | 9990 | Correct | NNCC |  | Carson City | 1968 | 7000 | 2014-05-01 | Four to Ten Years | Long-Term Needs | 3 | 3500
0128EXT3 | EXTERIOR FINISHES | 0128 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls, repairing and painting the stucco and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | LAUNDRY/CENTRAL PLANT | 9990 | Correct | NNCC |  | Carson City | 1968 | 7000 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35000
2003ELE1 | GFCI DUPLEX OUTLET REPLACEMENT | 2003 | There is an electrical duplex outlet under the sink which is not GFCI protected. This outlet should be changed to a GFCI type outlet per the NEC. This project would provide for the purchase and installation of a GFCI duplex outlet for the safety of the occupants. | GUARD TOWER 1 | 9988 | Correct | WSCC |  | Carson City | 1998 | 402 | 2014-05-13 | Immediate to Two Years | Currently Critical | 1 | 300
2003EXT1 | EXTERIOR FINISHES | 2003 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the metal panels, windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | GUARD TOWER 1 | 9988 | Correct | WSCC |  | Carson City | 1998 | 402 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
2003INT1 | INTERIOR FINISHES | 2003 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 06/07/1999 and 05/18/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/13/2014. | GUARD TOWER 1 | 9988 | Correct | WSCC |  | Carson City | 1998 | 402 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2250
2003HVA1 | HVAC EQUIPMENT REPLACEMENT | 2003 | The packaged HVAC unit is more than 15 years old and should be scheduled for replacement. It is not energy efficient and has reached the end of its expected and useful life. This project would provide for installation of a new HVAC packaged unit and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC unit and all required connections to utilities. | GUARD TOWER 1 | 9988 | Correct | WSCC |  | Carson City | 1998 | 402 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12500
2034ELE1 | GFCI DUPLEX OUTLET REPLACEMENT | 2034 | There is an electrical duplex outlet under the sink in each restroom which is not GFCI protected. These outlets should be changed to GFCI type outlets per the NEC. This project would provide for the purchase and installation of two GFCI duplex outlets for the safety of the occupants. | GUARD TOWER 2 | 9988 | Correct | WSCC |  | Carson City | 1998 | 402 | 2014-05-13 | Immediate to Two Years | Currently Critical | 1 | 600
2003EXT2 | SLIDING GLASS DOOR REPLACEMENT | 2003 | The sliding glass door is damaged from age and general wear and tear and has reached the end of its expected life. This project would provide for the replacement of the sliding glass door assembly with a new door, frame and hardware. Removal and disposal of the existing door is included in this estimate. | GUARD TOWER 1 | 9988 | Correct | WSCC |  | Carson City | 1998 | 402 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
2034INT1 | INTERIOR FINISHES | 2034 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 06/07/1999 and 05/18/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/13/2014. | GUARD TOWER 2 | 9988 | Correct | WSCC |  | Carson City | 1998 | 402 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2250
2034HVA1 | HVAC EQUIPMENT REPLACEMENT | 2034 | The packaged HVAC unit is more than 15 years old and should be scheduled for replacement. It is not energy efficient and has reached the end of its expected and useful life. This project would provide for installation of a new HVAC packaged unit and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC unit and all required connections to utilities. | GUARD TOWER 2 | 9988 | Correct | WSCC |  | Carson City | 1998 | 402 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12500
2034PLM1 | WATER HEATER REPLACEMENT | 2034 | There are two 5 gallon electric water heaters in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, these units are showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that two new on-demand electric water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. | GUARD TOWER 2 | 9988 | Correct | WSCC |  | Carson City | 1998 | 402 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
2034EXT2 | SLIDING GLASS DOOR REPLACEMENT | 2034 | The sliding glass door is damaged from age and general wear and tear and has reached the end of its expected life. This project would provide for the replacement of the sliding glass door assembly with a new door, frame and hardware. Removal and disposal of the existing door is included in this estimate. | GUARD TOWER 2 | 9988 | Correct | WSCC |  | Carson City | 1998 | 402 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
2034EXT1 | EXTERIOR FINISHES | 2034 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the metal panels, windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | GUARD TOWER 2 | 9988 | Correct | WSCC |  | Carson City | 1998 | 402 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
9988SIT7 | ASPHALT PAVING INSTALLATION | 9988 | There is no asphalt paving connecting Building #1 to the access road between Housing Unit #2 and the Multi-Purpose building. This project would provide asphalt cement paving for a 20' wide access road from the existing paving to the back side of Unit #1. The estimate includes grading, 6" base, compaction and installation of 4" thick asphalt cement paving. | WARM SPRINGS CORRECTIONAL CENTER SITE | 9988 | Correct | WSCC |  | Carson City | 1962 |  | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
9988ADA1 | ADA PARKING UPGRADES | 9988 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The existing ADA parking spaces and path of travel to the entrance of the building do not meet the requirements of the code. The slopes are out of compliance, the configuration of the spaces, loading zones and path of travel to the entrance are not compliant. This project provides funding to bring the existing ADA parking space up to code including removal of the asphalt and replacement with P.C. concrete, installing a concrete path of travel to the entrance, updated signage, re-striping, re-grading and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | WARM SPRINGS CORRECTIONAL CENTER SITE | 9988 | Correct | WSCC |  | Carson City | 1962 |  | 2014-05-13 | Immediate to Two Years | Currently Critical | 1 | 45000
9988SEC1 | VIDEO SURVEILLANCE SYSTEM INSTALLATION | 9988 | There are no security cameras or recording systems for the prison site except for a few isolated areas and in Housing Unit 4. This is a safety issue as all areas cannot be seen by the security staff or recorded in case of an incident. This project would provide funding for the installation of a site wide surveillance camera and recording system and all required connections to utility systems. This project is a lump sum estimate for budgeting purposes. Final design of the system and amount of cameras would be determined by an in depth site survey and programming and may affect the final proposed cost estimate. This project or a portion thereof was previously recommended in the FCA report dated 05/18/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/13/2014. | WARM SPRINGS CORRECTIONAL CENTER SITE | 9988 | Correct | WSCC |  | Carson City | 1962 |  | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 650000
9988SIT6 | CRACK FILL & SEAL ASPHALT PAVING | 9988 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the paving site wide including access roads, parking areas and exercise yards. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 180,000 square feet of asphalt area was used to generate this estimate. | WARM SPRINGS CORRECTIONAL CENTER SITE | 9988 | Correct | WSCC |  | Carson City | 1962 |  | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 108000
0116PLM1 | WATER CLOSET AND LAVATORY REPLACEMENT | 0116 | The existing water closets and lavatories in 45 of the inmate cells are made of vitreous china. These types of fixtures are damaged and broken frequently and weapons can be made from the broken pieces which creates a security risk. Stainless steel units are more durable and are recommended to be installed. This project would provide for replacing the existing water closets and lavatories with a stainless steel combination water closet with lavatory unit that is suicide resistant. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 06/07/1999 and 05/18/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/13/2014. | HOUSING UNIT 2 | 9988 | Correct | WSCC |  | Carson City | 1977 | 11555 | 2014-05-13 | Immediate to Two Years | Currently Critical | 1 | 232500
0117INT1 | INTERIOR FINISHES | 0117 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 05/18/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/13/2014. | HOUSING UNIT 4 | 9988 | Correct | WSCC |  | Carson City | 1998 | 44600 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 230000
0117EXT2 | EXTERIOR FINISHES | 0117 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete walls, painting the doors and trim and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/18/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/13/2014. | HOUSING UNIT 4 | 9988 | Correct | WSCC |  | Carson City | 1998 | 44600 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 92000
0117EXT3 | ROOF REPLACEMENT | 0117 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1995. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. | HOUSING UNIT 4 | 9988 | Correct | WSCC |  | Carson City | 1998 | 44600 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 552000
0116SFT1 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0116 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 06/07/1999 and 05/18/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/13/2014. | HOUSING UNIT 2 | 9988 | Correct | WSCC |  | Carson City | 1977 | 11555 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5776
0116HVA1 | EXHAUST FAN REPLACEMENT | 0116 | The existing exhaust fans that serve the restrooms and showers are original equipment and are not providing adequate ventilation. This project would provide for the removal of the existing exhaust fan assemblies and the purchase and installation of new exhaust fan assemblies including connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 06/07/1999 and 05/18/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/13/2014. | HOUSING UNIT 2 | 9988 | Correct | WSCC |  | Carson City | 1977 | 11555 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
0116EXT4 | WINDOW REPLACEMENT | 0116 | The louvered windows are original, single pane construction in metal frames. These older windows are drafty, not energy efficient and the louver mechanisms are problematic. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 66 units. Removal and disposal of the existing windows is included in this estimate. | HOUSING UNIT 2 | 9988 | Correct | WSCC |  | Carson City | 1977 | 11555 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 79200
0116EXT3 | EXTERIOR FINISHES | 0116 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the stucco and concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT 2 | 9988 | Correct | WSCC |  | Carson City | 1977 | 11555 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 57775
0116ADA3 | ADA SHOWER REMODEL | 0116 | The building has a shower/ bathing room in each of the three wings. The ceramic tiles, fixtures, and drains are broken and failing. None of the shower stalls are ADA accessible or compliant. This project would provide for a complete remodel of all three shower rooms. One of the showers should be an ADA compliant stainless steel shower cabinet complete with accessible plumbing fixtures, seat, etc. Included in this estimate is removal and replacement of the fixtures and finishes in all three shower rooms. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 05/18/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/13/2014. | HOUSING UNIT 2 | 9988 | Correct | WSCC |  | Carson City | 1977 | 11555 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 75000
0117ENR1 | HVAC EQUIPMENT REPLACEMENT | 0117 | The HVAC system was installed in 1998 and is original to the building. It consists of two natural gas-fired boilers, rooftop air-conditioners and rooftop air handlers. The system is not energy efficient and will reach the end of its expected and useful life in the next 5-8 years. This project would provide for installation of a new HVAC system and cleaning of the existing duct work and grilles. The new system shall be designed to significantly reduce electrical and natural gas usage in order to comply with the 2009 IECC and ASHRAE 90.1 and to reduce utility costs. This project includes removal and disposal of the existing HVAC units and all required connections to utilities | HOUSING UNIT 4 | 9988 | Correct | WSCC |  | Carson City | 1998 | 44600 | 2014-05-13 | Four to Ten Years | Long-Term Needs | 3 | 690000
0118ADA3 | ADA BREAK ROOM REMODEL | 0118 | There are two small Employee Lounges in the building and a Lab Room with cabinets and a sink. The kitchenettes and associated cabinets are original to the building. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and countertops are delaminating and failing. This project recommends the replacement of the existing kitchen countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards For Accessible Design should be incorporated into the design such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. | MULTI-PURPOSE/CULINARY/INFIRMARY | 9988 | Correct | WSCC |  | Carson City | 1980 | 21600 | 2014-05-13 | Immediate to Two Years | Currently Critical | 1 | 45000
0116INT3 | INTERIOR FINISHES | 0116 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HOUSING UNIT 2 | 9988 | Correct | WSCC |  | Carson City | 1977 | 11555 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 57775
0118SFT1 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0118 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 06/07/1999 and 05/18/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/13/2014. | MULTI-PURPOSE/CULINARY/INFIRMARY | 9988 | Correct | WSCC |  | Carson City | 1980 | 21600 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10800
0118ADA1 | ADA RESTROOM UPGRADE | 0118 | The staff restroom and inmate shower in the Medical area are not ADA compliant. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom and remodeling the shower. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 06/07/1999 and 05/18/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/13/2014. | MULTI-PURPOSE/CULINARY/INFIRMARY | 9988 | Correct | WSCC |  | Carson City | 1980 | 21600 | 2014-05-13 | Immediate to Two Years | Currently Critical | 1 | 35000
0118ADA2 | ADA SIGNAGE | 0118 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 05/18/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/13/2014. | MULTI-PURPOSE/CULINARY/INFIRMARY | 9988 | Correct | WSCC |  | Carson City | 1980 | 21600 | 2014-05-13 | Immediate to Two Years | Currently Critical | 1 | 22500
0118EXT3 | EXTERIOR FINISHES | 0118 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | MULTI-PURPOSE/CULINARY/INFIRMARY | 9988 | Correct | WSCC |  | Carson City | 1980 | 21600 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 108000
0122EXT3 | EXTERIOR FINISHES | 0122 | It is important to maintain the finish, weather resistance and appearance of the building which is over 50 years old. There are numerous areas where the mortar is failing, missing and not sealed properly. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting the wood finishes, re-pointing the stone where needed and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and re-pointed in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 05/18/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/13/2014. | COTTAGE #5 | 9988 | Correct | WSCC |  | Carson City | 1957 | 480 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7200
0118INT6 | VCT FLOORING REPLACEMENT | 0118 | The VCT (vinyl composite tile) flooring in the Dining Room is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. | MULTI-PURPOSE/CULINARY/INFIRMARY | 9988 | Correct | WSCC |  | Carson City | 1980 | 21600 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16200
0118HVA3 | HYDRONIC HEATER REPLACEMENT | 0118 | The building is partially heated by two roof-mounted hydronic heaters. They are original to the building and have reached the end of their useful life. This project provides for disposal of the existing units and replacement with two new roof-mounted units including connections to utilities. | MULTI-PURPOSE/CULINARY/INFIRMARY | 9988 | Correct | WSCC |  | Carson City | 1980 | 21600 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0118EXT2 | CLEAN ROOF DEBRIS | 0118 | The roof on this building was in fair condition at the time of the survey but debris was observed in certain areas. The roof has grease from the culinary exhaust fan leaking on the roof and dead birds and other items in the roof drains. This project would provide for the cleaning of the roof membrane using cleaning materials approved by the roofing manufacturer. Using the proper cleaning agents per the roofing manufacturer should not void the warranty. The roof should be cleaned as soon as possible. This project or a portion thereof was previously recommended in the FCA report dated 05/18/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/13/2014. | MULTI-PURPOSE/CULINARY/INFIRMARY | 9988 | Correct | WSCC |  | Carson City | 1980 | 21600 | 2014-05-13 | Immediate to Two Years | Currently Critical | 1 | 500
0119EXT3 | EXTERIOR FINISHES | 0119 | It is important to maintain the finish, weather resistance and appearance of the building which is over 50 years old. There are numerous areas where the mortar is failing, missing and not sealed properly. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting the wood finishes, re-pointing the stone where needed and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and re-pointed in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 05/18/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/13/2014. | COTTAGE #2 | 9988 | Correct | WSCC |  | Carson City | 1957 | 576 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8640
0097EXT3 | EXTERIOR FINISHES | 0097 | It is important to maintain the finish, weather resistance and appearance of the building which is over 50 years old. There are numerous areas where the mortar is failing, missing and not sealed properly. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting the wood finishes, re-pointing the stone where needed and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and re-pointed in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 05/18/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/13/2014. | COTTAGE #6 | 9988 | Correct | WSCC |  | Carson City | 1957 | 576 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8640
0116EXT5 | ROOF REPLACEMENT | 0116 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1992. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. | HOUSING UNIT 2 | 9988 | Correct | WSCC |  | Carson City | 1977 | 11555 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 138660
0121EXT3 | EXTERIOR FINISHES | 0121 | It is important to maintain the finish, weather resistance and appearance of the building which is over 50 years old. There are numerous areas where the mortar is failing, missing and not sealed properly. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting the wood finishes, re-pointing the stone where needed and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and re-pointed in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 05/18/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/13/2014. | COTTAGE #4 | 9988 | Correct | WSCC |  | Carson City | 1957 | 576 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8640
0118INT5 | INTERIOR FINISHES | 0118 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | MULTI-PURPOSE/CULINARY/INFIRMARY | 9988 | Correct | WSCC |  | Carson City | 1980 | 21600 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 108000
0115SFT2 | EXTERIOR STAIR REPLACEMENT | 0115 | There are two sets of stairs coming out of the building that are not code compliant and are due for replacement. The exterior concrete stairway that leads out from the Administration area is deteriorating and missing proper handrails. Spalling and cracking have occurred to the point of exposing rebar and causing a tripping hazard. It has only one handrail and does not have a proper landing at the bottom of the stairway. It appears these stairs are original to the building. The exterior steel stairway that leads out of "C" Wing does not have a compliant landing from the exit door and is missing a handrail. This project recommends the removal and replacement of the stairways and handrails in accordance with IBC Sections 1009 and 1012. This project or a portion thereof was previously recommended in the FCA report dated 05/18/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/13/2014. | ADMINISTRATION/GATEHOUSE/UNIT 1 | 9988 | Correct | WSCC |  | Carson City | 1962 | 19442 | 2014-05-13 | Immediate to Two Years | Currently Critical | 1 | 30000
0116EXT2 | EXTERIOR DOOR REPLACEMENT | 0116 | The existing exterior metal doors and frames appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the purchase and installation of 10 new security grade metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 05/18/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/13/2014. | HOUSING UNIT 2 | 9988 | Correct | WSCC |  | Carson City | 1977 | 11555 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 40000
0115ADA6 | ACCESSIBLE ENTRANCE RAMP | 0115 | This facility has an ADA accessible ramp located on the north side of the building at the main entrance. This ramp is on the accessible path of travel from the accessible parking space to the entrance of the building. The ramp does not have proper slopes, landings or handrails. This project would provide for an upgrade to the ramp to make it fully ADA compliant. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | ADMINISTRATION/GATEHOUSE/UNIT 1 | 9988 | Correct | WSCC |  | Carson City | 1962 | 19442 | 2014-05-13 | Immediate to Two Years | Currently Critical | 1 | 35000
0115INT2 | FLOORING REPLACEMENT | 0115 | The VCT (vinyl composite tile), sheet vinyl and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base. This project or a portion thereof was previously recommended in the FCA report dated 06/07/1999 and 05/18/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/13/2014. | ADMINISTRATION/GATEHOUSE/UNIT 1 | 9988 | Correct | WSCC |  | Carson City | 1962 | 19442 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 175000
0115ADA2 | ADA SIGNAGE | 0115 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | ADMINISTRATION/GATEHOUSE/UNIT 1 | 9988 | Correct | WSCC |  | Carson City | 1962 | 19442 | 2014-05-13 | Immediate to Two Years | Currently Critical | 1 | 1500
0115SEC1 | CELL DOORS, LOCKS AND MECHANISMS REPLACEMENT | 0115 | The existing control panel appeared to be operating properly but technology has changed, replacement parts are hard to find for performing routine and emergency maintenance and it is reaching the end of its expected life. The current electronic controls do not cover the cell doors which are currently on a key system. This project would provide a new electronic touch screen door control system for the sally ports and 60 cell doors in this unit. All doors and frames on inmate cells would require replacement to accommodate the electric locks; conduit and conductors would have to be run to all cells. This project is in design under CIP 11-M14 and the estimate is based off of that project. This project or a portion thereof was previously recommended in the FCA report dated 05/18/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/13/2014. | ADMINISTRATION/GATEHOUSE/UNIT 1 | 9988 | Correct | WSCC |  | Carson City | 1962 | 19442 | 2014-05-13 | Immediate to Two Years | Currently Critical | 1 | 1244200
0115ADA4 | ADA SHOWER REMODELS | 0115 | The inmate housing portion of this building has showers in each wing. None of the shower stalls are ADA accessible or compliant. The shower stalls are all showing signs of age, deterioration and inmate abuse. This project would provide for remodeling all of the showers including one ADA compliant stainless steel shower cabinet to be installed to provide shower facilities for the disabled. Included in this estimate is removal and replacement of the existing shower stalls and installation of stainless steel shower units. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 05/18/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/13/2014. | ADMINISTRATION/GATEHOUSE/UNIT 1 | 9988 | Correct | WSCC |  | Carson City | 1962 | 19442 | 2014-05-13 | Immediate to Two Years | Currently Critical | 1 | 500000
0115ADA3 | ADA RESTROOM REMODEL | 0115 | There are several staff and inmate restroom throughout the building. Some of them have accessible elements, but none are fully compliant. They do not meet the current Americans with Disabilities Act (ADA) requirements. A complete retrofit of two restrooms is necessary. This project would provide funding for construction of two unisex accessible restrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | ADMINISTRATION/GATEHOUSE/UNIT 1 | 9988 | Correct | WSCC |  | Carson City | 1962 | 19442 | 2014-05-13 | Immediate to Two Years | Currently Critical | 1 | 30000
0115EXT4 | EXTERIOR DOOR REPLACEMENT | 0115 | The existing exterior metal doors and frames appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement and installation of 14 new security grade metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | ADMINISTRATION/GATEHOUSE/UNIT 1 | 9988 | Correct | WSCC |  | Carson City | 1962 | 19442 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 56000
0115EXT3 | WINDOW REPLACEMENT | 0115 | The exterior windows are original, dual pane construction in metal frames. These older windows are not insulated and not energy efficient. This project recommends replacing the windows with dual pane security rated window systems. This estimate is for the replacement of 124 units. Removal and disposal of the existing windows is included in this estimate. | ADMINISTRATION/GATEHOUSE/UNIT 1 | 9988 | Correct | WSCC |  | Carson City | 1962 | 19442 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 148800
0115INT4 | INTERIOR FINISHES | 0115 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 05/18/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/13/2014. | ADMINISTRATION/GATEHOUSE/UNIT 1 | 9988 | Correct | WSCC |  | Carson City | 1962 | 19442 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 97210
0115EXT2 | EXTERIOR FINISHES | 0115 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/18/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/13/2014. | ADMINISTRATION/GATEHOUSE/UNIT 1 | 9988 | Correct | WSCC |  | Carson City | 1962 | 19442 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 97210
0115ADA1 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0115 | This building contains 3 water fountains that are not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of six drinking fountains to meet the ADA requirements, a high and low fountain in each of the three separate secured areas. This project or a portion thereof was previously recommended in the FCA report dated 05/18/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/13/2014. | ADMINISTRATION/GATEHOUSE/UNIT 1 | 9988 | Correct | WSCC |  | Carson City | 1962 | 19442 | 2014-05-13 | Immediate to Two Years | Currently Critical | 1 | 12000
0115ADA5 | ADA ACCESSIBLE COUNTER | 0115 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The security counter at the entrance of the building does not meet current ADA requirements. Section 904.4 of the ADA Standards For Accessible Design states that a portion of the counter surface that is 36" long minimum and 36" high maximum above the finish floor shall be provided. This project will provide an accessible counter space in accordance with this requirement. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | ADMINISTRATION/GATEHOUSE/UNIT 1 | 9988 | Correct | WSCC |  | Carson City | 1962 | 19442 | 2014-05-13 | Immediate to Two Years | Currently Critical | 1 | 1500
0116SEC1 | CELL DOORS, LOCKS AND MECHANISMS REPLACEMENT | 0116 | The existing control panel appeared to be operating properly but technology has changed, replacement parts are hard to find for performing routine and emergency maintenance and it is reaching the end of its expected life. The current electronic controls do not cover all of the cell doors which are currently on a key system. This project would provide a new electronic touch screen door control system for 54 cell doors in this unit. All doors and frames on inmate cells would require replacement to accommodate the electric locks; conduit and conductors would have to be run to all cells. | HOUSING UNIT 2 | 9988 | Correct | WSCC |  | Carson City | 1977 | 11555 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000000
0116PLM2 | WATER HEATER REPLACEMENT | 0116 | There are two 100 gallon natural gas-fired water heaters in the building. One of them is currently not operational. It is recommended that a new natural gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | HOUSING UNIT 2 | 9988 | Correct | WSCC |  | Carson City | 1977 | 11555 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0116ENR1 | HVAC REPLACEMENT | 0116 | The HVAC system was installed in 1977 and is original to the building. It consists of a natural gas-fired boiler, a chiller and several fan coil units. The system is not energy efficient and has reached the end of its expected and useful life. This project would provide for installation of a new HVAC system and cleaning of the existing duct work and grilles. The new system shall be designed to significantly reduce electrical and natural gas usage in order to comply with the 2009 IECC and ASHRAE 90.1 and to reduce utility costs. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. This project is funded under CIP 13-M18 and the estimate is based off of that project. | HOUSING UNIT 2 | 9988 | Correct | WSCC |  | Carson City | 1977 | 11555 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 250000
0115INT5 | INTERIOR WINDOW REPLACEMENT | 0115 | There are two interior windows near the entrance that are cracked and should be replaced. This estimate is for the replacement of 2 units. Removal and disposal of the existing windows is included in this estimate. | ADMINISTRATION/GATEHOUSE/UNIT 1 | 9988 | Correct | WSCC |  | Carson City | 1962 | 19442 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
1419PLM2 | BACKFLOW PREVENTER REPLACEMENT | 1419 | There is a backflow preventer on the main water line coming into the building. It is leaking and should be scheduled for replacement. This project would provide for replacing the backflow preventer. | HOUSING UNIT #5 | 9941 | Correct | ESP |  | Ely | 1989 | 29870 | 2015-04-29 | Immediate to Two Years | Currently Critical | 1 | 2000
1420EXT4 | ROOF REPLACEMENT | 1420 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 15 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2006. It is recommended that this building be re-roofed in the next 4-5 years to be consistent with the roofing program and the end of the warranty period. | HOUSING UNIT #6 | 9941 | Correct | ESP |  | Ely | 1989 | 29870 | 2015-04-29 | Four to Ten Years | Long-Term Needs | 3 | 358440
1420EXT2 | EXTERIOR FINISHES | 1420 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sealing and painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years, and that it be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | HOUSING UNIT #6 | 9941 | Correct | ESP |  | Ely | 1989 | 29870 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 149350
1420ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 1420 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | HOUSING UNIT #6 | 9941 | Correct | ESP |  | Ely | 1989 | 29870 | 2015-04-29 | Immediate to Two Years | Currently Critical | 1 | 4000
1420SEC2 | ELECTRONIC LOCKS/ CONTROLS REPLACEMENT | 1420 | The controls for the door locks and security systems are built on a custom panel and interface. The controls are difficult to repair, parts are becoming increasingly difficult to locate, and the type and configuration of the switches are limited by the physical size of the consoles. This project recommends replacing the existing mechanical switching system with a computer system and electronic interface. Remote costs and secure facility allowance were included in the project estimates. This project or a portion thereof was previously recommended in the FCA report dated 06/04/2002 and 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | HOUSING UNIT #6 | 9941 | Correct | ESP |  | Ely | 1989 | 29870 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 565000
1419EXT4 | ROOF REPLACEMENT | 1419 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 15 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2006. It is recommended that this building be re-roofed in the next 4-5 years to be consistent with the roofing program and the end of the warranty period. | HOUSING UNIT #5 | 9941 | Correct | ESP |  | Ely | 1989 | 29870 | 2015-04-29 | Four to Ten Years | Long-Term Needs | 3 | 358440
1419HVA1 | HEAT EXCHANGER REPLACEMENTS | 1419 | The two shell and tube heat exchangers in the building were installed in 1987 and are original to the building. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of two new plate frame heat exchangers, one for the domestic water and one for the mechanical system. This project includes removal and disposal of the existing units and all required connections to utilities. | HOUSING UNIT #5 | 9941 | Correct | ESP |  | Ely | 1989 | 29870 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16000
1419ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 1419 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | HOUSING UNIT #5 | 9941 | Correct | ESP |  | Ely | 1989 | 29870 | 2015-04-29 | Immediate to Two Years | Currently Critical | 1 | 4000
1419EXT2 | EXTERIOR FINISHES | 1419 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sealing and painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years, and that it be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | HOUSING UNIT #5 | 9941 | Correct | ESP |  | Ely | 1989 | 29870 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 149350
1617INT1 | INTERIOR FINISHES | 1617 | The interior finishes are in fair condition. It is recommended that the interior walls be sealed with a concrete and grout sealer at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to sealing, all surfaces should be repaired and prepped. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | ESP SEWAGE GRINDER BUILDING | 9941 | Correct | ESP |  | Ely | 1999 | 860 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4300
1419INT1 | INTERIOR FINISHES | 1419 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that it be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | HOUSING UNIT #5 | 9941 | Correct | ESP |  | Ely | 1989 | 29870 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 149350
1419SEC2 | ELECTRONIC LOCKS/ CONTROLS REPLACEMENT | 1419 | The controls for the door locks and security systems are built on a custom panel and interface. The controls are difficult to repair, parts are becoming increasingly difficult to locate, and the type and configuration of the switches are limited by the physical size of the consoles. This project recommends replacing the existing mechanical switching system with a computer system and electronic interface. Remote costs and secure facility allowance were included in the project estimates. This project or a portion thereof was previously recommended in the FCA report dated 06/04/2002 and 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | HOUSING UNIT #5 | 9941 | Correct | ESP |  | Ely | 1989 | 29870 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 565000
1419PLM1 | WATER TREATMENT SYSTEM REPLACEMENT | 1419 | The existing water softening/ treatment systems in the building are currently not operational. They are original to the building and approaching the end of their lifecycles. Failure of the equipment causes wear and tear on the domestic water supply lines, plumbing fixtures and HVAC equipment. This project would provide for the replacement of the existing water softeners/ treatment systems with new equipment. This project would also provide for a chemical treatment program including an updated chemicals control system, service, and employee training provided by a qualified water treatment vendor. | HOUSING UNIT #5 | 9941 | Correct | ESP |  | Ely | 1989 | 29870 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
1427HVA1 | HVAC REPLACEMENT | 1427 | The existing HVAC system consists of a small unit heater and a rooftop air handler. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of new HVAC units, ductwork and piping modifications, chemical treatment, temperature control modifications, testing, balancing and commissioning. | BUILDING #13 - ARMORY | 9941 | Correct | ESP |  | Ely | 1987 | 1680 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25200
1417PLM1 | WATER TREATMENT SYSTEM REPLACEMENT | 1417 | The existing water softening/ treatment systems in the building are currently not operational. They are original to the building and approaching the end of their lifecycles. Failure of the equipment causes wear and tear on the domestic water supply lines, plumbing fixtures and HVAC equipment. This project would provide for the replacement of the existing water softeners/ treatment systems with new equipment. This project would also provide for a chemical treatment program including an updated chemicals control system, service, and employee training provided by a qualified water treatment vendor. | HOUSING UNIT #3 | 9941 | Correct | ESP |  | Ely | 1987 | 29870 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
1417EXT4 | ROOF REPLACEMENT | 1417 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 15 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2008. It is recommended that this building be re-roofed in the next 6-7 years to be consistent with the roofing program and the end of the warranty period. | HOUSING UNIT #3 | 9941 | Correct | ESP |  | Ely | 1987 | 29870 | 2015-04-29 | Four to Ten Years | Long-Term Needs | 3 | 358440
1417EXT2 | EXTERIOR FINISHES | 1417 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sealing and painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years, and that it be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | HOUSING UNIT #3 | 9941 | Correct | ESP |  | Ely | 1987 | 29870 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 149350
1417ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 1417 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | HOUSING UNIT #3 | 9941 | Correct | ESP |  | Ely | 1987 | 29870 | 2015-04-29 | Immediate to Two Years | Currently Critical | 1 | 4000
1417HVA1 | HEAT EXCHANGER REPLACEMENTS | 1417 | The two shell and tube heat exchangers in the building were installed in 1987 and are original to the building. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of two new plate frame heat exchangers, one for the domestic water and one for the mechanical system. This project includes removal and disposal of the existing units and all required connections to utilities. | HOUSING UNIT #3 | 9941 | Correct | ESP |  | Ely | 1987 | 29870 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16000
1417PLM2 | BACKFLOW PREVENTER REPLACEMENT | 1417 | There is a backflow preventer on the main water line coming into the building. It is leaking and should be scheduled for replacement. This project would provide for replacing the backflow preventer. | HOUSING UNIT #3 | 9941 | Correct | ESP |  | Ely | 1987 | 29870 | 2015-04-29 | Immediate to Two Years | Currently Critical | 1 | 2000
1427EXT2 | EXTERIOR FINISHES | 1427 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sealing and painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years, and that it be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | BUILDING #13 - ARMORY | 9941 | Correct | ESP |  | Ely | 1987 | 1680 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8400
1418SEC2 | ELECTRONIC LOCKS/ CONTROLS REPLACEMENT | 1418 | The controls for the door locks and security systems are built on a custom panel and interface. The controls are difficult to repair, parts are becoming increasingly difficult to locate, and the type and configuration of the switches are limited by the physical size of the consoles. This project recommends replacing the existing mechanical switching system with a computer system and electronic interface. Remote costs and secure facility allowance were included in the project estimates. This project or a portion thereof was previously recommended in the FCA report dated 06/04/2002 and 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | HOUSING UNIT #4 | 9941 | Correct | ESP |  | Ely | 1987 | 29870 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 565000
1420INT1 | INTERIOR FINISHES | 1420 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that it be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | HOUSING UNIT #6 | 9941 | Correct | ESP |  | Ely | 1989 | 29870 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 149350
1418EXT4 | ROOF REPLACEMENT | 1418 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 15 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2008. It is recommended that this building be re-roofed in the next 6-7 years to be consistent with the roofing program and the end of the warranty period. | HOUSING UNIT #4 | 9941 | Correct | ESP |  | Ely | 1987 | 29870 | 2015-04-29 | Four to Ten Years | Long-Term Needs | 3 | 358440
1432HVA1 | HVAC REPLACEMENT | 1432 | The combination in-wall HVAC unit and small electric heater are original to the building and should be scheduled for replacement. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of a new combination unit and electric heater. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | TOWER #4 | 9941 | Correct | ESP |  | Ely | 1987 | 290 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
1417SEC2 | ELECTRONIC LOCKS/ CONTROLS REPLACEMENT | 1417 | The controls for the door locks and security systems are built on a custom panel and interface. The controls are difficult to repair, parts are becoming increasingly difficult to locate, and the type and configuration of the switches are limited by the physical size of the consoles. This project recommends replacing the existing mechanical switching system with a computer system and electronic interface. Remote costs and secure facility allowance were included in the project estimates. This project or a portion thereof was previously recommended in the FCA report dated 06/04/2002 and 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | HOUSING UNIT #3 | 9941 | Correct | ESP |  | Ely | 1987 | 29870 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 565000
1418INT1 | INTERIOR FINISHES | 1418 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that it be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | HOUSING UNIT #4 | 9941 | Correct | ESP |  | Ely | 1987 | 29870 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 149350
1427ADA1 | ADA RESTROOM REMODEL | 1427 | The building does not have an accessible restroom. The existing restroom does not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | BUILDING #13 - ARMORY | 9941 | Correct | ESP |  | Ely | 1987 | 1680 | 2015-04-29 | Immediate to Two Years | Currently Critical | 1 | 15000
1426ADA1 | RESTROOM REMODEL | 1426 | The restroom is original to the building and in overall poor condition. The finishes, fixtures, cabinets, toilets, showers and exhaust fans are showing signs of wear and deterioration. The ceramic tile in the showers is failing and many tiles have fallen off exposing the wood framing to water. This project would provide for a complete remodel of the restroom including complying with the 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design. The removal and disposal of the existing fixtures and finishes is included in this estimate. | BUILDING #12 - TRUSTEE DORMITORY | 9941 | Correct | ESP |  | Ely | 1987 | 3600 | 2015-04-29 | Immediate to Two Years | Currently Critical | 1 | 45000
1427EXT3 | ROOF REPLACEMENT | 1427 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 15 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2008. It is recommended that this building be re-roofed in the next 6-7 years to be consistent with the roofing program and the end of the warranty period. | BUILDING #13 - ARMORY | 9941 | Correct | ESP |  | Ely | 1987 | 1680 | 2015-04-29 | Four to Ten Years | Long-Term Needs | 3 | 20160
1417INT1 | INTERIOR FINISHES | 1417 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that it be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | HOUSING UNIT #3 | 9941 | Correct | ESP |  | Ely | 1987 | 29870 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 149350
1617EXT1 | EXTERIOR FINISHES | 1617 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sealing and painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years, and that it be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | ESP SEWAGE GRINDER BUILDING | 9941 | Correct | ESP |  | Ely | 1999 | 860 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4300
1428INT1 | INTERIOR FINISHES | 1428 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years, and that it be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | BUILDING #14 - GATEHOUSE | 9941 | Correct | ESP |  | Ely | 1987 | 1350 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6750
1432PLM1 | RESTROOM FIXTURE REPLACEMENT | 1432 | The restroom fixtures in the Tower are worn and damaged from many years of use including the water closet, lavatory and faucet. Many fixtures are or have been leaking and have caused extensive scaling and staining to the fixtures themselves. It is recommended that all fixtures be replaced with new units. This project includes removal and disposal of the existing fixtures and installation of new fixtures. | TOWER #4 | 9941 | Correct | ESP |  | Ely | 1987 | 290 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
1432PLM2 | WATER HEATER REPLACEMENT | 1432 | There is a 7 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new on-demand electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | TOWER #4 | 9941 | Correct | ESP |  | Ely | 1987 | 290 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
1418EXT2 | EXTERIOR FINISHES | 1418 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sealing and painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years, and that it be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | HOUSING UNIT #4 | 9941 | Correct | ESP |  | Ely | 1987 | 29870 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 149350
1418ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 1418 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | HOUSING UNIT #4 | 9941 | Correct | ESP |  | Ely | 1987 | 29870 | 2015-04-29 | Immediate to Two Years | Currently Critical | 1 | 4000
1426INT2 | BREAK ROOM REMODEL | 1426 | The kitchenette and associated cabinets in the break room are original to the building. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and counter tops are delaminating and failing. This project recommends the replacement of the existing kitchen counters, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. This estimate includes disposal of the existing materials. | BUILDING #12 - TRUSTEE DORMITORY | 9941 | Correct | ESP |  | Ely | 1987 | 3600 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
1423INT2 | FLOORING REPLACEMENT | 1423 | The sheet vinyl flooring in the Infirmary and vinyl composition tile (VCT) in the Library, Chapel and the Visitor's Room is approaching the end of its useful life and has some damage. It is recommended that the flooring in the building be replaced. This project would provide for new 12x12 VCT and sheet vinyl to be installed. Removal and disposal of the old, damaged flooring is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | BUILDING #9 - SCHEDULED SERVICES | 9941 | Correct | ESP |  | Ely | 1987 | 56500 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 204000
1428EXT2 | ROOF REPLACEMENT | 1428 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 15 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2006. It is recommended that this building be re-roofed in the next 4-5 years to be consistent with the roofing program and the end of the warranty period. | BUILDING #14 - GATEHOUSE | 9941 | Correct | ESP |  | Ely | 1987 | 1350 | 2015-04-29 | Four to Ten Years | Long-Term Needs | 3 | 16200
1428ENV1 | NONABSORBENT FINISHES | 1428 | 2012 IBC Section 1210 requires the installation of smooth, hard, nonabsorbent surfaces in the following restroom areas: on floors in toilet and bathing rooms that extends upward onto the walls at least 6 inches, within 2 feet of the sides of urinals and water closets to a height of 4 feet above the floor and in shower compartments to a height not less than 70 inches above the drain inlet. There are several areas of painted gypsum board near fixtures in the restrooms that do not meet these requirements. This project recommends adding tile to the non-compliant areas to comply with this code section. This project or a portion thereof was previously recommended in the FCA report dated 06/04/2002 and 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | BUILDING #14 - GATEHOUSE | 9941 | Correct | ESP |  | Ely | 1987 | 1350 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
1425INT1 | INTERIOR FINISHES | 1425 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years, and that it be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | BUILDING #11 - WAREHOUSE/CENTRAL PLANT | 9941 | Correct | ESP |  | Ely | 1987 | 35370 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 176850
1428EXT1 | EXTERIOR FINISHES | 1428 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sealing and painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years, and that it be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | BUILDING #14 - GATEHOUSE | 9941 | Correct | ESP |  | Ely | 1987 | 1350 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6750
1428ADA1 | ADA ACCESSIBLE COUNTER | 1428 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The Security desk in the Gatehouse has a counter for the employees and public to approach which does not meet current requirements. Section 904.4 of the ADA Standards For Accessible Design states that a portion of the counter surface that is 36" long minimum and 36" high maximum above the finish floor shall be provided. This project will provide an accessible counter space in accordance with this requirement. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | BUILDING #14 - GATEHOUSE | 9941 | Correct | ESP |  | Ely | 1987 | 1350 | 2015-04-29 | Immediate to Two Years | Currently Critical | 1 | 1500
1429HVA1 | HVAC REPLACEMENT | 1429 | The combination in-wall HVAC unit and small electric heater are original to the building and should be scheduled for replacement. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of a new combination unit and electric heater. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | TOWER #1 | 9941 | Correct | ESP |  | Ely | 1987 | 290 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
1425EXT2 | EXTERIOR FINISHES | 1425 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sealing and painting the concrete masonry unit walls, repairing stained and damaged CMU and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years, and that it be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | BUILDING #11 - WAREHOUSE/CENTRAL PLANT | 9941 | Correct | ESP |  | Ely | 1987 | 35370 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 176850
1426EXT2 | EXTERIOR FINISHES | 1426 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sealing and painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years, and that it be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | BUILDING #12 - TRUSTEE DORMITORY | 9941 | Correct | ESP |  | Ely | 1987 | 3600 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18000
1424HVA4 | COMPRESSOR REPLACEMENTS | 1424 | There are 2 compressors on the roof serving the 5 refrigerators and 1 compressor serving the freezers. They were not included in the recent HVAC Replacement projects and should be scheduled for replacement. This project would provide for new condensers to be installed including all required connections to utilities. The estimate includes removal and disposal of the existing equipment. | BUILDING #10 - WORK & RECREATION | 9941 | Correct | ESP |  | Ely | 1987 | 48600 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 115000
1430SEC1 | WINDOW REPLACEMENT | 1430 | The windows in the guard tower are original to the building. They are foggy and difficult to see through. Many of the seals are broken and dust and wind comes through. Due to the security issues of seeing clearly out of the tower, this project recommends replacing the windows. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | TOWER #2 | 9941 | Correct | ESP |  | Ely | 1987 | 290 | 2015-04-29 | Immediate to Two Years | Currently Critical | 1 | 24000
1423EXT2 | EXTERIOR FINISHES | 1423 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sealing and painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years, and that it be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | BUILDING #9 - SCHEDULED SERVICES | 9941 | Correct | ESP |  | Ely | 1987 | 56500 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 282500
1425HVA1 | HEAT EXCHANGER REPLACEMENTS | 1425 | The two shell and tube heat exchangers in the building were installed in 1987 and are original to the building. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of two new plate frame heat exchangers, one for the domestic water and one for the mechanical system. This project includes removal and disposal of the existing units and all required connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | BUILDING #11 - WAREHOUSE/CENTRAL PLANT | 9941 | Correct | ESP |  | Ely | 1987 | 35370 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16000
1429EXT3 | ROOF REPLACEMENT | 1429 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 15 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2006. It is recommended that this building be re-roofed in the next 4-5 years to be consistent with the roofing program and the end of the warranty period. | TOWER #1 | 9941 | Correct | ESP |  | Ely | 1987 | 290 | 2015-04-29 | Four to Ten Years | Long-Term Needs | 3 | 3480
1429PLM2 | WATER HEATER REPLACEMENT | 1429 | There is a 7 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new on-demand electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | TOWER #1 | 9941 | Correct | ESP |  | Ely | 1987 | 290 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
1429PLM1 | RESTROOM FIXTURE REPLACEMENT | 1429 | The restroom fixtures in the Tower are worn and damaged from many years of use including the water closet, lavatory and faucet. Many fixtures are or have been leaking and have caused extensive scaling and staining to the fixtures themselves. It is recommended that all fixtures be replaced with new units. This project includes removal and disposal of the existing fixtures and installation of new fixtures. | TOWER #1 | 9941 | Correct | ESP |  | Ely | 1987 | 290 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
1425EXT3 | EXTERIOR STAIR REPAIRS | 1425 | The 2 sets of exterior concrete stairs on the south side of the building are worn and weathered which has caused significant spalling and cracking. This project recommends repairing the steps to ensure that they remain code compliant as well as to prevent further damage. Chapter 10, Section1012 of the 2012 IBC was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | BUILDING #11 - WAREHOUSE/CENTRAL PLANT | 9941 | Correct | ESP |  | Ely | 1987 | 35370 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
1429INT1 | INTERIOR FINISHES | 1429 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | TOWER #1 | 9941 | Correct | ESP |  | Ely | 1987 | 290 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5800
1424HVA3 | BOILER REPLACEMENT | 1424 | The Kewanee steam boiler servicing the building was installed almost 30 years ago and should be scheduled for replacement. The life expectancy of this unit is 20 to 25 years with proper maintenance and water treatment programs. Replacement parts for performing routine and emergency maintenance are hard to find for this older equipment. The controls and mixing valves should be replaced for the same reasons. This project would provide for the removal and disposal of the existing boiler, controls and mixing valves and replacement with new equipment including all required connections to utilities and equipment. The estimate is based on a 150 PSI steam boiler, associated equipment and new equipment to replace the electric heaters. The existing chemical water treatment system will need to be tested and adjusted once equipment is operational. $2,000 is included in this estimate for testing of the chemical water treatment system. | BUILDING #10 - WORK & RECREATION | 9941 | Correct | ESP |  | Ely | 1987 | 48600 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 125000
1430PLM1 | RESTROOM FIXTURE REPLACEMENT | 1430 | The restroom fixtures in the Tower are worn and damaged from many years of use including the water closet, lavatory and faucet. Many fixtures are or have been leaking and have caused extensive scaling and staining to the fixtures themselves. It is recommended that all fixtures be replaced with new units. This project includes removal and disposal of the existing fixtures and installation of new fixtures. | TOWER #2 | 9941 | Correct | ESP |  | Ely | 1987 | 290 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
1430INT1 | INTERIOR FINISHES | 1430 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | TOWER #2 | 9941 | Correct | ESP |  | Ely | 1987 | 290 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5800
1430PLM2 | WATER HEATER REPLACEMENT | 1430 | There is a 7 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new on-demand electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | TOWER #2 | 9941 | Correct | ESP |  | Ely | 1987 | 290 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
1430HVA1 | HVAC REPLACEMENT | 1430 | The combination in-wall HVAC unit and small electric heater are original to the building and should be scheduled for replacement. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of a new combination unit and electric heater. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | TOWER #2 | 9941 | Correct | ESP |  | Ely | 1987 | 290 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
1423INT5 | JANITORS CLOSET REPAIRS | 1423 | The mop sinks in the Janitors Closets are mounted adjacent to gypsum board and are showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. Typical of seven Janitors Closets. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | BUILDING #9 - SCHEDULED SERVICES | 9941 | Correct | ESP |  | Ely | 1987 | 56500 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9800
1424PLM1 | GREASE INTERCEPTOR REPLACEMENT | 1424 | The underground grease interceptor to the west of the building is not currently operating correctly. Maintenance staff reported that the metal structure is two thirds disintegrated underground. This project would provide for the purchase and installation of a new grease interceptor and connection to the existing sewer system. | BUILDING #10 - WORK & RECREATION | 9941 | Correct | ESP |  | Ely | 1987 | 48600 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
1425EXT5 | ROOF REPLACEMENT | 1425 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 15 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2006. It is recommended that this building be re-roofed in the next 4-5 years to be consistent with the roofing program and the end of the warranty period. | BUILDING #11 - WAREHOUSE/CENTRAL PLANT | 9941 | Correct | ESP |  | Ely | 1987 | 35370 | 2015-04-29 | Four to Ten Years | Long-Term Needs | 3 | 424440
1425ADA1 | ADA RESTROOM REMODELS | 1425 | The existing Staff and Inmate restrooms in the building do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for remodeling two restrooms into ADA compliant restrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | BUILDING #11 - WAREHOUSE/CENTRAL PLANT | 9941 | Correct | ESP |  | Ely | 1987 | 35370 | 2015-04-29 | Immediate to Two Years | Currently Critical | 1 | 30000
1425PLM1 | WATER HEATER REPLACEMENT | 1425 | There is a 30 gallon electric water heater in the Auto Shop. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed for more efficient use of energy. This estimate includes: 100 feet of gas pipe, fittings, couplers, and labor for installation. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | BUILDING #11 - WAREHOUSE/CENTRAL PLANT | 9941 | Correct | ESP |  | Ely | 1987 | 35370 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
1425SFT1 | EXIT SIGN UPGRADE | 1425 | The existing exit signs in this building are older types and should be replaced with new self-illuminated or LED style signs with battery-backed internal systems. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 06/04/2002 and 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | BUILDING #11 - WAREHOUSE/CENTRAL PLANT | 9941 | Correct | ESP |  | Ely | 1987 | 35370 | 2015-04-29 | Immediate to Two Years | Currently Critical | 1 | 5000
1424EXT2 | EXTERIOR FINISHES | 1424 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sealing and painting the concrete masonry unit walls, repairing cracked and damaged CMU and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years, and that it be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | BUILDING #10 - WORK & RECREATION | 9941 | Correct | ESP |  | Ely | 1987 | 48600 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 243000
1424INT1 | INTERIOR FINISHES | 1424 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years, and that it be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | BUILDING #10 - WORK & RECREATION | 9941 | Correct | ESP |  | Ely | 1987 | 48600 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 243000
1424INT2 | CULINARY FLOORING REPLACEMENT | 1424 | The epoxy floor covering in the Culinary is worn and damaged and should be resurfaced. This project provides for cleaning and repairing the existing floor, applying a bonding agent, pouring a new polymer surface and applying an appropriate finish product. The product must meet the requirements of the health department for food service and preparation. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | BUILDING #10 - WORK & RECREATION | 9941 | Correct | ESP |  | Ely | 1987 | 48600 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 250000
1424INT5 | JANITORS CLOSET REPAIRS | 1424 | The mop sinks in the Janitors Closets are mounted adjacent to gypsum board and are showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. Typical of two Janitors Closets. | BUILDING #10 - WORK & RECREATION | 9941 | Correct | ESP |  | Ely | 1987 | 48600 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2800
1424EXT3 | ROOF REPLACEMENT | 1424 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 15 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2006. It is recommended that this building be re-roofed in the next 4-5 years to be consistent with the roofing program and the end of the warranty period. | BUILDING #10 - WORK & RECREATION | 9941 | Correct | ESP |  | Ely | 1987 | 48600 | 2015-04-29 | Four to Ten Years | Long-Term Needs | 3 | 583200
1424ADA1 | ADA RESTROOM REMODELS | 1424 | There are 5 restrooms throughout the building that do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for construction of five accessible restrooms including two restrooms in the gymnasium, the inmate restroom in the Culinary and two restrooms in the Maintenance Shop. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | BUILDING #10 - WORK & RECREATION | 9941 | Correct | ESP |  | Ely | 1987 | 48600 | 2015-04-29 | Immediate to Two Years | Currently Critical | 1 | 125000
1421SEC2 | ELECTRONIC LOCKS/ CONTROLS REPLACEMENT | 1421 | The controls for the door locks and security systems are built on a custom panel and interface. The controls are difficult to repair, parts are becoming increasingly difficult to locate, and the type and configuration of the switches are limited by the physical size of the consoles. This project recommends replacing the existing mechanical switching system with a computer system and electronic interface. Remote costs and secure facility allowance were included in the project estimates. This project or a portion thereof was previously recommended in the FCA report dated 06/04/2002 and 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | HOUSING UNIT #7 | 9941 | Correct | ESP |  | Ely | 1989 | 29870 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 565000
1428INT2 | JANITORS CLOSET REPAIRS | 1428 | The mop sink in the Janitors Closet is mounted adjacent to painted plywood and is showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | BUILDING #14 - GATEHOUSE | 9941 | Correct | ESP |  | Ely | 1987 | 1350 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
1427INT1 | INTERIOR FINISHES | 1427 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years, and that it be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | BUILDING #13 - ARMORY | 9941 | Correct | ESP |  | Ely | 1987 | 1680 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8400
1424SFT2 | ANSUL SYSTEM REPLACEMENT | 1424 | The Ansul fire suppression system in the Culinary is approaching the end of its useful life. This project recommends replacing the existing suppression system and implementing a comprehensive testing and service schedule. Removal and disposal of the existing system is included in the estimate. | BUILDING #10 - WORK & RECREATION | 9941 | Correct | ESP |  | Ely | 1987 | 48600 | 2015-04-29 | Immediate to Two Years | Currently Critical | 1 | 43200
1424ELE1 | ELECTRICAL UPGRADE | 1424 | This building was constructed before the high demand for electrical services were needed for computers and other electrical devices. As time has progressed, the buildings electrical demand and system has changed. It is utilized to its current maximum potential. The electrical panels and receptacles are at their limit. It is recommended the entire system be upgraded to meet the evolving needs of the building. | BUILDING #10 - WORK & RECREATION | 9941 | Correct | ESP |  | Ely | 1987 | 48600 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 972000
1424HVA2 | HEAT EXCHANGER REPLACEMENT | 1424 | The two shell and tube heat exchangers in the building were installed in 1987 and are original to the building. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of two new plate frame heat exchangers, one for the domestic water and one for the mechanical system. This project includes removal and disposal of the existing units and all required connections to utilities. | BUILDING #10 - WORK & RECREATION | 9941 | Correct | ESP |  | Ely | 1987 | 48600 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16000
1424SFT1 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 1424 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 06/04/2002 and 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | BUILDING #10 - WORK & RECREATION | 9941 | Correct | ESP |  | Ely | 1987 | 48600 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12500
1424INT4 | CLOTHES DRYER REPLACEMENTS | 1424 | Four of the commercial tumbler dryers in the laundry are original to the building and are troublesome and problematic to operate. Considering the age of the machines and the evolving needs of the facility it is recommended to replace them. This project provides for removal and disposal of the existing tumbler dryers with new units. A total of 4 dryers was used for this estimate. | BUILDING #10 - WORK & RECREATION | 9941 | Correct | ESP |  | Ely | 1987 | 48600 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 32000
1428PLM1 | WATER HEATER REPLACEMENT | 1428 | There is a 30 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed for more efficient use of energy. This estimate includes: 100 feet of gas pipe, fittings, couplers, and labor for installation. Removal and disposal of the existing equipment is included in this estimate. | BUILDING #14 - GATEHOUSE | 9941 | Correct | ESP |  | Ely | 1987 | 1350 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
1426ADA2 | TDD INSTALLATION | 1426 | There is telephone in the building for inmates that is not equipped with a telecommunications device for the deaf (TDD). In order to comply with ADA requirements it is recommended to install a TDD system in the non-contact visitation area. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | BUILDING #12 - TRUSTEE DORMITORY | 9941 | Correct | ESP |  | Ely | 1987 | 3600 | 2015-04-29 | Immediate to Two Years | Currently Critical | 1 | 20000
1426EXT3 | ROOF REPLACEMENT | 1426 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 15 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2006. It is recommended that this building be re-roofed in the next 4-5 years to be consistent with the roofing program and the end of the warranty period. | BUILDING #12 - TRUSTEE DORMITORY | 9941 | Correct | ESP |  | Ely | 1987 | 3600 | 2015-04-29 | Four to Ten Years | Long-Term Needs | 3 | 43200
1425HVA2 | BOILER BURNER REPLACEMENTS | 1425 | The three boilers are original to the building. The burner assemblies have become problematic and parts are hard to come by. They are reaching the end of their expected lifetime. This project provides for the removal and disposal of the existing burners and installation of new burner assemblies on all three boilers. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | BUILDING #11 - WAREHOUSE/CENTRAL PLANT | 9941 | Correct | ESP |  | Ely | 1987 | 35370 | 2015-04-29 | Immediate to Two Years | Currently Critical | 1 | 75000
1429EXT2 | EXTERIOR FINISHES | 1429 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete walls, painting the doors and trim and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | TOWER #1 | 9941 | Correct | ESP |  | Ely | 1987 | 290 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5800
1424ENV2 | TRASH COMPACTOR REPLACEMENT | 1424 | The two existing trash compactors are original to the building and due for replacement. The compactors are rusted, have been damaged by heavy equipment and do not function properly anymore. This project would provide for replacing the existing compactors with two new 30 yard self-contained trash compactors. | BUILDING #10 - WORK & RECREATION | 9941 | Correct | ESP |  | Ely | 1987 | 48600 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 150000
1423ADA3 | ADA RESTROOM REMODEL | 1423 | The existing restrooms in the Law Library do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for remodeling the Men's and Women's restrooms into ADA compliant restrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | BUILDING #9 - SCHEDULED SERVICES | 9941 | Correct | ESP |  | Ely | 1987 | 56500 | 2015-04-29 | Immediate to Two Years | Currently Critical | 1 | 30000
1432EXT3 | ROOF REPLACEMENT | 1432 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 15 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2006. It is recommended that this building be re-roofed in the next 4-5 years to be consistent with the roofing program and the end of the warranty period. | TOWER #4 | 9941 | Correct | ESP |  | Ely | 1987 | 290 | 2015-04-29 | Four to Ten Years | Long-Term Needs | 3 | 3480
1422SEC2 | ELECTRONIC LOCKS/ CONTROLS REPLACEMENT | 1422 | The controls for the door locks and security systems are built on a custom panel and interface. The controls are difficult to repair, parts are becoming increasingly difficult to locate, and the type and configuration of the switches are limited by the physical size of the consoles. This project recommends replacing the existing mechanical switching system with a computer system and electronic interface. Remote costs and secure facility allowance were included in the project estimates. This project or a portion thereof was previously recommended in the FCA report dated 06/04/2002 and 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | HOUSING UNIT #8 | 9941 | Correct | ESP |  | Ely | 1989 | 29870 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 565000
1423INT7 | BREAK ROOM REMODELS | 1423 | The kitchenette and associated cabinets in the employee break rooms are original to the building. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and counter tops are delaminating and failing. This project recommends the replacement of the existing kitchen counters, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. This estimate includes disposal of the existing materials. | BUILDING #9 - SCHEDULED SERVICES | 9941 | Correct | ESP |  | Ely | 1987 | 56500 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 125000
1423ENR2 | LIGHTING UPGRADE | 1423 | The existing lighting fixtures are the older T-8 type which are of poor quality, and are failing prematurely. This project will upgrade fixtures to higher efficiency units with a longer life cycle. LED lamps are suggested to replace the T-8 lamps currently installed. Occupancy sensors will be installed in restrooms, conference rooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | BUILDING #9 - SCHEDULED SERVICES | 9941 | Correct | ESP |  | Ely | 1987 | 56500 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 84750
1422ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 1422 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | HOUSING UNIT #8 | 9941 | Correct | ESP |  | Ely | 1989 | 29870 | 2015-04-29 | Immediate to Two Years | Currently Critical | 1 | 4000
1422EXT4 | ROOF REPLACEMENT | 1422 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 15 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2006. It is recommended that this building be re-roofed in the next 4-5 years to be consistent with the roofing program and the end of the warranty period. | HOUSING UNIT #8 | 9941 | Correct | ESP |  | Ely | 1989 | 29870 | 2015-04-29 | Four to Ten Years | Long-Term Needs | 3 | 358440
1422INT1 | INTERIOR FINISHES | 1422 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that it be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | HOUSING UNIT #8 | 9941 | Correct | ESP |  | Ely | 1989 | 29870 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 149350
1430EXT4 | ROOF REPLACEMENT | 1430 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 15 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2006. It is recommended that this building be re-roofed in the next 4-5 years to be consistent with the roofing program and the end of the warranty period. | TOWER #2 | 9941 | Correct | ESP |  | Ely | 1987 | 290 | 2015-04-29 | Four to Ten Years | Long-Term Needs | 3 | 3480
1423HVA3 | HEAT EXCHANGER REPLACEMENTS | 1423 | The two shell and tube heat exchangers in the building were installed in 1987 and are original to the building. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of two new plate frame heat exchangers, one for the domestic water and one for the mechanical system. This project includes removal and disposal of the existing units and all required connections to utilities. | BUILDING #9 - SCHEDULED SERVICES | 9941 | Correct | ESP |  | Ely | 1987 | 56500 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16000
1429SEC1 | WINDOW REPLACEMENT | 1429 | The windows in the guard tower are original to the building. They are foggy and difficult to see through. Many of the seals are broken and dust and wind comes through. Due to the security issues of seeing clearly out of the tower, this project recommends replacing the windows. Removal and disposal of the existing windows is included in this estimate. | TOWER #1 | 9941 | Correct | ESP |  | Ely | 1987 | 290 | 2015-04-29 | Immediate to Two Years | Currently Critical | 1 | 24000
1423INT6 | INTERIOR FINISHES | 1423 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 5-6 years and that it be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | BUILDING #9 - SCHEDULED SERVICES | 9941 | Correct | ESP |  | Ely | 1987 | 56500 | 2015-04-29 | Four to Ten Years | Long-Term Needs | 3 | 282500
1423INT4 | HOSPITAL CRASH RAIL REPLACEMENT | 1423 | The medical wing has a crash guard system installed to protect the walls from damage from gurneys and medical equipment. Over the years, it has sustained moderate damage and is approaching the end of its useful life. This project provides for the replacement of the existing system with a new one, including vinyl cover and aluminum retaining clips. This project or a portion thereof was previously recommended in the FCA report dated 06/04/2002 and 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | BUILDING #9 - SCHEDULED SERVICES | 9941 | Correct | ESP |  | Ely | 1987 | 56500 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
1423ELE1 | ELECTRICAL UPGRADE | 1423 | This building was constructed before the high demand for electrical services were needed for computers and other electrical devices. As time has progressed, the buildings electrical demand and system has changed. It is utilized to its current maximum potential. The electrical panels and receptacles are at their limit. It is recommended the entire system be upgraded to meet the evolving needs of the building. | BUILDING #9 - SCHEDULED SERVICES | 9941 | Correct | ESP |  | Ely | 1987 | 56500 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1130000
1423EXT4 | INTERIOR WALL INSULATION | 1423 | The building is constructed of concrete masonry units (CMU) with minimal insulation. The north facing exterior wall does not provide enough insulation in the colder months of the year. Maintenance staff has had ongoing difficulties balancing the heating to provide a comfortable work environment. This project recommends adding 2" rigid insulation, gypsum board and paint on the interior of the wall. The estimate is based on $12.00 per square foot of wall space. This project should be implemented concurrently with the Window Replacement project. | BUILDING #9 - SCHEDULED SERVICES | 9941 | Correct | ESP |  | Ely | 1987 | 56500 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 43200
1423PLM1 | BACKFLOW PREVENTER REPLACEMENT | 1423 | There are two backflow preventers in the mechanical room. They are both leaking and should be scheduled for replacement. This project would provide for replacing both backflow preventers. | BUILDING #9 - SCHEDULED SERVICES | 9941 | Correct | ESP |  | Ely | 1987 | 56500 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
1423ADA1 | ADA SIGNAGE | 1423 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 06/04/2002 and 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | BUILDING #9 - SCHEDULED SERVICES | 9941 | Correct | ESP |  | Ely | 1987 | 56500 | 2015-04-29 | Immediate to Two Years | Currently Critical | 1 | 7500
1423ADA2 | ADA PROJECTS | 1423 | The visitors area has eight non-contact visiting rooms. Visitors and inmates communicate via telephones. One set of the non-contact rooms should be equipped with telecommunications devices for the deaf and hearing impaired. This project includes two devices, associated power and wiring, and security devices to lock down or remove the devices when not in use. Funds are also included to remodel the counter at the guard observation area to comply with the proper height and configuration under accessibility requirements. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 06/04/2002 and 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | BUILDING #9 - SCHEDULED SERVICES | 9941 | Correct | ESP |  | Ely | 1987 | 56500 | 2015-04-29 | Immediate to Two Years | Currently Critical | 1 | 22000
1426INT1 | INTERIOR FINISHES | 1426 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years, and that it be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | BUILDING #12 - TRUSTEE DORMITORY | 9941 | Correct | ESP |  | Ely | 1987 | 3600 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18000
1427PLM1 | WATER HEATER REPLACEMENT | 1427 | There is a 30 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed for more efficient use of energy. This estimate includes: 100 feet of gas pipe, fittings, couplers, and labor for installation. Removal and disposal of the existing equipment is included in this estimate. | BUILDING #13 - ARMORY | 9941 | Correct | ESP |  | Ely | 1987 | 1680 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
1422EXT2 | EXTERIOR FINISHES | 1422 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sealing and painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years, and that it be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | HOUSING UNIT #8 | 9941 | Correct | ESP |  | Ely | 1989 | 29870 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 149350
1431HVA1 | HVAC REPLACEMENT | 1431 | The combination in-wall HVAC unit and small electric heater are original to the building and should be scheduled for replacement. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of a new combination unit and electric heater. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | TOWER #3 | 9941 | Correct | ESP |  | Ely | 1987 | 290 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
1430EXT2 | EXTERIOR FINISHES | 1430 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete walls, painting the doors and trim and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | TOWER #2 | 9941 | Correct | ESP |  | Ely | 1987 | 290 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5800
1431EXT2 | EXTERIOR FINISHES | 1431 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete walls, painting the doors and trim and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | TOWER #3 | 9941 | Correct | ESP |  | Ely | 1987 | 290 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5800
1431PLM1 | RESTROOM FIXTURE REPLACEMENT | 1431 | The restroom fixtures in the Tower are worn and damaged from many years of use including the water closet, lavatory and faucet. Many fixtures are or have been leaking and have caused extensive scaling and staining to the fixtures themselves. It is recommended that all fixtures be replaced with new units. This project includes removal and disposal of the existing fixtures and installation of new fixtures. | TOWER #3 | 9941 | Correct | ESP |  | Ely | 1987 | 290 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
1421ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 1421 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | HOUSING UNIT #7 | 9941 | Correct | ESP |  | Ely | 1989 | 29870 | 2015-04-29 | Immediate to Two Years | Currently Critical | 1 | 4000
1421HVA1 | HEAT EXCHANGER REPLACEMENTS | 1421 | The two shell and tube heat exchangers in the building were installed in 1987 and are original to the building. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of two new plate frame heat exchangers, one for the domestic water and one for the mechanical system. This project includes removal and disposal of the existing units and all required connections to utilities. | HOUSING UNIT #7 | 9941 | Correct | ESP |  | Ely | 1989 | 29870 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16000
1421PLM2 | BACKFLOW PREVENTER REPLACEMENT | 1421 | There is a backflow preventer on the main water line coming into the building. It is leaking and should be scheduled for replacement. This project would provide for replacing the backflow preventer. | HOUSING UNIT #7 | 9941 | Correct | ESP |  | Ely | 1989 | 29870 | 2015-04-29 | Immediate to Two Years | Currently Critical | 1 | 2000
1421PLM1 | WATER TREATMENT SYSTEM REPLACEMENT | 1421 | The existing water softening/ treatment systems in the building are currently not operational. They are original to the building and approaching the end of their lifecycles. Failure of the equipment causes wear and tear on the domestic water supply lines, plumbing fixtures and HVAC equipment. This project would provide for the replacement of the existing water softeners/ treatment systems with new equipment. This project would also provide for a chemical treatment program including an updated chemicals control system, service and employee training provided by a qualified water treatment vendor. | HOUSING UNIT #7 | 9941 | Correct | ESP |  | Ely | 1989 | 29870 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
1421EXT4 | ROOF REPLACEMENT | 1421 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 15 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2006. It is recommended that this building be re-roofed in the next 4-5 years to be consistent with the roofing program and the end of the warranty period. | HOUSING UNIT #7 | 9941 | Correct | ESP |  | Ely | 1989 | 29870 | 2015-04-29 | Four to Ten Years | Long-Term Needs | 3 | 358440
1423EXT3 | WINDOW REPLACEMENT | 1423 | The existing windows in this building are older dual pane wire construction. Many have broken seals and all are not energy efficient. This project would provide for the removal and replacement of the windows with new dual pane security rated window systems with higher insulation ratings. This project should be implemented concurrently with the Interior Wall Insulation project. | BUILDING #9 - SCHEDULED SERVICES | 9941 | Correct | ESP |  | Ely | 1987 | 56500 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 69600
1421INT1 | INTERIOR FINISHES | 1421 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that it be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | HOUSING UNIT #7 | 9941 | Correct | ESP |  | Ely | 1989 | 29870 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 149350
1423EXT5 | ROOF REPLACEMENT | 1423 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 15 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2006. It is recommended that this building be re-roofed in the next 4-5 years to be consistent with the roofing program and the end of the warranty period. | BUILDING #9 - SCHEDULED SERVICES | 9941 | Correct | ESP |  | Ely | 1987 | 56500 | 2015-04-29 | Four to Ten Years | Long-Term Needs | 3 | 678000
1431EXT3 | ROOF REPLACEMENT | 1431 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 15 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2006. It is recommended that this building be re-roofed in the next 4-5 years to be consistent with the roofing program and the end of the warranty period. | TOWER #3 | 9941 | Correct | ESP |  | Ely | 1987 | 290 | 2015-04-29 | Four to Ten Years | Long-Term Needs | 3 | 3480
1431PLM2 | WATER HEATER REPLACEMENT | 1431 | There is a 7 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new on-demand electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | TOWER #3 | 9941 | Correct | ESP |  | Ely | 1987 | 290 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
1431INT1 | INTERIOR FINISHES | 1431 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | TOWER #3 | 9941 | Correct | ESP |  | Ely | 1987 | 290 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5800
1431SEC1 | WINDOW REPLACEMENT | 1431 | The windows in the guard tower are original to the building. They are foggy and difficult to see through. Many of the seals are broken and dust and wind comes through. Due to the security issues of seeing clearly out of the tower, this project recommends replacing the windows. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | TOWER #3 | 9941 | Correct | ESP |  | Ely | 1987 | 290 | 2015-04-29 | Immediate to Two Years | Currently Critical | 1 | 24000
1432EXT2 | EXTERIOR FINISHES | 1432 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete walls, painting the doors and trim and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | TOWER #4 | 9941 | Correct | ESP |  | Ely | 1987 | 290 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5800
1432SEC1 | WINDOW REPLACEMENT | 1432 | The windows in the guard tower are original to the building. They are foggy and difficult to see through. Many of the seals are broken and dust and wind comes through. Due to the security issues of seeing clearly out of the tower, this project recommends replacing the windows. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | TOWER #4 | 9941 | Correct | ESP |  | Ely | 1987 | 290 | 2015-04-29 | Immediate to Two Years | Currently Critical | 1 | 24000
1432INT1 | INTERIOR FINISHES | 1432 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | TOWER #4 | 9941 | Correct | ESP |  | Ely | 1987 | 290 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5800
1423INT3 | COUNTERTOP REPLACEMENT | 1423 | The countertops throughout the building are showing signs of wear and tear particularly at the Formica edges and corners. The quality of construction and installation were inadequate for the high usage at these facilities, and the counter tops are delaminating and failing. This project recommends the replacement of the existing damaged countertops with heavy duty, quality finishes. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. This estimate includes disposal of the existing materials. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | BUILDING #9 - SCHEDULED SERVICES | 9941 | Correct | ESP |  | Ely | 1987 | 56500 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
1421EXT2 | EXTERIOR FINISHES | 1421 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sealing and painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years, and that it be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | HOUSING UNIT #7 | 9941 | Correct | ESP |  | Ely | 1989 | 29870 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 149350
2242EXT2 | FASCIA REPLACEMENT | 2242 | The wood fascia around the eaves of the roof is worn and weathered. This project would provide for removal and disposal of the existing wood fascia and replacement with a new primed and painted wood fascia board. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | EQUIPMENT STORAGE | 9941 | Correct | ESP |  | Ely | 1999 | 400 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
2242INT1 | INTERIOR FINISHES | 2242 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | EQUIPMENT STORAGE | 9941 | Correct | ESP |  | Ely | 1999 | 400 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
2242EXT3 | EXTERIOR DOOR REPLACEMENT | 2242 | The entrance to the building is a single leaf, commercial grade metal door assembly. The door and frame is old and damaged and are in need of replacement. This project would provide for the installation of a new metal door assembly. Painting of the new door and removal and disposal of the old door is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | EQUIPMENT STORAGE | 9941 | Correct | ESP |  | Ely | 1999 | 400 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
2242EXT1 | EXTERIOR FINISHES | 2242 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, replacing missing screw attachments, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 2-3 years and that it be scheduled on a cyclical basis based on environmental conditions. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | EQUIPMENT STORAGE | 9941 | Correct | ESP |  | Ely | 1999 | 400 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
2729EXT1 | EXTERIOR FINISHES | 2729 | It is important to maintain the finish, weather resistance and appearance of the water tank. This project would provide for the painting of the water tank to maintain it in a good, weather tight condition. It is recommended that this project be implemented in the next 2-3 years and that it be scheduled on a cyclical basis based on environmental conditions. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | WATER TANK | 9941 | Correct | ESP |  | Ely | 1987 | 1488 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14880
9941SIT7 | GATE OPERATOR REPLACEMENTS | 9941 | There is an automatic gate operator in the yard between the Administrative building and the Housing units and two at the Sally Port. The gate operators are malfunctioning, have been problematic, and have difficulty opening and closing the gates. This project recommends replacing the three gate operators with high quality operators that can handle heavy traffic as well as servicing the gates and related hardware to ensure prolonged operation. The gate operators will be required to meet UL Standard 325, per NRS 405.270. | ELY STATE PRISON SITE | 9941 | Correct | ESP |  | Ely | 1987 | 0 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
9941SIT4 | CONCRETE SIDEWALK REPAIRS | 9941 | The concrete sidewalks are in generally good condition, but there are several areas that require attention. Deterioration, spalling and cracking has occurred, mainly from exposure to the weather. In some areas the sidewalks have lost their texture and cause a slipping hazard. This project would provide for the removal and replacement of the damaged concrete sidewalks. 10,000 SF of 4" thick concrete sidewalk was used for this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | ELY STATE PRISON SITE | 9941 | Correct | ESP |  | Ely | 1987 | 0 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 100000
9941SIT8 | EXTERIOR SOLAR SITE LIGHTING UPGRADE | 9941 | There are approximately 20 existing light poles around the site not including the high mast lighting within the secured area. These older light fixtures are not energy efficient and several of the concrete bases are severely deteriorated. This project would provide for the installation of 20 solar powered LED exterior light fixtures, 20 foot tall poles and 30" diameter raised concrete bases. This installation will eliminate the need for trenching and electrical connections. Some of the existing poles and bases may be acceptable to re-use. If so, the estimate can be reduced accordingly. | ELY STATE PRISON SITE | 9941 | Correct | ESP |  | Ely | 1987 | 0 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 130000
9941HVA3 | HVAC AIR HANDLER REPLACEMENT - PHASE 2 | 9941 | The HVAC roof top air handling units are over 20 years old. There are 24 units throughout the site, of which this phase covers the remaining 12 units. They are not energy efficient, need constant repairs and have reached the end of their expected and useful life. This project would provide for the installation of twelve new HVAC packaged units and cleaning of the existing duct work. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. This project is in design under CIP 15-M01 and construction is scheduled to begin on 07/11/2016. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | ELY STATE PRISON SITE | 9941 | Correct | ESP |  | Ely | 1987 | 0 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3500000
9941SEC3 | STENTOFON SWITCH REPLACEMENT | 9941 | At the time of the survey the staff reported that the Stentofon communications system was not operating properly. This project provides funding to replace the Stentofon communications switch that has failed and is causing problems with the system. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | ELY STATE PRISON SITE | 9941 | Correct | ESP |  | Ely | 1987 | 0 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
9941SIT11 | FENCE FOOTING REPAIR | 9941 | The concrete footing for the perimeter security fencing has many areas that are in need of repair. The concrete is cracking and deteriorating and could eventually compromise the structural integrity of the fencing. This project would provide for repair or replacement of damaged sections of concrete as needed. | ELY STATE PRISON SITE | 9941 | Correct | ESP |  | Ely | 1987 | 0 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 60000
9941SIT2 | SITE DRAINAGE AT MANHOLES | 9941 | The Ely State Prison site has several manholes with 4160V equipment installed below grade and the drainage doesn't prevent water accumulations. Due to their location, staff are required to manually inspect and, when needed, lower sump pumps into the hole to drain the excess water. This creates a potential electrocution hazard. This project provides funding to install catch basins, French drains and additional drain piping as needed to carry the water away from the manholes. This project or a portion thereof was previously recommended in the FCA report dated 06/04/2002 and 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | ELY STATE PRISON SITE | 9941 | Correct | ESP |  | Ely | 1987 | 0 | 2015-04-29 | Immediate to Two Years | Currently Critical | 1 | 100000
9941HVA4 | ROOFTOP PACKAGED UNIT REPLACEMENT | 9941 | There are 13 small HVAC roof top units on the buildings that were not addressed by the recent HVAC Replacement projects. These units were installed in 1989. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of 13 new HVAC packaged units and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | ELY STATE PRISON SITE | 9941 | Correct | ESP |  | Ely | 1987 | 0 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 156000
9941SIT9 | SIDEWALK REPLACEMENT | 9941 | The sidewalks serving the entrances of Housing Units 5-8 are deteriorated and failing. In some areas cracks wider than four inches have been identified, and there is settling, spalling and ravelling in many locations. This project addresses removal and replacement of existing sidewalks as needed. 5,000 SF of 4" thick concrete sidewalk was used for this estimate. | ELY STATE PRISON SITE | 9941 | Correct | ESP |  | Ely | 1987 | 0 | 2015-04-29 | Immediate to Two Years | Currently Critical | 1 | 50000
9941HVA5 | EXHAUST FAN REPLACEMENTS | 9941 | The existing exhaust fans that serve the buildings are original equipment and are not providing adequate ventilation. There are 4 large kitchen hoods and 17 smaller exhaust fans on the housing units that should be scheduled for replacement. This project would provide for the removal of the existing exhaust fan assemblies and the purchase and installation of new exhaust fan assemblies including connections to utilities. | ELY STATE PRISON SITE | 9941 | Correct | ESP |  | Ely | 1987 | 0 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
9941SIT10 | ASPHALT CONCRETE REPLACEMENT | 9941 | The asphalt on the south side of the Warehouse near the fuel pumps is failing, with significant alligatoring, settling and cracks observed. The area sees high traffic volume and is used by heavy equipment which has contributed to the deterioration. This project covers the removal and replacement of the existing asphalt for the area. 4,000 square feet was used to generate this estimate. | ELY STATE PRISON SITE | 9941 | Correct | ESP |  | Ely | 1987 | 0 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 40000
9941SIT3 | IRRIGATION SYSTEM ADJUSTMENTS | 9941 | The existing irrigation system is spraying water on the side of the buildings inside the secured area, especially during windy conditions. There is noticeable damage to the exterior walls which can lead to extreme damage and possible mold growth if not addressed soon. This project would provide for the relocation of the sprinklers away from the buildings. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | ELY STATE PRISON SITE | 9941 | Correct | ESP |  | Ely | 1987 | 0 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
9941PLM1 | PLUMBING VALVE REPLACEMENTS | 9941 | The majority of the plumbing isolation valves on the site are gate valves original to the building. Many of these valves no longer completely stop water when closed. This project will provide funding to replace the faulty gate valves with ball valves. 18 valves was used for this estimate. This project or a portion thereof was previously recommended in the FCA report dated 06/04/2002 and 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | ELY STATE PRISON SITE | 9941 | Correct | ESP |  | Ely | 1987 | 0 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18000
9941SIT6 | CRACK FILL & SEAL ASPHALT PAVING | 9941 | It is important to maintain the asphalt concrete paving and concrete drainage swales on the site. This project would provide for replacing the swales and crack filling and sealing of the paving site wide including access roads, parking areas, the perimeter road and maintenance yard. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 174,240 square feet of asphalt area was used to generate this estimate. | ELY STATE PRISON SITE | 9941 | Correct | ESP |  | Ely | 1987 | 0 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 104544
0123INT1 | INTERIOR FINISHES | 0123 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years, and that it be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | HOUSING UNIT #2 | 9941 | Correct | ESP |  | Ely | 1987 | 29870 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 149350
0123SEC2 | ELECTRONIC LOCKS/ CONTROLS REPLACEMENT | 0123 | The controls for the door locks and security systems are built on a custom panel and interface. The controls are difficult to repair, parts are becoming increasingly difficult to locate, and the type and configuration of the switches are limited by the physical size of the consoles. This project recommends replacing the existing mechanical switching system with a computer system and electronic interface. Remote costs and secure facility allowance were included in the project estimates. This project or a portion thereof was previously recommended in the FCA report dated 06/04/2002 and 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | HOUSING UNIT #2 | 9941 | Correct | ESP |  | Ely | 1987 | 29870 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 565000
0123EXT2 | EXTERIOR FINISHES | 0123 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sealing and painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years, and that it be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | HOUSING UNIT #2 | 9941 | Correct | ESP |  | Ely | 1987 | 29870 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 149350
0123ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0123 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | HOUSING UNIT #2 | 9941 | Correct | ESP |  | Ely | 1987 | 29870 | 2015-04-29 | Immediate to Two Years | Currently Critical | 1 | 4000
0123EXT3 | ROOF REPLACEMENT | 0123 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 15 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2008. It is recommended that this building be re-roofed in the next 6-7 years to be consistent with the roofing program and the end of the warranty period. | HOUSING UNIT #2 | 9941 | Correct | ESP |  | Ely | 1987 | 29870 | 2015-04-29 | Four to Ten Years | Long-Term Needs | 3 | 358440
0699HVA1 | HEAT EXCHANGER REPLACEMENTS | 0699 | The two shell and tube heat exchangers in the building were installed in 1987 and are original to the building. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of two new plate frame heat exchangers, one for the domestic water and one for the mechanical system. This project includes removal and disposal of the existing units and all required connections to utilities. | HOUSING UNIT #1 | 9941 | Correct | ESP |  | Ely | 1987 | 29870 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16000
0699ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0699 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | HOUSING UNIT #1 | 9941 | Correct | ESP |  | Ely | 1987 | 29870 | 2015-04-29 | Immediate to Two Years | Currently Critical | 1 | 4000
0699PLM1 | WATER TREATMENT SYSTEM REPLACEMENT | 0699 | The existing water softening/ treatment systems in the building are currently not operational. They are original to the building and approaching the end of their lifecycles. Failure of the equipment causes wear and tear on the domestic water supply lines, plumbing fixtures and HVAC equipment. This project would provide for the replacement of the existing water softeners/ treatment systems with new equipment. This project would also provide for a chemical treatment program including an updated chemicals control system, service, and employee training provided by a qualified water treatment vendor. | HOUSING UNIT #1 | 9941 | Correct | ESP |  | Ely | 1987 | 29870 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0699EXT4 | ROOF REPLACEMENT | 0699 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 15 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2008. It is recommended that this building be re-roofed in the next 6-7 years to be consistent with the roofing program and the end of the warranty period. | HOUSING UNIT #1 | 9941 | Correct | ESP |  | Ely | 1987 | 29870 | 2015-04-29 | Four to Ten Years | Long-Term Needs | 3 | 358440
0699EXT2 | EXTERIOR FINISHES | 0699 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sealing and painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years, and that it be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | HOUSING UNIT #1 | 9941 | Correct | ESP |  | Ely | 1987 | 29870 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 149350
0699INT1 | INTERIOR FINISHES | 0699 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years, and that it be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | HOUSING UNIT #1 | 9941 | Correct | ESP |  | Ely | 1987 | 29870 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 149350
0699PLM2 | BACKFLOW PREVENTER REPLACEMENT | 0699 | There is a backflow preventer on the main water line coming into the building. It is leaking and should be scheduled for replacement. This project would provide for replacing the backflow preventer. | HOUSING UNIT #1 | 9941 | Correct | ESP |  | Ely | 1987 | 29870 | 2015-04-29 | Immediate to Two Years | Currently Critical | 1 | 2000
0699SEC2 | ELECTRONIC LOCKS/ CONTROLS REPLACEMENT | 0699 | The controls for the door locks and security systems are built on a custom panel and interface. The controls are difficult to repair, parts are becoming increasingly difficult to locate, and the type and configuration of the switches are limited by the physical size of the consoles. This project recommends replacing the existing mechanical switching system with a computer system and electronic interface. Remote costs and secure facility allowance were included in the project estimates. This project or a portion thereof was previously recommended in the FCA report dated 06/04/2002 and 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | HOUSING UNIT #1 | 9941 | Correct | ESP |  | Ely | 1987 | 29870 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 565000
2567ENR1 | LIGHTING REPLACEMENT | 2567 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Any electrical wiring upgrades are not included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | SALLY PORT (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 81 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 365
2567EXT2 | EXTERIOR FINISHES | 2567 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | SALLY PORT (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 81 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 810
2567INT1 | INTERIOR FINISHES | 2567 | The interior finishes are in poor condition. It is recommended that the interior walls and ceilings be painted at least once in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | SALLY PORT (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 81 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 810
2567INT2 | FLOORING REPLACEMENT | 2567 | The VCT (vinyl composite tile) flooring in the building is worn and damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | SALLY PORT (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 81 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 1134
2567EXT3 | EXTERIOR DOOR REPLACEMENT | 2567 | The existing exterior door to the Recreation / Gym is original to the building. It is showing signs of wear and deterioration from constant use and inmate abuse. Due to security concerns and the condition of the door, replacement is recommended. This project would provide for the removal and disposal of the existing door and frame, and replacement with new exterior security door including door frame, hardware, security glazing, painting and connections to the security system as required. A total of 1 door was used to generate this estimate. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | SALLY PORT (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 81 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 1500
2567EXT4 | ROOF REPLACEMENT | 2567 | The roof on this building was in poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1993. It is recommended to replace the singly-ply membrane and repair the Cor-ten roofing system as needed in the next 1-2 years to be consistent with the roofing program and the end of the warranty period. | SALLY PORT (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 81 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 972
9994ELE2 | TRANSFORMER AND DISTRIBUTION PANELS SERVICE | 9994 | Southern Nevada Correctional Center opened in 1978. There is evidence of deterioration on the transformer cabinets and main distribution panels site wide. There are no records of inspection or servicing of these electrical items. It is highly recommended that these items be serviced on an annual basis. This project would provide for a photo infrared inspection and servicing of all the transformer and main distribution panels. Other projects may be developed from the results of the inspections. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | SOUTHERN NV CORRECT CTR SITE(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 |  | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 15000
9994PLM1 | PLUMBING SCOPE SERVICE | 9994 | The plumbing supply lines and sewer lines should be thoroughly inspected prior to reoccupying the facility. After being abandoned, many problems can occur with the plumbing including breaks from shifting soils, blockages or deterioration from rust. It is recommended to have the piping scoped with a camera to determine whether there are any problems with the lines. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | SOUTHERN NV CORRECT CTR SITE(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 |  | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 6000
9994ELE3 | HIGH MAST LAMP REPLACEMENT | 9994 | There are 10 high mast security light poles throughout the facility that have 8 security lamps each. A lot of these lamps were burned out at the time of the survey and should be scheduled for replacement. This project provides for the purchase and installation of 80 security lamps for the high mast light poles. The cost includes removal and disposal of the existing lamps. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | SOUTHERN NV CORRECT CTR SITE(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 |  | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 5000
9994SIT5 | FACILITY START-UP / RECOMMISSIONING | 9994 | The Southern Nevada Correctional Center was vacant during the survey of 2016. During the site visit to all of the buildings, there were numerous plumbing leaks, damaged plumbing fixtures and active water leaks. The central plant was running at minimum capacity and some of the buildings' HVAC components had not been in service since the closure of the prison. This project would provide for anticipated start-up costs and recommissioning of the entire facility including complete HVAC, plumbing and waste line testing and repairs, culinary ansul fire protection and cooking equipment start-up and inspection, and fire protection system testing and inspection. The possible replacement of existing HVAC equipment in the central plant is not included in this estimate as it is unknown. Actual fixture replacement of plumbing fixtures and cooking equipment is not included in this project as it is unknown until facility is opened again. Projects for plumbing fixture replacement are addressed in the individual building project reports and mostly address replacement of porcelain fixtures with stainless steel. Kitchen equipment replacement is addressed in the individual building report. This is a budgetary allowance for anticipated costs associated with the start-up and preoccupancy of the facility. Any potential leaks or damage to the underground hot water loop, domestic water and waste lines in unknown due to facility not being in operation. This project is a priority one project and will need to be done prior to occupancy. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | SOUTHERN NV CORRECT CTR SITE(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 |  | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 3380000
9994SIT2 | ASPHALT CONCRETE REPLACEMENT | 9994 | The access road and the parking area around the Maintenance and Auto Shop area is in poor condition and has significant alligatoring and large cracks. The paving has deteriorated to the point that it is no longer viable to re-seal. This project would provide for the removal and disposal of the existing A.C. paving and installation of 80,000 square feet of A.C. paving over a compacted sub-base. This estimate includes striping for parking areas and safety zones and excludes the main public / employee parking area. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | SOUTHERN NV CORRECT CTR SITE(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 |  | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 400000
9994SIT4 | SITE DRAINAGE IMPROVEMENTS | 9994 | The buildings across the site have visible damage to the exterior walls and foundations from improper drainage. There are many areas where the grade does not slope away from the buildings allowing water to pool up against the walls. These areas show visible water damage to the stucco and will continue to cause damage. This project would create positive flow away from the buildings by regrading and installing French drains as needed. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | SOUTHERN NV CORRECT CTR SITE(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 |  | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 15000
0182PLM2 | 2" BACKFLOW ASSEMBLY | 0182 | State Health Law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of back siphonage or backpressure. This project allows for the installation of double check valves or reduced pressure principle backflow preventers as appropriate to the hazard and in appropriate locations near the potential source of contamination. Costs include an above ground vault, and allowance for 200 feet of 1" conduit to provide power for freeze protection. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 3 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 25000
0182EXT4 | ROOF REPLACEMENT | 0182 | The roof on this building was in poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1993. It is recommended to replace the singly-ply membrane and repair the Cor-ten roofing system as needed in the next 1-2 years to be consistent with the roofing program and the end of the warranty period. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 3 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 166200
0181ELE3 | ELECTRICAL UPGRADE | 0181 | This building was constructed before the high demand for electrical services were needed for computers, communications systems and other electrical devices. As time has progressed, the buildings electrical demand and communications system has changed. The electrical system is utilized to its current maximum potential and the communications system is outdated. The electrical panels, switches and receptacles are at their limit. The current wiring in the building is #14 and does not meet the current demand. #14 wiring is also against State Public Works Division's Adopted Standards, 8.5.4, for lighting and power circuits. It is recommended to upgrade the entire electrical system and communications system to meet the evolving needs of the building. | HOUSING UNIT 2 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 554000
0181EXT5 | EXTERIOR DOOR REPLACEMENT | 0181 | The existing exterior door to the Housing Unit 2 is original to the building. It is showing signs of wear and deterioration from constant use and inmate abuse. Due to security concerns and the condition of the door, replacement is recommended. This project would provide for the removal and disposal of the existing door and frame, and replacement with new exterior security door including door frame, hardware, security glazing, painting and connections to the security system as required. A total of 1 door was used to generate this estimate. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 2 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 1500
0181SEC1 | CONTROL PANEL, DOORS AND LOCKS REPLACEMENT | 0181 | Problems exist with the door control panel and door locks for the cells. The panel and locks are original equipment and should be scheduled for replacement. Buttons on the panel do not work or get stuck frequently and the door locks are not consistently responsive to the panel. Repairs to the control panel and locks are difficult because replacement parts are no longer being manufactured for the units. Improper operation will cause security risks to the staff and inmates. It is recommended that the door control panel and 56 door locks be replaced. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 2 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 840000
0181SEC2 | SECURITY SURVEILLANCE SYSTEM INSTALLATION | 0181 | There is no security camera or recording system in the Housing Unit 2 Building. This is a safety issue for the staff and inmates as all areas cannot be seen by the security staff or recorded in case of an incident. This project would provide for the installation of surveillance cameras and a security system for the entire building and all required connections to existing utility systems. | HOUSING UNIT 2 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 96950
0182INT4 | INTERIOR FINISHES | 0182 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 3 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 138500
0182EXT6 | EXTERIOR FINISHES | 0182 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 3 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 138500
0182SFT4 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0182 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10, 1011.6.2 exit sign illumination 5 foot candles (54 lux), was referenced for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 3 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 34625
0182PLM4 | WATER HEATER REPLACEMENT | 0182 | There are two 120 gallon electric water heaters in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 1-2 years. It is recommended that two new electric water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 3 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 15000
0182SEC1 | CONTROL PANEL, DOORS AND LOCKS REPLACEMENT | 0182 | Problems exist with the door control panel and door locks for the cells. The panel and locks are original equipment and should be scheduled for replacement. Buttons on the panel do not work or get stuck frequently and the door locks are not consistently responsive to the panel. Repairs to the control panel and locks are difficult because replacement parts are no longer being manufactured for the units. Improper operation will cause security risks to the staff and inmates. It is recommended that the door control panel and 56 door locks be replaced. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 3 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 840000
0182PLM5 | PLUMBING FIXTURE REPLACEMENT | 0182 | The plumbing fixtures in the cells are a mix of porcelain and stainless steel wall hung lavatories and water closets. These units are in poor condition and should be replaced with stainless steel fixtures designed for correctional facilities. This project would provide for the removal and replacement of the old porcelain plumbing fixtures with new stainless steel fixtures. The estimate is based on installing 50 separate water closets and sinks in the same place as the existing porcelain fixtures. If combination style units are feasible to install, there may be a cost savings on the materials, but additional work to install. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 3 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 375000
0182SFT5 | FIRE ALARM SYSTEM REPLACEMENT | 0182 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and no longer comply with current requirements. the current system is no longer operating. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | HOUSING UNIT 3 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 110800
0181SFT4 | FIRE ALARM SYSTEM REPLACEMENT | 0181 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and no longer comply with current requirements. The current system is no longer operating. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | HOUSING UNIT 2 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 110800
0182INT3 | LIGHTING UPGRADE | 0182 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, conference rooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 3 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 62325
0181PLM4 | WATER HEATER REPLACEMENT | 0181 | There are two 120 gallon electric water heaters in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 1-2 years. It is recommended that two new electric water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 2 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 15000
0180SEC2 | SECURITY SURVEILLANCE SYSTEM INSTALLATION | 0180 | There is no security camera or recording system in the Housing Unit 1 Building. This is a safety issue for the staff and inmates as all areas cannot be seen by the security staff or recorded in case of an incident. This project would provide for the installation of surveillance cameras and a security system for the entire building and all required connections to existing utility systems. | HOUSING UNIT 1 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 96950
0183SEC2 | SECURITY SURVEILLANCE SYSTEM INSTALLATION | 0183 | There is no security camera or recording system in the Housing Unit 4 Building. This is a safety issue for the staff and inmates as all areas cannot be seen by the security staff or recorded in case of an incident. This project would provide for the installation of surveillance cameras and a security system for the entire building and all required connections to existing utility systems. | HOUSING UNIT 4 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 96950
0180EXT6 | EXTERIOR FINISHES | 0180 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 1 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 138500
0182HVA2 | HVAC REPLACEMENT | 0182 | The Water Source Heat Pumps in the building should be scheduled for replacement. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of new Water Source Heat Pump units and the cleaning of the existing ducting and grilles. This project includes removal and disposal of the existing Water Source Heat Pump units and all required connections to utilities. | HOUSING UNIT 3 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 346250
0180SFT4 | FIRE ALARM REPLACEMENT | 0180 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and no longer comply with current requirements. the current system is no longer operating. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | HOUSING UNIT 1 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 110800
0180PLM3 | PLUMBING REPLACEMENT | 0180 | The sanitary wastewater and copper plumbing systems are showing signs of deterioration. Due to this deterioration, the systems are not working to their full potential. The copper lines have rusted and there are pin holes throughout the system. The lines are original to the site and are in poor condition. The hard water is also a contributing factor to this deterioration. Deposits within the pipes have caused restriction, and has slowed the water flow. This project would provide for the complete replacement of the sanitary sewer and copper piping system. | HOUSING UNIT 1 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 692500
0180SEC1 | DOORS, LOCKS AND CONTROL PANEL REPLACEMENT | 0180 | Problems exist with the door control panel and door locks for the cells. The panel and locks are original equipment and should be scheduled for replacement. Buttons on the panel do not work or get stuck frequently and the door locks are not consistently responsive to the panel. Repairs to the control panel and locks are difficult because replacement parts are no longer being manufactured for the units. Improper operation will cause security risks to the staff and inmates. It is recommended that the door control panel and 56 door locks be replaced. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 1 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 840000
0181SFT3 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0181 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10, 1011.6.2 exit sign illumination 5 foot candles (54 lux), was referenced for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 2 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 34625
0181INT4 | INTERIOR FINISHES | 0181 | The interior finishes are in poor condition. It is recommended that the interior walls and ceilings be painted at least once in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 2 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 138500
0181EXT6 | EXTERIOR FINISHES | 0181 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 2 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 138500
0181PLM5 | PLUMBING FIXTURE REPLACEMENT | 0181 | The plumbing fixtures in the cells are a mix of porcelain and stainless steel wall hung lavatories and water closets. These units are in poor condition and should be replaced with stainless steel fixtures designed for correctional facilities. This project would provide for the removal and replacement of the old porcelain plumbing fixtures with new stainless steel fixtures. The estimate is based on installing a 50 separate water closets and sinks in the same place as the existing porcelain fixtures. If combination style units are feasible to install, there may be a cost savings on the materials, but additional work to install. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 2 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 375000
0181EXT4 | ROOF REPLACEMENT | 0181 | The roof on this building was in poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1993. It is recommended to replace the singly-ply membrane and repair the Cor-ten roofing system as needed in the next 1-2 years to be consistent with the roofing program and the end of the warranty period. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 2 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 166200
0181PLM2 | 2" BACKFLOW ASSEMBLY | 0181 | State Health Law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of back siphonage or backpressure. This project allows for the installation of double check valves or reduced pressure principle backflow preventers as appropriate to the hazard and in appropriate locations near the potential source of contamination. Costs include an above ground vault, and allowance for 200 feet of 1" conduit to provide power for freeze protection. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 2 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 25000
0181PLM6 | PLUMBING REPLACEMENT | 0181 | The sanitary wastewater and copper plumbing systems are showing signs of deterioration. Due to this deterioration, the systems are not working to their full potential. The copper lines have rusted and there are pin holes throughout the system. The lines are original to the site and are in poor condition. The hard water is also a contributing factor to this deterioration. Deposits within the pipes have caused restriction, and has slowed the water flow. This project would provide for the complete replacement of the sanitary sewer and copper piping system. | HOUSING UNIT 2 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 692500
0181HVA2 | HVAC REPLACEMENT | 0181 | The Water Source Heat Pumps in the building should be scheduled for replacement. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of new Water Source Heat Pump units and the cleaning of the existing ducting and grilles. This project includes removal and disposal of the existing Water Source Heat Pump units and all required connections to utilities. | HOUSING UNIT 2 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 346250
0181INT3 | LIGHTING UPGRADE | 0181 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, conference rooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 2 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 62325
0184EXT4 | ROOF REPLACEMENT | 0184 | The roof on this building was in poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1993. It is recommended to replace the singly-ply membrane and repair the Cor-ten roofing system as needed in the next 1-2 years to be consistent with the roofing program and the end of the warranty period. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 5 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 166200
0183EXT4 | ROOF REPLACEMENT | 0183 | The roof on this building was in poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1993. It is recommended to replace the singly-ply membrane and repair the Cor-ten roofing system as needed in the next 1-2 years to be consistent with the roofing program and the end of the warranty period. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 4 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 166200
0184SFT3 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0184 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10, 1011.6.2 exit sign illumination 5 foot candles (54 Lux), was referenced for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 5 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 34625
0184PLM2 | 2" BACKFLOW ASSEMBLY | 0184 | State Health Law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of back siphonage or backpressure. This project allows for the installation of double check valves or reduced pressure principle backflow preventers as appropriate to the hazard and in appropriate locations near the potential source of contamination. Costs include an above ground vault, and allowance for 200 feet of 1" conduit to provide power for freeze protection. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016.. | HOUSING UNIT 5 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 25000
0184EXT6 | EXTERIOR FINISHES | 0184 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 5 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 138500
0184PLM4 | WATER HEATER REPLACEMENT | 0184 | There are two 120 gallon electric water heaters in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 1-2 years. It is recommended that two new electric water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 5 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 15000
0184PLM5 | PLUMBING FIXTURE REPLACEMENT | 0184 | Approximately half of the plumbing fixtures in the cells are separate porcelain wall hung lavatories and water closets. These units are in poor condition and should be replaced with stainless steel fixtures designed for correctional facilities. This project would provide for the removal and replacement of the old porcelain plumbing fixtures with new stainless steel fixtures. The estimate is based on installing a 50 separate water closets and sinks in the same place as the existing porcelain fixtures. If combination style units are feasible to install, there may be a cost savings on the materials, but additional work to install. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 5 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 375000
0183SFT4 | FIRE ALARM SYSTEM REPLACEMENT | 0183 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and no longer comply with current requirements. The current system is no longer operating. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | HOUSING UNIT 4 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 110800
0184SEC1 | CONTROL PANEL DOORS AND LOCKS REPLACEMENT | 0184 | Problems exist with the door control panel and door locks for the cells. The panel and locks are original equipment and should be scheduled for replacement. Buttons on the panel do not work or get stuck frequently and the door locks are not consistently responsive to the panel. Repairs to the control panel and locks are difficult because replacement parts are no longer being manufactured for the units. Improper operation will cause security risks to the staff and inmates. It is recommended that the door control panel and 56 door locks be replaced. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 5 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 840000
0183ELE3 | ELECTRICAL UPGRADE | 0183 | This building was constructed before the high demand for electrical services were needed for computers, communications systems and other electrical devices. As time has progressed, the buildings electrical demand and communications system has changed. The electrical system is utilized to its current maximum potential and the communications system is outdated. The electrical panels, switches and receptacles are at their limit. The current wiring in the building is #14 and does not meet the current demand. #14 wiring is also against State Public Works Division's Adopted Standards, 8.5.4, for lighting and power circuits. It is recommended to upgrade the entire electrical system and communications system to meet the evolving needs of the building. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 4 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 554000
0184INT3 | LIGHTING UPGRADE | 0184 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, conference rooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 5 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 62325
0184EXT7 | EXTERIOR DOOR REPLACEMENT | 0184 | The existing exterior door to the Housing Unit 5 is original to the building. It is showing signs of wear and deterioration from constant use and inmate abuse. Due to security concerns and the condition of the door, replacement is recommended. This project would provide for the removal and disposal of the existing door and frame, and replacement with new exterior security door including door frame, hardware, security glazing, painting and connections to the security system as required. A total of 1 door was used to generate this estimate. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 5 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 1500
0184SEC2 | SECURITY SURVEILLANCE SYSTEM INSTALLATION | 0184 | There is no security camera or recording system in the Housing Unit 5 Building. This is a safety issue for the staff and inmates as all areas cannot be seen by the security staff or recorded in case of an incident. This project would provide for the installation of surveillance cameras and a security system for the entire building and all required connections to existing utility systems. | HOUSING UNIT 5 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 96950
0184ELE3 | ELECTRICAL UPGRADE | 0184 | This building was constructed before the high demand for electrical services were needed for computers, communications systems and other electrical devices. As time has progressed, the buildings electrical demand and communications system has changed. The electrical system is utilized to its current maximum potential and the communications system is outdated. The electrical panels, switches and receptacles are at their limit. The current wiring in the building is #14 and does not meet the current demand. #14 wiring is also against State Public Works Division's Adopted Standards, 8.5.4, for lighting and power circuits. It is recommended to upgrade the entire electrical system and communications system to meet the evolving needs of the building. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 5 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 554000
0184PLM6 | PLUMBING REPLACEMENT | 0184 | The sanitary wastewater and copper plumbing systems are showing signs of deterioration. Due to this deterioration, the systems are not working to their full potential. The copper lines have rusted and there are pin holes throughout the system. The lines are original to the site and are in poor condition. The hard water is also a contributing factor to this deterioration. Deposits within the pipes have caused restriction, and has slowed the water flow. This project would provide for the complete replacement of the sanitary sewer and copper piping system. | HOUSING UNIT 5 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 692500
0184HVA2 | HVAC REPLACEMENT | 0184 | The Water Source Heat Pumps in the building should be scheduled for replacement. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of new Water Source Heat Pump units and the cleaning of the existing ducting and grilles. This project includes removal and disposal of the existing Water Source Heat Pump units and all required connections to utilities. | HOUSING UNIT 5 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 346250
0184SFT4 | FIRE ALARM SYSTEM REPLACEMENT | 0184 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and no longer comply with current requirements. The current system is no longer operating. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | HOUSING UNIT 5 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 110800
0184INT4 | INTERIOR FINISHES | 0184 | The interior finishes are in poor condition. It is recommended that the interior walls and ceilings be painted at least once in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 5 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 138500
0183EXT5 | WINDOW WEATHER-STRIPPING REPLACEMENT | 0183 | The exterior glazing currently has metal window stops and weather-stripping that is rusted, damaged and is in need of replacement, especially at the main entrance to the housing unit at grade level. This project would provide for the removal and replacement of the window stops and weather-stripping. This estimate includes painting to match existing conditions. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 4 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 9600
0182SEC2 | SECURITY SURVEILLANCE SYSTEM INSTALLATION | 0182 | There is no security camera or recording system in the Housing Unit 3 Building. This is a safety issue for the staff and inmates as all areas cannot be seen by the security staff or recorded in case of an incident. This project would provide for the installation of surveillance cameras and a security system for the entire building and all required connections to existing utility systems. | HOUSING UNIT 3 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 96950
0182ELE3 | ELECTRICAL UPGRADE | 0182 | This building was constructed before the high demand for electrical services were needed for computers, communications systems and other electrical devices. As time has progressed, the buildings electrical demand and communications system has changed. The electrical system is utilized to its current maximum potential and the communications system is outdated. The electrical panels, switches and receptacles are at their limit. The current wiring in the building is #14 and does not meet the current demand. #14 wiring is also against State Public Works Division's Adopted Standards, 8.5.4, for lighting and power circuits. It is recommended to upgrade the entire electrical system and communications system to meet the evolving needs of the building. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 3 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 554000
0182PLM6 | PLUMBING REPLACEMENT | 0182 | The sanitary wastewater and copper plumbing systems are showing signs of deterioration. Due to this deterioration, the systems are not working to their full potential. The copper lines have rusted and there are pin holes throughout the system. The lines are original to the site and are in poor condition. The hard water is also a contributing factor to this deterioration. Deposits within the pipes have caused restriction, and has slowed the water flow. This project would provide for the complete replacement of the sanitary sewer and copper piping system. | HOUSING UNIT 3 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 692500
0183SFT3 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0183 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10, 1011.6.2 exit sign illumination 5 foot candles (54 lux), was referenced for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 4 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 34625
0183SEC1 | CONTROL PANEL, DOORS AND LOCKS REPLACEMENT | 0183 | Problems exist with the door control panel and door locks for the cells. The panel and locks are original equipment and should be scheduled for replacement. Buttons on the panel do not work or get stuck frequently and the door locks are not consistently responsive to the panel. Repairs to the control panel and locks are difficult because replacement parts are no longer being manufactured for the units. Improper operation will cause security risks to the staff and inmates. It is recommended that the door control panel and 56 door locks be replaced. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 4 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 840000
0183PLM3 | 2" BACKFLOW ASSEMBLY | 0183 | State Health Law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of back siphonage or backpressure. This project allows for the installation of double check valves or reduced pressure principle backflow preventers as appropriate to the hazard and in appropriate locations near the potential source of contamination. Costs include an above ground vault, and allowance for 200 feet of 1" conduit to provide power for freeze protection. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 4 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 25000
0183PLM5 | PLUMBING REPLACEMENT | 0183 | The sanitary wastewater and copper plumbing systems are showing signs of deterioration. Due to this deterioration, the systems are not working to their full potential. The copper lines have rusted and there are pin holes throughout the system. The lines are original to the site and are in poor condition. The hard water is also a contributing factor to this deterioration. Deposits within the pipes have caused restriction, and has slowed the water flow. This project would provide for the complete replacement of the sanitary sewer and copper piping system. | HOUSING UNIT 4 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 692500
0183PLM1 | PLUMBING FIXTURE REPLACEMENT | 0183 | Approximately half of the plumbing fixtures in the cells are separate porcelain wall hung lavatories and water closets. These units are in poor condition and should be replaced with stainless steel fixtures designed for correctional facilities. This project would provide for the removal and replacement of the old porcelain plumbing fixtures with new stainless steel fixtures. The estimate is based on installing a 50 separate water closets and sinks in the same place as the existing porcelain fixtures. If combination style units are feasible to install, there may be a cost savings on the materials, but additional work to install. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 4 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 375000
0182EXT5 | EXTERIOR DOOR REPLACEMENT | 0182 | The existing exterior door to the Housing Unit 3 is original to the building. It is showing signs of wear and deterioration from constant use and inmate abuse. Due to security concerns and the condition of the door, replacement is recommended. This project would provide for the removal and disposal of the existing door and frame, and replacement with new exterior security door including door frame, hardware, security glazing, painting and connections to the security system as required. A total of 1 door was used to generate this estimate. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 3 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 1500
0183INT4 | INTERIOR FINISHES | 0183 | The interior finishes are in poor condition. It is recommended that the interior walls and ceilings be painted at least once in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 4 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 138500
0183INT3 | LIGHTING UPGRADE | 0183 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, conference rooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 4 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 62325
0183EXT6 | EXTERIOR FINISHES | 0183 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 4 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 138500
0180EXT5 | EXTERIOR DOOR REPLACEMENT | 0180 | The existing exterior door to the Housing Unit 1 is original to the building. It is showing signs of wear and deterioration from constant use and inmate abuse. Due to security concerns and the condition of the door, replacement is recommended. This project would provide for the removal and disposal of the existing door and frame, and replacement with new exterior security door including door frame, hardware, security glazing, painting and connections to the security system as required. A total of 1 door was used to generate this estimate. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 1 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 1500
0183EXT7 | EXTERIOR DOOR REPLACEMENT | 0183 | The existing exterior door to the Housing Unit 4 is original to the building. It is showing signs of wear and deterioration from constant use and inmate abuse. Due to security concerns and the condition of the door, replacement is recommended. This project would provide for the removal and disposal of the existing door and frame, and replacement with new exterior security door including door frame, hardware, security glazing, painting and connections to the security system as required. A total of 1 door was used to generate this estimate. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 4 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 1500
0179ADA3 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0179 | This building contains a water fountain. The 2012 IBC Section 1109.5 states where a water fountain is provided, at least half should be accessible. This project would provide funding for the purchase and installation of a new accessible fixed high/ low ADA drinking fountain. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | CHAPEL/ LAW LIBRARY (VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 4000
0183HVA2 | HVAC REPLACEMENT | 0183 | The Water Source Heat Pumps in the building should be scheduled for replacement. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of new Water Source Heat Pump units and the cleaning of the existing ducting and grilles. This project includes removal and disposal of the existing Water Source Heat Pump units and all required connections to utilities. | HOUSING UNIT 4 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 346250
0183PLM4 | WATER HEATER REPLACEMENT | 0183 | There are two 120 gallon electric water heaters in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 1-2 years. It is recommended that two new electric water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 4 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 15000
0178SFT3 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0178 | The building is a B occupancy per the 2012 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | EDUCATION A (VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 50800
0179EXT4 | EXTERIOR DOOR REPLACEMENT | 0179 | The existing exterior doors to the Chapel/Law Library are original to the building. They are showing signs of wear and deterioration from constant use and inmate abuse. Due to security concerns and the condition of the doors, replacement is recommended. This project would provide for the removal and disposal of the existing doors and frames, and replacement with new exterior security doors including door frames, hardware, security glazing, painting and connections to the security system as required. A total of 4 doors was used to generate this estimate. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | CHAPEL/ LAW LIBRARY (VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 6000
0176PLM4 | WATER HEATER REPLACEMENT | 0176 | There is a 30 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 1-2 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | ADMINISTRATION/ VISITATION(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 11950 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 2500
0176INT4 | INTERIOR FINISHES | 0176 | The interior finishes are in poor condition. It is recommended that the interior walls and ceilings be painted prior to occupancy. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in areas where water is present, such as the kitchen and bathrooms, for added durability. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | ADMINISTRATION/ VISITATION(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 11950 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 119500
0176PLM5 | PLUMBING REPLACEMENT | 0176 | The sanitary wastewater and copper plumbing systems are showing signs of deterioration. Due to this deterioration, the systems are not working to their full potential. The copper lines have rusted and there are pin holes throughout the system. The lines are original to the site and are in poor condition. The hard water is also a contributing factor to this deterioration. Deposits within the pipes have caused restriction, and has slowed the water flow. This project would provide for the complete replacement of the sanitary sewer and copper piping system. | ADMINISTRATION/ VISITATION(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 11950 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 298750
0176ELE2 | ELECTRICAL UPGRADE | 0176 | This building was constructed before the high demand for electrical services were needed for computers, communications systems and other electrical devices. As time has progressed, the buildings electrical demand and communications system has changed. The electrical system is utilized to its current maximum potential and the communications system is outdated. The electrical panels, switches and receptacles are at their limit. The current wiring in the building is #14 and does not meet the current demand. #14 wiring is also against State Public Works Division's Adopted Standards, 8.5.4, for lighting and power circuits. It is recommended to upgrade the entire electrical system and communications system to meet the evolving needs of the building. | ADMINISTRATION/ VISITATION(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 11950 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 298750
0176SFT4 | FIRE ALARM SYSTEM REPLACEMENT | 0176 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and no longer comply with current requirements. The current system is no longer operating. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | ADMINISTRATION/ VISITATION(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 11950 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 95600
0176ADA5 | REMOVE/ REPLACE CONCRETE PATIO | 0176 | Outside of the Visitation Room is a concrete patio with stairs and terraces which provides an outdoor space to visit with inmates. The patio is in disrepair with major cracks in the concrete, stairs that do not comply with code and no compliance with ADA requirements. This project would provide for removal of the existing improvements and installation of a new flat concrete patio which complies with all applicable codes. Removal and disposal of the existing concrete is included in this estimate. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | ADMINISTRATION/ VISITATION(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 11950 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 22500
0178EXT3 | EXTERIOR FINISHES | 0178 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | EDUCATION A (VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 63500
0176HVA1 | HVAC REPLACEMENT | 0176 | The Water Source Heat Pumps in the building should be scheduled for replacement. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of new Water Source Heat Pump units and the cleaning of the existing ducting and grilles. This project includes removal and disposal of the existing Water Source Heat Pump units and all required connections to utilities. | ADMINISTRATION/ VISITATION(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 11950 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 298750
0178EXT2 | ROOF REPLACEMENT | 0178 | The roof on this building was in poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1993. It is recommended to replace the singly-ply membrane and repair the Cor-ten roofing system as needed in the next 1-2 years to be consistent with the roofing program and the end of the warranty period. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | EDUCATION A (VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 76200
0178SFT1 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0178 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10, 1011.6.2 exit sign illumination 5 foot candles (54 lux), was referenced for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | EDUCATION A (VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 15875
0178ADA3 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0178 | This building contains a water fountain. The 2012 IBC Section 1109.5 states where a water fountain is provided, at least half should be accessible. This project would provide funding for the purchase and installation of a new accessible fixed high/ low ADA drinking fountain. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | EDUCATION A (VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 4000
0178INT3 | LIGHTING UPGRADE | 0178 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, closets and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | EDUCATION A (VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 28575
0178ADA2 | ADA SIGNAGE | 0178 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | EDUCATION A (VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 1500
0178ADA1 | LEVER ACTION HARDWARE INSTALLATION | 0178 | Section 4.13.9 of the Americans with Disabilities Act Accessible Guidelines (ADAAG) states that handles, pulls, latches, locks and other operating devices on accessible doors shall have a shape that is easy to grasp with one hand and does not require tight grasping, tight pinching, or twisting of the wrist to operate. It is recommended that compliant hardware be installed in this building to meet these guidelines. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | EDUCATION A (VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 10000
0178PLM1 | 2" BACKFLOW ASSEMBLY, VAULT, AND POWER | 0178 | State Health Law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of back siphonage or backpressure. This project allows for the installation of double check valves or reduced pressure principle backflow preventers as appropriate to the hazard and in appropriate locations near the potential source of contamination. Costs include an above ground vault, and allowance for 200 feet of 1" conduit to provide power for freeze protection. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | EDUCATION A (VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 25000
0176ENR1 | LIGHTING UPGRADE | 0176 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, conference rooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | ADMINISTRATION/ VISITATION(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 11950 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 53775
0188PLM5 | PLUMBING FIXTURE REPLACEMENT | 0188 | Approximately half of the plumbing fixtures in the cells are separate porcelain wall hung lavatories and water closets. These units are in poor condition and should be replaced with stainless steel fixtures designed for correctional facilities. This project would provide for the removal and replacement of the old porcelain plumbing fixtures with new stainless steel fixtures. The estimate is based on installing 10 separate water closets and sinks in the same place as the existing porcelain fixtures. If combination style units are feasible to install, there may be a cost savings on the materials, but additional work to install. | MEDICAL UNIT 8 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 5150 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 75000
0185PLM2 | 2" BACKFLOW ASSEMBLY | 0185 | State Health Law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of back siphonage or backpressure. This project allows for the installation of double check valves or reduced pressure principle backflow preventers as appropriate to the hazard and in appropriate locations near the potential source of contamination. Costs include an above ground vault, and allowance for 200 feet of 1" conduit to provide power for freeze protection. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 6 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 25000
0176ADA2 | TDD INSTALLATION | 0176 | The visitation area is not equipped with a telecommunications device for the deaf (TDD). In order to comply with ADA requirements it is recommended to install a TDD system in the non-contact visitation area. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) was used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | ADMINISTRATION/ VISITATION(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 11950 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 20000
0176PLM1 | 2" BACKFLOW ASSEMBLY, VAULT, AND POWER | 0176 | State Health Law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of back siphonage or backpressure. This project allows for the installation of double check valves or reduced pressure principle backflow preventers as appropriate to the hazard and in appropriate locations near the potential source of contamination. Costs include an above ground vault, and allowance for 200 feet of 1" conduit to provide power for freeze protection. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | ADMINISTRATION/ VISITATION(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 11950 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 25000
0176ADA1 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0176 | This building contains a water fountain. The 2012 IBC Section 1109.5 states where a water fountain is provided, at least half should be accessible. This project would provide funding for the purchase and installation of a new accessible fixed high/ low ADA drinking fountain. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | ADMINISTRATION/ VISITATION(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 11950 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 4000
0176ADA3 | LEVER ACTION HARDWARE INSTALLATION | 0176 | Section 4.13.9 of the Americans with Disabilities Act Accessible Guidelines (ADAAG) states that handles, pulls, latches, locks and other operating devices on accessible doors shall have a shape that is easy to grasp with one hand and does not require tight grasping, tight pinching, or twisting of the wrist to operate. It is recommended that compliant hardware be installed in this building to meet these guidelines. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | ADMINISTRATION/ VISITATION(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 11950 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 12000
0176SEC1 | SECURITY SURVEILLANCE SYSTEM INSTALLATION | 0176 | There is no security camera or recording system in the Administration/ Visitation Building. This is a safety issue for the staff and inmates as all areas cannot be seen by the security staff or recorded in case of an incident. This project would provide for the installation of surveillance cameras and a security system for the entire building and all required connections to existing utility systems. | ADMINISTRATION/ VISITATION(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 11950 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 83650
0176SFT2 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0176 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10, 1011.6.2 exit sign illumination 5 foot candles (54 Lux), was referenced for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | ADMINISTRATION/ VISITATION(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 11950 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 29875
0178INT4 | INTERIOR FINISHES | 0178 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | EDUCATION A (VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 63500
0176ADA4 | ADA SIGNAGE | 0176 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria and is confusing for public access to visitation. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | ADMINISTRATION/ VISITATION(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 11950 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 5000
0176ADA6 | RESTROOM REMODELS | 0176 | The water closets and the lavatories in the six restrooms throughout the building are worn from many years of use and being idle due to multiple closures. It is recommended that all fixtures be replaced with new units. The new units and restroom layouts are also required to comply with ADA requirements. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | ADMINISTRATION/ VISITATION(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 11950 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 30000
0176EXT4 | ROOF REPLACEMENT | 0176 | The roof on this building was in poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1993. It is recommended to replace the singly-ply membrane and repair the Cor-ten roofing system as needed in the next 1-2 years to be consistent with the roofing program and the end of the warranty period. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | ADMINISTRATION/ VISITATION(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 11950 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 143400
0176EXT2 | REPLACE WINDOWS | 0176 | The steel framed window assemblies are damaged from exposure and age and the frames and stops should be scheduled for replacement. They are located in the Visitation room and near the employee entrance to the Warden's Office. The frames and glazing stops are rusting and approaching failure due to water infiltration at joints, adjacency to grade and expansion and contraction over time. The heat and exposure to the sun have warped and bent the frames and glazing stops beyond repair. This project will include removal and disposal of the existing frame assembly and replacement with new steel frames and glazing stops. Reinstallation of the existing glazing panels is included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | ADMINISTRATION/ VISITATION(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 11950 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 139200
0176EXT5 | EXTERIOR FINISHES | 0176 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | ADMINISTRATION/ VISITATION(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 11950 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 119500
0176EXT6 | EXTERIOR DOOR REPLACEMENT | 0176 | The existing exterior doors to the Administration/ Visitation are original to the building. They are showing signs of wear and deterioration from constant use and inmate abuse. Due to security concerns and the condition of the doors, replacement is recommended. This project would provide for the removal and disposal of the existing doors and frames, and replacement with new exterior security doors including door frames, hardware, security glazing, painting and connections to the security system as required. A total of 9 doors was used to generate this estimate. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | ADMINISTRATION/ VISITATION(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 11950 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 13500
0176SFT3 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0176 | The building is a B occupancy per the 2012 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | ADMINISTRATION/ VISITATION(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 11950 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 95600
0180PLM2 | 2" BACKFLOW ASSEMBLY, VAULT, AND POWER | 0180 | State Health Law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of back siphonage or backpressure. This project allows for the installation of double check valves or reduced pressure principle backflow preventers as appropriate to the hazard and in appropriate locations near the potential source of contamination. Costs include an above ground vault, and allowance for 200 feet of 1" conduit to provide power for freeze protection. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 1 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 25000
0179EXT2 | ROOF REPLACEMENT | 0179 | The roof on this building was in poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1993. It is recommended to replace the singly-ply membrane and repair the Cor-ten roofing system as needed in the next 1-2 years to be consistent with the roofing program and the end of the warranty period. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | CHAPEL/ LAW LIBRARY (VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 76200
0179PLM5 | WATER HEATER REPLACEMENT | 0179 | There is a 30 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 1-2 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | CHAPEL/ LAW LIBRARY (VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 2500
0179SEC1 | SECURITY SURVEILLANCE SYSTEM INSTALLATION | 0179 | There is no security camera or recording system in the Chapel/Law Library Building. This is a safety issue for the staff and inmates as all areas cannot be seen by the security staff or recorded in case of an incident. This project would provide for the installation of surveillance cameras and a security system for the entire building and all required connections to existing utility systems. | CHAPEL/ LAW LIBRARY (VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 44450
0179ELE2 | ELECTRICAL UPGRADE | 0179 | This building was constructed before the high demand for electrical services were needed for computers, communications systems and other electrical devices. As time has progressed, the buildings electrical demand and communications system has changed. The electrical system is utilized to its current maximum potential and the communications system is outdated. The electrical panels, switches and receptacles are at their limit. The current wiring in the building is #14 and does not meet the current demand. #14 wiring is also against State Public Works Division's Adopted Standards, 8.5.4, for lighting and power circuits. It is recommended to upgrade the entire electrical system and communications system to meet the evolving needs of the building. | CHAPEL/ LAW LIBRARY (VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 254000
0179PLM4 | PLUMBING REPLACEMENT | 0179 | The sanitary wastewater and copper plumbing systems are showing signs of deterioration. Due to this deterioration, the systems are not working to their full potential. The copper lines have rusted and there are pin holes throughout the system. The lines are original to the site and are in poor condition. The hard water is also a contributing factor to this deterioration. Deposits within the pipes have caused restriction, and has slowed the water flow. This project would provide for the complete replacement of the sanitary sewer and copper piping system. | CHAPEL/ LAW LIBRARY (VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 158750
0179HVA1 | HVAC REPLACEMENT | 0179 | The Water Source Heat Pumps in the building should be scheduled for replacement. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of new Water Source Heat Pump units and the cleaning of the existing ducting and grilles. This project includes removal and disposal of the existing Water Source Heat Pump units and all required connections to utilities. | CHAPEL/ LAW LIBRARY (VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 158750
0178ADA4 | RESTROOM REMODEL | 0178 | The water closets and the lavatories in the three restrooms and the lavatory in the hallway are worn from many years of use and inactivity. It is recommended that all fixtures be replaced with new units. The new units and restroom layouts are also required to comply with ADA requirements. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | EDUCATION A (VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 90000
0180SFT3 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0180 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10, 1011.6.2 exit sign illumination 5 foot candles (54 lux), was referenced for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 1 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 34625
0179EXT3 | EXTERIOR FINISHES | 0179 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | CHAPEL/ LAW LIBRARY (VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 63500
0180PLM4 | WATER HEATER REPLACEMENT | 0180 | There are two 120 gallon electric water heaters in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 1-2 years. It is recommended that two new electric water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 1 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 15000
0180PLM5 | PLUMBING FIXTURE REPLACEMENT | 0180 | The plumbing fixtures in the cells are separate porcelain wall hung lavatories and water closets. These units are in poor condition and should be replaced with stainless steel fixtures designed for correctional facilities. This project would provide for the removal and replacement of the old porcelain plumbing fixtures with new stainless steel fixtures. The estimate is based on installing a 100 separate water closets and sinks in the same place as the existing porcelain fixtures. If combination style units are feasible to install, there may be a cost savings on the materials, but additional costs would be incurred for relocating plumbing. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 1 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 375000
0180ENR1 | LIGHTING UPGRADE | 0180 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, conference rooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 1 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 62325
0180EXT4 | ROOF REPLACEMENT | 0180 | The roof on this building was in poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1993. It is recommended to replace the singly-ply membrane and repair the Cor-ten roofing system as needed in the next 1-2 years to be consistent with the roofing program and the end of the warranty period. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 1 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 166200
0180ELE3 | ELECTRICAL UPGRADE | 0180 | This building was constructed before the high demand for electrical services were needed for computers, communications systems and other electrical devices. As time has progressed, the buildings electrical demand and communications system has changed. The electrical system is utilized to its current maximum potential and the communications system is outdated. The electrical panels, switches and receptacles are at their limit. The current wiring in the building is #14 and does not meet the current demand. #14 wiring is also against State Public Works Division's Adopted Standards, 8.5.4, for lighting and power circuits. It is recommended to upgrade the entire electrical system and communications system to meet the evolving needs of the building. | HOUSING UNIT 1 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 554000
0180INT4 | INTERIOR FINISHES | 0180 | The interior finishes are in poor condition. It is recommended that the interior walls and ceilings be painted at least once in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 1 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 138500
0179SFT4 | FIRE ALARM SYSTEM REPLACEMENT | 0179 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and no longer comply with current requirements. The current system is no longer operating. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | CHAPEL/ LAW LIBRARY (VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 50800
0179ADA1 | LEVER ACTION HARDWARE INSTALLATION | 0179 | Section 4.13.9 of the Americans with Disabilities Act Accessible Guidelines (ADAAG) states that handles, pulls, latches, locks and other operating devices on accessible doors shall have a shape that is easy to grasp with one hand and does not require tight grasping, tight pinching, or twisting of the wrist to operate. It is recommended that compliant hardware be installed in this building to meet these guidelines. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | CHAPEL/ LAW LIBRARY (VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 10000
0180HVA2 | HVAC REPLACEMENT | 0180 | The Water Source Heat Pumps in the building should be scheduled for replacement. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of new Water Source Heat Pump units and the cleaning of the existing ducting and grilles. This project includes removal and disposal of the existing Water Source Heat Pump units and all required connections to utilities. | HOUSING UNIT 1 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 346250
0178ELE2 | ELECTRICAL UPGRADE | 0178 | This building was constructed before the high demand for electrical services were needed for computers, communications systems and other electrical devices. As time has progressed, the buildings electrical demand and communications system has changed. The electrical system is utilized to its current maximum potential and the communications system is outdated. The electrical panels, switches and receptacles are at their limit. The current wiring in the building is #14 and does not meet the current demand. #14 wiring is also against State Public Works Division's Adopted Standards, 8.5.4, for lighting and power circuits. It is recommended to upgrade the entire electrical system and communications system to meet the evolving needs of the building. | EDUCATION A (VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 254000
0178PLM4 | PLUMBING REPLACEMENT | 0178 | The sanitary wastewater and copper plumbing systems are showing signs of deterioration. Due to this deterioration, the systems are not working to their full potential. The copper lines have rusted and there are pin holes throughout the system. The lines are original to the site and are in poor condition. The hard water is also a contributing factor to this deterioration. Deposits within the pipes have caused restriction, and has slowed the water flow. This project would provide for the complete replacement of the sanitary sewer and copper piping system. | EDUCATION A (VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 158750
0178SEC1 | SECURITY SURVEILLANCE SYSTEM INSTALLATION | 0178 | There is no security camera or recording system in the Education Building. This is a safety issue for the staff and inmates as all areas cannot be seen by the security staff or recorded in case of an incident. This project would provide for the installation of surveillance cameras and a security system for the entire building and all required connections to existing utility systems. | EDUCATION A (VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 44450
0178EXT4 | EXTERIOR DOOR REPLACEMENT | 0178 | The existing exterior doors to the Education are original to the building. They are showing signs of wear and deterioration from constant use and inmate abuse. Due to security concerns and the condition of the doors, replacement is recommended. This project would provide for the removal and disposal of the existing doors and frames, and replacement with new exterior security doors including door frames, hardware, security glazing, painting and connections to the security system as required. A total of 5 doors was used to generate this estimate. | EDUCATION A (VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 7500
0178HVA1 | HVAC REPLACEMENT | 0178 | The Water Source Heat Pumps in the building should be scheduled for replacement. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of new Water Source Heat Pump units and the cleaning of the existing ducting and grilles. This project includes removal and disposal of the existing Water Source Heat Pump units and all required connections to utilities. | EDUCATION A (VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 158750
0179PLM1 | 2" BACKFLOW ASSEMBLY, VAULT, AND POWER | 0179 | State Health Law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of back siphonage or backpressure. This project allows for the installation of double check valves or reduced pressure principle backflow preventers as appropriate to the hazard and in appropriate locations near the potential source of contamination. Costs include an above ground vault, and allowance for 200 feet of 1" conduit to provide power for freeze protection. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | CHAPEL/ LAW LIBRARY (VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 25000
0179INT3 | LIGHTING UPGRADE | 0179 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, closets and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | CHAPEL/ LAW LIBRARY (VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 28575
0179ADA5 | RESTROOM REMODEL | 0179 | The water closets and the lavatories in the three restrooms are worn from many years of use. It is recommended that all fixtures be replaced with new units. The new units and restroom layouts are also required to comply with ADA requirements. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | CHAPEL/ LAW LIBRARY (VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 90000
0179SFT3 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0179 | The building is a B occupancy per the 2012 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | CHAPEL/ LAW LIBRARY (VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 88900
0179INT2 | CARPET/ TILE REPLACEMENT | 0179 | The VCT (vinyl composite tile) and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the next 1-2 years. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | CHAPEL/ LAW LIBRARY (VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 88900
0179ADA2 | ADA SIGNAGE | 0179 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | CHAPEL/ LAW LIBRARY (VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 1500
0179SFT1 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0179 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10, 1011.6.2 exit sign illumination 5 foot candles (54 lux), was referenced for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | CHAPEL/ LAW LIBRARY (VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 15875
0179ADA4 | ADA UPGRADES - STAGE | 0179 | The Chapel is lacking an accessible path to the stage. The stage is required to have an accessible path to it per the Americans with Disabilities Act (ADA) regulations. This project would provide for an accessible ramp or powered lift to access the stage. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | CHAPEL/ LAW LIBRARY (VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 2500
0179INT4 | INTERIOR FINISHES | 0179 | The interior finishes are in poor condition. It is recommended that the interior walls and ceilings be painted at least once in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped including the damaged area where the HVAC unit was removed. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | CHAPEL/ LAW LIBRARY (VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 63500
0178PLM5 | WATER HEATER REPLACEMENT | 0178 | There is a 30 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 1-2 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | EDUCATION A (VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 2500
0178SFT5 | FIRE ALARM SYSTEM REPLACEMENT | 0178 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and no longer comply with current requirements. The current system is no longer operating. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | EDUCATION A (VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 50800
0192SFT8 | FIRE ALARM REPLACEMENT | 0192 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and no longer comply with current requirements. The current system is no longer operating. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | AUTO MAINT SHOP/ WAREHOUSE(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 5030 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 40240
0192EXT2 | OVERHEAD COILING DOOR REPLACEMENT | 0192 | There is a 10'x14' overhead coiling door which is damaged and does not function properly. Exposure and wind have caused the door to bend, crack and lose the finish. It is original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead coiling door and replacement with new manually operated overhead coiling door. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | AUTO MAINT SHOP/ WAREHOUSE(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 5030 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 10000
0192PLM1 | 2" BACKFLOW ASSEMBLY | 0192 | State Health Law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of back siphonage or backpressure. This project allows for the installation of double check valves or reduced pressure principle backflow preventers as appropriate to the hazard and in appropriate locations near the potential source of contamination. Costs include an above ground vault, and allowance for 200 feet of 1" conduit to provide power for freeze protection. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | AUTO MAINT SHOP/ WAREHOUSE(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 5030 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 25000
0192ADA2 | LEVER ACTION HARDWARE INSTALLATION | 0192 | Section 4.13.9 of the Americans with Disabilities Act Accessible Guidelines (ADAAG) states that handles, pulls, latches, locks and other operating devices on accessible doors shall have a shape that is easy to grasp with one hand and does not require tight grasping, tight pinching, or twisting of the wrist to operate. It is recommended that compliant hardware be installed in this building to meet these guidelines. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | AUTO MAINT SHOP/ WAREHOUSE(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 5030 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 3000
0192ADA1 | ADA SIGNAGE | 0192 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | AUTO MAINT SHOP/ WAREHOUSE(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 5030 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 3000
0192INT2 | INTERIOR FINISHES | 0192 | The interior finishes are in poor condition. It is recommended that the interior walls and ceilings be painted at least once in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | AUTO MAINT SHOP/ WAREHOUSE(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 5030 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 50300
0192ADA3 | ADA RESTROOM REMODEL | 0192 | The building does not have an accessible restroom. The existing restroom does not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | AUTO MAINT SHOP/ WAREHOUSE(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 5030 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 30000
0192SFT6 | HANDRAIL INSTALLATION | 0192 | There are two steps leading from one bay to the next that do not have handrails. This project recommends the installation of handrails on both sides of the stairs, with proper returns and supports. NRS 338.180, 2012 IBC Chapter 10, Section 1012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | AUTO MAINT SHOP/ WAREHOUSE(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 5030 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 5000
0192EXT5 | EXTERIOR DOOR REPLACEMENT | 0192 | The existing exterior doors to the Auto Maintenance Shop/Warehouse are original to the building. They are showing signs of wear and deterioration from constant use and inmate abuse. Due to security concerns and the condition of the doors, replacement is recommended. This project would provide for the removal and disposal of the existing doors and frames and replacement with new exterior security doors including door frames, hardware, security glazing, painting and connections to the security system as required. A total of 3 doors was used to generate this estimate. | AUTO MAINT SHOP/ WAREHOUSE(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 5030 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 4500
0190SFT5 | FIRE ALARM SYSTEM REPLACEMENT | 0190 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and no longer comply with current requirements. The current system is no longer operating. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | CULINARY/ DINING/ CENTRAL PLANT(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 14000 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 112000
0192SFT7 | INTERIOR LANDING INSTALLATION | 0192 | There is an out-swinging interior door in the building which swings out over a step and does not have a landing. This does not comply with 2012 IBC Section 1008.1 which requires a proper landing and for the landing to be not more than 1/2" below the threshold. This project would provide for the installation of a compliant landing for the door. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | AUTO MAINT SHOP/ WAREHOUSE(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 5030 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 2000
0192SFT2 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0192 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10, 1011.6.2 exit sign illumination 5 foot candles (54 lux), was referenced for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | AUTO MAINT SHOP/ WAREHOUSE(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 5030 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 12575
0192PLM3 | WATER HEATER REPLACEMENT | 0192 | There is a 30 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 1-2 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | AUTO MAINT SHOP/ WAREHOUSE(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 5030 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 2500
0192SFT5 | MEZZANINE REMOVAL | 0192 | The second floor mezzanine appears to be constructed without building permits or structural calculations. Since the mezzanine is now enclosed, it does not meet the building code's definition of a mezzanine. The area also does not have proper ventilation, smoke detectors or compliant stairs and railings. This project would provide funding for the removal of the second floor mezzanine and stairs. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | AUTO MAINT SHOP/ WAREHOUSE(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 5030 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 10000
0192PLM4 | PLUMBING REPLACEMENT | 0192 | The sanitary wastewater and copper plumbing systems are showing signs of deterioration. Due to this deterioration, the systems are not working to their full potential. The copper lines have rusted and there are pin holes throughout the system. The lines are original to the site and are in poor condition. The hard water is also a contributing factor to this deterioration. Deposits within the pipes have caused restriction, and has slowed the water flow. This project would provide for the complete replacement of the sanitary sewer and copper piping system. | AUTO MAINT SHOP/ WAREHOUSE(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 5030 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 50300
0193INT1 | STRUCTURAL ASSESSMENT | 0193 | A second floor area was added to this building accessed via two different wooden staircases. There is no record of a CIP project for this work or of any structural evaluations having been conducted. This project recommends that a licensed engineer perform a structural investigation to assess the load bearing capacity of the structure. Future projects would be based on this report. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | MAINTENANCE SHOP (VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 3850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 5000
0193EXT4 | EXTERIOR FINISHES | 0193 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | MAINTENANCE SHOP (VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 3850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 38500
0193INT3 | INTERIOR FINISHES | 0193 | The interior finishes are in poor condition. It is recommended that the painted gypsum board interior walls and ceilings be painted at least once in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | MAINTENANCE SHOP (VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 3850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 38500
0193INT2 | JANITORS CLOSET REPAIRS | 0193 | The mop sinks in the Janitor Closets are mounted adjacent to gypsum board and are showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. Typical of two Janitor Closets. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | MAINTENANCE SHOP (VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 3850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 5600
0193ENR1 | LIGHTING UPGRADE | 0193 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, closets and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | MAINTENANCE SHOP (VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 3850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 17325
0192EXT4 | EXTERIOR FINISHES | 0192 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting and sealing the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | AUTO MAINT SHOP/ WAREHOUSE(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 5030 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 50300
0191ADA1 | ADA SIGNAGE | 0191 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | LAUNDRY & DRY CLEANING (VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 2400 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 3000
0190SEC1 | SECURITY SURVEILLANCE SYSTEM INSTALLATION | 0190 | There is no security cameras or recording system in the Culinary/Dining/Central Plant building. This is a safety issue for the staff and inmates as all areas cannot be seen by the security staff or recorded in case of an incident. This project would provide for the installation of surveillance cameras and a security system for the entire building and all required connections to existing utility systems. | CULINARY/ DINING/ CENTRAL PLANT(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 14000 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 98000
0190PLM3 | BOILER SYSTEM REPLACEMENT | 0190 | There are two hot water boilers servicing the prison. The life expectancy of these units is 20 to 25 years with proper water treatment programs and maintenance. Replacement parts for performing routine and/or emergency maintenance are difficult to locate due to the equipment’s age. This project would provide for the removal and disposal of the existing boilers, controls and mixing valves and replacement with new equipment, including all required connections to utilities and equipment. The existing chemical water treatment system will need to be tested and adjusted once the equipment is operational. $2,000 is included in this estimate for testing of the chemical water treatment system. | CULINARY/ DINING/ CENTRAL PLANT(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 14000 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 500000
0190EXT4 | EXTERIOR DOOR REPLACEMENT | 0190 | The existing exterior doors to the Culinary/Dining/Central Plant are original to the building. They are showing signs of wear and deterioration from constant use and inmate abuse. Due to security concerns and the condition of the doors, replacement is recommended. This project would provide for the removal and disposal of the existing doors and frames and replacement with new exterior security doors including door frames, hardware, security glazing, painting and connections to the security system as required. A total of 15 doors was used to generate this estimate. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | CULINARY/ DINING/ CENTRAL PLANT(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 14000 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 22500
0190ADA3 | ADA UPGRADES - DINING | 0190 | The building is lacking an accessible path of travel through the interior, the ramp in the Dining area is not compliant and there are no accessible dining tables installed. The building is used for serving inmates meals and is required to have accessible facilities per the Americans with Disabilities Act (ADA) regulations. This project would provide for an accessible path of travel, ramp from the dining area to the service line and an accessible dining table in the building. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | CULINARY/ DINING/ CENTRAL PLANT(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 14000 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 25000
0191PLM1 | 2" BACKFLOW ASSEMBLY | 0191 | State Health Law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of back siphonage or backpressure. This project allows for the installation of double check valves or reduced pressure principle backflow preventers as appropriate to the hazard and in appropriate locations near the potential source of contamination. Costs include an above ground vault, and allowance for 200 feet of 1" conduit to provide power for freeze protection. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | LAUNDRY & DRY CLEANING (VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 2400 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 25000
0191SFT1 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0191 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10, 1011.6.2 exit sign illumination 5 foot candles (54 lux), was referenced for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | LAUNDRY & DRY CLEANING (VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 2400 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 6000
0191EXT2 | ROOF REPLACEMENT | 0191 | The roof on this building was in poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1993. It is recommended that this building be re-roofed in the next 1-2 years to be consistent with the roofing program and the end of the warranty period. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | LAUNDRY & DRY CLEANING (VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 2400 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 28800
0191HVA1 | STEAM BOILER REPLACEMENT | 0191 | The steam boiler that powers the laundry equipment has been removed for use at an occupied facility. This project would provide for the installation of a new electric steam boiler including all required connections to utilities and equipment. The estimate is based on a 518 KW electric steam boiler. The existing chemical water treatment system will need to be tested and adjusted once equipment is operational. $2,000 is included in this estimate for testing of chemical water treatment system. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | LAUNDRY & DRY CLEANING (VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 2400 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 85000
0192ELE1 | LIGHTING UPGRADE | 0192 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, closets and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | AUTO MAINT SHOP/ WAREHOUSE(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 5030 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 22635
0191ADA2 | ADA RESTROOM UPGRADE | 0191 | The building does not have an accessible restroom. The existing restroom does not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom. These items may include a new sink, toilet, hardware, mirror, fixtures, flooring and paint. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | LAUNDRY & DRY CLEANING (VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 2400 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 30000
0192EXT1 | ROOF REPLACEMENT | 0192 | The single-ply roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1993. It is recommended that this building be re-roofed in the next 1-2 years to be consistent with the roofing program and the end of the warranty period. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | AUTO MAINT SHOP/ WAREHOUSE(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 5030 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 60360
0191EXT4 | EXTERIOR FINISHES | 0191 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. There are areas where the stucco is damaged from equipment hitting the walls and leaks from the rooftop HVAC equipment. This project includes funds to repair the damaged areas prior to painting. It is recommended that the building be painted in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | LAUNDRY & DRY CLEANING (VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 2400 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 24000
0191INT3 | INTERIOR FINISHES | 0191 | The interior finishes are in poor condition. It is recommended that the interior walls and ceilings be painted at least once in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | LAUNDRY & DRY CLEANING (VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 2400 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 24000
0191HVA2 | HVAC REPLACEMENT | 0191 | There are two evaporative coolers installed on the roof of this building. They are severely scaled and have reached the end of their useful and expected life. This project would provide for two new evaporative coolers to be installed, and would include all required connections to the utilities. The estimate includes removal and disposal of the old evaporative coolers. The water source heat pumps in this building are also being recommended for replacement. These heat pumps are not energy efficient, and have reached the end of their expected and useful life. This project would provide for installation of new water source heat pump units and the cleaning of the existing ducting and grilles. This project includes removal and disposal of the existing water source heat pump units and all required connections to utilities. | LAUNDRY & DRY CLEANING (VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 2400 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 60000
0191ELE1 | ELECTRICAL UPGRADE | 0191 | This building was constructed before the high demand for electrical services were needed for computers, communications systems and other electrical devices. As time has progressed, the buildings electrical demand and communications system has changed. The electrical system is utilized to its current maximum potential and the communications system is outdated. The electrical panels, switches and receptacles are at their limit. The current wiring in the building is #14 and does not meet the current demand. #14 wiring is also against State Public Works Division's Adopted Standards, 8.5.4, for lighting and power circuits. It is recommended to upgrade the entire electrical system and communications system to meet the evolving needs of the building. | LAUNDRY & DRY CLEANING (VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 2400 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 96000
0191SFT5 | FIRE ALARM REPLACEMENT | 0191 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and no longer comply with current requirements. The current system is no longer operating. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | LAUNDRY & DRY CLEANING (VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 2400 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 19200
0191EXT3 | EXTERIOR DOOR REPLACEMENT | 0191 | The existing exterior doors to the Laundry & Dry Cleaning are original to the building. They are showing signs of wear and deterioration from constant use and inmate abuse. Due to security concerns and the condition of the doors, replacement is recommended. This project would provide for the removal and disposal of the existing doors and frames and replacement with new exterior security doors including door frames, hardware, security glazing, painting and connections to the security system as required. A total of 6 doors was used to generate this estimate. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | LAUNDRY & DRY CLEANING (VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 2400 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 9000
0191PLM3 | PLUMBING REPLACEMENT | 0191 | The sanitary wastewater and copper plumbing systems are showing signs of deterioration. Due to this deterioration, the systems are not working to their full potential. The copper lines have rusted and there are pin holes throughout the system. The lines are original to the site and are in poor condition. The hard water is also a contributing factor to this deterioration. Deposits within the pipes have caused restriction, and has slowed the water flow. This project would provide for the complete replacement of the sanitary sewer and copper piping system. | LAUNDRY & DRY CLEANING (VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 2400 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 120000
0192SFT4 | VEHICLE EXHAUST EXTRACTION SYSTEM | 0192 | The Auto Maintenance Shop has no exhaust extraction system to remove toxic exhaust fumes. In enclosed areas where motor vehicles operate, mechanical ventilation shall be provided per the 2012 IBC 406.6.3 and UMC 502.14. This project would provide for the purchase and installation of a vehicle exhaust extraction system including, hoses, automatic shut off, electrical connections and roof mounted exhaust fans and equipment as provided by manufacturer. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | AUTO MAINT SHOP/ WAREHOUSE(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 5030 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 50000
0193SFT4 | EMERGENCY EYE WASH STATION | 0193 | The building has outdated containers of eye wash solution. Where the eyes or body of any person may be exposed to injurious corrosive materials, suitable facilities for quick drenching or flushing of the eyes and body shall be provided within the work area for immediate emergency use, reference OSHA 1910.151(c). This project would provide funding for the purchase and installation of an emergency eye and body wash station. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | MAINTENANCE SHOP (VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 3850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 6000
0191INT2 | LIGHTING UPGRADE | 0191 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, closets and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | LAUNDRY & DRY CLEANING (VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 2400 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 10800
0195PLM3 | PLUMBING FIXTURES REPLACEMENT | 0195 | The existing water closet and sink are reaching the end of their expected life. They are worn and damaged from many years of use and should be scheduled for replacement. This project would provide for the installation of a new water closet and sink including all plumbing parts and connections. Removal and disposal of the old fixtures is included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | GUARD TOWER 2 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1982 | 288 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 3000
0193HVA1 | EXHAUST FAN INSTALLATION - WELDING AREA | 0193 | The building has a welding area. Depending on what type of material is being welded, it may require a local hood and ventilation system. This project would provide funding for the engineering, exhaust fan, ducting, electrical connections, installation and repairs to the roof as required. OSHA 1910.252(3) was referenced for this project. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | MAINTENANCE SHOP (VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 3850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 15000
0193HVA2 | HVAC REPLACEMENT | 0193 | There are four electric heaters/air conditioning units installed in the Maintenance Shop. They are in poor condition and have reached the end of their useful and expected life. This project would provide for four new electric heaters/air conditioning units to be installed, and would include all required connections to the electrical. The estimate includes removal and disposal of the old heating/air conditioning units. The water source heat pumps in this building are also being recommended for replacement. These heat pumps are not energy efficient, and have reached the end of their expected and useful life. This project would provide for installation of new water source heat pump units and the cleaning of the existing ducting and grilles. This project includes removal and disposal of the existing water source heat pump units and all required connections to utilities. | MAINTENANCE SHOP (VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 3850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 96250
0193PLM4 | PLUMBING REPLACEMENT | 0193 | The sanitary wastewater and copper plumbing systems are showing signs of deterioration. Due to this deterioration, the systems are not working to their full potential. The copper lines have rusted and there are pin holes throughout the system. The lines are original to the site and are in poor condition. The hard water is also a contributing factor to this deterioration. Deposits within the pipes have caused restriction, and has slowed the water flow. This project would provide for the complete replacement of the sanitary sewer and copper piping system. | MAINTENANCE SHOP (VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 3850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 38500
0193SFT7 | PIPE BOLLARD INSTALLATION | 0193 | The Maintenance Shop has two sectional overhead doors. These areas are in need of bollards to protect the building. This project would provide funding for 4 eight inch diameter bollards to be located on each side of the sectional overhead doors at the exterior. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | MAINTENANCE SHOP (VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 3850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 2000
0193PLM1 | 2" BACKFLOW ASSEMBLY | 0193 | State Health Law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of back siphonage or backpressure. This project allows for the installation of double check valves or reduced pressure principle backflow preventers as appropriate to the hazard and in appropriate locations near the potential source of contamination. Costs include an above ground vault, and allowance for 200 feet of 1" conduit to provide power for freeze protection. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | MAINTENANCE SHOP (VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 3850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 25000
0195HVA1 | HVAC REPLACEMENT | 0195 | The building is conditioned by one wall-mounted heat pump. It is reaching the end of its useful and expected life. This project would provide for a new heat pump to be installed including all required connections to utilities. The estimate includes removal and disposal of the old heat pump. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | GUARD TOWER 2 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1982 | 288 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 10000
0195PLM4 | WATER HEATER REPLACEMENT | 0195 | There is a 10 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 1-2 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | GUARD TOWER 2 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1982 | 288 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 2500
0195INT3 | FLOORING REPLACEMENT | 0195 | The VCT (vinyl composite tile) flooring in the Guard Tower is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | GUARD TOWER 2 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1982 | 288 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 4032
0193SFT6 | FIRE ALARM SYSTEM REPLACEMENT | 0193 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and no longer comply with current requirements. The current system is no longer operating. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | MAINTENANCE SHOP (VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 3850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 30800
0195EXT1 | ROOF REPLACEMENT | 0195 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. Interior ceiling stains and exterior soffit stains indicate that there are active leaks. It is recommended that this building be re-roofed in the next 1-2 years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | GUARD TOWER 2 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1982 | 288 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 3456
0195ENR1 | LIGHTING UPGRADE | 0195 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed where appropriate for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | GUARD TOWER 2 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1982 | 288 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 2000
0195PLM1 | 2" BACKFLOW ASSEMBLY | 0195 | State Health Law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of back siphonage or backpressure. This project allows for the installation of double check valves or reduced pressure principle backflow preventers as appropriate to the hazard and in appropriate locations near the potential source of contamination. Costs include an above ground vault, and allowance for 200 feet of 1" conduit to provide power for freeze protection. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | GUARD TOWER 2 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1982 | 288 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 25000
0195INT2 | INTERIOR FINISHES | 0195 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | GUARD TOWER 2 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1982 | 288 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 25600
0195EXT3 | EXTERIOR DOOR REPLACEMENT | 0195 | The existing exterior doors to the Guard Tower are original to the building. They are showing signs of wear and deterioration. Due to security concerns and the condition of the doors, replacement is recommended. This project would provide for the removal and disposal of the existing doors and frames and replacement with new exterior security doors including door frames, hardware, security glazing, painting and connections to the security system as required. A total of 2 doors was used to generate this estimate. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | GUARD TOWER 2 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1982 | 288 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 3000
0195EXT2 | EXTERIOR SIDING REPLACEMENT | 0195 | The Tower has a painted masonite siding that is due for replacement. The existing siding is in poor condition and will no longer hold paint. This project recommends removing the masonite siding and replacing it with T1-11 panels finished with an oil-based stain. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | GUARD TOWER 2 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1982 | 288 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 75000
0195SFT2 | FIRE ALARM INSTALLATION | 0195 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and no longer comply with current requirements. The current system is no longer operating. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | GUARD TOWER 2 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1982 | 288 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 2304
0195PLM5 | PLUMBING REPLACEMENT | 0195 | The sanitary wastewater and copper plumbing systems are showing signs of deterioration. Due to this deterioration, the systems are not working to their full potential. The copper lines have rusted and there are pin holes throughout the system. The lines are original to the site and are in poor condition. The hard water is also a contributing factor to this deterioration. Deposits within the pipes have caused restriction, and has slowed the water flow. This project would provide for the complete replacement of the sanitary sewer and copper piping system. | GUARD TOWER 2 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1982 | 288 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 14400
0195ELE1 | ELECTRICAL UPGRADE | 0195 | This building was constructed before the high demand for electrical services were needed for computers, communications systems and other electrical devices. As time has progressed, the buildings electrical demand and communications system has changed. The electrical system is utilized to its current maximum potential and the communications system is outdated. The electrical panels, switches and receptacles are at their limit. The current wiring in the building is #14 and does not meet the current demand. #14 wiring is also against State Public Works Division's Adopted Standards, 8.5.4, for lighting and power circuits. It is recommended to upgrade the entire electrical system and communications system to meet the evolving needs of the building. | GUARD TOWER 2 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1982 | 288 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 11520
0185PLM4 | WATER HEATER REPLACEMENT | 0185 | There are two 120 gallon electric water heaters in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 1-2 years. It is recommended that two new electric water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 6 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 15000
0188ADA6 | ADA ACCESSIBLE COUNTER | 0188 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The admitting station has a service counter for the inmates and staff to approach which does not meet current codes. Section 7.2 of the Americans with Disabilities Act Accessible Guidelines (ADAAG) states that the counter must have a portion which is at least 36" in length with a maximum height of 36" above the finish floor. This project will provide an accessible counter space in accordance with this requirement. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | MEDICAL UNIT 8 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 5150 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 2000
0195SFT1 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0195 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10, 1011.6.2 exit sign illumination 5 foot candles (54 lux), was referenced for this project. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | GUARD TOWER 2 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1982 | 288 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 2000
0194PLM3 | PLUMBING FIXTURES REPLACEMENT | 0194 | The existing water closet and sink are reaching the end of their expected life. They are worn and damaged from many years of use and should be scheduled for replacement. This project would provide for the installation of a new water closet and sink including all plumbing parts and connections. Removal and disposal of the old fixtures is included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | GUARD TOWER 1 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1982 | 288 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 3000
0192HVA1 | HVAC REPLACEMENT | 0192 | There are two electric heaters installed in the Auto Maint Shop. They are in poor condition and have reached the end of their useful and expected life. This project would provide for two new electric heaters to be installed, and would include all required connections to the electrical. The estimate includes removal and disposal of the old electric heaters. The water source heat pumps in this building are also being recommended for replacement. These heat pumps are not energy efficient, and have reached the end of their expected and useful life. This project would provide for installation of new water source heat pump units and the cleaning of the existing ducting and grilles. This project includes removal and disposal of the existing water source heat pump units and all required connections to utilities. | AUTO MAINT SHOP/ WAREHOUSE(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 5030 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 125750
0193EXT3 | OVERHEAD COILING DOOR REPLACEMENT | 0193 | There are two 10'x12' overhead coiling doors which are damaged and do not function properly. Exposure and wind have caused the doors to bend, crack and lose their finish. They are original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead coiling doors and replacement with new manually operated overhead coiling doors. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | MAINTENANCE SHOP (VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 3850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 20000
0193ADA1 | LEVER ACTION HARDWARE INSTALLATION | 0193 | Section 4.13.9 of the Americans with Disabilities Act Accessible Guidelines (ADAAG) states that handles, pulls, latches, locks and other operating devices on accessible doors shall have a shape that is easy to grasp with one hand and does not require tight grasping, tight pinching, or twisting of the wrist to operate. It is recommended that compliant hardware be installed in this building to meet these guidelines. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | MAINTENANCE SHOP (VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 3850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 2500
0193SFT2 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0193 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10, 1011.6.2 exit sign illumination 5 foot candles (54 lux), was referenced for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | MAINTENANCE SHOP (VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 3850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 9625
0194SFT2 | FIRE ALARM INSTALLATION | 0194 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and no longer comply with current requirements. The current system is no longer operating. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | GUARD TOWER 1 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1982 | 288 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 2304
0194PLM5 | PLUMBING REPLACEMENT | 0194 | The sanitary wastewater and copper plumbing systems are showing signs of deterioration. Due to this deterioration, the systems are not working to their full potential. The copper lines have rusted and there are pin holes throughout the system. The lines are original to the site and are in poor condition. The hard water is also a contributing factor to this deterioration. Deposits within the pipes have caused restriction, and has slowed the water flow. This project would provide for the complete replacement of the sanitary sewer and copper piping system. | GUARD TOWER 1 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1982 | 288 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 14400
0194EXT2 | EXTERIOR DOOR REPLACEMENT | 0194 | The existing exterior doors to the Guard Tower are original to the building. They are showing signs of wear and deterioration. Due to security concerns and the condition of the doors, replacement is recommended. This project would provide for the removal and disposal of the existing doors and frames and replacement with new exterior security doors including door frames, hardware, security glazing, painting and connections to the security system as required. A total of 2 doors was used to generate this estimate. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | GUARD TOWER 1 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1982 | 288 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 3000
0194ELE1 | ELECTRICAL UPGRADE | 0194 | This building was constructed before the high demand for electrical services were needed for computers, communications systems and other electrical devices. As time has progressed, the buildings electrical demand and communications system has changed. The electrical system is utilized to its current maximum potential and the communications system is outdated. The electrical panels, switches and receptacles are at their limit. The current wiring in the building is #14 and does not meet the current demand. #14 wiring is also against State Public Works Division's Adopted Standards, 8.5.4, for lighting and power circuits. It is recommended to upgrade the entire electrical system and communications system to meet the evolving needs of the building. | GUARD TOWER 1 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1982 | 288 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 11520
0193EXT5 | EXTERIOR DOOR REPLACEMENT | 0193 | The existing exterior doors to the Auto Maintenance Shop are original to the building. They are showing signs of wear and deterioration from constant use and inmate abuse. Due to security concerns and the condition of the doors, replacement is recommended. This project would provide for the removal and disposal of the existing doors and frames and replacement with new exterior security doors including door frames, hardware, security glazing, painting and connections to the security system as required. A total of 2 doors was used to generate this estimate. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | MAINTENANCE SHOP (VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 3850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 3000
0194PLM1 | 2" BACKFLOW ASSEMBLY | 0194 | State Health Law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of back siphonage or backpressure. This project allows for the installation of double check valves or reduced pressure principle backflow preventers as appropriate to the hazard and in appropriate locations near the potential source of contamination. Costs include an above ground vault, and allowance for 200 feet of 1" conduit to provide power for freeze protection. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | GUARD TOWER 1 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1982 | 288 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 25000
0193EXT1 | ROOF REPLACEMENT | 0193 | The roof on this building was in poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1993. It is recommended that this building be re-roofed in the next 1-2 years to be consistent with the roofing program and the end of the warranty period. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | MAINTENANCE SHOP (VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 3850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 46200
0194PLM4 | WATER HEATER REPLACEMENT | 0194 | There is a 10 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 1-2 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | GUARD TOWER 1 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1982 | 288 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 2500
0194INT3 | FLOORING REPLACEMENT | 0194 | The VCT (vinyl composite tile) flooring in the Guard Tower is damaged and has reached the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | GUARD TOWER 1 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1982 | 288 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 4032
0194INT2 | INTERIOR FINISHES | 0194 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | GUARD TOWER 1 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1982 | 288 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 25600
0194ENR1 | LIGHTING UPGRADE | 0194 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed where appropriate for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | GUARD TOWER 1 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1982 | 288 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 2000
0194SFT1 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0194 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10, 1011.6.2 exit sign illumination 5 foot candles (54 lux), was referenced for this project. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | GUARD TOWER 1 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1982 | 288 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 2000
0194HVA1 | HVAC REPLACEMENT | 0194 | The building is conditioned by one wall-mounted heat pump. It is reaching the end of its useful and expected life. This project would provide for a new heat pump to be installed including all required connections to utilities. The estimate includes removal and disposal of the old heat pump. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | GUARD TOWER 1 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1982 | 288 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 10000
0193ELE1 | ELECTRICAL UPGRADE | 0193 | This building was constructed before the high demand for electrical services were needed for computers, communications systems and other electrical devices. As time has progressed, the buildings electrical demand and communications system has changed. The electrical system is utilized to its current maximum potential and the communications system is outdated. The electrical panels, switches and receptacles are at their limit. The current wiring in the building is #14 and does not meet the current demand. #14 wiring is also against State Public Works Division's Adopted Standards, 8.5.4, for lighting and power circuits. It is recommended to upgrade the entire electrical system and communications system to meet the evolving needs of the building. | MAINTENANCE SHOP (VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 3850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 154000
0193PLM3 | WATER HEATER REPLACEMENT | 0193 | There is a 30 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 1-2 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | MAINTENANCE SHOP (VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 3850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 2500
0193ADA2 | ADA RESTROOM REMODEL | 0193 | The building does not have an accessible restroom. The existing restroom does not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | MAINTENANCE SHOP (VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 3850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 30000
0194EXT3 | ROOF REPLACEMENT | 0194 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. Interior ceiling stains and exterior soffit stains indicate that there are active leaks. It is recommended that this building be re-roofed in the next 1-2 years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | GUARD TOWER 1 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1982 | 288 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 3456
0187SFT4 | CONTROL PANEL, DOORS AND LOCKS REPLACEMENT | 0187 | Problems exist with the door control panel and door locks for the cells. The panel and locks are original equipment and should be scheduled for replacement. Buttons on the panel do not work or get stuck frequently and the door locks are not consistently responsive to the panel. Repairs to the control panel and locks are difficult because replacement parts are no longer being manufactured for the units. Improper operation will cause security risks to the staff and inmates. It is recommended that the door control panel and 56 door locks be replaced. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 7 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 18090 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 840000
0185EXT4 | ROOF REPLACEMENT | 0185 | The roof on this building was in poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1993. It is recommended to replace the singly-ply membrane and repair the Cor-ten roofing system as needed in the next 1-2 years to be consistent with the roofing program and the end of the warranty period. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 6 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 166200
0186EXT2 | EXTERIOR FINISHES | 0186 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | RECREATION/ GYM (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 12800 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 128000
0186PLM1 | 2" BACKFLOW ASSEMBLY | 0186 | State Health Law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of back siphonage or backpressure. This project allows for the installation of double check valves or reduced pressure principle backflow preventers as appropriate to the hazard and in appropriate locations near the potential source of contamination. Costs include an above ground vault, and allowance for 200 feet of 1" conduit to provide power for freeze protection. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | RECREATION/ GYM (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 12800 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 25000
0186INT3 | FLOORING REPLACEMENT | 0186 | The composite flooring in the gymnasium and the VCT (vinyl composite tile) in the Gun Post are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of a new composite floor in the gymnasium and 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the Gun Post in the next 1-2 years. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | RECREATION/ GYM (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 12800 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 204800
0186EXT4 | EXTERIOR DOOR REPLACEMENT | 0186 | The existing exterior doors to the Recreation / Gym are original to the building. They are showing signs of wear and deterioration from constant use and inmate abuse. Due to security concerns and the condition of the doors, replacement is recommended. This project would provide for the removal and disposal of the existing doors and frames, and replacement with new exterior security doors including door frames, hardware, security glazing, painting and connections to the security system as required. A total of 5 doors was used to generate this estimate. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | RECREATION/ GYM (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 12800 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 7500
0186SEC2 | SECURITY SURVEILLANCE SYSTEM INSTALLATION | 0186 | There is no security camera or recording system in the Recreation/Gym Building. This is a safety issue for the staff and inmates as all areas cannot be seen by the security staff or recorded in case of an incident. This project would provide for the installation of surveillance cameras and a security system for the entire building and all required connections to existing utility systems. | RECREATION/ GYM (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 12800 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 89600
0186PLM4 | PLUMBING REPLACEMENT | 0186 | The sanitary wastewater and copper plumbing systems are showing signs of deterioration. Due to this deterioration, the systems are not working to their full potential. The copper lines have rusted and there are pin holes throughout the system. The lines are original to the site and are in poor condition. The hard water is also a contributing factor to this deterioration. Deposits within the pipes have caused restriction, and has slowed the water flow. This project would provide for the complete replacement of the sanitary sewer and copper piping system. | RECREATION/ GYM (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 12800 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 128000
0186HVA1 | HVAC REPLACEMENT | 0186 | The Water Source Heat Pumps in the building should be scheduled for replacement. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of new Water Source Heat Pump units and the cleaning of the existing ducting and grilles. This project includes removal and disposal of the existing Water Source Heat Pump units and all required connections to utilities. | RECREATION/ GYM (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 12800 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 320000
0186ADA4 | LEVER ACTION HARDWARE INSTALLATION | 0186 | Section 4.13.9 of the Americans with Disabilities Act Accessible Guidelines (ADAAG) states that handles, pulls, latches, locks and other operating devices on accessible doors shall have a shape that is easy to grasp with one hand and does not require tight grasping, tight pinching, or twisting of the wrist to operate. It is recommended that compliant hardware be installed in this building to meet these guidelines. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | RECREATION/ GYM (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 12800 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 6000
0187INT4 | LIGHTING UPGRADE | 0187 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, conference rooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 7 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 18090 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 81405
0185ADA4 | ADA SIGNAGE | 0185 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 6 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 4000
0187PLM6 | PLUMBING FIXTURE REPLACEMENT | 0187 | Approximately half of the plumbing fixtures in the cells are separate porcelain wall hung lavatories and water closets. These units are in poor condition and should be replaced with stainless steel fixtures designed for correctional facilities. This project would provide for the removal and replacement of the old porcelain plumbing fixtures with new stainless steel fixtures. The estimate is based on installing a 50 separate water closets and sinks in the same place as the existing porcelain fixtures. If combination style units are feasible to install, there may be a cost savings on the materials, but additional work to install. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 7 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 18090 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 375000
0187ADA6 | ADA UPGRADES | 0187 | 3% of the cells in each housing unit are required to comply with ADA accessibility guidelines. This unit does not have any accessible cells, showers, drinking fountains or path of travel through the unit. This project would provide for 2 accessible cells, 1 accessible shower, 2 accessible drinking fountains, a compliant path of travel from the entrance of the building to these areas and any other necessary upgrades. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 7 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 18090 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 70000
0187EXT4 | EXTERIOR FINISHES | 0187 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 7 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 18090 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 180900
0187ELE3 | ELECTRICAL REPLACEMENT | 0187 | This building was constructed before the high demand for electrical services were needed for computers, communications systems and other electrical devices. As time has progressed, the buildings electrical demand and communications system has changed. The electrical system is utilized to its current maximum potential and the communications system is outdated. The electrical panels, switches and receptacles are at their limit. The current wiring in the building is #14 and does not meet the current demand. #14 wiring is also against State Public Works Division's Adopted Standards, 8.5.4, for lighting and power circuits. It is recommended to upgrade the entire electrical system and communications system to meet the evolving needs of the building. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 7 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 18090 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 723600
0187ADA1 | LEVER ACTION HARDWARE INSTALLATION | 0187 | Section 4.13.9 of the Americans with Disabilities Act Accessible Guidelines (ADAAG) states that handles, pulls, latches, locks and other operating devices on accessible doors shall have a shape that is easy to grasp with one hand and does not require tight grasping, tight pinching, or twisting of the wrist to operate. It is recommended that compliant hardware be installed in this building to meet these guidelines. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 7 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 18090 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 3000
0187PLM5 | WATER HEATER REPLACEMENT | 0187 | There are two 120 gallon electric water heaters in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 1-2 years. It is recommended that two new electric water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 7 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 18090 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 15000
0187EXT3 | ROOF REPLACEMENT | 0187 | The roof on this building was in poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1993. It is recommended to replace the singly-ply membrane and repair the Cor-ten roofing system as needed in the next 1-2 years to be consistent with the roofing program and the end of the warranty period. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 7 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 18090 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 217080
0187ADA5 | ADA SIGNAGE | 0187 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 7 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 18090 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 3000
0186SFT5 | FIRE ALARM SYSTEM REPLACEMENT | 0186 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and no longer comply with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 "If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure". When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | RECREATION/ GYM (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 12800 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 102400
0186SFT3 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0186 | The building has a floor area greater than 12,000 square feet. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | RECREATION/ GYM (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 12800 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 179200
0186ENR1 | LIGHTING UPGRADE | 0186 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, conference rooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | RECREATION/ GYM (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 12800 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 57600
0186SFT2 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0186 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10, 1011.6.2 exit sign illumination 5 foot candles (54 Lux), was referenced for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | RECREATION/ GYM (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 12800 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 32000
0186EXT3 | ROOF REPLACEMENT | 0186 | The roof on this building was in poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1993. It is recommended to replace the singly-ply membrane and repair the Cor-ten roofing system as needed in the next 1-2 years to be consistent with the roofing program and the end of the warranty period. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | RECREATION/ GYM (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 12800 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 153600
0192ELE2 | ELECTRICAL UPGRADE | 0192 | This building was constructed before the high demand for electrical services were needed for computers, communications systems and other electrical devices. As time has progressed, the buildings electrical demand and communications system has changed. The electrical system is utilized to its current maximum potential and the communications system is outdated. The electrical panels, switches and receptacles are at their limit. The current wiring in the building is #14 and does not meet the current demand. #14 wiring is also against State Public Works Division's Adopted Standards, 8.5.4, for lighting and power circuits. It is recommended to upgrade the entire electrical system and communications system to meet the evolving needs of the building. | AUTO MAINT SHOP/ WAREHOUSE(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 5030 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 201200
0186ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0186 | This building contains a water fountain. The 2012 IBC Section 1109.5 states where a water fountain is provided, at least half should be accessible. This project would provide funding for the purchase and installation of a new accessible fixed high/ low ADA drinking fountain. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | RECREATION/ GYM (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 12800 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 4000
0190EXT5 | EXTERIOR FINISHES | 0190 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. There are areas where the stucco is damaged from equipment hitting the walls and leaks from the rooftop HVAC equipment. This project includes funds to repair the damaged areas prior to painting. It is recommended that the building be painted in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | CULINARY/ DINING/ CENTRAL PLANT(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 14000 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 140000
0186INT1 | INTERIOR FINISHES | 0186 | The interior finishes are in poor condition. It is recommended that the interior walls and ceilings be painted at least once in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | RECREATION/ GYM (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 12800 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 128000
0186ELE2 | ELECTRICAL UPGRADE | 0186 | This building was constructed before the high demand for electrical services were needed for computers, communications systems and other electrical devices. As time has progressed, the buildings electrical demand and communications system has changed. The electrical system is utilized to its current maximum potential and the communications system is outdated. The electrical panels, switches and receptacles are at their limit. The current wiring in the building is #14 and does not meet the current demand. #14 wiring is also against State Public Works Division's Adopted Standards, 8.5.4, for lighting and power circuits. It is recommended to upgrade the entire electrical system and communications system to meet the evolving needs of the building. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | RECREATION/ GYM (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 12800 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 512000
0185INT3 | LIGHTING UPGRADE | 0185 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, conference rooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 6 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 62325
0186ADA1 | ADA SIGNAGE | 0186 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | RECREATION/ GYM (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 12800 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 4000
0185SEC1 | CONTROL PANEL, DOORS AND LOCKS REPLACEMENT | 0185 | Problems exist with the door control panel and door locks for the cells. The panel and locks are original equipment and should be scheduled for replacement. Buttons on the panel do not work or get stuck frequently and the door locks are not consistently responsive to the panel. Repairs to the control panel and locks are difficult because replacement parts are no longer being manufactured for the units. Improper operation will cause security risks to the staff and inmates. It is recommended that the door control panel and 56 door locks be replaced. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 6 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 840000
0185PLM5 | PLUMBING REPLACEMENT | 0185 | The sanitary wastewater and copper plumbing systems are showing signs of deterioration. Due to this deterioration, the systems are not working to their full potential. The copper lines have rusted and there are pin holes throughout the system. The lines are original to the site and are in poor condition. The hard water is also a contributing factor to this deterioration. Deposits within the pipes have caused restriction, and has slowed the water flow. This project would provide for the complete replacement of the sanitary sewer and copper piping system. | HOUSING UNIT 6 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 692500
0185EXT5 | EXTERIOR DOOR REPLACEMENT | 0185 | The existing exterior door to the Housing Unit 6 is original to the building. It is showing signs of wear and deterioration from constant use and inmate abuse. Due to security concerns and the condition of the door, replacement is recommended. This project would provide for the removal and disposal of the existing door and frame, and replacement with new exterior security door including door frame, hardware, security glazing, painting and connections to the security system as required. A total of 1 door was used to generate this estimate. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 6 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 1500
0185SFT4 | FIRE ALARM SYSTEM REPLACEMENT | 0185 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and no longer comply with current requirements. The current system is no longer operating. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | HOUSING UNIT 6 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 110800
0185ELE4 | ELECTRICAL UPGRADE | 0185 | This building was constructed before the high demand for electrical services were needed for computers, communications systems and other electrical devices. As time has progressed, the buildings electrical demand and communications system has changed. The electrical system is utilized to its current maximum potential and the communications system is outdated. The electrical panels, switches and receptacles are at their limit. The current wiring in the building is #14 and does not meet the current demand. #14 wiring is also against State Public Works Division's Adopted Standards, 8.5.4, for lighting and power circuits. It is recommended to upgrade the entire electrical system and communications system to meet the evolving needs of the building. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 6 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 554000
0185HVA2 | HVAC REPLACEMENT | 0185 | The Water Source Heat Pumps in the building should be scheduled for replacement. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of new Water Source Heat Pump units and the cleaning of the existing ducting and grilles. This project includes removal and disposal of the existing Water Source Heat Pump units and all required connections to utilities. | HOUSING UNIT 6 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 346250
0185SEC2 | SECURITY SURVEILLANCE SYSTEM INSTALLATION | 0185 | There is no security camera or recording system in the Housing Unit 6 Building. This is a safety issue for the staff and inmates as all areas cannot be seen by the security staff or recorded in case of an incident. This project would provide for the installation of surveillance cameras and a security system for the entire building and all required connections to existing utility systems. | HOUSING UNIT 6 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 96950
0185SFT3 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0185 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10, 1011.6.2 exit sign illumination 5 foot candles (54 Lux), was referenced for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 6 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 34625
0185PLM3 | PLUMBING FIXTURE REPLACEMENT | 0185 | Approximately half of the plumbing fixtures in the cells are separate porcelain wall hung lavatories and water closets. These units are in poor condition and should be replaced with stainless steel fixtures designed for correctional facilities. This project would provide for the removal and replacement of the old porcelain plumbing fixtures with new stainless steel fixtures. The estimate is based on installing a 44 separate water closets and sinks in the same place as the existing porcelain fixtures. If combination style units are feasible to install, there may be a cost savings on the materials, but additional work to install. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 6 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 375000
0187INT3 | INTERIOR FINISHES | 0187 | The interior finishes are in poor condition. It is recommended that the interior walls and ceilings be painted at least once in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 7 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 18090 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 180900
0186SFT4 | WINDOW INSTALLATION | 0186 | The upper level room overlooking the gymnasium is missing several window panels. A total of nine panels have been removed creating a safety hazard. It is recommended to reinstall the glazing panels. This estimate is for the purchase and installation 9-6'x5' security glazing panels. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | RECREATION/ GYM (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 12800 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 21600
0190PLM1 | 2" BACKFLOW ASSEMBLY, VAULT, AND POWER | 0190 | State Health Law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of back siphonage or backpressure. This project allows for the installation of double check valves or reduced pressure principle backflow preventers as appropriate to the hazard and in appropriate locations near the potential source of contamination. Costs include an above ground vault, and allowance for 200 feet of 1" conduit to provide power for freeze protection. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | CULINARY/ DINING/ CENTRAL PLANT(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 14000 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 25000
0187PLM4 | 2" BACKFLOW ASSEMBLY | 0187 | State Health Law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of back siphonage or backpressure. This project allows for the installation of double check valves or reduced pressure principle backflow preventers as appropriate to the hazard and in appropriate locations near the potential source of contamination. Costs include an above ground vault, and allowance for 200 feet of 1" conduit to provide power for freeze protection. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 7 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 18090 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 30000
0188EXT4 | EXTERIOR DOOR REPLACEMENT | 0188 | The existing exterior doors to the Housing Unit 8 are original to the building. They are showing signs of wear and deterioration from constant use and inmate abuse. Due to security concerns and the condition of the doors, replacement is recommended. This project would provide for the removal and disposal of the existing doors and frames and replacement with new exterior security doors including door frames, hardware, security glazing, painting and connections to the security system as required. A total of 10 doors was used to generate this estimate. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | MEDICAL UNIT 8 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 5150 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 15000
0188SFT3 | FIRE ALARM SYSTEM REPLACEMENT | 0188 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and no longer comply with current requirements. The current system is no longer operating. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | MEDICAL UNIT 8 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 5150 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 41200
0188HVA1 | HVAC REPLACEMENT | 0188 | The Water Source Heat Pumps in the building should be scheduled for replacement. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of new Water Source Heat Pump units and the cleaning of the existing ducting and grilles. This project includes removal and disposal of the existing Water Source Heat Pump units and all required connections to utilities. | MEDICAL UNIT 8 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 5150 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 128750
0188SEC1 | CONTROL PANEL, DOORS AND LOCKS REPLACEMENT | 0188 | Problems exist with the door control panel and door locks for the controlled doors. The panel and locks are original equipment and should be scheduled for replacement. Buttons on the panel do not work or get stuck frequently and the door locks are not consistently responsive to the panel. Repairs to the control panel and locks are difficult because replacement parts are no longer being manufactured for the units. Improper operation will cause security risks to the staff and inmates. It is recommended that the door control panel and 10 door locks be replaced. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | MEDICAL UNIT 8 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 5150 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 150000
0188ELE3 | ELECTRICAL UPGRADE | 0188 | This building was constructed before the high demand for electrical services were needed for computers, communications systems and other electrical devices. As time has progressed, the buildings electrical demand and communications system has changed. The electrical system is utilized to its current maximum potential and the communications system is outdated. The electrical panels, switches and receptacles are at their limit. The current wiring in the building is #14 and does not meet the current demand. #14 wiring is also against State Public Works Division's Adopted Standards, 8.5.4, for lighting and power circuits. It is recommended to upgrade the entire electrical system and communications system to meet the evolving needs of the building. | MEDICAL UNIT 8 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 5150 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 206000
0188INT3 | INTERIOR FINISHES | 0188 | The interior finishes are in poor condition. It is recommended that the interior walls and ceilings be painted at least once in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | MEDICAL UNIT 8 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 5150 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 51500
0190ADA4 | RESTROOM REMODEL | 0190 | The water closets and the lavatories in the five restrooms throughout the building are worn from many years of use and being idle due to multiple closures. It is recommended that all fixtures be replaced with new units. At least two of the new units and restroom layouts are also required to comply with ADA requirements. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | CULINARY/ DINING/ CENTRAL PLANT(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 14000 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 150000
0188EXT3 | EXTERIOR FINISHES | 0188 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | MEDICAL UNIT 8 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 5150 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 51500
0190EXT3 | ROOF REPLACEMENT | 0190 | The roof on this building was in poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1993. It is recommended to replace the singly-ply membrane and repair the Cor-ten roofing system as needed in the next 1-2 years to be consistent with the roofing program and the end of the warranty period. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | CULINARY/ DINING/ CENTRAL PLANT(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 14000 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 168000
0188PLM3 | WATER HEATER REPLACEMENT | 0188 | There is a 30 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 1-2 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | MEDICAL UNIT 8 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 5150 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 2500
0190INT1 | INTERIOR FINISHES | 0190 | The interior finishes are in poor condition. It is recommended that the interior walls and ceilings be painted at least once in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | CULINARY/ DINING/ CENTRAL PLANT(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 14000 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 140000
0190ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0190 | This building contains a water fountain. The 2012 IBC Section 1109.5 states where a water fountain is provided, at least half should be accessible. This project would provide funding for the purchase and installation of a new accessible fixed high/ low ADA drinking fountain. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | CULINARY/ DINING/ CENTRAL PLANT(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 14000 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 4000
0190INT2 | LIGHTING UPGRADE | 0190 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, conference rooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | CULINARY/ DINING/ CENTRAL PLANT(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 14000 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 63000
0190ADA1 | ADA SIGNAGE | 0190 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | CULINARY/ DINING/ CENTRAL PLANT(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 14000 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 3000
0190SFT1 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0190 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10, 1011.6.2 exit sign illumination 5 foot candles (54 Lux), was referenced for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | CULINARY/ DINING/ CENTRAL PLANT(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 14000 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 35000
0190CUL1 | KITCHEN EQUIPMENT REPLACEMENT | 0190 | Most of the kitchen cooking equipment has been removed from the building to supply occupied facilities. The equipment that is still installed is original to the building and has reached the end of its lifetime. It is recommended that the equipment be scheduled for replacement in the next one to two years, including ovens and hoods, grills, sinks and dishwashers. This project provides for the removal and disposal of the existing equipment and replacement with new equipment. The propane tanks have been removed from the site. If any propane fired equipment is installed, additional costs must be included for the purchase and installation of the propane system. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | CULINARY/ DINING/ CENTRAL PLANT(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 14000 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 300000
0190ELE2 | ELECTRICAL UPGRADE | 0190 | This building was constructed before the high demand for electrical services were needed for computers, communications systems and other electrical devices. As time has progressed, the buildings electrical demand and communications system has changed. The electrical system is utilized to its current maximum potential and the communications system is outdated. The electrical panels, switches and receptacles are at their limit. The current wiring in the building is #14 and does not meet the current demand. #14 wiring is also against State Public Works Division's Adopted Standards, 8.5.4, for lighting and power circuits. It is recommended to upgrade the entire electrical system and communications system to meet the evolving needs of the building. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | CULINARY/ DINING/ CENTRAL PLANT(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 14000 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 560000
0190PLM4 | PLUMBING REPLACEMENT | 0190 | The sanitary wastewater and copper plumbing systems are showing signs of deterioration. Due to this deterioration, the systems are not working to their full potential. The copper lines have rusted and there are pin holes throughout the system. The lines are original to the site and are in poor condition. The hard water is also a contributing factor to this deterioration. Deposits within the pipes have caused restriction, and has slowed the water flow. This project would provide for the complete replacement of the sanitary sewer and copper piping system. | CULINARY/ DINING/ CENTRAL PLANT(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 14000 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 700000
0190HVA1 | HVAC REPLACEMENT | 0190 | Four evaporative coolers are installed on the roof of this building. They are severely scaled and have reached the end of their useful and expected life. This project would provide for four new evaporative coolers to be installed including all required connections to utilities. The estimate includes removal and disposal of the old coolers. The water source heat pumps in this building are also being recommended for replacement. These heat pumps are not energy efficient, and have reached the end of their expected and useful life. This project would provide for installation of new water source heat pump units and the cleaning of the existing ducting and grilles. This project includes removal and disposal of the existing water source heat pump units and all required connections to utilities. | CULINARY/ DINING/ CENTRAL PLANT(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 14000 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 350000
0190SFT3 | FIRE SUPPRESSION SYSTEM INSTALLATION/ UPGRADE | 0190 | The building has a floor area greater than 12,000 square feet. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention for the areas not currently sprinklered in the event the building is remodeled or an addition is undertaken. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | CULINARY/ DINING/ CENTRAL PLANT(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 14000 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 196000
0188EXT2 | ROOF REPLACEMENT | 0188 | The roof on this building was in poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1993. It is recommended to replace the singly-ply membrane and repair the Cor-ten roofing system as needed in the next 1-2 years to be consistent with the roofing program and the end of the warranty period. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | MEDICAL UNIT 8 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 5150 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 61800
0186ADA5 | ADA RESTROOM/ SHOWER REMODEL | 0186 | The existing restroom and shower area is in poor condition and does not meet ADA accessibility standards. This project would provide for the remodeling of the restroom / shower area including new floor tile and wall finishes, fixtures and providing ADA compliance. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | RECREATION/ GYM (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 12800 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 37000
0187SFT5 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0187 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10, 1011.6.2 exit sign illumination 5 foot candles (54 Lux), was referenced for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 7 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 18090 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 45225
0187SEC1 | SECURITY SURVEILLANCE SYSTEM INSTALLATION | 0187 | There is no security camera or recording system in the Housing Unit 7 Building. This is a safety issue for the staff and inmates as all areas cannot be seen by the security staff or recorded in case of an incident. This project would provide for the installation of surveillance cameras and a security system for the entire building and all required connections to existing utility systems. | HOUSING UNIT 7 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 18090 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 126630
0187EXT5 | EXTERIOR DOOR REPLACEMENT | 0187 | The existing exterior door to the Housing Unit 7 is original to the building. It is showing signs of wear and deterioration from constant use and inmate abuse. Due to security concerns and the condition of the door, replacement is recommended. This project would provide for the removal and disposal of the existing door and frame, and replacement with new exterior security door including door frame, hardware, security glazing, painting and connections to the security system as required. A total of 1 door was used to generate this estimate. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 7 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 18090 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 1500
0185EXT6 | EXTERIOR FINISHES | 0185 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 6 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 138500
0187PLM7 | PLUMBING REPLACEMENT | 0187 | The sanitary wastewater and copper plumbing systems are showing signs of deterioration. Due to this deterioration, the systems are not working to their full potential. The copper lines have rusted and there are pin holes throughout the system. The lines are original to the site and are in poor condition. The hard water is also a contributing factor to this deterioration. Deposits within the pipes have caused restriction, and has slowed the water flow. This project would provide for the complete replacement of the sanitary sewer and copper piping system. | HOUSING UNIT 7 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 18090 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 904500
0185INT4 | INTERIOR FINISHES | 0185 | The interior finishes are in poor condition. It is recommended that the interior walls and ceilings be painted at least once in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 6 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 138500
0187HVA2 | HVAC REPLACEMENT | 0187 | The Water Source Heat Pumps in the building should be scheduled for replacement. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of new Water Source Heat Pump units and the cleaning of the existing ducting and grilles. This project includes removal and disposal of the existing Water Source Heat Pump units and all required connections to utilities. | HOUSING UNIT 7 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 18090 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 452250
0194EXT1 | EXTERIOR SIDING REPLACEMENT | 0194 | The Tower has a painted masonite siding that is due for replacement. The existing siding is in poor condition and will no longer hold paint. This project recommends removing the masonite siding and replacing it with T1-11 panels finished with an oil-based stain. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | GUARD TOWER 1 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1982 | 288 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 75000
0188ADA3 | ADA SIGNAGE | 0188 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | MEDICAL UNIT 8 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 5150 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 2000
0187INT1 | REPAIR ELEVATOR | 0187 | This building has an elevator, but it has been out of service for some time, and it does not comply with ADA standards. This project would provide funding to repair the elevator to improve maintenance, facilitate control of this building and comply with the ICC/ANSI A117.2009 Section 407. These repairs are to include but not limited to updating the control panel, door reversing light beams, call button, hall station upgrades, and a hands-free telephone. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 7 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 18090 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 80000
0188ADA1 | LEVER ACTION HARDWARE INSTALLATION | 0188 | Section 4.13.9 of the Americans with Disabilities Act Accessible Guidelines (ADAAG) states that handles, pulls, latches, locks and other operating devices on accessible doors shall have a shape that is easy to grasp with one hand and does not require tight grasping, tight pinching, or twisting of the wrist to operate. It is recommended that compliant hardware be installed in this building to meet these guidelines. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | MEDICAL UNIT 8 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 5150 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 15000
0188ELE2 | ROOFTOP SECURITY LIGHT REMOVAL | 0188 | The building has roof-mounted security lights that have been superseded by the installation of a high-mast security lighting system. This project will provide funding for the removal of the fixtures, conduit and associated wiring removed back to the panel. This will free up capacity for other electrical needs in the buildings. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | MEDICAL UNIT 8 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 5150 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 2500
0188ENR1 | LIGHTING UPGRADE | 0188 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, conference rooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | MEDICAL UNIT 8 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 5150 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 23175
0188ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0188 | This building contains a water fountain. The 2012 IBC Section 1109.5 states where a water fountain is provided, at least half should be accessible. This project would provide funding for the purchase and installation of a new accessible fixed high/ low ADA drinking fountain. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | MEDICAL UNIT 8 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 5150 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 4000
0188SFT2 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0188 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10, 1011.6.2 exit sign illumination 5 foot candles (54 Lux), was referenced for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | MEDICAL UNIT 8 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 5150 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 12875
0188PLM1 | 2" BACKFLOW ASSEMBLY | 0188 | State Health Law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of back siphonage or backpressure. This project allows for the installation of double check valves or reduced pressure principle backflow preventers as appropriate to the hazard and in appropriate locations near the potential source of contamination. Costs include an above ground vault, and allowance for 200 feet of 1" conduit to provide power for freeze protection. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | MEDICAL UNIT 8 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 5150 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 25000
0188ADA7 | ADA RESTROOM REMODELS | 0188 | The accessible restrooms in the building are not completely compliant and do not have stainless steel, institutional-grade equipment. A complete retrofit is necessary. This project would provide funding for remodeling the four Men's and Women's restrooms into ADA compliant restrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint including that the fixtures are institutional-grade, stainless steel fixtures. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | MEDICAL UNIT 8 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 5150 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 30000
0188SEC2 | SECURITY SURVEILLANCE SYSTEM INSTALLATION | 0188 | There is no security camera or recording system in the Medical Unit 8 Building. This is a safety issue for the staff and inmates as all areas cannot be seen by the security staff or recorded in case of an incident. This project would provide for the installation of surveillance cameras and a security system for the entire building and all required connections to existing utility systems. | MEDICAL UNIT 8 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 5150 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 36050
0188PLM4 | PLUMBING REPLACEMENT | 0188 | The sanitary wastewater and copper plumbing systems are showing signs of deterioration. Due to this deterioration, the systems are not working to their full potential. The copper lines have rusted and there are pin holes throughout the system. The lines are original to the site and are in poor condition. The hard water is also a contributing factor to this deterioration. Deposits within the pipes have caused restriction, and has slowed the water flow. This project would provide for the complete replacement of the sanitary sewer and copper piping system. | MEDICAL UNIT 8 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 5150 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 257500
0187SFT6 | FIRE ALARM SYSTEM REPLACEMENT | 0187 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and no longer comply with current requirements. The current system is no longer operating. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | HOUSING UNIT 7 (VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 18090 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 144720
1618ADA4 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 1618 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of one drinking fountain to meet the ADA requirements. This project or a portion thereof was previously recommended in the FCA report dated 09/11/2000 and 07/12/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2016. | HOUSING/ CULINARY UNIT | 9975 | Correct | TCC |  | Tonopah | 1990 | 12948 | 2016-06-07 | Immediate to Two Years | Currently Critical | 1 | 4000
1619INT3 | INTERIOR FINISHES | 1619 | It is recommended to paint the interior walls and ceilings at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | MULTI-PURPOSE BUILDING | 9975 | Correct | TCC |  | Tonopah | 1990 | 7000 | 2016-06-07 | Four to Ten Years | Long-Term Needs | 3 | 70000
1618ENR1 | LIGHTING UPGRADE | 1618 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures, ballasts and lighting to current standards, resulting in increased efficiency and reduced costs associated with illumination. Occupancy sensors will be installed in restrooms and other low occupancy areas for additional savings. Electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/11/2000 and 07/12/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2016. | HOUSING/ CULINARY UNIT | 9975 | Correct | TCC |  | Tonopah | 1990 | 12948 | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 103584
1618EXT4 | LOADING DOCK REPAIRS | 1618 | The loading dock behind the culinary area and the driveway leading up to it are worn and damaged and in need of repair. This project provides for the repairing and resurfacing of the concrete, as well as installing new hardware, such as the truck guard. This project or a portion thereof was previously recommended in the FCA report dated 07/12/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2016. | HOUSING/ CULINARY UNIT | 9975 | Correct | TCC |  | Tonopah | 1990 | 12948 | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
1618ADA3 | RESTROOM AND ADA REMODEL | 1618 | The bathroom and shower rooms are in overall poor condition. The countertops in each wing show signs of wear and deterioration. Extensive use, combined with repetitive water being spilled, has caused the laminate top to separate from the wooden underlayment and should be replaced. The tile on the floors and walls of the bathrooms are damaged and worn and should be replaced. This project provides for a complete remodel of the bathrooms and shower rooms. The restrooms do not meet ADA regulations. A retrofit is necessary to comply with ICC/ANSI A117.1-2009 Sections 603 - 604 and 2012 ICC Chapter 11. Given the current configuration of the restrooms, the work will include the installation of a new toilet, sink, grab bars, faucets, mirrors, dispensers, hardware and an accessible shower stall. Some minor design work will be required and may impact the final cost estimate. This estimate is for three Men's restroom facilities, one in each residential wing. The removal and disposal of the old restroom fixtures is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/11/2000 and 07/12/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2016. | HOUSING/ CULINARY UNIT | 9975 | Correct | TCC |  | Tonopah | 1990 | 12948 | 2016-06-07 | Immediate to Two Years | Currently Critical | 1 | 1500000
1618HVA1 | EVAPORATIVE COOLER REPLACEMENT | 1618 | Ten evaporative coolers are installed on the roof of the building. They are in poor condition and it is recommended that these units be replaced in the next 2-3 years. Utility connections are included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/11/2000 and 07/12/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2016. | HOUSING/ CULINARY UNIT | 9975 | Correct | TCC |  | Tonopah | 1990 | 12948 | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 40000
1618HVA4 | BOILERS AND HEATING SYSTEM RENOVATION | 1618 | There are two 500 MBH hot water boilers; one 100 MBH water heater; one 40 MBH water heater; circulation pumps, and baseboard heaters that are used for the heating system in this building. The life expectancy of the heating system is between 20 to 25 years with proper maintenance and with the use of a water treatment program. This heating system is original to the building and dates back to 1990. Replacement parts for routine and emergency maintenance are hard to find. This project would provide for the removal and disposal of the existing heating system and the installation of a new heating system, to include all required connections to the existing utilities. The existing chemical water treatment system will need to be tested and adjusted once the equipment is operational. $2,000 is included in this estimate for testing the chemical water treatment system. This project or a portion thereof was previously recommended in the FCA report dated 07/12/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2016. | HOUSING/ CULINARY UNIT | 9975 | Correct | TCC |  | Tonopah | 1990 | 12948 | 2016-06-07 | Four to Ten Years | Long-Term Needs | 3 | 353500
1619EXT6 | EXTERIOR DOOR REPLACEMENT | 1619 | The existing exterior doors to the Multi-Purpose building are original. They are showing signs of wear and deterioration from constant use and inmate abuse. Due to security concerns and the condition of the doors, replacement is recommended. This project would provide for the removal and disposal of the existing doors and frames and the replacement with new exterior security doors including door frames, hardware, security glazing, painting and connections to the security system as required. A total of 6 doors were used to generate this estimate. | MULTI-PURPOSE BUILDING | 9975 | Correct | TCC |  | Tonopah | 1990 | 7000 | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24000
1621INT1 | INTERIOR FINISHES | 1621 | It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and every 5-7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 07/12/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2016. | PUMP HOUSE | 9975 | Correct | TCC |  | Tonopah | 1990 | 672 | 2016-06-07 | Four to Ten Years | Long-Term Needs | 3 | 6720
1618INT8 | FLOORING REPLACEMENT | 1618 | The VCT flooring in the Housing Unit is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. | HOUSING/ CULINARY UNIT | 9975 | Correct | TCC |  | Tonopah | 1990 | 12948 | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 87399
1618ADA1 | ADA RESTROOM REMODEL | 1618 | The staff and visitors restroom does not meet ADA regulations. A retrofit is necessary to comply with ICC/ANSI A117.1-2009 Sections 603- 604, 2012 IBC Chapter 11 and ADAAG. Given the current configuration of the restroom, the work will include the installation of a new toilet, sink, grab bars, faucets, mirrors, dispensers, hardware and an accessible shower stall. Some minor design work will be required and may impact the final cost estimate. This estimate is for one men's restroom facility. The removal and disposal of the old restroom fixtures is included in this estimate. This project should be done concurrent with the restroom remodel project. This project or a portion thereof was previously recommended in the FCA report dated 09/11/2000 and 07/12/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2016. | HOUSING/ CULINARY UNIT | 9975 | Correct | TCC |  | Tonopah | 1990 | 12948 | 2016-06-07 | Immediate to Two Years | Currently Critical | 1 | 50000
1618ADA2 | ADA SIGNAGE | 1618 | ADA regulations pertaining to building access has established building signage criteria for permanent spaces for buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with these criteria. This project would provide for accessible signage which is required under the ADA. All signage shall conform to ICC/ANSI A117.1-2009 Chapter 7 requirements. This project or a portion thereof was previously recommended in the FCA report dated 09/11/2000 and 07/12/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2016. | HOUSING/ CULINARY UNIT | 9975 | Correct | TCC |  | Tonopah | 1990 | 12948 | 2016-06-07 | Immediate to Two Years | Currently Critical | 1 | 3000
1619INT2 | STAIRS AND HANDRAIL REPLACEMENT | 1619 | The existing interior stairs on the east side are constructed of wood and do not meet current building codes. Also, the hand rails do not meet the requirements in the 2012 IBC section 1012. This project would provide for the removal and disposal of the existing stairs and construction of a new wood framed set of stairs and handrails. The door swings outward, therefore, a three foot wide landing will be required at the top of the stairs and is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/12/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2016. | MULTI-PURPOSE BUILDING | 9975 | Correct | TCC |  | Tonopah | 1990 | 7000 | 2016-06-07 | Immediate to Two Years | Currently Critical | 1 | 15000
1618INT7 | INTERIOR FINISHES | 1618 | It is recommended to paint the interior walls and ceilings in the next 2-3 years. Prior to painting, all surfaces should be repaired and adequately prepared to receive the coating. An epoxy-based paint should be utilized in wet areas for durability. | HOUSING/ CULINARY UNIT | 9975 | Correct | TCC |  | Tonopah | 1990 | 12948 | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 129480
1618SFT4 | EXTERIOR LANDING INSTALLATION | 1618 | Section 1008.1 of the 2012 IBC describes the requirements for doors, including floor elevations and landings. The floor or landing shall be at the same elevation on each side of the door, the exterior landing shall not exceed a 2-percent slope and shall have a length measured in the direction of travel of not less than 44 inches. The landings at two of the doors of the building do not comply with this code and pose a safety hazard. This project would provide for the installation of compliant landings. | HOUSING/ CULINARY UNIT | 9975 | Correct | TCC |  | Tonopah | 1990 | 12948 | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
1618PLM3 | WATER HEATER REPLACEMENT | 1618 | There are (3) ninety one gallon propane-fired water heaters in the building. The average life span of a water heater is 8-10 years. The units are showing signs of wear and should be scheduled for replacement within the next year. It is recommended that new propane-fired water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. | HOUSING/ CULINARY UNIT | 9975 | Correct | TCC |  | Tonopah | 1990 | 12948 | 2016-06-07 | Immediate to Two Years | Currently Critical | 1 | 9000
1618HVA5 | AIR CONDITIONER INSTALLATION | 1618 | The server room is not sufficiently cooled by the existing HVAC system. If the room is too warm, the computer equipment will prematurely age and may fail due to overheating. It is recommended to install an air conditioning system in the room to ensure that the temperature is properly regulated. This project would provide for the purchase and installation of one air conditioner, to include all required connections to existing utilities. | HOUSING/ CULINARY UNIT | 9975 | Correct | TCC |  | Tonopah | 1990 | 12948 | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
1618EXT3 | EXTERIOR DOOR REPLACEMENT | 1618 | There are nine existing exterior doors that are damaged from abuse and age. This project would provide for the removal of the existing doors and the purchase and installation of new metal doors. All hardware and painting is included in this estimate. Hardware to include security keys and fusible locks. This estimate is for 9 doors. This project or a portion thereof was previously recommended in the FCA report dated 07/12/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2016. | HOUSING/ CULINARY UNIT | 9975 | Correct | TCC |  | Tonopah | 1990 | 12948 | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 36000
1618HVA3 | EXHAUST FAN REPLACEMENT | 1618 | Many of the exhaust fans in the restrooms and shower areas were inoperative and/or damaged at the time of the survey. Due to building code requirements and excessive humidity concerns, this project would provide funding for the purchase and installation of high volume commercial exhaust fans. | HOUSING/ CULINARY UNIT | 9975 | Correct | TCC |  | Tonopah | 1990 | 12948 | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
1618INT5 | INTERIOR DOOR ASSEMBLY REPLACEMENT | 1618 | The existing interior door assemblies are damaged from abuse and age. This project would provide for the removal of the existing door assemblies and the purchase and installation of new metal door assemblies. All hardware, including lever action door handles and painting is included in this estimate. Hardware is to include security keys and fusible links (for one-hour door assemblies) or where applicable. A total of 27 doors were used for this estimate. This project or a portion thereof was previously recommended in the FCA report dated 07/12/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2016. | HOUSING/ CULINARY UNIT | 9975 | Correct | TCC |  | Tonopah | 1990 | 12948 | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 108000
1618INT9 | DEDICATED CIRCUIT/ MICROWAVE | 1618 | The housing unit does not have adequate power supply for the use of the microwaves that are located in the hallway. This project would provide for twelve (20 ampere) dedicated circuits to be run to the microwave location and for the purchase of twelve new microwaves. This project includes the hook-up to the electrical panel and breakers. | HOUSING/ CULINARY UNIT | 9975 | Correct | TCC |  | Tonopah | 1990 | 12948 | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19200
1618EXT5 | WINDOW REPLACEMENT | 1618 | The windows are original, double pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, wire mesh and higher efficiency units. This estimate is for the replacement of 70 units. Removal and disposal of the existing windows is included in this estimate. | HOUSING/ CULINARY UNIT | 9975 | Correct | TCC |  | Tonopah | 1990 | 12948 | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 105000
1618EXT6 | EXTERIOR FINISHES | 1618 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING/ CULINARY UNIT | 9975 | Correct | TCC |  | Tonopah | 1990 | 12948 | 2016-06-07 | Four to Ten Years | Long-Term Needs | 3 | 129480
1618SFT5 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 1618 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/ or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. | HOUSING/ CULINARY UNIT | 9975 | Correct | TCC |  | Tonopah | 1990 | 12948 | 2016-06-07 | Immediate to Two Years | Currently Critical | 1 | 4000
1619EXT1 | EXTERIOR FINISHES | 1619 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. This project should be completed on a cyclical basis based on environmental conditions. This project or a portion thereof was previously recommended in the FCA report dated 09/12/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2016. | MULTI-PURPOSE BUILDING | 9975 | Correct | TCC |  | Tonopah | 1990 | 7000 | 2016-06-07 | Four to Ten Years | Long-Term Needs | 3 | 70000
1619ADA3 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 1619 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | MULTI-PURPOSE BUILDING | 9975 | Correct | TCC |  | Tonopah | 1990 | 7000 | 2016-06-07 | Immediate to Two Years | Currently Critical | 1 | 4000
1618INT6 | RESURFACE CULINARY WING FLOOR | 1618 | The painted concrete floor in the culinary wing is worn and damaged and should be resurfaced. This project provides for cleaning and repairing the existing floor, applying a bonding agent, pouring a new polymer surface and applying an appropriate finish product. This project or a portion thereof was previously recommended in the FCA report dated 07/12/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2016. | HOUSING/ CULINARY UNIT | 9975 | Correct | TCC |  | Tonopah | 1990 | 12948 | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10500
1619HVA3 | HEATER REPLACEMENT | 1619 | The gymnasium part of the building is heated by four ceiling mounted propane-fired heating units. They are original to the building and two of the units were missing at the time of the survey. They have reached the end of their useful life. This project provides for the disposal of the existing units and replacement with four new propane-fired units including connections to utilities. | MULTI-PURPOSE BUILDING | 9975 | Correct | TCC |  | Tonopah | 1990 | 7000 | 2016-06-07 | Immediate to Two Years | Currently Critical | 1 | 10000
1621EXT3 | EXTERIOR FINISHES | 1621 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is; sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | PUMP HOUSE | 9975 | Correct | TCC |  | Tonopah | 1990 | 672 | 2016-06-07 | Four to Ten Years | Long-Term Needs | 3 | 6720
1621ENR4 | LIGHTING UPGRADE | 1621 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 07/12/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2016. | PUMP HOUSE | 9975 | Correct | TCC |  | Tonopah | 1990 | 672 | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5376
1621SFT7 | EXTERIOR LANDING INSTALLATION | 1621 | There are two out-swinging exterior doors which swing out over dirt and do not have a landing. This does not comply with 2012 IBC Section 1008.1 which requires a proper landing and for the landing to not be more than 1/2" below the threshold. This project would provide for the installation of compliant landings. | PUMP HOUSE | 9975 | Correct | TCC |  | Tonopah | 1990 | 672 | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
1619HVA2 | HVAC EQUIPMENT REPLACEMENT | 1619 | The HVAC split system was installed in 1990. It is not energy efficient and has reached the end of its expected and useful life. This project would provide for the installation of a new HVAC split system and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing equipment and all required connections to utilities. | MULTI-PURPOSE BUILDING | 9975 | Correct | TCC |  | Tonopah | 1990 | 7000 | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
1619ENR1 | LIGHTING UPGRADE | 1619 | The existing lighting fixtures are the older fluorescent and metal halide type, and are not energy efficient. This project will upgrade fixtures, ballasts and lighting to current standards, resulting in increased efficiency and reduced costs associated with illumination. Occupancy sensors will be installed in restrooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/11/2000 and 07/12/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2016. | MULTI-PURPOSE BUILDING | 9975 | Correct | TCC |  | Tonopah | 1990 | 7000 | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 56000
1619EXT2 | EXTERIOR SIDING REPLACEMENT | 1619 | The corrugated metal panels covering the building are original and the lower section of the walls should be scheduled for replacement. Many of the panels are damaged from general wear and tear. This project would provide for the removal and the disposal of the existing panels and the replacement with new pre-painted metal panels. | MULTI-PURPOSE BUILDING | 9975 | Correct | TCC |  | Tonopah | 1990 | 7000 | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5780
1619ADA1 | ADA RESTROOM REMODEL | 1619 | The restroom does not meet current ADA regulations. A retrofit is necessary to comply with ICC/ANSI A117.1-2009 Sections 603 - 604 and 2012 ICC Chapter 11. Given the current configuration of the restroom, the work will include the installation of a new toilet, sink, grab bars, faucet, mirror, dispensers and door hardware. Some minor design work will be required and may impact the final cost estimate. This estimate is for one unisex restroom facility. The removal and disposal of the existing restroom fixtures is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/11/2000 and 07/12/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2016. | MULTI-PURPOSE BUILDING | 9975 | Correct | TCC |  | Tonopah | 1990 | 7000 | 2016-06-07 | Immediate to Two Years | Currently Critical | 1 | 50000
1619PLM4 | PLUMBING REPLACEMENT | 1619 | There is a water softener upstairs in the storage room that is draining into an open sewer line. It does not have a P-Trap. This creates an "off gas" of Hydrogen Sulfide into the air. Hydrogen Sulfide can cause irritation to the eyes and respiratory tract and can cause headaches, dizziness, drowsiness, nausea and nervousness. Exposure to high concentrations of Hydrogen Sulfide can be fatal at extremely high levels. This project will remove the sewer line serving the water softener. A new sewer line will be installed that will correct the deficiencies per IPC 2012. This estimate includes the removal and disposal of the existing system, as required. | MULTI-PURPOSE BUILDING | 9975 | Correct | TCC |  | Tonopah | 1990 | 7000 | 2016-06-07 | Immediate to Two Years | Currently Critical | 1 | 3000
1619EXT4 | WINDOW REPLACEMENT | 1619 | The existing windows in this building are single pane wire mesh construction. Some are broken and all are not energy efficient. This project would provide for the removal and replacement of the 4 windows with new dual pane security rated window systems. | MULTI-PURPOSE BUILDING | 9975 | Correct | TCC |  | Tonopah | 1990 | 7000 | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9600
1619PLM2 | WATER HEATER REPLACEMENT | 1619 | There is a 97 gallon propane-fired water heater in the building. The average life span of a water heater is 8-10 years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new propane-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | MULTI-PURPOSE BUILDING | 9975 | Correct | TCC |  | Tonopah | 1990 | 7000 | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
1619SFT3 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 1619 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. | MULTI-PURPOSE BUILDING | 9975 | Correct | TCC |  | Tonopah | 1990 | 7000 | 2016-06-07 | Immediate to Two Years | Currently Critical | 1 | 4000
1619ADA2 | ADA SIGNAGE | 1619 | ADA regulations pertaining to building access has established building signage criteria for permanent spaces for buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with these criteria. This project would provide for accessible signage which is required under the ADA. All signage shall conform to ICC/ANSI A117.1-2009 Chapter 7 requirements. This project or a portion thereof was previously recommended in the FCA report dated 09/11/2000 and 07/12/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2016. | MULTI-PURPOSE BUILDING | 9975 | Correct | TCC |  | Tonopah | 1990 | 7000 | 2016-06-07 | Immediate to Two Years | Currently Critical | 1 | 2500
1621SFT1 | EGRESS LIGHTING UPGRADE | 1621 | The existing emergency egress illumination is outdated and does not meet current standards as required by the 2012 ICC Chapter 10, Section 1006.1. This project would provide for the installation of new emergency egress lighting including connections to existing utilities. This project or a portion thereof was previously recommended in the FCA report dated 07/12/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2016. | PUMP HOUSE | 9975 | Correct | TCC |  | Tonopah | 1990 | 672 | 2016-06-07 | Immediate to Two Years | Currently Critical | 1 | 750
1619PLM1 | WATER TREATMENT SYSTEM REPLACEMENT | 1619 | The existing water softening/ treatment systems in the building are currently not operational. They are original to the building and approaching the end of their lifecycles. Failure of the equipment causes wear and tear on the domestic water supply lines and plumbing fixtures. This project would provide for the replacement of the existing water softeners/ treatment systems with new equipment. This project would also provide for a chemical treatment program including an updated chemicals control system, service and employee training provided by a qualified water treatment vendor. The annual costs are not included in the project cost. The annual maintenance fee charged by the water treatment vendor would be determined after an investigation of the water system is complete. For budgeting purposes a $12,000 annual maintenance fee is suggested. | MULTI-PURPOSE BUILDING | 9975 | Correct | TCC |  | Tonopah | 1990 | 7000 | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
2723INT1 | INTERIOR FINISHES | 2723 | It is important to maintain water quality, quantity and the interior finish of the Water Tank. This project would include hiring certified divers or draining the tank to inspect and clean the interior walls, and to weld, sandblast and perform repairs and add protective coatings, if needed. It is important to follow all ANSI, NSF and AWWA approved ways to disinfect and repair water tanks. The standard recommendation is to conduct a comprehensive inspection inside the water tank every 5 years, except for newly constructed tanks. Newly constructed water tanks should be inspected within 10 years of service and every 5 years thereafter. | WATER TANK | 9975 | Correct | TCC |  | Tonopah | 1990 | 1133 | 2016-06-07 | Immediate to Two Years | Currently Critical | 1 | 5000
2723EXT1 | EXTERIOR FINISHES | 2723 | It is important to maintain the finish, weather resistance and appearance of the tank. This project recommends work to protect the exterior of the tank to include; preparation for painting, caulk and paint. It is recommended for this project to be implemented in the next 2-3 years. It is also recommended to conduct inspections and testing on a cyclical basis per NAC 445. This project or a portion thereof was previously recommended in the FCA report dated 07/16/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2016. | WATER TANK | 9975 | Correct | TCC |  | Tonopah | 1990 | 1133 | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11330
2723EXT2 | GUARDRAIL INSTALLATION | 2723 | The Water Tank is used to store water for fire protection. It is an AWWA D100 tank. 360° guardrails should be installed per NFPA 22 standards which designate the requirements for water tanks used for private fire protection. This project would provide for the purchase and installation of new guardrails to be located at the top of the water tank. | WATER TANK | 9975 | Correct | TCC |  | Tonopah | 1990 | 1133 | 2016-06-07 | Immediate to Two Years | Currently Critical | 1 | 12000
2724INT1 | INTERIOR FINISHES | 2724 | It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and every 5-7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 07/16/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2016. | DUMP STATION | 9975 | Correct | TCC |  | Tonopah | 1990 | 36 | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 360
2724EXT1 | EXTERIOR FINISHES | 2724 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 1-2 years and is recommended on a cyclical basis based on environmental conditions. This project or a portion thereof was previously recommended in the FCA report dated 07/16/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2016. | DUMP STATION | 9975 | Correct | TCC |  | Tonopah | 1990 | 36 | 2016-06-07 | Immediate to Two Years | Currently Critical | 1 | 360
2724EXT2 | EXTERIOR SIDING REPLACEMENT | 2724 | The storage shed has painted T1-11 siding that is due for replacement. The existing siding is in poor condition and will no longer hold paint. This project recommends removing the T1-11 siding and replacing it with new T1-11 siding finished with an oil-based stain or paint. | DUMP STATION | 9975 | Correct | TCC |  | Tonopah | 1990 | 36 | 2016-06-07 | Four to Ten Years | Long-Term Needs | 3 | 900
2724EXT3 | ROOF REPLACEMENT | 2724 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 1-2 years with a new 50 year asphalt composition roofing shingle and new underlayment. This estimate includes removal and disposal of the old roofing. | DUMP STATION | 9975 | Correct | TCC |  | Tonopah | 1990 | 36 | 2016-06-07 | Immediate to Two Years | Currently Critical | 1 | 432
9975SIT1 | REMOVE OLD FOUNDATION | 9975 | The concrete stem wall foundation structure (used for the weight lifting) remains in the ground. Some of the hardware remains such as Simpson Strong Ties, which pose an injury hazard. This project provides for the demolition and disposal of the remaining foundation and hardware at the weight lifting area. This estimate is for contractor pricing. Using inmate labor will reduce the cost. This project or a portion thereof was previously recommended in the FCA report dated 07/12/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2016. | TONOPAH CONSERVATION CAMP SITE | 9975 | Correct | TCC |  | Tonopah | 1990 |  | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7000
9975SFT1 | GAS LINE SERVICE | 9975 | The propane tank farm has a damaged braided steel flex line after the pressure regulator. During the time of the survey there was a strong odor of gas. This project would provide for a licensed plumber to test all gas lines within the propane tank farm and repair any needed items. When completed, the licensed plumber should perform a manometer test on the gas lines. This project will provide for the replacement of the damaged flex line, the repair of any leaks and will certify the propane lines and tanks. | TONOPAH CONSERVATION CAMP SITE | 9975 | Correct | TCC |  | Tonopah | 1990 |  | 2016-06-07 | Immediate to Two Years | Currently Critical | 1 | 15000
9975ADA2 | ADA ACCESSIBLE PATH OF TRAVEL | 9975 | The existing sidewalks throughout the site have deteriorated and are failing. In some areas cracks wider than four inches have been identified and there is settling in a number of locations. This project addresses the removal and replacement of the existing sidewalks site-wide with sidewalks providing curbing and rails where needed to address accessibility concerns. This project includes providing an accessible path of travel from the parking lot to the visitor’s area to meet ADA requirements. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 07/12/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2016. | TONOPAH CONSERVATION CAMP SITE | 9975 | Correct | TCC |  | Tonopah | 1990 |  | 2016-06-07 | Immediate to Two Years | Currently Critical | 1 | 100000
9975ADA1 | ADA PARKING | 9975 | The ADA provides for accessibility to sites and services for people with physical limitations. This project would provide for (1) concrete van accessible ADA parking space/ loading space and the pouring of a concrete walkway to reach and meet up with the existing walkway/ sidewalk. This will require grading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. 1000 square feet of concrete was used for this estimate. It is recommended that this project coincide with the paving project. This project or a portion thereof was previously recommended in the FCA report dated 09/11/2000 and 07/12/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2016. | TONOPAH CONSERVATION CAMP SITE | 9975 | Correct | TCC |  | Tonopah | 1990 |  | 2016-06-07 | Immediate to Two Years | Currently Critical | 1 | 30000
9975SIT6 | SITE DRAINAGE UPGRADES | 9975 | The grade does not slope away from the buildings effectively. Water has pooled against the foundation. In the winter months, as the water freezes against the foundation, over time, this can cause damage to the foundation. It is recommended per IBC 1804.3, site grading the ground immediately adjacent to the foundation shall be sloped away from the building at a slope of not less than one vertical in 20 units horizontal (5-percent slope) for a minimum distance of 10 feet (3048 mm) measured perpendicular to the face of the wall. If physical obstructions or lot lines prohibit 10 feet (3048 mm) of horizontal distance, a 5-precent slope shall be provided to an approved alternative method of diverting water away from the foundation. Swales used for the purpose shall be sloped a minimum of 2 percent where located within 10 feet (3048 mm) of the building foundation. Impervious surfaces within 10 feet (3048 mm) of the building foundation shall be sloped a minimum of 2 percent away from the building. This project would create positive flow away from the buildings. Additional drainage swales shall be installed, as needed. It is recommended that the grading be completed within 2-3 years. | TONOPAH CONSERVATION CAMP SITE | 9975 | Correct | TCC |  | Tonopah | 1990 |  | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 75000
9975SIT0 | SITE BOLLARDS | 9975 | There are two above ground fuel tanks on the site, one for diesel and one for unleaded gasoline that do not have adequate bollard coverage. Per IFC 2012 Section 312 Vehicle Impact Protection, this project recommends that steel posts be installed, not less than 4 inches in diameter and filled with concrete. The spacing shall not be more than 4 feet between posts on center and located not less than 3 feet from each gas tank. This project would provide funding for ten new bollards to be located in-between the other bollards around the tanks. | TONOPAH CONSERVATION CAMP SITE | 9975 | Correct | TCC |  | Tonopah | 1990 |  | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
9975SEC1 | SITE POLE LIGHT INSTALLATION | 9975 | The entrance road and parking area have insufficient lighting. Considering the environment of the site, this area needs to be well lit. This project would provide funding for the purchase and installation of 12 additional 30 foot tall light poles including 30" diameter raised concrete bases, electrical trenching, conduit, wiring and connections to existing utilities. This project or a portion thereof was previously recommended in the FCA report dated 09/11/2000 and 07/12/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2016. | TONOPAH CONSERVATION CAMP SITE | 9975 | Correct | TCC |  | Tonopah | 1990 |  | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 110448
1394INT3 | FLOORING REPLACEMENT | 1394 | The floor covering throughout this building is in poor condition and has reached the end of its useful life. The current floor covering is Vinyl Composition Tile (VCT) in the corridors and circulation areas, sheet vinyl in restrooms and carpet in office and sleeping areas. This project would provide funding to replace all of the floor coverings with VCT and non-slip sheet vinyl in the restrooms. This project or a portion there of was previously recommended in the FCA report dated 09/21/2000 and 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | ADMINISTRATION/ HOUSING UNIT | 9972 | Correct | HCC |  | Winnemucca | 1986 | 12478 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 124780
1394PLM3 | EVAPORATIVE COOLER REPLACEMENT | 1394 | There are currently nine evaporative coolers mounted on the roof of the Housing Unit, three for each wing. They are severely scaled and have reached the end of their serviceable life. This project would provide for nine new evaporative coolers to be installed, and includes removal and disposal of the old evaporative coolers and utility connections to the new units. This project or a portion there of was previously recommended in the FCA report dated 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | ADMINISTRATION/ HOUSING UNIT | 9972 | Correct | HCC |  | Winnemucca | 1986 | 12478 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 36000
1394ELE3 | ELECTRICAL UPGRADE | 1394 | The building has numerous electrical outlets and switches which are missing covers or broken, extension cords that are used to supply electrical power, and exposed electrical wires on equipment and the distribution system in attic. This project would provide for repairs and/or replacement of the damaged electrical outlets and switches, installation of 110volt ground fault circuit interrupter (GFCI) outlets, as needed, and repairing the exposed electrical. This project or a portion there of was previously recommended in the FCA report dated 09/21/2000 and 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | ADMINISTRATION/ HOUSING UNIT | 9972 | Correct | HCC |  | Winnemucca | 1986 | 12478 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 5000
1394ADA1 | ADA RESTROOM UPGRADE | 1394 | The building does not have an accessible restroom. The existing restroom does not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for remodeling the Men's and Women's restrooms per ADA regulations. Items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 International Building Code (IBC), ICC/ANSI A117.1 - 2009, Nevada Revised Statutes (NRS) 338.180 and the most current version of the ADA Standards For Accessible Design were used as references for this project. This project or a portion there of was previously recommended in the FCA report dated 09/21/2000 and 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | ADMINISTRATION/ HOUSING UNIT | 9972 | Correct | HCC |  | Winnemucca | 1986 | 12478 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 40000
1394SEC1 | EXTERIOR DOOR REPLACEMENT | 1394 | The existing exterior metal doors and frames appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement and installation of seven new metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 09/21/2000 and 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | ADMINISTRATION/ HOUSING UNIT | 9972 | Correct | HCC |  | Winnemucca | 1986 | 12478 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 28000
1394ELE2 | EXHAUST FAN REPLACEMENT | 1394 | Many of the exhaust fans in the restrooms and shower areas were inoperative and/or damaged at the time of the survey. Due to building code requirements and excessive humidity concerns, this project would provide funding for the purchase and installation of 10 high volume commercial exhaust fans. This project or a portion there of was previously recommended in the FCA report dated 09/21/2000 and 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | ADMINISTRATION/ HOUSING UNIT | 9972 | Correct | HCC |  | Winnemucca | 1986 | 12478 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 20000
1394SIT1 | REPLACE EXIT STAIRS, SIDEWALK AND RAMP | 1394 | The concrete sidewalk and exit stairs for the housing unit appear to be part of the original construction. They are deteriorating mainly from exposure to the weather. Spalling and cracking has occurred, and in some instances they are unsafe. The stairs are not up to current code (existing 8" risers at entry, cannot exceed 7" per chapter 10 of the 2012 IBC) and there is not an ADA accessible entrance. This project would provide funding for the removal and replacement of the sidewalk, main entrance concrete stairs, including other exit stairs, and construction of an ADA accessible ramp into the building. This project or a portion there of was previously recommended in the FCA report dated 09/21/2000 and 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | ADMINISTRATION/ HOUSING UNIT | 9972 | Correct | HCC |  | Winnemucca | 1986 | 12478 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 75000
1397HVA2 | REPLACE EVAPORATIVE COOLERS | 1397 | Evaporative coolers are installed on the side of this building. They are severely scaled and have reached the end of their useful and expected life. This project would provide for 2 new evaporative coolers to be installed including all required connections to utilities. The estimate includes removal and disposal of the old coolers. This project or a portion thereof was previously recommended in the FCA report dated 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | MULTI-PURPOSE BUILDING | 9972 | Correct | HCC |  | Winnemucca | 1986 | 7000 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
1397INT4 | DOOR HARDWARE REPLACEMENT | 1397 | The doors have manually operated flush bolts with a padlock on the outside of each door. International Building Code (IBC) 2012 chapter 10 Means of Egress, section 1008, manually operated flush bolts or surface bolts are not permitted. This project is to install new Schlage grade 1 or approved equal keyed ADA approved dead bolts and levers. | MULTI-PURPOSE BUILDING | 9972 | Correct | HCC |  | Winnemucca | 1986 | 7000 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 4000
1397ELE1 | LIGHTING UPGRADE | 1397 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2000 and 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | MULTI-PURPOSE BUILDING | 9972 | Correct | HCC |  | Winnemucca | 1986 | 7000 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24500
1398EXT3 | EXTERIOR FINISHES | 1398 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | STORAGE SHED | 9972 | Correct | HCC |  | Winnemucca | 1986 | 188 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 1880
1398INT1 | INTERIOR FINISHES | 1398 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | STORAGE SHED | 9972 | Correct | HCC |  | Winnemucca | 1986 | 188 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1880
1398EXT4 | EXTERIOR DOOR REPLACEMENT | 1398 | There are two exterior doors that are damaged from abuse and age. This project would provide for the removal of the existing doors and the purchase and installation of new solid core wood doors. All hardware and painting is included in this estimate. Hardware to include security keys and fusible locks. This estimate is for 2 doors. | STORAGE SHED | 9972 | Correct | HCC |  | Winnemucca | 1986 | 188 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
1398SFT1 | EXTERIOR LANDING INSTALLATION | 1398 | There is an out-swinging exterior door from the building which swings out over a step and does not have a landing that complies with International Building Code (IBC) 2012. IBC section 1008 requires a landing to be not more than 1/2" below the threshold. This project would provide for the installation of a compliant landing for the door. | STORAGE SHED | 9972 | Correct | HCC |  | Winnemucca | 1986 | 188 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
1398EXT1 | ROOF REPLACEMENT | 1398 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next year with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. | STORAGE SHED | 9972 | Correct | HCC |  | Winnemucca | 1986 | 188 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 2256
1397INT5 | INTERIOR FINISHES | 1397 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | MULTI-PURPOSE BUILDING | 9972 | Correct | HCC |  | Winnemucca | 1986 | 7000 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 70000
1397PLM2 | SEDIMENT TRAP INSTALLATION | 1397 | The gas line serving the appliances in the Multi-Purpose Building does not have sediment traps. Per International Fuel Gas Code (IFGC) 2012, section 408, where a sediment trap is not incorporated as part of the appliance, a sediment trap shall be installed downstream of the appliance shutoff valve as close to the inlet of the appliance as practical. The sediment trap shall be either; a tee fitting, having a capped nipple, of any length, installed vertically in the bottommost opening of the tee, or other device approved as an effective sediment trap. This project would provide for all labor and materials to have sediment traps installed near all gas appliances. | MULTI-PURPOSE BUILDING | 9972 | Correct | HCC |  | Winnemucca | 1986 | 7000 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 2000
1397PLM5 | PLUMBING REPLACEMENT | 1397 | The sanitary wastewater and copper plumbing systems are showing signs of deterioration. Due to this deterioration, the systems are not working to their full potential. The copper lines have rusted and the ABS sanitary wastewater line are off gassing in several locations due to improper repairs from inmates. The lines are original to the site and are in poor condition. The hard water is also a contributing factor to this deterioration. Deposits within the pipes have caused restriction, and has slowed the water flow. This project would provide for the complete replacement of the sanitary sewer and copper piping system. | MULTI-PURPOSE BUILDING | 9972 | Correct | HCC |  | Winnemucca | 1986 | 7000 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 175000
1397EXT1 | EXTERIOR FINISHES | 1397 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MULTI-PURPOSE BUILDING | 9972 | Correct | HCC |  | Winnemucca | 1986 | 7000 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14000
1397SEC1 | EXTERIOR DOOR REPLACEMENT | 1397 | The existing exterior metal doors and frames appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement and installation of five new metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2000 and 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | MULTI-PURPOSE BUILDING | 9972 | Correct | HCC |  | Winnemucca | 1986 | 7000 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
1397HVA1 | FURNACE REPLACEMENT | 1397 | The existing ceiling-mounted propane fired furnaces appear to be original to the building and have reached the end of their expected life. They are showing signs of aging and at the time of the survey were inoperable. This project would provide for the removal and disposal of the old furnaces and installation of 4 new ceiling-mounted propane fired furnaces. This project or a portion thereof was previously recommended in the FCA report dated 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | MULTI-PURPOSE BUILDING | 9972 | Correct | HCC |  | Winnemucca | 1986 | 7000 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
1397SFT3 | HANDRAIL INSTALLATION | 1397 | The handrail serving the stairs to the Mezzanine does not meet the 2012 International Building Code (IBC) 1009.11 which requires two handrails and extensions. This project would provide for the installation of new handrails in the stairwell. This project should coincide with any projects related to the Mezzanine structural recommendations project. This project or a portion thereof was previously recommended in the FCA report dated 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | MULTI-PURPOSE BUILDING | 9972 | Correct | HCC |  | Winnemucca | 1986 | 7000 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 2500
1397STR1 | STRUCTURAL REPAIRS | 1397 | A storage area has been constructed in the Maintenance Shop, accessed via stairs. There is no record of a Capital Improvement Project (CIP) for this work or of any structural evaluations having been conducted. This project recommends adding structural members to the existing framing to ensure proper load bearing capacity. This will require a structural design from a licensed engineer, inspections and permitting which are not included in the estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | MULTI-PURPOSE BUILDING | 9972 | Correct | HCC |  | Winnemucca | 1986 | 7000 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 8000
1397PLM1 | WATER HEATER REPLACEMENT | 1397 | There is a electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next year. It is recommended that a new on-demand electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2000 and 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | MULTI-PURPOSE BUILDING | 9972 | Correct | HCC |  | Winnemucca | 1986 | 7000 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 3750
1397ENV1 | DUST COLLECTION SYSTEM INSTALLATION | 1397 | The existing wood working equipment has only partial dust collection capacity. In order to reduce the possibility of damage or injury, each piece of equipment should have full collection capability. This project will provide for the replacement of the existing system and installation of additional capacity to minimize explosion hazard and disruption to production. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2000 and 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | MULTI-PURPOSE BUILDING | 9972 | Correct | HCC |  | Winnemucca | 1986 | 7000 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 20000
1394INT1 | REPLACE SUBFLOORING | 1394 | Areas exist where the sub-floor has been damaged due to water infiltration and a lack of bracing in the rooms, hallways, showers and bathroom areas. Age and constant traffic have contributed to the deterioration. This project would provide funding to remove the existing damaged sub-floor and install new bracing and plywood sub-flooring where needed. This work should be performed prior to installing new toilets, urinals and any other remodeling of the bathrooms and rooms. This project or a portion there of was previously recommended in the FCA report dated 09/21/2000 and 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | ADMINISTRATION/ HOUSING UNIT | 9972 | Correct | HCC |  | Winnemucca | 1986 | 12478 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 30000
1398EXT2 | EXTERIOR SIDING REPLACEMENT | 1398 | The storage shed has painted T1-11 siding that is due for replacement. The existing siding is in poor condition and will no longer hold paint. This project recommends removing the T1-11 siding and replacing it with new T1-11 siding finished with an oil-based stain or paint. | STORAGE SHED | 9972 | Correct | HCC |  | Winnemucca | 1986 | 188 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3760
1397SFT2 | FIRE ALARM SYSTEM REPLACEMENT | 1397 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and due to this the system no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to Nevada Administrative Code (NAC) 477.917 "If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure". When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 International Building Code (IBC) chapter 9, section 907 and the State Fire Marshal's requirements. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2000 and 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | MULTI-PURPOSE BUILDING | 9972 | Correct | HCC |  | Winnemucca | 1986 | 7000 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 56000
1400INT1 | INTERIOR FINISHES | 1400 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | PUMP HOUSE | 9972 | Correct | HCC |  | Winnemucca | 1987 | 320 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3200
1400ENR1 | INSULATE BUILDING | 1400 | The building is not insulated and is not energy efficient. Due to this, the heater continuously runs and the water pipes are at risk of damage caused by freezing temperatures. This project will install (R19) batt insulation in the walls and (R38) batt insulation in the ceiling with impermeable vinyl surface to help moderate temperature fluctuations. | PUMP HOUSE | 9972 | Correct | HCC |  | Winnemucca | 1987 | 320 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 4800
1400EXT1 | EXTERIOR SIDING REPLACEMENT | 1400 | The Pump House has painted plywood siding that is due for replacement. The existing siding is in poor condition and will no longer hold paint. This project recommends removing the plywood siding and replacing it with T1-11 panels finished with an oil-based paint. | PUMP HOUSE | 9972 | Correct | HCC |  | Winnemucca | 1987 | 320 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6400
1400EXT3 | EXTERIOR DOOR REPLACEMENT | 1400 | The exterior metal doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the double door assembly with new metal doors, frames and hardware. Removal and disposal of the existing doors is included in this estimate. | PUMP HOUSE | 9972 | Correct | HCC |  | Winnemucca | 1987 | 320 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
1400HVA2 | ELECTRIC HEATER REPLACEMENT | 1400 | There are two electric heaters in the building that are not adequate and have reached the end of their expected life. This project recommends replacing the two electric heaters and installing an additional electric heater. The estimate includes removal and disposal of the existing equipment. | PUMP HOUSE | 9972 | Correct | HCC |  | Winnemucca | 1987 | 320 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 6000
1400EXT2 | EXTERIOR FINISHES | 1400 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | PUMP HOUSE | 9972 | Correct | HCC |  | Winnemucca | 1987 | 320 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 3200
1395ADA3 | ADA UPGRADES | 1395 | The existing threshold at the door entrance exceeds ½ inch. Americans with Disabilities Act (ADA) requirements state that the threshold should not be any higher than ½ inch for accessibility, ICC/ANSI A117.1-2009 404.2.5. The door knobs on the building are round and require a gripping action. Section 4.13.9 of the Americans with Disabilities Act Accessible Guidelines (ADAAG) states that handles, pulls, latches, locks and other operating devices on accessible doors shall have a shape that is easy to grasp with one hand and does not require tight grasping, tight pinching, or twisting of the wrist to operate. This project would provide funding for the removal and replacement of the threshold and the door knobs to meet these requirements. This project or a portion there of was previously recommended in the FCA report dated 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | CAFETERIA/ CULINARY BUILDING | 9972 | Correct | HCC |  | Winnemucca | 1986 | 7000 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 15000
1397INT1 | GYPSUM BOARD REPAIR | 1397 | Water leaks and moisture has damaged the gypsum board in the laundry room. If the gypsum board is not removed and replaced, the moisture potentially could cause mold and dry-rot. This project recommends removing the gypsum board, and replacing it with green board and installing Fiberglass Reinforced Panels (FRP). Per International Building Code (IBC) 2012 section 1210 was used as a reference fro this project. This project or a portion thereof was previously recommended in the FCA report dated 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | MULTI-PURPOSE BUILDING | 9972 | Correct | HCC |  | Winnemucca | 1986 | 7000 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
1394SFT2 | FLUE REPLACEMENT | 1394 | There are several water heater and heater flues in the building, which do not comply with International Mechanical Code (IMC) 2012 chapter 8, chimneys and vents. The vents were installed with improper flues and per section 804 direct vent terminations vent terminals for direct vented appliances shall be installed in accordance with the manufacturer’s installation instructions. The vents, in some cases, are too close to combustibles and don’t have the proper clearances, per IMC 2012 this can cause a fire hazard. The flex ductwork is connected with metal tape and per 803.10.1 supports and joints ductwork shall be fastened with sheet metal screws, rivets or other approved means. Some of the flues are aluminum flex ducts and per 803.8 vent connector construction, vent connectors shall be constructed of metal. The minimum thickness of the connector shall be (no. 28 gage) for galvanized steel. The flues are in poor condition and have cracks. Per 801.18.2 flue passageways, the flue liner, chimney inner wall or vent inner wall shall be continuous and shall be free of cracks, gaps, perforations or other damage or deteriorations, which would allow the escape of combustion products, including gases, moisture and creosote. It is recommended that all flues throughout the building be replaced. Replacements shall meet the manufacture’s specifications and IMC 2012. The flues should be installed by a licensed contractor. This project would provide funds to replace all the flues throughout the building. | ADMINISTRATION/ HOUSING UNIT | 9972 | Correct | HCC |  | Winnemucca | 1986 | 12478 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 48000
1397SFT1 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 1397 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. International Building Code (IBC) 2012 chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2000 and 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | MULTI-PURPOSE BUILDING | 9972 | Correct | HCC |  | Winnemucca | 1986 | 7000 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 3500
1394SFT4 | CARBON MONOXIDE DETECTOR INSTALLATION | 1394 | International Fire Code (IFC) 2012 section 908.7 carbon monoxide alarms group I or R occupancies located in a building containing a fuel-burning appliance or in a building which has an attached garage shall be equipped with a single-station carbon monoxide alarm. The carbon monoxide alarm shall be listed as complying with UL 2034 and be installed and maintained in accordance with National Fire Protection Agency (NFPA) 720 and the manufacturer’s instructions. This project would provide funding for the purchase and installation of 3 carbon monoxide alarms in accordance with this code. | ADMINISTRATION/ HOUSING UNIT | 9972 | Correct | HCC |  | Winnemucca | 1986 | 12478 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 600
1394ADA6 | ADA DOOR HARDWARE REPLACEMENT | 1394 | The 2010 ADA Standards for Accessible Design states that handles, pulls, latches, locks and other operable parts on doors and gates shall be operable with one hand and shall not require tight grasping, pinching, or twisting of the wrist. The force to activate operable parts shall be 5 pounds maximum. It is recommended that proper lever hardware be installed on all of the interior and exterior doors in this building to meet these requirements. The 2012 IBC, ICC/ANSI A117.1 - 2009, Nevada Revised Statutes (NRS) 338.180 and sections 309.4 and 404.2.7 of the 2010 ADA Standards For Accessible Design were used as a reference for this project. | ADMINISTRATION/ HOUSING UNIT | 9972 | Correct | HCC |  | Winnemucca | 1986 | 12478 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 56250
1394PLM5 | WATER HEATER REPLACEMENT | 1394 | There are three 97 gallon propane water heaters in the building. The average lifespan of a water heater is eight to ten years. The units were installed in 2013. It is recommended that 3 new propane water heaters, straps, braided steel hose, expansion tanks, ball valves, new flex gas lines and pans be installed in the next 5-6 years. Removal and disposal of the existing equipment is included in this estimate. | ADMINISTRATION/ HOUSING UNIT | 9972 | Correct | HCC |  | Winnemucca | 1986 | 12478 | 2016-07-07 | Four to Ten Years | Long-Term Needs | 3 | 9000
1394HVA2 | HEATER REPLACEMENT | 1394 | The heating system was installed in 1997. It consists of propane gas-fired furnaces. The system is not energy efficient and has reached the end of its expected and useful life. This project would provide for the installation of new heating systems and the cleaning of the existing duct work and grilles. The new systems shall be designed to significantly reduce electrical and propane usage in order to comply with the 2012 International Energy conservation Code (IECC) and American Society of Heating Refrigerating and Air-Conditioning Engineers (ASHRAE) 90.1 and to reduce utility costs. This project includes the removal and the disposal of the existing heating units and all required connections to utilities. | ADMINISTRATION/ HOUSING UNIT | 9972 | Correct | HCC |  | Winnemucca | 1986 | 12478 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
1395ADA1 | ADA RESTROOM UPGRADE | 1395 | The culinary area is often used for an inmate visitation area. The men's and women's designated restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for construction of two unisex accessible restrooms. Items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 International Building Code (IBC), ICC/ANSI A117.1 - 2009, Nevada Revised Statutes (NRS) 338.180 and the most current version of the ADA Standards For Accessible Design were used as references for this project. This project or a portion there of was previously recommended in the FCA report dated 09/21/2000 and 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | CAFETERIA/ CULINARY BUILDING | 9972 | Correct | HCC |  | Winnemucca | 1986 | 7000 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 25000
1395ADA2 | ADA SIGNAGE | 1395 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2012 International Building Code (IBC), ICC/ANSI A117.1 - 2009, Nevada Revised Statutes (NRS) 338.180 and the most current version of the ADA Standards For Accessible Design were used as references for this project. This project or a portion there of was previously recommended in the FCA report dated 09/21/2000 and 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | CAFETERIA/ CULINARY BUILDING | 9972 | Correct | HCC |  | Winnemucca | 1986 | 7000 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 3000
1395CUL1 | ADA ACCESSIBLE COUNTER | 1395 | The plastic laminate countertop for serving food is: non Americans with Disabilities Act (ADA) compliant, is separating, falling down and has deteriorated to a point where it presents health, safety and sanitation issues. This project would provide funding for the removal of the existing countertop and installation of a new plastic laminate countertop. Section 904.4 of the ADA Standards for Accessible Design states that a portion of the counter surface that is 36" long minimum and 36" high maximum above the finish floor shall be provided. This project will provide an accessible counter space in accordance with this requirement. The 2012 International Building Code (IBC), ICC/ANSI A117.1 - 2009, Nevada Revised Statutes (NRS) 338.180 and the most current version of the ADA Standards For Accessible Design were used as references for this project. This project or a portion there of was previously recommended in the FCA report dated 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | CAFETERIA/ CULINARY BUILDING | 9972 | Correct | HCC |  | Winnemucca | 1986 | 7000 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 12750
1395INT3 | FLOORING REPLACEMENT | 1395 | The floor coverings throughout this building are in generally poor condition and have reached the end of their serviceable lives. At the present time, most of the floor surfaces have been removed in the cafeteria and culinary area. This presents health and sanitation issues. The remaining floor covering has 12" Vinyl Composition Tile (VCT) floor covering. This project would provide funding to replace the entire floor with non-slip sheet vinyl, and includes removing and installing the Culinary preparation and cooking equipment, tables and chairs. This project or a portion there of was previously recommended in the FCA report dated 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | CAFETERIA/ CULINARY BUILDING | 9972 | Correct | HCC |  | Winnemucca | 1986 | 7000 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 63000
1395SFT3 | FIRE SUPPRESSION SYSTEM INSTALLATION | 1395 | The building is a B occupancy per the 2012 International Building Code (IBC). Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 or R-2 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. This project or a portion there of was previously recommended in the FCA report dated 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | CAFETERIA/ CULINARY BUILDING | 9972 | Correct | HCC |  | Winnemucca | 1986 | 7000 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 98000
1395ELE1 | LIGHTING UPGRADE | 1395 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 09/21/2000 and 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | CAFETERIA/ CULINARY BUILDING | 9972 | Correct | HCC |  | Winnemucca | 1986 | 7000 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 56000
1396INT1 | VCT FLOORING REPLACEMENT | 1396 | The Vinyl Composite Tile (VCT) flooring in the Gatehouse/ Guard Shack is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. | GATEHOUSE/ GUARD SHACK | 9972 | Correct | HCC |  | Winnemucca | 1987 | 36 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 324
1397ADA1 | ADA RESTROOM REMODEL | 1397 | The building does not have an accessible restroom. The existing restroom does not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom. Items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 International Building Code (IBC), ICC/ANSI A117.1 - 2009, Nevada Revised Statutes (NRS) 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2000 and 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | MULTI-PURPOSE BUILDING | 9972 | Correct | HCC |  | Winnemucca | 1986 | 7000 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 15000
1394SFT3 | FIRE SUPPRESSION SYSTEM INSTALLATION | 1394 | This building does not have an automatic fire suppression system. This building has more than 12,000 square feet on the first floor. Current state regulations require state-owned buildings having more than 12,000 square feet on one floor, or more than 24,000 square feet total, must be retrofitted with fire sprinklers during the next remodel or addition. Also, this building is equipped with an automatic fire detection and alarm system. This project would provide funding for the installation of fire sprinklers, including backflow prevention devices, and a visual/audible alarm notification, in accordance with ADA requirements. | ADMINISTRATION/ HOUSING UNIT | 9972 | Correct | HCC |  | Winnemucca | 1986 | 12478 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 174692
1396EXT0 | EXTERIOR FINISHES | 1396 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2000 and 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | GATEHOUSE/ GUARD SHACK | 9972 | Correct | HCC |  | Winnemucca | 1987 | 36 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 360
1395HVA1 | EXHAUST HOOD INSTALLATION | 1395 | Section 507.2.2 of the Uniform Mechanical Code (UMC) states, "Hoods shall be installed at or above all commercial-type dishwashing machines and similar equipment which produce comparable amounts of steam..." This project would provide funding to install a Type II exhaust hood above the dishwasher in the culinary area. This project will provide for an exhaust hood, roofing repairs, electrical and installation. This project or a portion there of was previously recommended in the FCA report dated 09/21/2000 and 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | CAFETERIA/ CULINARY BUILDING | 9972 | Correct | HCC |  | Winnemucca | 1986 | 7000 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 9200
1394PLM2 | PLUMBING REPLACEMENT | 1394 | The plumbing and waste system is older and in poor condition. Most of the system appears to be original to the building and should be scheduled for replacement. The sewer lines are rusted and failing especially underground. This project would provide for replacement all of the water and sewer lines in the building. This estimate includes removal and disposal of the existing system as required. This project or a portion there of was previously recommended in the FCA report dated 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | ADMINISTRATION/ HOUSING UNIT | 9972 | Correct | HCC |  | Winnemucca | 1986 | 12478 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 187170
1395SFT6 | EGRESS LIGHTING INSTALLATION | 1395 | There are older emergency egress lighting units in this building. These units have a finite lifespan, and this project recommends their replacement with new egress lights, and to also provide additional lights on the main exit routes and in individual rooms as needed. | CAFETERIA/ CULINARY BUILDING | 9972 | Correct | HCC |  | Winnemucca | 1986 | 7000 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 1350
1395EXT1 | EXTERIOR FINISHES | 1395 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion there of was previously recommended in the FCA report dated 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | CAFETERIA/ CULINARY BUILDING | 9972 | Correct | HCC |  | Winnemucca | 1986 | 7000 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14000
1395EXT7 | EXTERIOR SIDING REPLACEMENT | 1395 | The corrugated metal panels covering the building are original and should be scheduled for replacement. Many of the panels are damaged from general wear and tear. This project would provide for the removal and the disposal of the existing panels and the replacement with new pre-painted metal panels. The estimate is based on 340 linear feet of 4' wide panels at $17.00 per linear foot. | CAFETERIA/ CULINARY BUILDING | 9972 | Correct | HCC |  | Winnemucca | 1986 | 7000 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5780
1395HVA2 | EVAPORATIVE COOLER REPLACEMENT | 1395 | An evaporative cooler is installed on the side of this building. It is severely scaled and has reached the end of its useful and expected life. This project would provide for a new evaporative cooler to be installed, including all required connections to utilities. The estimate includes removal and disposal of the old evaporative cooler. | CAFETERIA/ CULINARY BUILDING | 9972 | Correct | HCC |  | Winnemucca | 1986 | 7000 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
1395ADA4 | ADA TABLE UPGRADE | 1395 | Per the United States Access Board Section 226.1 where dining surfaces are provided for the consumption of food or drink, at least 5 percent of the seating spaces and standing spaces at the dining surfaces shall comply with 902. ICC ANSI-A117.1-2009 section 902 which says, if fixed seating is provided, a loose seat or open space for a wheelchair location must be available at those accessible tables. This project would provide funding to remove 4 of the fixed seats, which will allow access for four wheel chairs. | CAFETERIA/ CULINARY BUILDING | 9972 | Correct | HCC |  | Winnemucca | 1986 | 7000 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 4000
1395PLM1 | WATER HEATER REPLACEMENT | 1395 | There is a 97 gallon propane water heater in the building. The average lifespan of a water heater is eight to ten years. This water heater was installed in 2013. This project would provide for a new propane water heater, seismic straps, braided steel hose, expansion tank, ball valves, new flex gas line and pan to be installed in the next 5-6 years. Removal and disposal of the existing equipment is also included in this estimate. | CAFETERIA/ CULINARY BUILDING | 9972 | Correct | HCC |  | Winnemucca | 1986 | 7000 | 2016-07-07 | Four to Ten Years | Long-Term Needs | 3 | 3000
1395SFT5 | FLUE REPLACEMENT | 1395 | There are several water heater flues in the building, which do not comply with International Mechanical Code (IMC) 2012 chapter 8, chimneys and vents. The vents were installed with improper flues and per section 804 direct vent terminations vent terminals for direct vented appliances shall be installed in accordance with the manufacturer’s installation instructions. The vents, in some cases, are too close to combustibles and don’t have the proper clearances, per IMC 2012 this can cause a fire hazard. The flex ductwork is connected with metal tape and per 803.10.1 supports and joints ductwork shall be fastened with sheet metal screws, rivets or other approved means. Some of the flues are aluminum flex ducts and per 803.8 vent connector construction, vent connectors shall be constructed of metal. The minimum thickness of the connector shall be (no. 28 gage) for galvanized steel. The flues are in poor condition and have cracks. Per 801.18.2 flue passageways, the flue liner, chimney inner wall or vent inner wall shall be continuous and shall be free of cracks, gaps, perforations or other damage or deteriorations, which would allow the escape of combustion products, including gases, moisture and creosote. It is recommended that all flues throughout the building be replaced. Replacements shall meet the manufacture’s specifications and IMC 2012. The flues should be installed by a licensed contractor. This project would provide funds to replace all the flues throughout the building. | CAFETERIA/ CULINARY BUILDING | 9972 | Correct | HCC |  | Winnemucca | 1986 | 7000 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 8000
1395INT2 | INTERIOR FINISHES | 1395 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA report dated 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | CAFETERIA/ CULINARY BUILDING | 9972 | Correct | HCC |  | Winnemucca | 1986 | 7000 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 70000
1396INT2 | INTERIOR FINISHES | 1396 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | GATEHOUSE/ GUARD SHACK | 9972 | Correct | HCC |  | Winnemucca | 1987 | 36 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 360
2554INT1 | INTERIOR FINISHES | 2554 | It is important to maintain water quality, quantity and the interior finish of the water tank. This project would include hiring certified divers or draining the tank to inspect and clean the interior walls, and to weld, sandblast and perform repairs and add protective coatings, if needed. It is important to follow all American National Standards Institute (ANSI), National Sanitation Foundation (NSF) and American Water Works Association (AWWA) approved ways to disinfect and repair water tanks. The standard recommendation is to conduct a comprehensive inspection inside the water tank every 5 years, except for newly constructed tanks. Newly constructed water tanks should be inspected within 10 years of service and every 5 years thereafter. | WATER TANK | 9972 | Correct | HCC |  | Winnemucca | 2006 | 1500 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 5000
2554EXT2 | EXTERIOR FINISHES | 2554 | It is important to maintain the finish, weather resistance and appearance of the water tank. This project would provide for the painting of the water tank and caulking of the joints to maintain a weather tight condition. It is recommended that this project is implemented in the next 2-3 years and is recommended on a cyclical basis based on environmental conditions. This project or a portion thereof was previously recommended in the FCA report dated 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | WATER TANK | 9972 | Correct | HCC |  | Winnemucca | 2006 | 1500 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
2554EXT3 | GUARDRAIL | 2554 | The National Fire Protection Association (NFPA) 22 standard designates the requirements for water tanks used for private fire protection. This tank is used to store water for fire protection and is an American Water Works Association (AWWA) D100 tank that is required to have 360° guardrails. This project would provide for the purchase and installation of new guardrails to be located at the top of the water tank. | WATER TANK | 9972 | Correct | HCC |  | Winnemucca | 2006 | 1500 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 12000
9972SIT4 | SITE DRAINAGE UPGRADES | 9972 | The grade does not slope away effectively from the buildings. Water has pooled against the foundation. In the winter months, as the water freezes against the foundation, over time, this can cause damage to the foundation. It is recommended per International Building Code (IBC) 1804.3 Site Grading the ground immediately adjacent to the foundation shall be sloped away from the building at a slope of not less than one vertical in 20 units horizontal (5-percent slope) for a minimum distance of 10 feet (3048 mm) measured perpendicular to the face of the wall. This project would create a 5% slope away from the buildings. Additional drainage swales shall be installed, as needed. It is recommended that the grading be completed within 2-3 years. | HUMBOLDT CONSERVATION CAMP SITE | 9972 | Correct | HCC |  | Winnemucca | 1986 |  | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 75000
3786INT1 | INTERIOR FINISHES | 3786 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | WASTEWATER TREATMENT BUILDING | 9972 | Correct | HCC |  | Winnemucca | 2006 | 120 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1200
3786EXT2 | EXTERIOR DOOR REPLACEMENT | 3786 | The exterior metal door is damaged from age and general wear and tear and has reached the end of its expected life. This project would provide for the replacement of the door assembly with a new metal door, frame and hardware. Removal and disposal of the existing door is included in this estimate. | WASTEWATER TREATMENT BUILDING | 9972 | Correct | HCC |  | Winnemucca | 2006 | 120 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
9972SIT2 | BUILDING SIGNAGE | 9972 | The site contains numerous buildings with no signage identifying function or contents. Some of the buildings contain flammable liquids or gases. In case of emergency the buildings should be identified for safety purposes. This project would provide funding for signage to be installed on all of the buildings. This project or a portion thereof was previously recommended in the FCA report dated 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | HUMBOLDT CONSERVATION CAMP SITE | 9972 | Correct | HCC |  | Winnemucca | 1986 |  | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 6000
3754INT1 | INTERIOR FINISHES | 3754 | It is recommended to maintain the Fiberglass Reinforced Panels (FRP) at least once in the next 4-5 years. This will include cleaning all surfaces, if needed, adding additional adhesive or fasteners to the FRP, caulking and to make necessary repairs to expansion joints and moldings. This project should be scheduled on a cyclical basis to maintain the integrity of the structure. | ARSENIC TREATMENT BUILDING | 9972 | Correct | HCC |  | Winnemucca | 2010 | 160 | 2016-07-07 | Four to Ten Years | Long-Term Needs | 3 | 1600
9972SIT3 | SITE BOLLARDS | 9972 | The site has a fueling area for agency vehicles. The above ground fuel tank requires bollards for protection from vehicle impact per International Fire Code (IFC) 2012. This project would provide for the purchase and installation of 12 - 8" concrete filled steel bollards to protect the fuel tank. This project or a portion thereof was previously recommended in the FCA report dated 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | HUMBOLDT CONSERVATION CAMP SITE | 9972 | Correct | HCC |  | Winnemucca | 1986 |  | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 12000
9972SIT1 | SIDEWALK REPLACEMENT | 9972 | The sidewalks serving the buildings on this site are deteriorated and failing. In some areas cracks wider than four inches have been identified, and there is settling in many locations. This project addresses removal and replacement of existing sidewalks as needed. 4" thick concrete sidewalks were used for this estimate. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. This project includes providing an accessible path of travel from the ADA parking area through the gatehouse to the visitors area which is located in the Housing Unit. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2000 and 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | HUMBOLDT CONSERVATION CAMP SITE | 9972 | Correct | HCC |  | Winnemucca | 1986 |  | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 76000
9972SIT8 | CRACK FILL & SEAL ASPHALT PAVING | 9972 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the paving site wide including access roads, parking areas and driving test areas. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 87,120 square feet of asphalt area was used to generate this estimate. It is recommended that this project coincide with the ADA Parking Space project. This project or a portion thereof was previously recommended in the FCA report dated 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | HUMBOLDT CONSERVATION CAMP SITE | 9972 | Correct | HCC |  | Winnemucca | 1986 |  | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 108900
3786EXT1 | EXTERIOR FINISHES | 3786 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | WASTEWATER TREATMENT BUILDING | 9972 | Correct | HCC |  | Winnemucca | 2006 | 120 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1200
9972SEC2 | EXTERIOR LIGHTING | 9972 | The entrance road, parking area and site have insufficient, poor and none functional lighting. Considering the environment of the site, this area needs to be well lit. This project will provide funding for the purchase and installation of 30 additional LED fixtures; 30’ light poles and 30" diameter raised concrete bases; electrical trenching; conduit; wiring, and required connections to the existing utilities. The light poles should match the existing light poles located in the surrounding area. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2000 and 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | HUMBOLDT CONSERVATION CAMP SITE | 9972 | Correct | HCC |  | Winnemucca | 1986 |  | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 240000
3754SFT1 | EXTERIOR FINISHES | 3754 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | ARSENIC TREATMENT BUILDING | 9972 | Correct | HCC |  | Winnemucca | 2010 | 160 | 2016-07-07 | Four to Ten Years | Long-Term Needs | 3 | 1600
9972ADA2 | ADA PARKING SPACE AND PATH OF TRAVEL | 9972 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The existing ADA parking space does not meet the current requirements. This project will provide funding to bring the existing ADA parking space up to code, and will include the removal of the asphalt and replacement with P.C. concrete, updated signage, re-striping, re-grading and any other necessary upgrades. This project will also provide for the addition of a path of travel from the parking space to the gate to the visitor’s entrance. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | HUMBOLDT CONSERVATION CAMP SITE | 9972 | Correct | HCC |  | Winnemucca | 1986 |  | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 30000
9972SIT5 | HAZARDOUS COMMUNICATION PROGRAM | 9972 | Due to the storage of hazardous materials, this site shall comply with International Fire Code (IFC) 2012 Chapter 4 Emergency Planning and Preparedness, and have a written Hazardous Materials Management Plan, including but not limited to, Section 5003 Safety Data Sheets, Section 406 Employee Training and Response Procedures and Section 407 Hazard Communication. Chapter 50 Section 5001 will provide additional assistance in devising and implementing a hazardous communication program. | HUMBOLDT CONSERVATION CAMP SITE | 9972 | Correct | HCC |  | Winnemucca | 1986 |  | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 2000
9972ENV1 | ABOVE GROUND WASTE OIL TANK CONTAINMENT | 9972 | The existing above ground waste oil tank is located on dirt. This project would install a concrete slab under the tank to prevent soil contamination and provide secondary containment and make it easier for maintenance and operations personnel to access the tank. | HUMBOLDT CONSERVATION CAMP SITE | 9972 | Correct | HCC |  | Winnemucca | 1986 |  | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 2200
9972SEC0 | FENCE UPGRADE | 9972 | The chain link perimeter fence is currently 7’ high. For security purposes the staff has requested repairs to the bottom tension wire to prevent inmates from bending the fence up and crawling underneath. This project will provide for 2000’ of new tension wire that will be installed at the bottom of the existing perimeter fence. It will also provide for the removal of dirt that has built up along the fence. | HUMBOLDT CONSERVATION CAMP SITE | 9972 | Correct | HCC |  | Winnemucca | 1986 |  | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 10000
1391INT4 | INTERIOR FINISHES | 1391 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | MULTI-PURPOSE/ GYMNASIUM | 9974 | Correct | WCC |  | Wells | 1985 | 7000 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 70000
1391HVA1 | HEATER REPLACEMENT | 1391 | The building is heated by one wall mounted propane-fired heating unit. It is original to the building and is reaching the end of its useful life. This project provides for disposal of the existing unit and replacement with a new propane-fired unit including connections to utilities. | MULTI-PURPOSE/ GYMNASIUM | 9974 | Correct | WCC |  | Wells | 1985 | 7000 | 2016-08-24 | Four to Ten Years | Long-Term Needs | 3 | 4500
1391SFT3 | BATTERY STORAGE | 1391 | Section 608 of the 2012 IFC explains the requirements for stationary storage of battery systems. This project will provide funding for the proper way to store, charge and/or use batteries indoors. IFC Section 608 states batteries shall have safety caps, spill control and neutralization, mechanical ventilation and/or cabinet ventilation, supervision over the mechanical ventilation, building or cabinet signage, seismically braced, and a smoke alarm. This project would provide funding for the requirement of Section 608 of the 2012 IFC. | MULTI-PURPOSE/ GYMNASIUM | 9974 | Correct | WCC |  | Wells | 1985 | 7000 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 25000
1391SFT4 | FLUE VENT REPLACEMENT | 1391 | There are several flue vents in the building which do not comply with IMC 2012 chapter 8, chimneys and vents. The flue vents were installed with improper flues and per section 804 direct vent terminations vent terminals for direct vented appliances shall be installed in accordance with the manufacturer’s installation instructions. The flue vents, in some cases, are too close to combustibles and don’t have the proper clearances, per IMC 2012 this can cause a fire hazard. It is recommended that all flue vents throughout the building be replaced. Replacements shall meet the manufacture’s specifications and IMC 2012. The flue vents should be installed by a licensed contractor. This project would provide funds to replace all the flue vents throughout the building. | MULTI-PURPOSE/ GYMNASIUM | 9974 | Correct | WCC |  | Wells | 1985 | 7000 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 8000
1391EXT7 | EXTERIOR SIDING REPLACEMENT | 1391 | The corrugated metal panels covering the building are original and should be scheduled for replacement. Many of the panels are damaged from general wear and tear. This project would provide for the removal and the disposal of the existing panels and the replacement with new pre-painted metal panels. | MULTI-PURPOSE/ GYMNASIUM | 9974 | Correct | WCC |  | Wells | 1985 | 7000 | 2016-08-24 | Four to Ten Years | Long-Term Needs | 3 | 150000
1391INT6 | DOOR HARDWARE REPLACEMENT | 1391 | The doors have manually operated flush bolts with a padlock on the outside of each door. Per IBC 2012 Chapter 10 Means of Egress, Section 1008, manually operated flush bolts or surface bolts are not permitted. This project would install new Schlage grade 1 or approved equal keyed ADA approved dead bolts and levers. | MULTI-PURPOSE/ GYMNASIUM | 9974 | Correct | WCC |  | Wells | 1985 | 7000 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 7000
1391EXT4 | EXTERIOR DOOR REPLACEMENT | 1391 | The exterior metal doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the three exterior doors with new metal doors, frames and hardware. Removal and disposal of the existing doors is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2000 and 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | MULTI-PURPOSE/ GYMNASIUM | 9974 | Correct | WCC |  | Wells | 1985 | 7000 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
1391ENV1 | BIRD ABATEMENT | 1391 | The building has been inhabited by birds. The birds introduce a potential risk of disease, cause maintenance problems with the roofing systems and cost labor time for general clean-up. This project would provide for the removal and the disposal of bird debris, eggs and carcasses from the site and building by a licensed pest control business. | MULTI-PURPOSE/ GYMNASIUM | 9974 | Correct | WCC |  | Wells | 1985 | 7000 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 3000
1391PLM3 | WATER TREATMENT SYSTEM REPLACEMENT | 1391 | The existing water softening/ treatment systems in the building are currently not operational. They are original to the building and have approached the end of their expected life. Failure of the equipment causes wear and tear on the domestic water supply lines, clothes washing equipment, and plumbing fixtures. This project would provide for the replacement of the existing water softeners/ treatment systems with new equipment. This project would also provide for a chemical treatment program, including an updated chemicals control system, service and employee training provided by a qualified water treatment vendor. The annual maintenance fee charged by the water treatment vendor would be determined after an investigation of the water system is complete. These annual costs are not included in this project cost. For budgeting purposes, a $12,000 annual maintenance fee is suggested. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | MULTI-PURPOSE/ GYMNASIUM | 9974 | Correct | WCC |  | Wells | 1985 | 7000 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
1391EXT1 | WINDOW REPLACEMENT | 1391 | The windows are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, energy efficient units. This estimate is for the replacement of 3 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2000 and 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | MULTI-PURPOSE/ GYMNASIUM | 9974 | Correct | WCC |  | Wells | 1985 | 7000 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7200
1391ENR2 | REPLACE INSULATION | 1391 | There are numerous areas of damaged insulation at the ceiling that is in need of replacement. This project would provide for the removal of the ceiling insulation and would install a faced R-38 insulation which will help to reduce energy costs. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2000 and 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | MULTI-PURPOSE/ GYMNASIUM | 9974 | Correct | WCC |  | Wells | 1985 | 7000 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 28000
1391ENR1 | LIGHTING UPGRADE | 1391 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2000 and 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | MULTI-PURPOSE/ GYMNASIUM | 9974 | Correct | WCC |  | Wells | 1985 | 7000 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 56000
1391ADA2 | ADA SIGNAGE | 1391 | ADA regulations pertaining to building access, route of travel and restrooms has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances, route of travel inside the building and restrooms. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2000 and 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | MULTI-PURPOSE/ GYMNASIUM | 9974 | Correct | WCC |  | Wells | 1985 | 7000 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 600
1391EXT2 | OVERHEAD DOOR REPLACEMENT | 1391 | There is a 10'x12' overhead coiling door which is damaged and does not function properly. Exposure and wind have caused the door to bend, crack and lose its finish. It has also been struck and dented by vehicles. It is original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead coiling door and replacement with a new manually operated overhead coiling door. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2000 and 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | MULTI-PURPOSE/ GYMNASIUM | 9974 | Correct | WCC |  | Wells | 1985 | 7000 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
1391ADA1 | ADA RESTROOM UPGRADE | 1391 | The building does not have an accessible restroom. The existing restroom does not meet the ADA requirements. A complete retrofit is necessary. This project would provide funding for construction of one unisex accessible restroom. Items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2000 and 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | MULTI-PURPOSE/ GYMNASIUM | 9974 | Correct | WCC |  | Wells | 1985 | 7000 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 15000
1391EXT5 | EXTERIOR FINISHES | 1391 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking, sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | MULTI-PURPOSE/ GYMNASIUM | 9974 | Correct | WCC |  | Wells | 1985 | 7000 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 14000
1391SFT2 | INTERIOR STAIR HANDRAIL REPLACEMENT | 1391 | There are two sets of interior stair handrails that are older and do not meet code for safety or accessibility. The gripping surfaces are incorrect and they are not continuous from the top to the bottom of the landings. This project recommends the installation of handrails on both sides of the stairs, with proper returns and supports. Removal and disposal of the existing railings is included in this estimate. NRS 338.180, 2012 IBC Chapter 10, Section 1012, ICC/ANSI A117.1 - 2009 and the most current version of the ADAAG were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | MULTI-PURPOSE/ GYMNASIUM | 9974 | Correct | WCC |  | Wells | 1985 | 7000 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 18000
1391PLM2 | WATER HEATER REPLACEMENT | 1391 | There is a 100 gallon propane-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new propane-fired water heater be installed. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | MULTI-PURPOSE/ GYMNASIUM | 9974 | Correct | WCC |  | Wells | 1985 | 7000 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
1391PLM1 | LAUNDRY ROOM REMODEL | 1391 | The Laundry Room does not have enough space or equipment to keep up with demand. The equipment takes up most of the floor space leaving very little space to maneuver. It is recommended to remodel the area creating a larger space for the Laundry Room and to upgrade the existing equipment. This project would provide for remodeling the area and replacing the existing washers and dryers. Removal and disposal of the existing equipment and construction materials is included in the estimate. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | MULTI-PURPOSE/ GYMNASIUM | 9974 | Correct | WCC |  | Wells | 1985 | 7000 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 60000
1391INT5 | GYMNASIUM FLOOR REPAIRS | 1391 | The concrete floor in the gymnasium is worn and damaged and should be resurfaced. This project provides for cleaning and repairing the existing floor, applying a bonding agent, pouring a new polymer surface, and applying an appropriate finish product where applicable. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | MULTI-PURPOSE/ GYMNASIUM | 9974 | Correct | WCC |  | Wells | 1985 | 7000 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
1391EXT6 | ROOF REPLACEMENT | 1391 | The standing seam metal roof on this building was in poor condition at the time of the survey and had active leaks. It is recommended that this building be re-roofed in the next 1-2 years with a new single-ply roofing system which will be installed directly over the existing metal roof. This will allow the roof to qualify for the statewide roofing program warranty and preventative maintenance agreement. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | MULTI-PURPOSE/ GYMNASIUM | 9974 | Correct | WCC |  | Wells | 1985 | 7000 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 84000
1391ELE3 | ELECTRICAL UPGRADE | 1391 | The existing electrical system in the building is old, has exposed romex, loose wiring, and is at its maximum capacity. This project would provide for a complete upgrade to the system. It would include new stranded wires in conduit and to remove the existing Romex wiring throughout the building. It would secure the loose wiring and add a new subpanel with increased capacity. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | MULTI-PURPOSE/ GYMNASIUM | 9974 | Correct | WCC |  | Wells | 1985 | 7000 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 175000
1391SFT1 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 1391 | The emergency egress lighting is nonexistent and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2000 and 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | MULTI-PURPOSE/ GYMNASIUM | 9974 | Correct | WCC |  | Wells | 1985 | 7000 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 14000
2136SFT1 | EXTERIOR LANDING INSTALLATION | 2136 | There are two out-swinging exterior doors on the building, which swing out over a step that does not have a landing. This does not comply with 2012 IBC Section 1008.1, which requires a proper landing and for the landing to not be more than 1/2" below the threshold. This project would provide for the installation of compliant landings. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | PUMP HOUSE | 9974 | Correct | WCC |  | Wells | 1984 | 125 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 5000
2137EXT2 | ROOF REPLACEMENT | 2137 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 4-5 years with a new 50 year asphalt composition shingle roof and new underlayment. This estimate includes removal and disposal of the old roof. | TOOL STORAGE SHED | 9974 | Correct | WCC |  | Wells | 1985 | 144 | 2016-08-24 | Four to Ten Years | Long-Term Needs | 3 | 1728
2137INT1 | INTERIOR FINISHES | 2137 | It is recommended to paint the interior walls and ceilings at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | TOOL STORAGE SHED | 9974 | Correct | WCC |  | Wells | 1985 | 144 | 2016-08-24 | Four to Ten Years | Long-Term Needs | 3 | 1440
2137EXT1 | EXTERIOR FINISHES | 2137 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding, priming and painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | TOOL STORAGE SHED | 9974 | Correct | WCC |  | Wells | 1985 | 144 | 2016-08-24 | Four to Ten Years | Long-Term Needs | 3 | 1440
2136ENR1 | LIGHTING UPGRADE | 2136 | The existing lighting fixture is the older incandescent type, and is not energy efficient. This project will upgrade the fixture to a higher efficiency unit with a longer life cycle. A 5,000K LED is suggested. An occupancy sensor will be installed for additional savings. Any electrical wiring upgrades are not included in this estimate. | PUMP HOUSE | 9974 | Correct | WCC |  | Wells | 1984 | 125 | 2016-08-24 | Four to Ten Years | Long-Term Needs | 3 | 1000
2136EXT2 | ROOF REPLACEMENT | 2136 | The asphalt roofing system on the building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition shingle roof and new underlayment. This estimate includes removal and disposal of the old roof. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | PUMP HOUSE | 9974 | Correct | WCC |  | Wells | 1984 | 125 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
2136ELE1 | GFCI DUPLEX OUTLET REPLACEMENT | 2136 | There is an outlet in the Pump House building which is not GFCI protected. This outlet should be changed to GFCI type outlet per the NEC. This project would provide for the purchase and installation of one GFCI outlet. | PUMP HOUSE | 9974 | Correct | WCC |  | Wells | 1984 | 125 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 400
2136INT1 | INTERIOR FINISHES | 2136 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | PUMP HOUSE | 9974 | Correct | WCC |  | Wells | 1984 | 125 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1250
2136EXT1 | EXTERIOR FINISHES | 2136 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding, priming and painting of the wood and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | PUMP HOUSE | 9974 | Correct | WCC |  | Wells | 1984 | 125 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1250
2136EXT3 | EXTERIOR DOOR REPLACEMENT | 2136 | The existing exterior metal doors and frames appear to be original to the building. They are damaged and are showing signs of wear and deterioration and are no longer plumb, due to building foundation settling. This project would provide for the removal and replacement of two new metal door assemblies including frames, locks, hardware and painting. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | PUMP HOUSE | 9974 | Correct | WCC |  | Wells | 1984 | 125 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
2137ADA1 | ADA UPGRADES | 2137 | The existing threshold at the door entrance exceeds ½ inch. ADA requirements state that the threshold should not be any higher than ½ inch for accessibility, ICC/ANSI A117.1-2009 404.2.5. The door dead bolt on the door is round and requires a gripping action. Section 4.13.9 of the ADAAG states that handles, pulls, latches, locks and other operating devices on accessible doors shall have a shape that is easy to grasp with one hand and does not require tight grasping, tight pinching, or twisting of the wrist to operate. This project would provide funding for the removal and replacement of the threshold and the door dead bolt to meet these requirements. | TOOL STORAGE SHED | 9974 | Correct | WCC |  | Wells | 1985 | 144 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 6000
2993INT2 | DOOR HARDWARE REPLACEMENT | 2993 | The door has a manually operated flush bolt with a padlock on the outside of each door. Per IBC 2012 Chapter 10 Means of Egress, Section 1008, manually operated flush bolts or surface bolts are not permitted. This project is to install new Schlage grade 1 or approved equal keyed ADA approved lever. | NDF STORAGE SHED #2 | 9974 | Correct | WCC |  | Wells | 1985 | 144 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 1000
2993EXT1 | EXTERIOR FINISHES | 2993 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | NDF STORAGE SHED #2 | 9974 | Correct | WCC |  | Wells | 1985 | 144 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 1440
2993EXT2 | ROOF REPLACEMENT | 2993 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition shingle roof and new underlayment. This estimate includes removal and disposal of the old roof. | NDF STORAGE SHED #2 | 9974 | Correct | WCC |  | Wells | 1985 | 144 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1728
2993SFT1 | EXTERIOR LANDING INSTALLATION | 2993 | There is an out-swinging exterior door which swings out over dirt and does not have a landing in compliance with IBC 2012. IBC Section 1008 requires a landing to be not more than 1/2" below the threshold. This project would provide for the installation of a compliant landing for the door. | NDF STORAGE SHED #2 | 9974 | Correct | WCC |  | Wells | 1985 | 144 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 5000
2994INT2 | DOOR HARDWARE REPLACEMENT | 2994 | The door has a manually operated flush bolt with a padlock on the outside of each door. Per IBC 2012 Chapter 10 Means of Egress, Section 1008, manually operated flush bolts or surface bolts are not permitted. This project is to install new Schlage grade 1 or approved equal keyed ADA approved lever. | FUEL STATION STORAGE SHED | 9974 | Correct | WCC |  | Wells | 1985 | 91 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 1000
2994ENR1 | LIGHTING UPGRADE | 2994 | The existing light fixture is the older fluorescent type, and is not energy efficient. This project will upgrade the fixture to a higher efficiency unit with a longer life cycle. 5,000K LED lamps, without the ballast, is suggested, and new tombstones (if needed). An occupancy sensor will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | FUEL STATION STORAGE SHED | 9974 | Correct | WCC |  | Wells | 1985 | 91 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 728
9974PLM1 | SEPTIC SYSTEM REPLACEMENT | 9974 | The septic system serving the site is failing. This project recommends replacing the septic tank and moving the leach field. The estimate includes abandoning and filling the old septic tank and the installation of a new tank and leach field. This estimate is for an engineered system which will conform to all required environmental rules and regulations including NDEP. | WELLS CONSERVATION CAMP SITE | 9974 | Correct | WCC |  | Wells | 1984 |  | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 200000
9974SEC3 | SECURITY SYSTEM INSTALLATION | 9974 | There is no central security camera or recording system for the site. This is a safety issue for the public, staff and inmates as all areas cannot be seen by the security staff or recorded in case of an incident. This project would provide for the installation of surveillance cameras and a security system for the entire site and all required connections to existing utility systems. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | WELLS CONSERVATION CAMP SITE | 9974 | Correct | WCC |  | Wells | 1984 |  | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 75000
2995EXT1 | EXTERIOR FINISHES | 2995 | It is important to maintain the finish, weather resistance and appearance of the Water Tank. This project recommends work to protect the exterior of the Water Tank to include; preparation for painting, caulk and paint. It is recommended for this project to be implemented in the next 2-3 years. It is recommended to conduct inspections and testing on a cyclical basis based per NAC 445. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | WATER TANK | 9974 | Correct | WCC |  | Wells | 1985 | 250 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
2994EXT2 | ROOF REPLACEMENT | 2994 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition shingle roof and new underlayment. This estimate includes removal and disposal of the old roof. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | FUEL STATION STORAGE SHED | 9974 | Correct | WCC |  | Wells | 1985 | 91 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1092
9974ADA3 | ADA ACCESSIBLE PATH OF TRAVEL | 9974 | The ADA provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the office are necessary to comply with ADA accessibility requirements. This project would provide for a concrete van accessible ADA parking and loading space and concrete walkway to the existing sidewalk. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. 750 square feet of concrete was used for this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2000 and 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | WELLS CONSERVATION CAMP SITE | 9974 | Correct | WCC |  | Wells | 1984 |  | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 18750
9974SEC1 | INSTALL EXTERIOR SITE LIGHTING | 9974 | The site has minimal site lighting in the parking lot and between the buildings which is a security and safety concern. This project would provide funding for the purchase and installation of twelve 20'-0" high light poles including 30" diameter raised concrete bases, electrical trenching, conduit, wiring and connections to existing utilities. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2000 and 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | WELLS CONSERVATION CAMP SITE | 9974 | Correct | WCC |  | Wells | 1984 |  | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 110400
9974ADA2 | ADA SIDEWALK REPLACEMENT | 9974 | The sidewalks serving the buildings and recreation areas on this site are constructed of pieces of concrete. An ADA accessible path of travel should be provided. This project addresses the removal and the replacement of the existing concrete pieces, as needed, to provide new concrete sidewalks. 4,800 SF of 4" thick concrete was used for this estimate. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and ADAAG - 2010 were referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2000 and 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | WELLS CONSERVATION CAMP SITE | 9974 | Correct | WCC |  | Wells | 1984 |  | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 72000
2994ELE1 | GFCI OUTLETS | 2994 | The existing receptacles in the Fuel Station Storage Shed are standard duplex receptacles. The 2011 NEC 210.8 requires these locations to have GFCI protection. This project would provide for removing the standard receptacles and installing GFCI receptacles. | FUEL STATION STORAGE SHED | 9974 | Correct | WCC |  | Wells | 1985 | 91 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 800
2994SFT1 | PROPANE TANK RELOCATION | 2994 | There is an above ground propane storage tank at the front of the building. According to Table 3504.2.1 of the 2012 IFC, flammable gases must be stored at least 5 feet away from a building of non-rated construction. This project would provide for relocating the propane storage tank to comply with code. | FUEL STATION STORAGE SHED | 9974 | Correct | WCC |  | Wells | 1985 | 91 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 3500
2994EXT1 | EXTERIOR FINISHES | 2994 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is the painting of the wood gables, door and fascia, caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | FUEL STATION STORAGE SHED | 9974 | Correct | WCC |  | Wells | 1985 | 91 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 364
2995INT1 | INTERIOR FINISHES | 2995 | It is important to maintain water quality, quantity and the interior finish of the Water Tank. This project would include hiring certified divers or draining the tank to inspect and clean the interior walls, and to weld, sandblast and perform repairs and add protective coatings, if needed. It is important to follow all ANSI, NSF and AWWA approved ways to disinfect and repair water tanks. The standard recommendation is to conduct a comprehensive inspection inside the Water Tank every 5 years, except for newly constructed tanks. Newly constructed water tanks should be inspected within 10 years of service and every 5 years thereafter. | WATER TANK | 9974 | Correct | WCC |  | Wells | 1985 | 250 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 5000
2994SFT2 | EXTERIOR LANDING INSTALLATION | 2994 | There is an out-swinging exterior door which swings out over dirt and does not have a landing in compliance with IBC 2012. IBC Section 1008 requires a landing to be not more than 1/2" below the threshold. This project would provide for the installation of a compliant landing for the door. | FUEL STATION STORAGE SHED | 9974 | Correct | WCC |  | Wells | 1985 | 91 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 5000
0708EXT3 | EXTERIOR FINISHES | 0708 | It is important to maintain the finish, weather resistance, energy efficiency and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | HOUSING/ CULINARY/ ADMINISTRATION | 9974 | Correct | WCC |  | Wells | 1984 | 14000 | 2016-08-24 | Four to Ten Years | Long-Term Needs | 3 | 140000
0708ADA2 | ADA SIGNAGE | 0708 | The ADA regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with these criteria. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2000 and 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | HOUSING/ CULINARY/ ADMINISTRATION | 9974 | Correct | WCC |  | Wells | 1984 | 14000 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 2500
0708ADA1 | ADA RESTROOM REMODEL | 0708 | There are no ADA compliant restrooms in the facility. There should be an ADA restroom for visitors as well as for the inmates. The existing visitors restroom, the inmate restrooms and shower rooms will require a complete retrofit. This project would provide funding for construction of a unisex accessible restroom for visitors and an accessible restroom and shower area for the inmates in one of the housing wings. These items may include a new sink, toilet, shower, hardware, mirrors, fixtures, flooring and paint. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and ADAAG - 2010 were referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2000 and 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | HOUSING/ CULINARY/ ADMINISTRATION | 9974 | Correct | WCC |  | Wells | 1984 | 14000 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 150000
0708SFT1 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0708 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2000 and 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | HOUSING/ CULINARY/ ADMINISTRATION | 9974 | Correct | WCC |  | Wells | 1984 | 14000 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 28000
0708SEC1 | INSTALL ALARMS ON BACK DOORS OF CULINARY | 0708 | Add delayed egress alarms to all exterior doors. These are 30 second delayed egress magnetic locks that interface with the fire alarm. Under normal conditions they give off an "attempt to egress tone" and then unlock the door 30 seconds after being activated by pushing on the crash bar. The locks automatically release upon activation of the fire alarm. They also have a bypass feature for times when the door needs to be left open or unalarmed i.e. making deliveries, etc. The alarms also have remote annunciators that can be located in one or more locations i.e. control room, etc. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2000 and 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | HOUSING/ CULINARY/ ADMINISTRATION | 9974 | Correct | WCC |  | Wells | 1984 | 14000 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 70000
0708HVA1 | EXHAUST HOOD INSTALLATION | 0708 | Section 507.2.2 of the UMC states, Hoods shall be installed at or above all commercial-type dishwashing machines and similar equipment which produce comparable amounts of steam. This project would provide funding to install a Type II exhaust hood above the dishwasher in the culinary area. This project will provide for an exhaust hood, roofing repairs, electrical and installation. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | HOUSING/ CULINARY/ ADMINISTRATION | 9974 | Correct | WCC |  | Wells | 1984 | 14000 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 9200
0708INT1 | CULINARY FLOOR REPLACEMENT | 0708 | The painted concrete floor in the kitchen is worn and damaged and should be resurfaced. This project provides for cleaning and repairing the existing floor, applying a bonding agent, pouring a new polymer surface and applying an appropriate finish product. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2000 and 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | HOUSING/ CULINARY/ ADMINISTRATION | 9974 | Correct | WCC |  | Wells | 1984 | 14000 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 9200
0708PLM1 | PLUMBING REPLACEMENT | 0708 | The plumbing and waste system is older and in poor condition. Most of the system appears to be original to the building and should be scheduled for replacement. The sewer lines are rusted and failing especially underground. This project would provide for replacement all of the water and sewer lines in the building. This estimate includes removal and disposal of the existing system as required. | HOUSING/ CULINARY/ ADMINISTRATION | 9974 | Correct | WCC |  | Wells | 1984 | 14000 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 210000
0708SFT8 | SMOKE CARBON MONOXIDE ALARM | 0708 | Section 907.2.11 of the 2012 IBC and 2012 IFC explains the requirements for smoke alarms in dwelling units including installing and maintaining smoke alarms in each sleeping room and on the ceiling or wall outside of each separate sleeping area in the immediate vicinity of bedrooms. Per IFC 2012 Section 908.7 carbon monoxide alarms group I or R occupancies located in a building containing a fuel-burning appliance or in a building which has an attached garage shall be equipped with single-station carbon monoxide alarm. The carbon monoxide alarm shall be listed as complying with UL 2034 and be installed and maintained in accordance with NFPA 720 and the manufacturer’s instructions. State Fire Marshal NAC 477.915 (3) requires that smoke detectors and carbon monoxide alarms be connected to the wiring of the building with a battery backup. This project would provide funding for the purchase and installation of a smoke alarm and combo smoke alarm and carbon monoxide alarm in accordance with these codes. | HOUSING/ CULINARY/ ADMINISTRATION | 9974 | Correct | WCC |  | Wells | 1984 | 14000 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 13500
0708SFT9 | EXTERIOR LANDING INSTALLATION | 0708 | There are two out-swinging exterior doors on the building, which swing out over a step that does not have a landing. This does not comply with 2012 IBC Section 1008.1, which requires a proper landing and for the landing to not be more than 1/2" below the threshold. This project would provide for the installation of compliant landings. | HOUSING/ CULINARY/ ADMINISTRATION | 9974 | Correct | WCC |  | Wells | 1984 | 14000 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 10000
0708EXT5 | GUTTER REPLACEMENT | 0708 | The existing gutter on the building and downspouts have numerous joints that have proven impossible to seal against leaks. The leaking gutters and downspouts will cause premature deterioration to the building finishes and the site hardscape. The downspouts currently terminate within inches of the rain gutter with no continuous drainage away from the building. This project would replace the existing segmented gutter with seamless gutter, downspouts and extensions to approximately 5'-0" away from the perimeter of the building. | HOUSING/ CULINARY/ ADMINISTRATION | 9974 | Correct | WCC |  | Wells | 1984 | 14000 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 55000
0708ADA7 | ADA UPGRADES | 0708 | Section 4.13.9 of the ADAAG states that handles, pulls, latches, locks and other operating devices on accessible doors shall have a shape that is easy to grasp with one hand and does not require tight grasping, tight pinching, or twisting of the wrist to operate. Lever-operated mechanisms, push-type mechanisms, and U-shaped handles are acceptable designs. It is recommended that proper lever hardware be installed in this building to meet these requirements. | HOUSING/ CULINARY/ ADMINISTRATION | 9974 | Correct | WCC |  | Wells | 1984 | 14000 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 27000
0708HVA3 | EVAPORATIVE COOLER REPLACEMENT | 0708 | There are currently nine evaporative coolers mounted on the roof of the Housing Unit, three for each wing. They are severely scaled and have reached the end of their serviceable life. This project would provide for nine new evaporative coolers to be installed, and includes removal and disposal of the old evaporative coolers and utility connections to the new units. | HOUSING/ CULINARY/ ADMINISTRATION | 9974 | Correct | WCC |  | Wells | 1984 | 14000 | 2016-08-24 | Four to Ten Years | Long-Term Needs | 3 | 16000
0708SFT5 | FLUE REPLACEMENT | 0708 | There are several flues in the building, which do not comply with IMC 2012 chapter 8, chimneys and vents. The flue vents were installed with improper flues and per section 804 direct vent terminations vent terminals for direct vented appliances shall be installed in accordance with the manufacturer’s installation instructions. The vents, in some cases, are too close to combustibles and don’t have the proper clearances, per IMC 2012 this can cause a fire hazard. The ductwork is connected with metal tape and per 803.10.1 supports and joints ductwork shall be fastened with sheet metal screws, rivets or other approved means. The flues are in poor condition and have cracks. Per 801.18.2 flue passageways, the flue liner, chimney inner wall or vent inner wall shall be continuous and shall be free of cracks, gaps, perforations or other damage or deteriorations, which would allow the escape of combustion products, including gases, moisture and creosote. It is recommended that all flues throughout the building be replaced. Replacements shall meet the manufacture’s specifications and IMC 2012. The flues should be installed by a licensed contractor. This project would provide funds to replace all the flues throughout the building. | HOUSING/ CULINARY/ ADMINISTRATION | 9974 | Correct | WCC |  | Wells | 1984 | 14000 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 48000
0708INT4 | INTERIOR FINISHES | 0708 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2000 and 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | HOUSING/ CULINARY/ ADMINISTRATION | 9974 | Correct | WCC |  | Wells | 1984 | 14000 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 140000
0708ADA3 | ADA RAMP UPGRADE | 0708 | The ramp at the entrance to the building does not fully meet ADA ramp accessibility guidelines. The design and geometry of rails are incorrect and there is no curb on the open side of the ramp. This project recommends the installation of new handrails and a curb to comply with current ADA accessibility standards. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | HOUSING/ CULINARY/ ADMINISTRATION | 9974 | Correct | WCC |  | Wells | 1984 | 14000 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 35000
0708EXT4 | EXTERIOR DOOR REPLACEMENT | 0708 | The existing exterior metal doors and frames appear to be original to the building. They are damaged and showing signs of wear and deterioration from constant use and inmate abuse. This project would provide for the removal and replacement of ten new metal door assemblies including frames, locks, hardware and painting. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | HOUSING/ CULINARY/ ADMINISTRATION | 9974 | Correct | WCC |  | Wells | 1984 | 14000 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 40000
0708INT5 | VCT FLOORING REPLACEMENT | 0708 | The VCT flooring throughout the building is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | HOUSING/ CULINARY/ ADMINISTRATION | 9974 | Correct | WCC |  | Wells | 1984 | 14000 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 126000
0708PLM2 | WATER TREATMENT SYSTEM REPLACEMENT | 0708 | The existing water softening/ treatment systems in the building are currently not operational. They are original to the building and approaching the end of their lifecycles. Failure of the equipment causes wear and tear on the domestic water supply lines, plumbing fixtures and HVAC equipment. This project would provide for the replacement of the existing water softeners/ treatment systems with new equipment. This project would also provide for a chemical treatment program including an updated chemicals control system, service and employee training provided by a qualified water treatment vendor. The annual maintenance fee charged by the water treatment vendor would be determined after an investigation of the water system is complete. These annual costs are not included in this project cost. For budgeting purposes, a $12,000 annual maintenance fee is suggested. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | HOUSING/ CULINARY/ ADMINISTRATION | 9974 | Correct | WCC |  | Wells | 1984 | 14000 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0708SFT2 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0708 | This building does not have an automatic fire suppression system and has more than 12,000 square feet on the first floor. Current state regulations require state-owned buildings having more than 12,000 square feet on one floor, or more than 24,000 square feet total, must be retrofitted with fire sprinklers during the next remodel or addition. This project would provide funding for the installation of fire sprinklers, including backflow prevention devices. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | HOUSING/ CULINARY/ ADMINISTRATION | 9974 | Correct | WCC |  | Wells | 1984 | 14000 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 196000
0708SIT1 | SITE DRAINAGE UPGRADES | 0708 | The grade does not slope away effectively from the buildings. Water has pooled against the foundation. In the winter months, as the water freezes against the foundation, over time, this can cause damage to the foundation. It is recommended per IBC 1804.3 Site Grading the ground immediately adjacent to the foundation shall be sloped away from the building at a slope of not less than one vertical in 20 units horizontal (5-percent slope) for a minimum distance of 10 feet (3048 mm) measured perpendicular to the face of the wall. This project would create a 5% slope away from the buildings. Additional drainage swales shall be installed, as needed. It is recommended that the grading be completed within 2-3 years. | HOUSING/ CULINARY/ ADMINISTRATION | 9974 | Correct | WCC |  | Wells | 1984 | 14000 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 75000
0708ENR5 | LIGHTING UPGRADE | 0708 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | HOUSING/ CULINARY/ ADMINISTRATION | 9974 | Correct | WCC |  | Wells | 1984 | 14000 | 2016-08-24 | Four to Ten Years | Long-Term Needs | 3 | 112000
0708ENR2 | WATER HEATER REPLACEMENT | 0708 | There are five 100 gallon propane-fired water heaters throughout the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended to replace the water heaters with an energy efficient on-demand tankless water heaters. The estimate is based on the purchase and installation of five 7.4 gallon per minute propane gas fired units and includes disposal of the old equipment. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | HOUSING/ CULINARY/ ADMINISTRATION | 9974 | Correct | WCC |  | Wells | 1984 | 14000 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
0708ENR3 | BOILER REPLACEMENT | 0708 | There are two hot water boilers servicing the building. They are original to the building dating back to 1984. The life expectancy of these units is 20 to 25 years with proper maintenance and water treatment programs. Replacement parts for performing routine and emergency maintenance are hard to find for this old equipment. The controls and mixing valves should be replaced for the same reasons. This project would provide for the removal and disposal of the existing boilers, controls and mixing valve and replacement with new energy efficient equipment including all required connections to utilities and equipment. The estimate is based on a 300 MBH output hot water boiler. This project should be implemented concurrently with the water treatment project. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | HOUSING/ CULINARY/ ADMINISTRATION | 9974 | Correct | WCC |  | Wells | 1984 | 14000 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 100000
0708HVA2 | AIR CONDITIONER INSTALLATION | 0708 | The server room is not sufficiently cooled by the existing HVAC system. If the room is too warm, the computer equipment will prematurely age and may fail due to overheating. It is recommended to install an air conditioning system in the room to ensure that the temperature is properly regulated. This project would provide for the purchase and installation of an air conditioner including all required connections to existing utilities. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | HOUSING/ CULINARY/ ADMINISTRATION | 9974 | Correct | WCC |  | Wells | 1984 | 14000 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 5000
0708SFT3 | FIRE ALARM SYSTEM UPGRADE | 0708 | This building is equipped with an automatic fire detection and alarm system that no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Per NAC 477.917, If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | HOUSING/ CULINARY/ ADMINISTRATION | 9974 | Correct | WCC |  | Wells | 1984 | 14000 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 56000
0708ADA5 | ADA TABLE UPGRADE | 0708 | Per the United States Access Board Section 226.1 where dining surfaces are provided for the consumption of food or drink, at least 5 percent of the seating spaces and standing spaces at the dining surfaces shall comply with 902. ICC ANSI-A117.1-2009 Section 902 which says, if fixed seating is provided, a loose seat or open space for a wheelchair location must be available at those accessible tables. This project would provide funding to remove 3 of the fixed seats, which will allow access for four wheel chairs. | HOUSING/ CULINARY/ ADMINISTRATION | 9974 | Correct | WCC |  | Wells | 1984 | 14000 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 3000
2172SEC1 | COMMUNICATIONS SYSTEM UPGRADE | 2172 | This building is equipped with a communications system that at the time of the survey was not working properly. The communications system provides paging, phone communications and communication to inmates. The communications system is an integral component of the notification and safety procedures for the inmates and staff. The system is problematic and replacement parts are no longer available. It is recommended that the communications system be upgraded. | HOUSING UNIT #8 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 222500
2172EXT1 | EXTERIOR FINISHES | 2172 | It is important to maintain the finish, weather resistance and appearance of the building. The caulked control joints in the CMU of the exterior surface of this building are uniformly deteriorated and should be removed and the joints re-caulked. The metal doors and window frames should be sanded and painted on a cyclical basis. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HOUSING UNIT #8 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 445000
2172EXT2 | ROOF REPLACEMENT | 2172 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2002. It is recommended that this building be re-roofed in the next 4-5 years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HOUSING UNIT #8 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 667500
2172STR1 | WALKWAY RAILING | 2172 | The perimeter roof walkway guardrail is failing. The railing is loose or not attached and is posing a potential safety problem. This project recommends an assessment be performed by a Structural Engineer to determine the cause and provide a design solution. Future projects will be based on the design solution recommendation. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HOUSING UNIT #8 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 3000
2172SFT3 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 2172 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT #8 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 9000
2104PLM1 | WATER HEATER REPLACEMENT | 2104 | There is an on-demand electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new on-demand electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | TOWER #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
2172ADA2 | TDD INSTALLATION | 2172 | The Housing Unit is not equipped with a TDD. In order to comply with ADA requirements it is recommended to install a TDD system in the Housing Unit. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | HOUSING UNIT #8 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 60000
2090EXT2 | ROOF REPLACEMENT | 2090 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time-frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2000. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. | INFIRMARY/ INTAKE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 32986 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 395832
2090ADA4 | ADA ACCESSIBLE COUNTER | 2090 | The ADA provides for accessibility to sites and services for people with physical limitations. The nurse’s station at the entrance of the building has a service counter which does not meet current requirements. Section 904.4 of the ADA Standards for Accessible Design states that a portion of the counter surface that is 36" long minimum and 36" high maximum above the finish floor shall be provided. This project will provide an accessible counter space in accordance with this requirement. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | INFIRMARY/ INTAKE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 32986 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 4000
2090SEC2 | CELL DOORS, LOCKS AND CONTROLS REPLACEMENT | 2090 | Infirmary/ Intake was constructed in 2000. The cell doors, locks and controls are original to the building and have been problematic due to inmate abuse and age. This project would provide for installing new cell doors, locks and controls. A total of 100 doors were used for this estimate. Removal and disposal of the existing equipment is included in this estimate. | INFIRMARY/ INTAKE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 32986 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 800000
2090SEC1 | DOOR CONTROLS SYSTEM REPLACEMENT | 2090 | The control panel/ inmate movement and control system in the housing unit is not working properly. The cell door indicator lights on the control panel are falsely representing the actual status of the cell doors. The officer sometimes cannot tell if the cell door is open or closed. This project would replace the existing secured door control system with a programmable logic controlled system using touch screens for actuation and door status. This project would replace the existing door control system and the outdated wiring. Removal and disposal of the existing equipment is included in this estimate. | INFIRMARY/ INTAKE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 32986 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
2172ADA1 | ADA TABLE UPGRADE | 2172 | Per the United States Access Board and ICC ANSI-A117.1-2009, at least 5 percent of the seating spaces shall be, if fixed seating is provided, a loose seat or open space for a wheelchair. This project would provide funding to remove 3 of the fixed seats, which will allow access for wheel chairs. | HOUSING UNIT #8 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 3000
2103SFT5 | EGRESS LIGHTING REPLACEMENT | 2103 | There are older emergency egress lighting units in this building. These units have a finite lifespan, and this project recommends their replacement with new egress lights, and to also provide additional lights on the main exit routes and in individual rooms as needed. | TOWER #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 1000
2104SFT3 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 2104 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | TOWER #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 9000
2102HVA1 | HVAC EQUIPMENT REPLACEMENT | 2102 | The HVAC unit was installed in 2000 and is not energy efficient. It has reached the end of its expected and useful life. This project would provide for the installation of a new HVAC unit and cleaning of the existing duct work and grilles. This project includes the removal and the disposal of the existing equipment and all required connections to the utilities. | TOWER #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11375
2102EXT3 | SLIDING GLASS DOOR REPLACEMENT | 2102 | The sliding glass door is damaged from age and general wear and tear and has reached the end of its expected life. This project would provide for the replacement of the sliding glass door assembly with a new door, frame and hardware. Removal and disposal of the existing door is included in this estimate. | TOWER #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 2500
2102SEC1 | DOORS, LOCKS AND CONTROLS REPLACEMENT | 2102 | Tower #3 was constructed in 2000. The doors, locks and controls are original to the building and have been problematic due to age. This project would provide for installing new doors, locks and controls. Removal and disposal of the existing equipment is included in this estimate. | TOWER #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
2103EXT1 | EXTERIOR FINISHES | 2103 | It is important to maintain the finish, weather resistance and appearance of the building. The caulked joints in the concrete panels, form much of the exterior surface of this building, and are uniformly deteriorated. The caulking should be removed and the joints should be re-caulked. The metal doors and window frames should be sanded and painted on a cyclical basis. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | TOWER #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4550
2103INT1 | INTERIOR FINISHES | 2103 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and adequately prepared to receive the coating. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | TOWER #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4550
2102SFT3 | BACKFLOW PREVENTER REPLACEMENT | 2102 | There is a backflow preventer for the fire suppression system in the building. It is leaking and should be scheduled for replacement. At the time of the survey the staff indicated they have rebuilt the backflow preventer several times, however it continues to leak. This project would provide for replacing the backflow preventer by a licensed fire suppression contractor. | TOWER #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 5000
2103SEC1 | DOORS, LOCKS AND CONTROLS REPLACEMENT | 2103 | Tower #5 was constructed in 2002. The doors, locks and controls are original to the building and have been problematic due to age. This project would provide for installing new doors, locks and controls. Removal and disposal of the existing equipment is included in this estimate. | TOWER #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
2090INT2 | FLOORING REPLACEMENT | 2090 | The VCT flooring in the Infirmary/ Intake is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. | INFIRMARY/ INTAKE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 32986 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 296874
2103EXT3 | ROOF REPLACEMENT | 2103 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2002. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. | TOWER #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5460
2103EXT2 | WINDOW REPLACEMENT | 2103 | The existing windows in this building are of single pane wire mesh construction. They are not energy efficient. This project would provide for the removal and replacement of the windows with new dual pane security rated windows. | TOWER #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 33600
2103PLM1 | WATER HEATER REPLACEMENT | 2103 | There is an on-demand electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new on-demand electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | TOWER #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
2103SFT4 | BACKFLOW PREVENTER REPLACEMENT | 2103 | There is a backflow preventer for the fire suppression system in the building. It is leaking and should be scheduled for replacement. At the time of the survey the staff indicated they have rebuilt the backflow preventer several times, however it continues to leak. This project would provide for replacing the backflow preventer by a licensed fire suppression contractor. | TOWER #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 5000
2103SFT3 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 2103 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | TOWER #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 9000
2103INT2 | FLOORING REPLACEMENT | 2103 | The VCT flooring in the building is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. | TOWER #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4095
2103HVA1 | HVAC EQUIPMENT REPLACEMENT | 2103 | The HVAC unit was installed in 2002 and is not energy efficient. It has reached the end of its expected and useful life. This project would provide for the installation of a new HVAC unit and cleaning of the existing duct work and grilles. This project includes the removal and the disposal of the existing equipment and all required connections to the utilities. | TOWER #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 11375
2948PLM3 | CELL WATER CONTROL SYSTEMS REPLACEMENT | 2948 | This building is equipped with cell water control systems that are outdated and should be scheduled for replacement. Problems exist with the current water control systems. It is increasingly difficult to find replacement parts and experienced repairmen to service the equipment. It is recommended to replace the water control systems. This project includes the replacement of the water controllers, piping, valves, access panels and all connections to the existing utilities. | HOUSING UNIT #11 | 9952 | Correct | HDSP |  | Indian Springs | 2009 | 51609 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 504000
2089SFT3 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 2089 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 9000
2089HVA1 | EXHAUST FAN INSTALLATION | 2089 | The mechanical room within the housing unit has plumbing fixtures and drains. Due to moisture in this room, the humidity is very high and there is an increase probability for indoor air quality concern. This project would provide for the purchase and installation of a new commercial grade exhaust fan and the assemblies and will include the connections to utilities. | HOUSING UNIT #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 10000
2089SFT6 | ROOF HATCH REPLACEMENT | 2089 | The roof hatches are original to the building and have reached the end of their useful life. The compression spring operators do not function properly, the latches and handles are worn and the seals and flashing have deteriorated. A faulty roof hatch is a safety hazard to anyone accessing the roof. This project would provide for the removal and the disposal of the existing roof hatches and for the purchase and installation of new roof hatches. | HOUSING UNIT #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 10000
2089HVA3 | EVAPORATIVE COOLER REPLACEMENT | 2089 | There is a guard stationed on the roof to look out onto the yard. They have one overhead swamp cooler to keep them cool in the warmer months. At the time of the survey the swamp cooler was not working. It is severely scaled and has reached the end of its useful and expected life. This project would provide for a new evaporative cooler to be installed including all required connections to utilities. The estimate includes removal and disposal of the old cooler. | HOUSING UNIT #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 4000
2948SFT3 | ROOF HATCH REPLACEMENT | 2948 | The roof hatch is original to the building and has reached the end of its useful life. The compression spring operators do not function properly, the latches and handles are worn and the seals and flashing have deteriorated. A faulty roof hatch is a safety hazard to anyone accessing the roof. This project would provide for removal and disposal of the existing roof hatch and purchase and installation of a new roof hatch. | HOUSING UNIT #11 | 9952 | Correct | HDSP |  | Indian Springs | 2009 | 51609 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 5000
2948SEC1 | COMMUNICATIONS SYSTEM UPGRADE | 2948 | This building is equipped with a communications system that at the time of the survey was not working properly. The communications system provides paging, phone communications and communication to inmates. The communications system is an integral component of the notification and safety procedures for the inmates and staff. The system is problematic and replacement parts are no longer available. It is recommended that the communications system be upgraded. | HOUSING UNIT #11 | 9952 | Correct | HDSP |  | Indian Springs | 2009 | 51609 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 258045
2102SFT4 | EGRESS LIGHTING REPLACEMENT | 2102 | There are older emergency egress lighting units in this building. These units have a finite lifespan, and this project recommends their replacement with new egress lights, and to also provide additional lights on the main exit routes and in individual rooms as needed. | TOWER #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 1000
2506SFT2 | FIRE ALARM SYSTEM REPLACEMENT | 2506 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and due to this, the system no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | GYMNASIUM | 9952 | Correct | HDSP |  | Indian Springs | 2004 | 14620 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 116960
2089SEC3 | DOOR CONTROLS SYSTEM REPLACEMENT | 2089 | The control panel/ inmate movement and control system in the housing unit is not working properly. The cell door indicator lights on the control panel are falsely representing the actual status of the cell doors. The officer sometimes cannot tell if the cell door is open or closed. This project would replace the existing secured door control system with a programmable logic controlled system using touch screens for actuation and door status. This project would replace the existing door control system and the outdated wiring. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HOUSING UNIT #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 1438241.25
2102SFT1 | FIRE ALARM SYSTEM REPLACEMENT | 2102 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and due to this, the system no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | TOWER #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 3640
2948PLM5 | COMPUTER WATER CONTROL SYSTEM REPLACEMENT | 2948 | This building is equipped with a computer water control system that is outdated and should be scheduled for replacement. Problems exist with the current computer water control system. It is increasingly difficult to find software updates and experienced repairmen to service the equipment. This project recommends the installation of a new computer water control system for the building. This system will monitor and control the water for all fixtures throughout the building. New electronic sensors will be installed on each water control system. | HOUSING UNIT #11 | 9952 | Correct | HDSP |  | Indian Springs | 2009 | 51609 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 50000
2948PLM1 | FLOOR DRAIN REPAIR | 2948 | The floor drain in the building is clogged and water has pooled around it. The standing water will prematurely deteriorate the building components as well as create a slipping hazard. This project would provide for a licensed contractor to clear the drain and provide any necessary repairs to prevent future problems. | HOUSING UNIT #11 | 9952 | Correct | HDSP |  | Indian Springs | 2009 | 51609 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 2000
2102ENR3 | LIGHTING UPGRADE | 2102 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | TOWER #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3640
2102INT2 | FLOORING REPLACEMENT | 2102 | The VCT flooring in the tower is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. | TOWER #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4095
2102SFT2 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 2102 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | TOWER #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 9000
2948PLM4 | SHOWER WATER CONTROL SYSTEMS REPLACEMENT | 2948 | This building is equipped with shower water control systems that are outdated and should be scheduled for replacement. Problems exist with the current shower water control systems. It is increasingly difficult to find replacement parts and experienced repairmen to service the equipment. This project includes the replacement of the shower water controllers, piping, valves, access panels, shower heads and all connections to the existing utilities. | HOUSING UNIT #11 | 9952 | Correct | HDSP |  | Indian Springs | 2009 | 51609 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 15000
2089PLM2 | CELL WATER CONTROL SYSTEMS REPLACEMENT | 2089 | This building is equipped with cell water control systems that are outdated and should be scheduled for replacement. Problems exist with the current water control systems. It is increasingly difficult to find replacement parts and experienced repairmen to service the equipment. It is recommended to replace the water control systems. This project includes the replacement of the water controllers, piping, valves, access panels and all connections to the existing utilities. | HOUSING UNIT #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 504000
2104SEC1 | DOORS, LOCKS AND CONTROLS REPLACEMENT | 2104 | Tower #6 was constructed in 2002. The doors, locks and controls are original to the building and have been problematic due to age. This project would provide for installing new doors, locks and controls. Removal and disposal of the existing equipment is included in this estimate. | TOWER #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
2506PLM1 | WATER HEATER REPLACEMENT | 2506 | There is a 66 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | GYMNASIUM | 9952 | Correct | HDSP |  | Indian Springs | 2004 | 14620 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1750
2506SFT3 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 2506 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | GYMNASIUM | 9952 | Correct | HDSP |  | Indian Springs | 2004 | 14620 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 9000
2506HVA1 | HVAC EQUIPMENT REPLACEMENT | 2506 | The air handlers, fan coils and related equipment are original to the building, dating back to 2004. The equipment has consistent problems and has reached its expected life span. This project recommends replacement of the air handlers, fan coils, ventilation equipment and exhaust fans. It is recommended that this project be implemented in the next 4-5 years to avoid possible failure and emergency funding for replacement. | GYMNASIUM | 9952 | Correct | HDSP |  | Indian Springs | 2004 | 14620 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 365500
2506ENR1 | LIGHTING UPGRADE | 2506 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | GYMNASIUM | 9952 | Correct | HDSP |  | Indian Springs | 2004 | 14620 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 116960
2506INT1 | INTERIOR FINISHES | 2506 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | GYMNASIUM | 9952 | Correct | HDSP |  | Indian Springs | 2004 | 14620 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 146200
2089INT5 | SHOWER UPGRADE | 2089 | There are twelve shower stalls in the building that are showing signs of failure and should be scheduled for repair or replacement. This project would provide for twelve stainless steel shower cabinets to be installed to provide shower facilities for the housing unit. Removal and disposal of the existing materials is included in the estimate. | HOUSING UNIT #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 300000
2506INT2 | JANITORS CLOSET REPAIRS | 2506 | The mop sink in the Janitors Closet has several cracks in the concrete and is leaking. This could lead to mold growth if not addressed. This project would provide for a new fiberglass mop sink and FRP to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | GYMNASIUM | 9952 | Correct | HDSP |  | Indian Springs | 2004 | 14620 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2800
2104ENR1 | LIGHTING UPGRADE | 2104 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | TOWER #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3640
2089ADA3 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 2089 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | HOUSING UNIT #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 4000
2089HVA2 | HVAC EQUIPMENT REPLACEMENT | 2089 | The air handlers, fan coils and related equipment are original to the building, dating back to 2000. The equipment has consistent problems and has reached its expected life span. This project recommends the replacement of all air handlers, fan coils, ventilation equipment and exhaust fans. It is recommended that this project be implemented in the next 2-3 years to avoid possible failure and emergency funding for replacement. | HOUSING UNIT #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 667500
2506EXT4 | WINDOW REPLACEMENT | 2506 | The existing windows in this building are of double pane wire mesh construction. Some are broken and all are not energy efficient. This project would provide for the removal and replacement of the windows with new dual pane security rated windows. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | GYMNASIUM | 9952 | Correct | HDSP |  | Indian Springs | 2004 | 14620 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 219300
2089ELE1 | ELECTRICAL TRANSFORMER REPLACEMENT | 2089 | The 50 kVA electrical transformer that provides services to the building was damaged at the time of inspection and does not function properly. This project recommends replacing the electrical transformer. | HOUSING UNIT #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
2089PLM1 | WATER HEATER REPLACEMENT | 2089 | There are two 18 gallon electric water heaters in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, these units are showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that two new electric water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. | HOUSING UNIT #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
2089SFT2 | SPRINKLER HEAD REPLACEMENT | 2089 | The existing fire suppression sprinkler heads are an older style and are susceptible to damage and misuse by the inmates. Inmates have tied strings to the sprinkler heads and have broken them in the past. This project recommends that all of the fire sprinkler heads in all cells be removed and replaced with a new state of the art tamper-resistant sprinkler heads. | HOUSING UNIT #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 40000
2506EXT3 | ROOF REPLACEMENT | 2506 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2004. It is recommended that this building be re-roofed in the next 7-8 years to be consistent with the roofing program and the end of the warranty period. | GYMNASIUM | 9952 | Correct | HDSP |  | Indian Springs | 2004 | 14620 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 175440
2104INT2 | FLOORING REPLACEMENT | 2104 | The VCT flooring in the building is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. | TOWER #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4095
2506SFT1 | EMERGENCY EGRESS LIGHTING INSTALLATION | 2506 | There is no emergency egress lighting in the band room or in the barber/ storage room areas. This project would provide for the purchase and installation of 2 emergency egress lights in these two rooms. Connections to existing utilities is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | GYMNASIUM | 9952 | Correct | HDSP |  | Indian Springs | 2004 | 14620 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 900
2089PLM3 | SHOWER WATER CONTROL SYSTEMS REPLACEMENT | 2089 | This building is equipped with shower water control systems that are outdated and should be scheduled for replacement. Problems exist with the current shower water control systems. It is increasingly difficult to find replacement parts and experienced repairmen to service the equipment. This project includes the replacement of the shower water controllers, piping, valves, access panels, shower heads and all connections to the existing utilities. | HOUSING UNIT #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
2103ENR1 | LIGHTING UPGRADE | 2103 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | TOWER #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3640
2103SFT2 | FIRE ALARM SYSTEM REPLACEMENT | 2103 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and due to this, the system no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | TOWER #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 3640
2089ADA4 | ADA SHOWER UPGRADE | 2089 | This project would provide for three ADA compliant stainless steel shower cabinets to be installed to provide shower facilities for the disabled. Included in this estimate is the installation of three stainless steel ADA compliant shower cabinet units complete with accessible plumbing fixtures, seats, etc. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | HOUSING UNIT #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 75000
2103ENV1 | PEST CONTROL | 2103 | There are numerous bird and rodent droppings throughout this building. Due to the potential risk of disease, this project provides for treatment and cleanup of the pigeon and rodent droppings by a licensed pest control business. | TOWER #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
2104EXT3 | ROOF REPLACEMENT | 2104 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2002. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. | TOWER #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5460
2104EXT1 | EXTERIOR FINISHES | 2104 | It is important to maintain the finish, weather resistance and appearance of the building. The caulked joints in the concrete panels, form much of the exterior surface of this building, and are uniformly deteriorated. The caulking should be removed and the joints should be re-caulked. The metal doors and window frames should be sanded and painted on a cyclical basis. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | TOWER #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4550
2104HVA1 | HVAC EQUIPMENT REPLACEMENT | 2104 | The HVAC unit was installed in 2002 and is not energy efficient. It has reached the end of its expected and useful life. This project would provide for the installation of a new HVAC unit and cleaning of the existing duct work and grilles. This project includes the removal and the disposal of the existing equipment and all required connections to the utilities. | TOWER #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 11375
2104EXT2 | WINDOW REPLACEMENT | 2104 | The existing windows in this building are of single pane wire mesh construction. They are not energy efficient. This project would provide for the removal and replacement of the windows with new dual pane security rated windows. | TOWER #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 33600
2172SFT5 | ELECTRICAL OUTLET & CABLE UPGRADES | 2172 | At the time of the survey the building had residential and commercial cover plates over the electrical outlets and coaxial wires. This poses a safety hazard allowing inmates to remove them and use them as weapons. This could be a safety hazard to inmates and guards. This project would provide for the installation of new security grade cover plates throughout the entire housing unit. | HOUSING UNIT #8 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 74592
2104SFT4 | BACKFLOW PREVENTER REPLACEMENT | 2104 | There is a backflow preventer for the fire suppression system in the building. It is leaking and should be scheduled for replacement. At the time of the survey the staff indicated they have rebuilt the backflow preventer several times, however it continues to leak. This project would provide for replacing the backflow preventer by a licensed fire suppression contractor. | TOWER #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 5000
2172HVA1 | EXHAUST FAN INSTALLATION | 2172 | The mechanical room within the housing unit has plumbing fixtures and drains. Due to moisture in this room, the humidity is very high and there is an increase probability for indoor air quality concern. This project would provide for the purchase and installation of a new commercial grade exhaust fan and the assemblies and will include the connections to utilities. | HOUSING UNIT #8 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 10000
2104SFT2 | FIRE ALARM SYSTEM REPLACEMENT | 2104 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and due to this, the system no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | TOWER #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 3640
2104SFT5 | EGRESS LIGHTING REPLACEMENT | 2104 | There are older emergency egress lighting units in this building. These units have a finite lifespan, and this project recommends their replacement with new egress lights, and to also provide additional lights on the main exit routes and in individual rooms as needed. | TOWER #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 1000
2089INT3 | JANITORS CLOSET REPAIRS | 2089 | The mop sink in the Janitors Closet is mounted adjacent to CMU and is showing signs of water damage. This project would provide FRP to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | HOUSING UNIT #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
2104INT1 | INTERIOR FINISHES | 2104 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and adequately prepared to receive the coating. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | TOWER #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4550
2175HVA1 | EXHAUST FAN INSTALLATION | 2175 | The mechanical room within the housing unit has plumbing fixtures and drains. Due to moisture in this room, the humidity is very high and there is an increase probability for indoor air quality concern. This project would provide for the purchase and installation of a new commercial grade exhaust fan and the assemblies and will include the connections to utilities. | HOUSING UNIT #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 10000
2177ENR1 | LIGHTING UPGRADE | 2177 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | TOWER #4 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3640
2176SFT2 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 2176 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | YARD TOWER | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 9000
2176ENR1 | INSULATE BUILDING | 2176 | The tower walls are structural steel with metal siding. The condenser for the cooling system is located inside on the middle level of the tower. During the summer months, the metal siding radiates heat and causes the cooling unit to trip off due to extreme temperatures. This project would provide for 4" thick foil faced rigid insulation to be installed on the inside of the guard tower to help minimize the heat gain on the interior of the guard tower. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | YARD TOWER | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
2176INT1 | INTERIOR FINISHES | 2176 | It is recommended to paint the interior walls and ceilings at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | YARD TOWER | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 4550
2176ENR2 | CONDENSER DUCTING | 2176 | The condensing unit located on the middle level of the tower is missing the duct from the outside air intake louver to the condensing unit. This may be a cause for the overheating of the unit. This project would provide for replacing this missing duct and associated connections. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | YARD TOWER | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
2176EXT1 | EXTERIOR FINISHES | 2176 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming, painting the metal panels and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended to paint the building in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | YARD TOWER | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 4550
2175SFT3 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 2175 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 9000
2176HVA1 | HVAC EQUIPMENT REPLACEMENT | 2176 | The HVAC unit was installed in 2000 and is not energy efficient. It has reached the end of its expected and useful life. This project would provide for the installation of a new HVAC unit and cleaning of the existing duct work and grilles. This project includes the removal and the disposal of the existing equipment and all required connections to the utilities. | YARD TOWER | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11375
2175ENR1 | LIGHTING UPGRADE | 2175 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | HOUSING UNIT #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 356000
2176SFT4 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 2176 | The building does not currently have exit signs and emergency egress lighting is insufficient. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC 2012 Chapter 10 was referenced for this project. | YARD TOWER | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 455
2175SFT1 | FIRE ALARM SYSTEM REPLACEMENT | 2175 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and due to this, the system no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | HOUSING UNIT #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 356000
2175ADA2 | TDD INSTALLATION | 2175 | The Housing Unit is not equipped with a TDD. In order to comply with ADA requirements it is recommended to install a TDD system in the Housing Unit. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | HOUSING UNIT #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 60000
2175SEC1 | COMMUNICATIONS SYSTEM UPGRADE | 2175 | This building is equipped with a communications system that at the time of the survey was not working properly. The communications system provides paging, phone communications and communication to inmates. The communications system is an integral component of the notification and safety procedures for the inmates and staff. The system is problematic and replacement parts are no longer available. It is recommended that the communications system be upgraded. | HOUSING UNIT #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 222500
2175ADA5 | ADA TABLE UPGRADE | 2175 | Per the United States Access Board and ICC ANSI-A117.1-2009, at least 5 percent of the seating spaces shall be, if fixed seating is provided, a loose seat or open space for a wheelchair. This project would provide funding to remove 3 of the fixed seats, which will allow access for wheel chairs. | HOUSING UNIT #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 3000
2175ADA4 | ADA SHOWER UPGRADE | 2175 | This project would provide for three ADA compliant stainless steel shower cabinets to be installed to provide shower facilities for the disabled. Included in this estimate is the installation of three stainless steel ADA compliant shower cabinet units complete with accessible plumbing fixtures, seats, etc. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | HOUSING UNIT #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 75000
2175SFT5 | ROOF HATCH REPLACEMENT | 2175 | The roof hatches are original to the building and have reached the end of their useful life. The compression spring operators do not function properly, the latches and handles are worn and the seals and flashing have deteriorated. A faulty roof hatch is a safety hazard to anyone accessing the roof. This project would provide for the removal and the disposal of the existing roof hatches and for the purchase and installation of new roof hatches. | HOUSING UNIT #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 10000
2175ADA3 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 2175 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | HOUSING UNIT #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 4000
2175INT2 | SHOWER UPGRADE | 2175 | There are twelve shower stalls in the building that are showing signs of failure and should be scheduled for repair or replacement. This project would provide for twelve stainless steel shower cabinets to be installed to provide shower facilities for the housing units. Removal and disposal of the existing materials is included in the estimate. | HOUSING UNIT #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 300000
2175SFT2 | SPRINKLER HEAD REPLACEMENT | 2175 | The existing fire suppression sprinkler heads are an older style and are susceptible to damage and misuse by the inmates. Inmates have tied strings to the sprinkler heads and have broken them in the past. This project recommends that all of the fire sprinkler heads in all cells be removed and replaced with a new state of the art tamper-resistant sprinkler heads. | HOUSING UNIT #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 40000
2177INT1 | INTERIOR FINISHES | 2177 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and adequately prepared to receive the coating. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | TOWER #4 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 4550
2172HVA2 | HVAC EQUIPMENT REPLACEMENT | 2172 | The air handlers, fan coils and related equipment are original to the building, dating back to 2002. The equipment has consistent problems and has reached its expected life span. This project recommends the replacement of all air handlers, fan coils, ventilation equipment and exhaust fans. It is recommended that this project be implemented in the next 4-5 years to avoid possible failure and emergency funding for replacement. | HOUSING UNIT #8 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 667500
2177SFT3 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 2177 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | TOWER #4 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 9000
2177SFT5 | EGRESS LIGHTING REPLACEMENT | 2177 | There are older emergency egress lighting units in this building. These units have a finite lifespan, and this project recommends their replacement with new egress lights, and to also provide additional lights on the main exit routes as needed. | TOWER #4 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
2177EXT2 | WINDOW REPLACEMENT | 2177 | The existing windows in this building are of single pane wire mesh construction. They are not energy efficient. This project would provide for the removal and replacement of the windows with new dual pane security rated windows. | TOWER #4 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 33600
2177SFT4 | BACKFLOW PREVENTER REPLACEMENT | 2177 | There is a backflow preventer for the fire suppression system in the building. It is leaking and should be scheduled for replacement. At the time of the survey the staff indicated they have rebuilt the backflow preventer several times, however it continues to leak. This project would provide for replacing the backflow preventer by a licensed fire suppression contractor. | TOWER #4 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 5000
2177PLM1 | WATER HEATER REPLACEMENT | 2177 | There is an on-demand electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new on-demand electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | TOWER #4 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
2177SEC1 | DOORS, LOCKS AND CONTROLS REPLACEMENT | 2177 | Tower #4 was constructed in 2002. The doors, locks and controls are original to the building and have been problematic due to age. This project would provide for installing new doors, locks and controls. Removal and disposal of the existing equipment is included in this estimate. | TOWER #4 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
2176ENR3 | LIGHTING UPGRADE | 2176 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | YARD TOWER | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3640
2177EXT1 | EXTERIOR FINISHES | 2177 | It is important to maintain the finish, weather resistance and appearance of the building. The caulked joints in the concrete panels form much of the exterior surface of this building, and are uniformly deteriorated. The caulking should be removed and the joints should be re-caulked. The metal doors and window frames should be sanded and painted on a cyclical basis. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | TOWER #4 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 4550
2175HVA3 | EVAPORATIVE COOLER REPLACEMENT | 2175 | There is a guard stationed on the roof to look out onto the yard. They have one overhead swamp cooler to keep them cool in the warmer months. At the time of the survey the swamp cooler was not working. It is severely scaled and has reached the end of its useful and expected life. This project would provide for a new evaporative cooler to be installed including all required connections to utilities. The estimate includes removal and disposal of the old cooler. | HOUSING UNIT #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 4000
2176INT2 | FLOORING REPLACEMENT | 2176 | The VCT flooring in the tower is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. | YARD TOWER | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4095
2176PLM2 | BACKFLOW PREVENTER REPLACEMENT | 2176 | There is a backflow preventer for the fire suppression system in the building. It is leaking and should be scheduled for replacement. At the time of the survey the staff indicated they have rebuilt the backflow preventer several times, however it continues to leak. This project would provide for replacing the backflow preventer by a licensed fire suppression contractor. | YARD TOWER | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
2176EXT3 | SLIDING GLASS DOOR REPLACEMENT | 2176 | The sliding glass door is damaged from age and general wear and tear and has reached the end of its expected life. This project would provide for the replacement of the sliding glass door assembly with a new door, frame and hardware. Removal and disposal of the existing door is included in this estimate. | YARD TOWER | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 2500
2176SEC1 | DOORS, LOCKS AND CONTROLS REPLACEMENT | 2176 | Yard Tower was constructed in 2000. The doors, locks and controls are original to the building and have been problematic due to age. This project would provide for installing new doors, locks and controls. Removal and disposal of the existing equipment is included in this estimate. | YARD TOWER | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
2176EXT2 | WINDOW REPLACEMENT | 2176 | The existing windows in this building are of single pane wire mesh construction. They are not energy efficient. This project would provide for the removal and replacement of the windows with new dual pane security rated windows. | YARD TOWER | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 19200
2176SFT1 | FIRE ALARM SYSTEM REPLACEMENT | 2176 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and due to this, the system no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | YARD TOWER | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 3640
2176ENV1 | PEST CONTROL | 2176 | There are numerous bird and rodent droppings throughout this building. Due to the potential risk of disease, this project provides for treatment and cleanup of the pigeon and rodent droppings by a licensed pest control business. | YARD TOWER | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
2176PLM1 | WATER HEATER REPLACEMENT | 2176 | There is an on-demand electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new on-demand electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | YARD TOWER | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
2177HVA1 | HVAC EQUIPMENT REPLACEMENT | 2177 | The HVAC unit was installed in 2002 and is not energy efficient. It has reached the end of its expected and useful life. This project would provide for the installation of a new HVAC unit and cleaning of the existing duct work and grilles. This project includes the removal and the disposal of the existing equipment and all required connections to the utilities. | TOWER #4 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 11375
2174SFT4 | ELECTRICAL OUTLET & CABLE UPGRADES | 2174 | At the time of the survey the building had residential and commercial cover plates over the electrical outlets and coaxial wires. This poses a safety hazard allowing inmates to remove them and use them as weapons. This could be a safety hazard to inmates and guards. This project would provide for the installation of new security grade cover plates throughout the entire housing unit. | HOUSING UNIT #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 74592
2174ADA3 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 2174 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | HOUSING UNIT #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 4000
2174SFT1 | SPRINKLER HEAD REPLACEMENT | 2174 | The existing fire suppression sprinkler heads are an older style and are susceptible to damage and misuse by the inmates. Inmates have tied strings to the sprinkler heads and have broken them in the past. This project recommends that all of the fire sprinkler heads in all cells be removed and replaced with a new state of the art tamper-resistant sprinkler heads. | HOUSING UNIT #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 40000
2174PLM1 | WATER HEATER REPLACEMENT | 2174 | There are two 18 gallon electric water heaters in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, these units are showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that two new electric water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. | HOUSING UNIT #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
2174ADA2 | TDD INSTALLATION | 2174 | The Housing Unit is not equipped with a TDD. In order to comply with ADA requirements it is recommended to install a TDD system in the Housing Unit. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | HOUSING UNIT #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 60000
2174SEC3 | DOOR CONTROLS SYSTEM REPLACEMENT | 2174 | The control panel/ inmate movement and control system in the housing unit is not working properly. The cell door indicator lights on the control panel are falsely representing the actual status of the cell doors. The officer sometimes cannot tell if the cell door is open or closed. This project would replace the existing secured door control system with a programmable logic controlled system using touch screens for actuation and door status. This project would replace the existing door control system and the outdated wiring. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HOUSING UNIT #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1438241.25
2174INT2 | SHOWER UPGRADE | 2174 | There are twelve shower stalls in the building that are showing signs of failure and should be scheduled for repair or replacement. This project would provide for twelve stainless steel shower cabinets to be installed to provide shower facilities for the housing units. Removal and disposal of the existing materials is included in the estimate. | HOUSING UNIT #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 300000
2174SEC2 | CELL DOORS, LOCKS AND CONTROLS REPLACEMENT | 2174 | The Housing Unit was constructed in 2002. The cell doors, locks and controls are original to the building and have been problematic due to inmate abuse and age. This project would provide for installing new cell doors, locks and controls. Removal and disposal of the existing equipment is included in this estimate. | HOUSING UNIT #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 421875
2175EXT2 | ROOF REPLACEMENT | 2175 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2002. It is recommended that this building be re-roofed in the next 4-5 years to be consistent with the roofing program and the end of the warranty period. | HOUSING UNIT #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 667500
2174HVA2 | HVAC EQUIPMENT REPLACEMENT | 2174 | The air handlers, fan coils and related equipment are original to the building, dating back to 2002. The equipment has consistent problems and has reached its expected life span. This project recommends the replacement of all air handlers, fan coils, ventilation equipment and exhaust fans. It is recommended that this project be implemented in the next 4-5 years to avoid possible failure and emergency funding for replacement. | HOUSING UNIT #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 667500
2174ENR1 | LIGHTING UPGRADE | 2174 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | HOUSING UNIT #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 356000
2174ADA4 | ADA SHOWER UPGRADE | 2174 | This project would provide for three ADA compliant stainless steel shower cabinets to be installed to provide shower facilities for the disabled. Included in this estimate is the installation of three stainless steel ADA compliant shower cabinet units complete with accessible plumbing fixtures, seats, etc. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | HOUSING UNIT #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 75000
2174SFT5 | ROOF HATCH REPLACEMENT | 2174 | The roof hatches are original to the building and have reached the end of their useful life. The compression spring operators do not function properly, the latches and handles are worn and the seals and flashing have deteriorated. A faulty roof hatch is a safety hazard to anyone accessing the roof. This project would provide for the removal and the disposal of the existing roof hatches and for the purchase and installation of new roof hatches. | HOUSING UNIT #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 10000
2174SEC1 | COMMUNICATIONS SYSTEM UPGRADE | 2174 | This building is equipped with a communications system that at the time of the survey was not working properly. The communications system provides paging, phone communications and communication to inmates. The communications system is an integral component of the notification and safety procedures for the inmates and staff. The system is problematic and replacement parts are no longer available. It is recommended that the communications system be upgraded. | HOUSING UNIT #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 222500
2174HVA3 | EVAPORATIVE COOLER REPLACEMENT | 2174 | There is a guard stationed on the roof to look out onto the yard. They have one overhead swamp cooler to keep them cool in the warmer months. At the time of the survey the swamp cooler was not working. It is severely scaled and has reached the end of its useful and expected life. This project would provide for a new evaporative cooler to be installed including all required connections to utilities. The estimate includes removal and disposal of the old cooler. | HOUSING UNIT #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 4000
2174ADA1 | ADA TABLE UPGRADE | 2174 | Per the United States Access Board and ICC ANSI-A117.1-2009, at least 5 percent of the seating spaces shall be, if fixed seating is provided, a loose seat or open space for a wheelchair. This project would provide funding to remove 3 of the fixed seats, which will allow access for wheel chairs. | HOUSING UNIT #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 3000
2174EXT2 | ROOF REPLACEMENT | 2174 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2002. It is recommended that this building be re-roofed in the next 4-5 years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HOUSING UNIT #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 667500
2174INT1 | INTERIOR FINISHES | 2174 | This project would provide funding to maintain the interior of the building. Included in the cost is painting the walls and ceilings, sealing the exposed masonry, repairing cracks in the masonry and replacing grout and caulk as needed. An epoxy-based paint should be utilized in wet areas for durability. It is recommended that the interior of the building be painted, sealed and repaired in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HOUSING UNIT #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 445000
2174STR1 | WALKWAY RAILING | 2174 | The perimeter roof walkway guardrail is failing. The railing is loose or not attached and is posing a potential safety problem. This project recommends an assessment be performed by a Structural Engineer to determine the cause and provide a design solution. Future projects will be based on the design solution recommendation. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HOUSING UNIT #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 3000
2174ELE1 | ELECTRICAL TRANSFORMER REPLACEMENT | 2174 | The 50 kVA electrical transformer that provides services to the building was damaged at the time of inspection and does not function properly. This project recommends replacing the electrical transformer. | HOUSING UNIT #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
2175STR1 | WALKWAY RAILING | 2175 | The perimeter roof walkway guardrail is failing. The railing is loose or not attached and is posing a potential safety problem. This project recommends an assessment be performed by a Structural Engineer to determine the cause and provide a design solution. Future projects will be based on the design solution recommendation. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HOUSING UNIT #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 3000
2177SFT2 | FIRE ALARM SYSTEM REPLACEMENT | 2177 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and due to this, the system no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | TOWER #4 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 3640
2175INT3 | JANITORS CLOSET REPAIRS | 2175 | The mop sink in the Janitors Closet is mounted adjacent to CMU and is showing signs of water damage. This project would provide FRP to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | HOUSING UNIT #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
2175SEC2 | CELL DOORS, LOCKS AND CONTROLS REPLACEMENT | 2175 | The Housing Unit was constructed in 2002. The cell doors, locks and controls are original to the building and have been problematic due to inmate abuse and age. This project would provide for installing new cell doors, locks and controls. Removal and disposal of the existing equipment is included in this estimate. | HOUSING UNIT #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 421875
2175SFT4 | ELECTRICAL OUTLET & CABLE UPGRADES | 2175 | At the time of the survey the building had residential and commercial cover plates over the electrical outlets and coaxial wires. This poses a safety hazard allowing inmates to remove them and use them as weapons. This could be a safety hazard to inmates and guards. This project would provide for the installation of new security grade cover plates throughout the entire housing unit. | HOUSING UNIT #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 74592
2175HVA2 | HVAC EQUIPMENT REPLACEMENT | 2175 | The air handlers, fan coils and related equipment are original to the building, dating back to 2002. The equipment has consistent problems and has reached its expected life span. This project recommends the replacement of all air handlers, fan coils, ventilation equipment and exhaust fans. It is recommended that this project be implemented in the next 4-5 years to avoid possible failure and emergency funding for replacement. | HOUSING UNIT #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 667500
2175PLM2 | CELL WATER CONTROL SYSTEMS REPLACEMENT | 2175 | This building is equipped with cell water control systems that are outdated and should be scheduled for replacement. Problems exist with the current water control systems. It is increasingly difficult to find replacement parts and experienced repairmen to service the equipment. It is recommended to replace the water control systems. This project includes the replacement of the water controllers, piping, valves, access panels and all connections to the existing utilities. | HOUSING UNIT #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 504000
2175PLM1 | WATER HEATER REPLACEMENT | 2175 | There are two 18 gallon electric water heaters in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, these units are showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that two new electric water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. | HOUSING UNIT #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
2175PLM4 | COMPUTER WATER CONTROL SYSTEM REPLACEMENT | 2175 | This building is equipped with a computer water control system that is outdated and should be scheduled for replacement. Problems exist with the current computer water control system. It is increasingly difficult to find software updates and experienced repairmen to service the equipment. This project recommends the installation of a new computer water control system for the building. This system will monitor and control the water for all fixtures throughout the building. New electronic sensors will be installed on each water control system. | HOUSING UNIT #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
2174INT3 | JANITORS CLOSET REPAIRS | 2174 | The mop sink in the Janitors Closet is mounted adjacent to CMU and is showing signs of water damage. This project would provide FRP to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | HOUSING UNIT #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
2175SEC3 | DOOR CONTROLS SYSTEM REPLACEMENT | 2175 | The control panel/ inmate movement and control system in the housing unit is not working properly. The cell door indicator lights on the control panel are falsely representing the actual status of the cell doors. The officer sometimes cannot tell if the cell door is open or closed. This project would replace the existing secured door control system with a programmable logic controlled system using touch screens for actuation and door status. This project would replace the existing door control system and the outdated wiring. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HOUSING UNIT #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1438241.25
2174SFT3 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 2174 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 9000
2175EXT1 | EXTERIOR FINISHES | 2175 | It is important to maintain the finish, weather resistance and appearance of the building. The caulked control joints in the CMU of the exterior surface of this building are uniformly deteriorated and should be removed and the joints re-caulked. The metal doors and window frames should be sanded and painted on a cyclical basis. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HOUSING UNIT #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 445000
2175INT1 | INTERIOR FINISHES | 2175 | This project would provide funding to maintain the interior of the building. Included in the cost is painting the walls and ceilings, sealing the exposed masonry, repairing cracks in the masonry and replacing grout and caulk as needed. An epoxy-based paint should be utilized in wet areas for durability. It is recommended that the interior of the building be painted, sealed and repaired in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HOUSING UNIT #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 445000
2174PLM4 | COMPUTER WATER CONTROL SYSTEM REPLACEMENT | 2174 | This building is equipped with a computer water control system that is outdated and should be scheduled for replacement. Problems exist with the current computer water control system. It is increasingly difficult to find software updates and experienced repairmen to service the equipment. This project recommends the installation of a new computer water control system for the building. This system will monitor and control the water for all fixtures throughout the building. New electronic sensors will be installed on each water control system. | HOUSING UNIT #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
2174PLM3 | SHOWER WATER CONTROL SYSTEMS REPLACEMENT | 2174 | This building is equipped with shower water control systems that are outdated and should be scheduled for replacement. Problems exist with the current shower water control systems. It is increasingly difficult to find replacement parts and experienced repairmen to service the equipment. This project includes the replacement of the shower water controllers, piping, valves, access panels, shower heads and all connections to the existing utilities. | HOUSING UNIT #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
2174PLM2 | CELL WATER CONTROL SYSTEMS REPLACEMENT | 2174 | This building is equipped with cell water control systems that are outdated and should be scheduled for replacement. Problems exist with the current water control systems. It is increasingly difficult to find replacement parts and experienced repairmen to service the equipment. It is recommended to replace the water control systems. This project includes the replacement of the water controllers, piping, valves, access panels and all connections to the existing utilities. | HOUSING UNIT #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 504000
2174SFT2 | FIRE ALARM SYSTEM REPLACEMENT | 2174 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and due to this, the system no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | HOUSING UNIT #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 356000
2174HVA1 | EXHAUST FAN INSTALLATION | 2174 | The mechanical room within the housing unit has plumbing fixtures and drains. Due to moisture in this room, the humidity is very high and there is an increase probability for indoor air quality concern. This project would provide for the purchase and installation of a new commercial grade exhaust fan and the assemblies and will include the connections to utilities. | HOUSING UNIT #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 10000
2175PLM3 | SHOWER WATER CONTROL SYSTEMS REPLACEMENT | 2175 | This building is equipped with shower water control systems that are outdated and should be scheduled for replacement. Problems exist with the current shower water control systems. It is increasingly difficult to find replacement parts and experienced repairmen to service the equipment. This project includes the replacement of the shower water controllers, piping, valves, access panels, shower heads and all connections to the existing utilities. | HOUSING UNIT #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
2175ELE1 | ELECTRICAL TRANSFORMER REPLACEMENT | 2175 | The 50 kVA electrical transformer that provides services to the building was damaged at the time of inspection and does not function properly. This project recommends replacing the electrical transformer. | HOUSING UNIT #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
2173SEC2 | CELL DOORS, LOCKS AND CONTROLS REPLACEMENT | 2173 | The Housing Unit was constructed in 2002. The cell doors, locks and controls are original to the building and have been problematic due to inmate abuse and age. This project would provide for installing new cell doors, locks and controls. Removal and disposal of the existing equipment is included in this estimate. | HOUSING UNIT #7 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 421875
2177INT2 | FLOORING REPLACEMENT | 2177 | The VCT flooring in Tower #4 is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. | TOWER #4 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4095
2173SFT2 | FIRE ALARM SYSTEM REPLACEMENT | 2173 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and due to this, the system no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | HOUSING UNIT #7 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 356000
2173SFT6 | ROOF HATCH REPLACEMENT | 2173 | The roof hatches are original to the building and have reached the end of their useful life. The compression spring operators do not function properly, the latches and handles are worn and the seals and flashing have deteriorated. A faulty roof hatch is a safety hazard to anyone accessing the roof. This project would provide for the removal and the disposal of the existing roof hatches and for the purchase and installation of new roof hatches. | HOUSING UNIT #7 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 10000
2173SFT4 | ELECTRICAL OUTLET & CABLE UPGRADES | 2173 | At the time of the survey the building had residential and commercial cover plates over the electrical outlets and coaxial wires. This poses a safety hazard allowing inmates to remove them and use them as weapons. This could be a safety hazard to inmates and guards. This project would provide for the installation of new security grade cover plates throughout the entire housing unit. | HOUSING UNIT #7 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 74592
2173PLM2 | CELL WATER CONTROL SYSTEMS REPLACEMENT | 2173 | This building is equipped with cell water control systems that are outdated and should be scheduled for replacement. Problems exist with the current water control systems. It is increasingly difficult to find replacement parts and experienced repairmen to service the equipment. It is recommended to replace the water control systems. This project includes the replacement of the water controllers, piping, valves, access panels and all connections to the existing utilities. | HOUSING UNIT #7 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 504000
2173HVA3 | EVAPORATIVE COOLER REPLACEMENT | 2173 | There is a guard stationed on the roof to look out onto the yard. They have one overhead swamp cooler to keep them cool in the warmer months. At the time of the survey the swamp cooler was not working. It is severely scaled and has reached the end of its useful and expected life. This project would provide for a new evaporative cooler to be installed including all required connections to utilities. The estimate includes removal and disposal of the old cooler. | HOUSING UNIT #7 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 4000
2173PLM3 | SHOWER WATER CONTROL SYSTEMS REPLACEMENT | 2173 | This building is equipped with shower water control systems that are outdated and should be scheduled for replacement. Problems exist with the current shower water control systems. It is increasingly difficult to find replacement parts and experienced repairmen to service the equipment. This project includes the replacement of the shower water controllers, piping, valves, access panels, shower heads and all connections to the existing utilities. | HOUSING UNIT #7 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
2173EXT1 | EXTERIOR FINISHES | 2173 | It is important to maintain the finish, weather resistance and appearance of the building. The caulked control joints in the CMU of the exterior surface of this building are uniformly deteriorated and should be removed and the joints re-caulked. The metal doors and window frames should be sanded and painted on a cyclical basis. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HOUSING UNIT #7 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 445000
2090SFT3 | FIRE ALARM SYSTEM REPLACEMENT | 2090 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and due to this, the system no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | INFIRMARY/ INTAKE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 32986 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 263888
2173EXT2 | ROOF REPLACEMENT | 2173 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2002. It is recommended that this building be re-roofed in the next 4-5 years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HOUSING UNIT #7 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 667500
2173PLM4 | COMPUTER WATER CONTROL SYSTEM REPLACEMENT | 2173 | This building is equipped with a computer water control system that is outdated and should be scheduled for replacement. Problems exist with the current computer water control system. It is increasingly difficult to find software updates and experienced repairmen to service the equipment. This project recommends the installation of a new computer water control system for the building. This system will monitor and control the water for all fixtures throughout the building. New electronic sensors will be installed on each water control system. | HOUSING UNIT #7 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
2173ELE1 | ELECTRICAL TRANSFORMER REPLACEMENT | 2173 | The 50 kVA electrical transformer that provides services to the building was damaged at the time of inspection and does not function properly. This project recommends replacing the electrical transformer. | HOUSING UNIT #7 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
2173ADA4 | ADA SHOWER UPGRADE | 2173 | This project would provide for three ADA compliant stainless steel shower cabinets to be installed to provide shower facilities for the disabled. Included in this estimate is the installation of three stainless steel ADA compliant shower cabinet units complete with accessible plumbing fixtures, seats, etc. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | HOUSING UNIT #7 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 75000
2173PLM1 | WATER HEATER REPLACEMENT | 2173 | There are two 18 gallon electric water heaters in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, these units are showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that two new electric water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. | HOUSING UNIT #7 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
2173ADA3 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 2173 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | HOUSING UNIT #7 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 4000
2173INT3 | JANITORS CLOSET REPAIRS | 2173 | The mop sink in the Janitors Closet is mounted adjacent to CMU and is showing signs of water damage. This project would provide FRP to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | HOUSING UNIT #7 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
2173SFT3 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 2173 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT #7 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 9000
2173INT2 | SHOWER UPGRADE | 2173 | There are twelve shower stalls in the building that are showing signs of failure and should be scheduled for repair or replacement. This project would provide for twelve stainless steel shower cabinets to be installed to provide shower facilities for the housing units. Removal and disposal of the existing materials is included in the estimate. | HOUSING UNIT #7 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 300000
2173SEC3 | DOOR CONTROLS SYSTEM REPLACEMENT | 2173 | The control panel/ inmate movement and control system in the housing unit is not working properly. The cell door indicator lights on the control panel are falsely representing the actual status of the cell doors. The officer sometimes cannot tell if the cell door is open or closed. This project would replace the existing secured door control system with a programmable logic controlled system using touch screens for actuation and door status. This project would replace the existing door control system and the outdated wiring. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HOUSING UNIT #7 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1438241.25
2172ELE1 | ELECTRICAL TRANSFORMER REPLACEMENT | 2172 | The 50 kVA electrical transformer that provides services to the building was damaged at the time of inspection and does not function properly. This project recommends replacing the electrical transformer. | HOUSING UNIT #8 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
2172ENR1 | LIGHTING UPGRADE | 2172 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | HOUSING UNIT #8 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 356000
2172PLM3 | SHOWER WATER CONTROL SYSTEMS REPLACEMENT | 2172 | This building is equipped with shower water control systems that are outdated and should be scheduled for replacement. Problems exist with the current shower water control systems. It is increasingly difficult to find replacement parts and experienced repairmen to service the equipment. This project includes the replacement of the shower water controllers, piping, valves, access panels, shower heads and all connections to the existing utilities. | HOUSING UNIT #8 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
2172INT3 | JANITORS CLOSET REPAIRS | 2172 | The mop sink in the Janitors Closet is mounted adjacent to CMU and is showing signs of water damage. This project would provide FRP to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | HOUSING UNIT #8 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
2172ADA3 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 2172 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | HOUSING UNIT #8 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 4000
2172PLM4 | COMPUTER WATER CONTROL SYSTEM REPLACEMENT | 2172 | This building is equipped with a computer water control system that is outdated and should be scheduled for replacement. Problems exist with the current computer water control system. It is increasingly difficult to find software updates and experienced repairmen to service the equipment. This project recommends the installation of a new computer water control system for the building. This system will monitor and control the water for all fixtures throughout the building. New electronic sensors will be installed on each water control system. | HOUSING UNIT #8 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
2172INT2 | SHOWER UPGRADE | 2172 | There are twelve shower stalls in the building that are showing signs of failure and should be scheduled for repair or replacement. This project would provide for twelve stainless steel shower cabinets to be installed to provide shower facilities for the housing units. Removal and disposal of the existing materials is included in the estimate. | HOUSING UNIT #8 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 300000
2172ADA4 | ADA SHOWER UPGRADE | 2172 | This project would provide for three ADA compliant stainless steel shower cabinets to be installed to provide shower facilities for the disabled. Included in this estimate is the installation of three stainless steel ADA compliant shower cabinet units complete with accessible plumbing fixtures, seats, etc. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | HOUSING UNIT #8 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 75000
2173STR1 | WALKWAY RAILING | 2173 | The perimeter roof walkway guardrail is failing. The railing is loose or not attached and is posing a potential safety problem. This project recommends an assessment be performed by a Structural Engineer to determine the cause and provide a design solution. Future projects will be based on the design solution recommendation. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HOUSING UNIT #7 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 3000
2089PLM4 | COMPUTER WATER CONTROL SYSTEM REPLACEMENT | 2089 | This building is equipped with a computer water control system that is outdated and should be scheduled for replacement. Problems exist with the current computer water control system. It is increasingly difficult to find software updates and experienced repairmen to service the equipment. This project recommends the installation of a new computer water control system for the building. This system will monitor and control the water for all fixtures throughout the building. New electronic sensors will be installed on each water control system. | HOUSING UNIT #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
2946ADA1 | ADA TABLE UPGRADE | 2946 | Per the United States Access Board and ICC ANSI-A117.1-2009, at least 5 percent of the seating spaces shall be, if fixed seating is provided, a loose seat or open space for a wheelchair. This project would provide funding to remove 3 of the fixed seats, which will allow access for wheel chairs. | HOUSING UNIT #12 | 9952 | Correct | HDSP |  | Indian Springs | 2008 | 52096 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 3000
2089SFT5 | ELECTRICAL OUTLET & CABLE UPGRADES | 2089 | At the time of the survey the building had residential and commercial cover plates over the electrical outlets and coaxial wires. This poses a safety hazard allowing inmates to remove them and use them as weapons. This could be a safety hazard to inmates and guards. This project would provide for the installation of new security grade cover plates throughout the entire housing unit. | HOUSING UNIT #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 74592
2172HVA3 | EVAPORATIVE COOLER REPLACEMENT | 2172 | There is a guard stationed on the roof to look out onto the yard. They have one overhead swamp cooler to keep them cool in the warmer months. At the time of the survey the swamp cooler was not working. It is severely scaled and has reached the end of its useful and expected life. This project would provide for a new evaporative cooler to be installed including all required connections to utilities. The estimate includes removal and disposal of the old cooler. | HOUSING UNIT #8 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 4000
2172SFT4 | FIRE ALARM SYSTEM REPLACEMENT | 2172 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and due to this, the system no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | HOUSING UNIT #8 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 356000
2172SFT2 | SPRINKLER HEAD REPLACEMENT | 2172 | The existing fire suppression sprinkler heads are an older style and are susceptible to damage and misuse by the inmates. Inmates have tied strings to the sprinkler heads and have broken them in the past. This project recommends that all of the fire sprinkler heads in all cells be removed and replaced with a new state of the art tamper-resistant sprinkler heads. | HOUSING UNIT #8 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 40000
2172SFT6 | ROOF HATCH REPLACEMENT | 2172 | The roof hatches are original to the building and have reached the end of their useful life. The compression spring operators do not function properly, the latches and handles are worn and the seals and flashing have deteriorated. A faulty roof hatch is a safety hazard to anyone accessing the roof. This project would provide for the removal and the disposal of the existing roof hatches and for the purchase and installation of new roof hatches. | HOUSING UNIT #8 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 10000
2172PLM1 | WATER HEATER REPLACEMENT | 2172 | There are two 18 gallon electric water heaters in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, these units are showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that two new electric water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. | HOUSING UNIT #8 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
2172SEC2 | CELL DOORS, LOCKS AND CONTROLS REPLACEMENT | 2172 | The Housing Unit was constructed in 2002. The cell doors, locks and controls are original to the building and have been problematic due to inmate abuse and age. This project would provide for installing new cell doors, locks and controls. Removal and disposal of the existing equipment is included in this estimate. | HOUSING UNIT #8 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 421875
2173INT1 | INTERIOR FINISHES | 2173 | This project would provide funding to maintain the interior of the building. Included in the cost is painting the walls and ceilings, sealing the exposed masonry, repairing cracks in the masonry and replacing grout and caulk as needed. An epoxy-based paint should be utilized in wet areas for durability. It is recommended that the interior of the building be painted, sealed and repaired in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HOUSING UNIT #7 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 445000
2172PLM2 | CELL WATER CONTROL SYSTEMS REPLACEMENT | 2172 | This building is equipped with cell water control systems that are outdated and should be scheduled for replacement. Problems exist with the current water control systems. It is increasingly difficult to find replacement parts and experienced repairmen to service the equipment. It is recommended to replace the water control systems. This project includes the replacement of the water controllers, piping, valves, access panels and all connections to the existing utilities. | HOUSING UNIT #8 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 588000
2178PLM1 | WATER HEATER REPLACEMENT | 2178 | There is a 50 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 8-9 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | WAREHOUSE/ MOTOR POOL | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 37041 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 1500
2090HVA2 | HVAC EQUIPMENT REPLACEMENT | 2090 | The air handler fan coils and related equipment are original to the building (2000). The equipment has consistent problems and has reached its expected life span. This project recommends replacement of all air handlers, fan coils, ventilation equipment and exhaust fans. It is recommended that this project be implemented in the next 2-3 years to avoid possible failure and emergency funding for replacement. | INFIRMARY/ INTAKE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 32986 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 494790
2090ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 2090 | This building contains several water fountains that are not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | INFIRMARY/ INTAKE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 32986 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 8000
2178ELE1 | GFCI OUTLETS | 2178 | The existing receptacles next to the drinking fountain and eye wash station are standard duplex receptacles. The 2011 NEC Code 210.8 require these locations to have GFCI protection. This project would provide for removing the standard receptacles and installing GFCI receptacles. | WAREHOUSE/ MOTOR POOL | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 37041 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 800
2178SFT4 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 2178 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | WAREHOUSE/ MOTOR POOL | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 37041 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 9000
2178ADA1 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 2178 | This building contains two water fountains that are not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | WAREHOUSE/ MOTOR POOL | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 37041 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 8000
2178HVA2 | HVAC EQUIPMENT REPLACEMENT | 2178 | The existing HVAC system consists of ceiling mounted hydronic heaters, 8 packaged heat pumps, 10 swamp coolers and an Evapco cooling tower. The HVAC system was installed in 2002. The HVAC system is not energy efficient and has reached the end of its expected and useful life. This project would provide for installation of new HVAC equipment. The new systems shall be designed to significantly reduce utility usage in order to comply with the 2012 IECC and ASHRAE 90.1. This project includes removal and disposal of the existing HVAC system and all required connections to utilities. | WAREHOUSE/ MOTOR POOL | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 37041 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 926025
2178ELE2 | ELECTRICAL AND COMMUNICATIONS UPGRADE | 2178 | This building was constructed before the high demand for electrical services were needed for computers, communications systems and other electrical devices. As time has progressed, the buildings electrical demand and communications system has changed. The electrical system is utilized to its current maximum potential and the communications system is outdated. The electrical panels, switches and receptacles are at their limit. It is recommended to upgrade the entire electrical system and communications system to meet the evolving needs of the building. | WAREHOUSE/ MOTOR POOL | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 37041 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 926025
2173ADA1 | ADA TABLE UPGRADE | 2173 | Per the United States Access Board and ICC ANSI-A117.1-2009, at least 5 percent of the seating spaces shall be, if fixed seating is provided, a loose seat or open space for a wheelchair. This project would provide funding to remove 3 of the fixed seats, which will allow access for wheel chairs. | HOUSING UNIT #7 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 3000
2178HVA3 | EXHAUST FAN REPLACEMENT | 2178 | The exhaust fans in the restrooms serving the Warehouse/ Motor Pool building were inoperative and/or damaged at the time of the survey. Due to building code requirements and excessive humidity concerns, this project would provide funding for the purchase and installation of high volume commercial exhaust fans. | WAREHOUSE/ MOTOR POOL | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 37041 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
2090ADA3 | ADA EMPLOYEE LOUNGE UPGRADES | 2090 | In order to comply with current ADA requirements, modification will be necessary for the employee lounge and the sinks. It is recommended to upgrade some of the features of the rooms for compliance with accessibility standards for employees. This project would provide funding for construction of an accessible sink and faucet, an accessible space at one of the dining tables and an accessible path of travel throughout the room. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | INFIRMARY/ INTAKE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 32986 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 4000
2178INT2 | JANITORS CLOSET REPAIRS | 2178 | The mop sink in the Janitors Closet is mounted adjacent to CMU and is showing signs of water damage. This project would provide FRP to be installed on the CMU walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | WAREHOUSE/ MOTOR POOL | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 37041 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
2178EXT2 | ROOF REPLACEMENT | 2178 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2002. It is recommended that this building be re-roofed in the next 4-5 years to be consistent with the roofing program and the end of the warranty period. | WAREHOUSE/ MOTOR POOL | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 37041 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 444492
2178ENR1 | LIGHTING UPGRADE | 2178 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | WAREHOUSE/ MOTOR POOL | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 37041 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 296328
2178PLM2 | WATER TREATMENT SYSTEM REPLACEMENT | 2178 | The existing water softening/ treatment systems in the building are currently not operational. They are original to the building and approaching the end of their lifecycles. Failure of the equipment causes wear and tear on the domestic water supply lines, plumbing fixtures and HVAC equipment. This project would provide for the replacement of the existing water softeners/ treatment systems with new equipment. This project would also provide for a chemical treatment program including an updated chemicals control system, service and employee training provided by a qualified water treatment vendor. The annual maintenance fee charged by the water treatment vendor would be determined after an investigation of the water system is complete. These annual costs are not included in this project cost. For budgeting purposes, a $12,000 maintenance fee is suggested. | WAREHOUSE/ MOTOR POOL | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 37041 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
2178INT1 | INTERIOR FINISHES | 2178 | This project would provide funding to maintain the interior of the building. Included in the cost is painting the walls and ceilings, sealing the exposed masonry, repairing cracks in the masonry and replacing grout and caulk as needed. An epoxy-based paint should be utilized in wet areas for durability. It is recommended that the interior of the building be painted, sealed and repaired in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | WAREHOUSE/ MOTOR POOL | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 37041 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 370410
2178SFT2 | LOADING DOCK | 2178 | The Warehouse/ Motor Pool has a loading dock. The loading dock is used by large trucks and tractor trailers to back in for loading and unloading supplies needed for the High Desert State Prison. There are no wheel blocks installed to prevent the movement of trucks or trailers loading or unloading, per OSHA 1910.178(m)(7) requirements. The forklifts are battery operated. Per OSHA 1910.178(g)(2), the charging area for the forklifts do not provide an area for; flushing and neutralizing spilled electrolytes; for fire protection; for protecting charging apparatus; from damage by trucks, and for adequate ventilation for dispersal of fumes for gassing batteries. This project addresses the installation of blocks for the loading ramp, installation of two bollards to protect the battery charging/ flushing area in case of spills and provide adequate ventilation for dispersal of fumes for gassing batteries. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | WAREHOUSE/ MOTOR POOL | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 37041 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 10000
2178EXT1 | EXTERIOR FINISHES | 2178 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | WAREHOUSE/ MOTOR POOL | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 37041 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 270410
2177ENV2 | PEST CONTROL | 2177 | There are numerous bird and rodent droppings throughout this building. Due to the potential risk of disease, this project provides for treatment and cleanup of the pigeon and rodent droppings by a licensed pest control business. | TOWER #4 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
2178SFT3 | FIRE ALARM SYSTEM REPLACEMENT | 2178 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and due to this the system no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | WAREHOUSE/ MOTOR POOL | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 37041 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 296328
2089SEC1 | COMMUNICATIONS SYSTEM UPGRADE | 2089 | This building is equipped with a communications system that at the time of the survey was not working properly. The communications system provides paging, phone communications and communication to inmates. The communications system is an integral component of the notification and safety procedures for the inmates and staff. The system is problematic and replacement parts are no longer available. It is recommended that the communications system be upgraded. | HOUSING UNIT #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 222500
2172INT1 | INTERIOR FINISHES | 2172 | This project would provide funding to maintain the interior of the building. Included in the cost is painting the walls and ceilings, sealing the exposed masonry, repairing cracks in the masonry and replacing grout and caulk as needed. An epoxy-based paint should be utilized in wet areas for durability. It is recommended that the interior of the building be painted, sealed and repaired in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HOUSING UNIT #8 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 445000
2173ADA2 | TDD INSTALLATION | 2173 | The Housing Unit is not equipped with a TDD. In order to comply with ADA requirements it is recommended to install a TDD system in the Housing Unit. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | HOUSING UNIT #7 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 60000
2173HVA1 | EXHAUST FAN INSTALLATION | 2173 | The mechanical room within the housing unit has plumbing fixtures and drains. Due to moisture in this room, the humidity is very high and there is an increase probability for indoor air quality concern. This project would provide for the purchase and installation of a new commercial grade exhaust fan and the assemblies and will include the connections to utilities. | HOUSING UNIT #7 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 10000
2173SEC1 | COMMUNICATIONS SYSTEM UPGRADE | 2173 | This building is equipped with a communications system that at the time of the survey was not working properly. The communications system provides paging, phone communications and communication to inmates. The communications system is an integral component of the notification and safety procedures for the inmates and staff. The system is problematic and replacement parts are no longer available. It is recommended that the communications system be upgraded. | HOUSING UNIT #7 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 222500
2173SFT5 | SPRINKLER HEAD REPLACEMENT | 2173 | The existing fire suppression sprinkler heads are an older style and are susceptible to damage and misuse by the inmates. Inmates have tied strings to the sprinkler heads and have broken them in the past. This project recommends that all of the fire sprinkler heads in all cells be removed and replaced with a new state of the art tamper-resistant sprinkler heads. | HOUSING UNIT #7 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 40000
2173ENR1 | LIGHTING UPGRADE | 2173 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | HOUSING UNIT #7 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 356000
2173HVA2 | HVAC EQUIPMENT REPLACEMENT | 2173 | The air handlers, fan coils and related equipment are original to the building, dating back to 2002. The equipment has consistent problems and has reached its expected life span. This project recommends the replacement of all air handlers, fan coils, ventilation equipment and exhaust fans. It is recommended that this project be implemented in the next 4-5 years to avoid possible failure and emergency funding for replacement. | HOUSING UNIT #7 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 667500
2089SFT4 | FIRE ALARM SYSTEM REPLACEMENT | 2089 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and due to this, the system no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | HOUSING UNIT #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 356000
2090ADA1 | ADA SHOWER UPGRADE | 2090 | This project would provide for nine ADA compliant stainless steel shower cabinets to be installed to provide shower facilities for the disabled. Included in this estimate is the installation of nine stainless steel ADA compliant shower cabinet units complete with accessible plumbing fixtures, seats, etc. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | INFIRMARY/ INTAKE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 32986 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 225000
2089EXT2 | ROOF REPLACEMENT | 2089 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2000. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. | HOUSING UNIT #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 667500
2090SFT2 | ANCHOR SHELVES | 2090 | OSHA recommends that the bottom of all columns be furnished with column base plates, and be anchored to the floor with anchor bolts capable of resisting the forces caused by the loads on the shelving unit. Per OSHA standard 1926.250(a)(1) All materials stored in tiers shall be stacked, racked, blocked, interlocked, or otherwise secured to prevent sliding, falling or collapse. This project would provide for a licensed contractor to install anchor bolts and properly secure the shelving units to the floor and to the other shelves. This project should be overseen by a licensed engineer or architect. | INFIRMARY/ INTAKE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 32986 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 10000
2089SEC2 | CELL DOORS, LOCKS AND CONTROLS REPLACEMENT | 2089 | The Housing Unit was constructed in 2000. The cell doors, locks and controls are original to the building and have been problematic due to inmate abuse and age. This project would provide for installing new cell doors, locks and controls. Removal and disposal of the existing equipment is included in this estimate. | HOUSING UNIT #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 421875
2090EXT1 | EXTERIOR FINISHES | 2090 | It is important to maintain the finish, weather resistance and appearance of the building. The caulked control joints in the CMU of the exterior surface of this building are uniformly deteriorated and should be removed and the joints re-caulked. The metal doors and window frames should be sanded and painted on a cyclical basis. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | INFIRMARY/ INTAKE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 32986 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 329860
2090HVA1 | VENTILATION | 2090 | At the time of the survey, the mechanical room was extremely warm. It did not appear to have air conditioning or ventilation. This is causing the motors to become hot and will cause premature failure. This project recommends adding a ventilation system for proper temperature control of the mechanical room. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | INFIRMARY/ INTAKE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 32986 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
2090INT1 | INTERIOR FINISHES | 2090 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | INFIRMARY/ INTAKE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 32986 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 329860
2505INT1 | INTERIOR FINISHES | 2505 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and adequately prepared to receive the coating. An epoxy-based paint should be utilized in wet areas for durability. | STORAGE BUILDING | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 144 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1440
2090SFT4 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 2090 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | INFIRMARY/ INTAKE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 32986 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 9000
2505EXT1 | EXTERIOR FINISHES | 2505 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | STORAGE BUILDING | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 144 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1440
2946ADA2 | TDD INSTALLATION | 2946 | The Housing Unit is not equipped with a TDD. In order to comply with ADA requirements it is recommended to install a TDD system in the Housing Unit. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | HOUSING UNIT #12 | 9952 | Correct | HDSP |  | Indian Springs | 2008 | 52096 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 60000
2089ENR1 | LIGHTING UPGRADE | 2089 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | HOUSING UNIT #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 356000
2086PLM1 | WATER HEATER REPLACEMENT | 2086 | There are two 18 gallon electric water heaters in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, these units are showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that two new electric water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. | HOUSING UNIT #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
2094SFT1 | EGRESS LIGHTING UPGRADE | 2094 | There are older emergency egress lighting units in this building. These units have a finite lifespan, and this project recommends their replacement with new egress lights, and to also provide additional lights on the main exit routes and in individual rooms as needed. | ADMINISTRATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 11175 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 5588
2095INT1 | INTERIOR FINISHES | 2095 | It is recommended to repair, paint or seal the interior concrete block walls at least once in the 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | GATEHOUSE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 6165 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 61650
2095EXT0 | EXTERIOR FINISHES | 2095 | It is important to maintain the finish, weather resistance and appearance of the building. The caulked control joints in the CMU of the exterior surface of this building are uniformly deteriorated and should be removed and the joints re-caulked. The metal doors and window frames should be sanded and painted on a cyclical basis. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | GATEHOUSE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 6165 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 61650
2086SFT6 | ROOF HATCH REPLACEMENT | 2086 | The roof hatches are original to the building and have reached the end of their useful life. The compression spring operators do not function properly, the latches and handles are worn and the seals and flashing have deteriorated. A faulty roof hatch is a safety hazard to anyone accessing the roof. This project would provide for the removal and the disposal of the existing roof hatches and for the purchase and installation of new roof hatches. | HOUSING UNIT #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 10000
2086PLM4 | COMPUTER WATER CONTROL SYSTEM REPLACEMENT | 2086 | This building is equipped with a computer water control system that is outdated and should be scheduled for replacement. Problems exist with the current computer water control system. It is increasingly difficult to find software updates and experienced repairmen to service the equipment. This project recommends the installation of a new computer water control system for the building. This system will monitor and control the water for all fixtures throughout the building. New electronic sensors will be installed on each water control system. | HOUSING UNIT #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
2086SFT2 | ELECTRICAL OUTLET & CABLE UPGRADES | 2086 | At the time of the survey the building had residential and commercial cover plates over the electrical outlets and coaxial wires. This poses a safety hazard allowing inmates to remove them and use them as weapons. This could be a safety hazard to inmates and guards. This project would provide for the installation of new security grade cover plates throughout the entire housing unit. | HOUSING UNIT #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 74592
2086SFT3 | FIRE ALARM SYSTEM REPLACEMENT | 2086 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and due to this, the system no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | HOUSING UNIT #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 356000
2086EXT3 | ROOF REPLACEMENT | 2086 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2000. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. | HOUSING UNIT #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 667500
2093SEC1 | DOOR CONTROLS SYSTEM REPLACEMENT | 2093 | The control panel/ inmate movement and control system in the building is not working properly. The cell door indicator lights on the control panel are falsely representing the actual status of the cell doors. The officer sometimes cannot tell if the cell door is open or closed. This project would replace the existing secured door control system with a programmable logic controlled system using touch screens for actuation and door status. This project would replace the existing door control system and the outdated wiring. Removal and disposal of the existing equipment is included in this estimate. | VISITATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 11194 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
2086HVA2 | HVAC EQUIPMENT REPLACEMENT | 2086 | The air handlers, fan coils and related equipment are original to the building, dating back to 2000. The equipment has consistent problems and has reached its expected life span. This project recommends the replacement of all air handlers, fan coils, ventilation equipment and exhaust fans. It is recommended that this project be implemented in the next 2-3 years to avoid possible failure and emergency funding for replacement. | HOUSING UNIT #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 667500
2094PLM2 | WATER HEATER REPLACEMENT | 2094 | There is a 40 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | ADMINISTRATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 11175 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
2086SEC1 | CELL DOORS, LOCKS AND CONTROLS REPLACEMENT | 2086 | The Housing Unit was constructed in 2000. The cell doors, locks and controls are original to the building and have been problematic due to inmate abuse and age. This project would provide for installing new cell doors, locks and controls. Removal and disposal of the existing equipment is included in this estimate. | HOUSING UNIT #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 421875
2086ELE1 | DOOR CONTROL SYSTEM REPLACEMENT | 2086 | The control panel/ inmate movement and control system in the housing unit is not working properly. The cell door indicator lights on the control panel are falsely representing the actual status of the cell doors. The officer sometimes cannot tell if the cell door is open or closed. This project would replace the existing secured door control system with a programmable logic controlled system using touch screens for actuation and door status. This project would replace the existing door control system and the outdated wiring. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HOUSING UNIT #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 1438241.25
2086HVA1 | EVAPORATIVE COOLER REPLACEMENT | 2086 | There is a guard stationed on the roof to look out onto the yard. They have one overhead swamp cooler to keep them cool in the warmer months. At the time of the survey the swamp cooler was not working. It is severely scaled and has reached the end of its useful and expected life. This project would provide for a new evaporative cooler to be installed including all required connections to utilities. The estimate includes removal and disposal of the old cooler. | HOUSING UNIT #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 4000
2086ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 2086 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | HOUSING UNIT #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 4000
2086SFT4 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 2086 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 9000
2087INT1 | INTERIOR FINISHES | 2087 | The interior finishes are in fair condition. It is recommended that the interior walls and floors be painted or sealed at least once in the next 2-3 years. Prior to painting or sealing, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HOUSING UNIT #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 445000
2087STR1 | WALKWAY RAILING | 2087 | The perimeter roof walkway guardrail is failing. The railing is loose or not attached and is posing a potential safety problem. This project recommends an assessment be performed by a Structural Engineer to determine the cause and provide a design solution. Future projects will be based on the design solution recommendation. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HOUSING UNIT #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 3000
2087EXT1 | EXTERIOR FINISHES | 2087 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide for caulking all control joints and penetrations on a cyclical basis. The metal doors and window frames should also be sanded and painted a on a cyclical basis. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HOUSING UNIT #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 445000
2086ELE2 | ELECTRICAL TRANSFORMER REPLACEMENT | 2086 | The 50 kVA electrical transformer that provides services to the building was damaged at the time of inspection and does not function properly. This project recommends replacing the electrical transformer. | HOUSING UNIT #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
2094PLM1 | WATER TREATMENT SYSTEM REPLACEMENT | 2094 | The existing water softening/ treatment systems in the building are currently not operational. They are original to the building and approaching the end of their lifecycles. Failure of the equipment causes wear and tear on the domestic water supply lines, plumbing fixtures and HVAC equipment. This project would provide for the replacement of the existing water softeners/ treatment systems with new equipment. This project would also provide for a chemical treatment program including an updated chemicals control system, service and employee training provided by a qualified water treatment vendor. The annual maintenance fee charged by the water treatment vendor would be determined after an investigation of the water system is complete. These annual costs are not included in this project cost. For budgeting purposes, a $12,000 maintenance fee is suggested. | ADMINISTRATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 11175 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
2088PLM1 | WATER HEATER REPLACEMENT | 2088 | There are two 18 gallon electric water heaters in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, these units are showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that two new electric water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. | HOUSING UNIT #4 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
2093INT3 | FLOORING REPLACEMENT | 2093 | The VCT in the building is damaged and reaching the end of its useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base in the next 2-3 years. | VISITATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 11194 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 45000
2093ADA2 | ADA ACCESSIBLE COUNTER | 2093 | The ADA provides for accessibility to sites and services for people with physical limitations. The lobby at the entrance of the building has a service counter for the public to approach which does not meet current requirements. Section 904.4 of the ADA Standards for Accessible Design states that a portion of the counter surface that is 36" long minimum and 36" high maximum above the finish floor shall be provided. This project will provide an accessible counter space in accordance with this requirement. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | VISITATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 11194 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 4000
2093SFT2 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 2093 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | VISITATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 11194 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 9000
2093INT2 | JANITORS CLOSET REPAIRS | 2093 | The walls adjacent to and above the janitor's closet mop sink did not have a water resistant finish. This project recommends the installation of fiberglass reinforced panels on the walls adjacent to the mop sink to a height of 54" above the finish floor. | VISITATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 11194 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
2093PLM1 | WATER TREATMENT SYSTEM REPLACEMENT | 2093 | The existing water softening/ treatment systems in the building are currently not operational. They are original to the building and approaching the end of their lifecycles. Failure of the equipment causes wear and tear on the domestic water supply lines, plumbing fixtures and HVAC equipment. This project would provide for the replacement of the existing water softeners/ treatment systems with new equipment. This project would also provide for a chemical treatment program including an updated chemicals control system, service and employee training provided by a qualified water treatment vendor. The annual maintenance fee charged by the water treatment vendor would be determined after an investigation of the water system is complete. These annual costs are not included in this project cost. For budgeting purposes, a $12,000 maintenance fee is suggested. | VISITATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 11194 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
2093SFT3 | FIRE ALARM SYSTEM REPLACEMENT | 2093 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and due to this, the system no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | VISITATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 11194 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 89400
2093ADA3 | ADA RESTROOM FIXTURES | 2093 | The fixtures in the ADA restrooms are worn and damaged from many years of use including the water closets, urinals, lavatories, faucets, shower heads and handles. Many fixtures are or have been leaking and have caused extensive scaling and staining to the fixtures themselves. It is recommended that all fixtures be replaced with new ADA compliant units. This project includes removal and disposal of the existing fixtures and installation of new fixtures. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | VISITATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 11194 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 1000
2094SFT2 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 2094 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | ADMINISTRATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 11175 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 9000
2094EXT1 | EXTERIOR FINISHES | 2094 | It is important to maintain the finish, weather resistance and appearance of the building. The caulked control joints in the CMU of the exterior surface of this building are uniformly deteriorated and should be removed and the joints re-caulked. The metal doors and window frames should be sanded and painted on a cyclical basis. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | ADMINISTRATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 11175 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 111750
2094HVA1 | VARIABLE FREQUENCY DRIVE REPLACEMENT | 2094 | The Variable Frequency Drives throughout the building have been disabled. Staff reports that the VFD's are problematic and have been by-passed from the HVAC system. This project would provide for purchase and installation of new VFD's. | ADMINISTRATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 11175 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35000
2094INT3 | FLOORING REPLACEMENT | 2094 | The VCT (vinyl composite tile) and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the next 2-3 years. | ADMINISTRATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 11175 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 100575
2094ELE1 | ELECTRICAL AND COMMUNICATIONS UPGRADE | 2094 | This building was constructed before the high demand for electrical services were needed for computers, communications systems and other electrical devices. As time has progressed, the buildings electrical demand and communications system has changed. The electrical system is utilized to its current maximum potential and the communications system is outdated. The electrical panels, switches and receptacles are at their limit. It is recommended to upgrade the entire electrical system and communications system to meet the evolving needs of the building. | ADMINISTRATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 11175 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 279375
2094SFT3 | FIRE ALARM SYSTEM REPLACEMENT | 2094 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and due to this the system no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 "If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure". When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | ADMINISTRATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 11175 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 89400
2094HVA2 | HVAC EQUIPMENT REPLACEMENT | 2094 | The air handlers, fan coils and related equipment are original to the building, dating back to 2000. The equipment has consistent problems and has reached its expected life span. This project recommends replacement of the air handlers, fan coils, ventilation equipment and exhaust fans. It is recommended that this project be implemented in the next 2-3 years to avoid possible failure and emergency funding for replacement. | ADMINISTRATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 11175 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 167625
2094ENR1 | LIGHTING UPGRADE | 2094 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | ADMINISTRATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 11175 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 89400
2947ELE2 | DOOR CONTROLS SYSTEM REPLACEMENT | 2947 | The control panel/ inmate movement and control system in the housing unit is not working properly. The cell door indicator lights on the control panel are falsely representing the actual status of the cell doors. The officer sometimes cannot tell if the cell door is open or closed. This project would replace the existing secured door control system with a programmable logic controlled system using touch screens for actuation and door status. This project would replace the existing door control system and the outdated wiring. Removal and disposal of the existing equipment is included in this estimate. | HOUSING UNIT #10 | 9952 | Correct | HDSP |  | Indian Springs | 2009 | 51609 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 1438241.25
2948EXT1 | EXTERIOR FINISHES | 2948 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT #11 | 9952 | Correct | HDSP |  | Indian Springs | 2009 | 51609 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 516090
2094EXT2 | ROOF REPLACEMENT | 2094 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2000. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. | ADMINISTRATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 11175 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 167625
2087ADA3 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 2087 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | HOUSING UNIT #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 4000
2094INT1 | INTERIOR FINISHES | 2094 | It is recommended that the interior walls be painted at least once in the next 2-3 years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | ADMINISTRATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 11175 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 111750
2095HVA1 | HVAC EQUIPMENT REPLACEMENT | 2095 | The air handlers, fan coils and related equipment are original to the building, dating back to 2000. The equipment has consistent problems and has reached its expected life span. This project recommends replacement of the air handlers, fan coils, ventilation equipment and exhaust fans. It is recommended that this project be implemented in the next 2-3 years to avoid possible failure and emergency funding for replacement. | GATEHOUSE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 6165 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 92475
2087PLM1 | WATER HEATER REPLACEMENT | 2087 | There are two 18 gallon electric water heaters in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, these units are showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that two new electric water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. | HOUSING UNIT #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
2088INT1 | INTERIOR FINISHES | 2088 | The interior finishes are in fair condition. It is recommended that the interior walls and floors be painted or sealed at least once in the next 2-3 years. Prior to painting or sealing, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HOUSING UNIT #4 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 445000
2088EXT1 | EXTERIOR FINISHES | 2088 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide for caulking all control joints and penetrations on a cyclical basis. The metal doors and window frames should also be sanded and painted a on a cyclical basis. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HOUSING UNIT #4 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 445000
2088ELE1 | ELECTRICAL TRANSFORMER REPLACEMENT | 2088 | The 50 kVA electrical transformer that provides services to the building was damaged at the time of inspection and does not function properly. This project recommends replacing the electrical transformer. | HOUSING UNIT #4 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
2095SEC1 | DOOR CONTROLS SYSTEM REPLACEMENT | 2095 | The control panel/ inmate movement and control system in the Gatehouse is not working properly. The cell door indicator lights on the control panel are falsely representing the actual status of the cell doors. The officer sometimes cannot tell if the cell door is open or closed. This project would replace the existing secured door control system with a programmable logic controlled system using touch screens for actuation and door status. This project would replace the existing door control system and the outdated wiring. Removal and disposal of the existing equipment is included in this estimate. | GATEHOUSE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 6165 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
2095ENR1 | LIGHTING UPGRADE | 2095 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | GATEHOUSE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 6165 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1536
2102EXT2 | WINDOW REPLACEMENT | 2102 | The existing windows in this building are of single pane wire mesh construction. They are not energy efficient. This project would provide for the removal and replacement of the windows with new dual pane security rated windows. | TOWER #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 19200
2095ELE1 | ELECTRICAL AND COMMUNICATIONS UPGRADE | 2095 | This building was constructed before the high demand for electrical services were needed for computers, communications systems and other electrical devices. As time has progressed, the buildings electrical demand and communications system has changed. The electrical system is utilized to its current maximum potential and the communications system is outdated. The electrical panels, switches and receptacles are at their limit. It is recommended to upgrade the entire electrical system and communications system to meet the evolving needs of the building. | GATEHOUSE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 6165 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 154125
2087SEC3 | DOOR CONTROLS SYSTEM REPLACEMENT | 2087 | The control panel/ inmate movement and control system in the housing unit is not working properly. The cell door indicator lights on the control panel are falsely representing the actual status of the cell doors. The officer sometimes cannot tell if the cell door is open or closed. This project would replace the existing secured door control system with a programmable logic controlled system using touch screens for actuation and door status. This project would replace the existing door control system and the outdated wiring. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HOUSING UNIT #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 1438241.25
2095INT3 | FLOORING REPLACEMENT | 2095 | The VCT flooring in the gymnasium is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. | GATEHOUSE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 6165 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 55485
2087HVA2 | HVAC EQUIPMENT REPLACEMENT | 2087 | The air handlers, fan coils and related equipment are original to the building, dating back to 2000. The equipment has consistent problems and has reached its expected life span. This project recommends the replacement of all air handlers, fan coils, ventilation equipment and exhaust fans. It is recommended that this project be implemented in the next 2-3 years to avoid possible failure and emergency funding for replacement. | HOUSING UNIT #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 667500
2507ADA1 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 2507 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | PRISON INDUSTRIES | 9952 | Correct | HDSP |  | Indian Springs | 2004 | 60000 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 12000
2095ADA1 | ADA SHOWER UPGRADE | 2095 | This project would provide for three ADA compliant stainless steel shower cabinets to be installed to provide shower facilities for the disabled. Included in this estimate is the installation of two stainless steel ADA compliant shower cabinet units complete with accessible plumbing fixtures, seats, etc. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | GATEHOUSE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 6165 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 50000
2095ADA2 | ADA ACCESSIBLE COUNTER | 2095 | The ADA provides for accessibility to sites and services for people with physical limitations. The lobby at the entrance of the building has a service counter for the public to approach which does not meet current requirements. Section 904.4 of the ADA Standards for Accessible Design states that a portion of the counter surface that is 36" long minimum and 36" high maximum above the finish floor shall be provided. This project will provide an accessible counter space in accordance with this requirement. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | GATEHOUSE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 6165 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 4000
2095ADA3 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 2095 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | GATEHOUSE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 6165 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 4000
2095EXT3 | ROOF REPLACEMENT | 2095 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2000. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. | GATEHOUSE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 6165 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 73980
2095PLM1 | WATER HEATER REPLACEMENT | 2095 | There are two 119 gallon electric water heaters in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, the units are showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that new electric water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. | GATEHOUSE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 6165 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
2095PLM2 | WATER TREATMENT SYSTEM REPLACEMENT | 2095 | The existing water softening/ treatment systems in the building are currently not operational. They are original to the building and approaching the end of their lifecycles. Failure of the equipment causes wear and tear on the domestic water supply lines, plumbing fixtures and HVAC equipment. This project would provide for the replacement of the existing water softeners/ treatment systems with new equipment. This project would also provide for a chemical treatment program including an updated chemicals control system, service and employee training provided by a qualified water treatment vendor. The annual maintenance fee charged by the water treatment vendor would be determined after an investigation of the water system is complete. These annual costs are not included in this project cost. For budgeting purposes, a $12,000 maintenance fee is suggested. | GATEHOUSE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 6165 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
2088HVA2 | HVAC EQUIPMENT REPLACEMENT | 2088 | The air handlers, fan coils and related equipment are original to the building, dating back to 2000. The equipment has consistent problems and has reached its expected life span. This project recommends replacement of the air handlers, fan coils, ventilation equipment and exhaust fans. It is recommended that this project be implemented in the next 2-3 years to avoid possible failure and emergency funding for replacement. | HOUSING UNIT #4 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 667500
2088SFT4 | FIRE ALARM SYSTEM REPLACEMENT | 2088 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and due to this, the system no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | HOUSING UNIT #4 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 356000
2948HVA2 | EXHAUST FAN INSTALLATION | 2948 | The mechanical room within the housing unit has plumbing fixtures and drains. Due to moisture in this room, the humidity is very high and there is an increase probability for indoor air quality concern. This project would provide for the purchase and installation of a new commercial grade exhaust fan and the assemblies and will include the connections to utilities. | HOUSING UNIT #11 | 9952 | Correct | HDSP |  | Indian Springs | 2009 | 51609 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 10000