2087SEC1 | COMMUNICATIONS SYSTEM UPGRADE | 2087 | This building is equipped with a communications system that at the time of the survey was not working properly. The communications system provides paging, phone communications and communication to inmates. The communications system is an integral component of the notification and safety procedures for the inmates and staff. The system is problematic and replacement parts are no longer available. It is recommended that the communications system be upgraded. | HOUSING UNIT #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 222500
2093ADA4 | ADA UPGRADES | 2093 | ADA regulations pertaining to building access, route of travel and restrooms has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances, route of travel inside the building and restrooms. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | VISITATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 11194 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 600
2087INT3 | JANITORS CLOSET REPAIRS | 2087 | The mop sink in the Janitors Closet is mounted adjacent to CMU and is showing signs of water damage. This project would provide FRP to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | HOUSING UNIT #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
2087SEC2 | CELL DOORS, LOCKS AND CONTROLS REPLACEMENT | 2087 | The Housing Unit was constructed in 2000. The cell doors, locks and controls are original to the building and have been problematic due to inmate abuse and age. This project would provide for installing new cell doors, locks and controls. Removal and disposal of the existing equipment is included in this estimate. | HOUSING UNIT #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 421875
2087SFT3 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 2087 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 9000
2087ADA2 | TDD INSTALLATION | 2087 | The Housing Unit is not equipped with a TDD. In order to comply with ADA requirements it is recommended to install a TDD system in the Housing Unit. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | HOUSING UNIT #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 60000
2087EXT2 | ROOF REPLACEMENT | 2087 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2000. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. | HOUSING UNIT #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 667500
2087SFT2 | SPRINKLER HEAD REPLACEMENT | 2087 | The existing fire suppression sprinkler heads are an older style and are susceptible to damage and misuse by the inmates. Inmates have tied strings to the sprinkler heads and have broken them in the past. This project recommends that all of the fire sprinkler heads in all cells be removed and replaced with a new state of the art tamper-resistant sprinkler heads. | HOUSING UNIT #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 40000
2087SFT6 | ROOF HATCH REPLACEMENT | 2087 | The roof hatches are original to the building and have reached the end of their useful life. The compression spring operators do not function properly, the latches and handles are worn and the seals and flashing have deteriorated. A faulty roof hatch is a safety hazard to anyone accessing the roof. This project would provide for the removal and the disposal of the existing roof hatches and for the purchase and installation of new roof hatches. | HOUSING UNIT #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 10000
2088STR1 | WALKWAY RAILING | 2088 | The perimeter roof walkway guardrail is failing. The railing is loose or not attached and is posing a potential safety problem. This project recommends an assessment be performed by a Structural Engineer to determine the cause and provide a design solution. Future projects will be based on the design solution recommendation. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HOUSING UNIT #4 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 2500
2087HVA3 | EVAPORATIVE COOLER REPLACEMENT | 2087 | There is a guard stationed on the roof to look out onto the yard. They have one overhead swamp cooler to keep them cool in the warmer months. At the time of the survey the swamp cooler was not working. It is severely scaled and has reached the end of its useful and expected life. This project would provide for a new evaporative cooler to be installed including all required connections to utilities. The estimate includes removal and disposal of the old cooler. | HOUSING UNIT #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 4000
2087SFT4 | FIRE ALARM SYSTEM REPLACEMENT | 2087 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and due to this, the system no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | HOUSING UNIT #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 356000
2087PLM4 | COMPUTER WATER CONTROL SYSTEM REPLACEMENT | 2087 | This building is equipped with a computer water control system that is outdated and should be scheduled for replacement. Problems exist with the current computer water control system. It is increasingly difficult to find software updates and experienced repairmen to service the equipment. This project recommends the installation of a new computer water control system for the building. This system will monitor and control the water for all fixtures throughout the building. New electronic sensors will be installed on each water control system. | HOUSING UNIT #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
2087ELE1 | ELECTRICAL TRANSFORMER REPLACEMENT | 2087 | The 50 kVA electrical transformer that provides services to the building was damaged at the time of inspection and does not function properly. This project recommends replacing the electrical transformer. | HOUSING UNIT #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
2087ADA1 | ADA TABLE UPGRADE | 2087 | Per the United States Access Board and ICC ANSI-A117.1-2009, at least 5 percent of the seating spaces shall be, if fixed seating is provided, a loose seat or open space for a wheelchair. This project would provide funding to remove 3 of the fixed seats, which will allow access for wheel chairs. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HOUSING UNIT #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 3000
2087PLM3 | SHOWER WATER CONTROL SYSTEMS REPLACEMENT | 2087 | This building is equipped with shower water control systems that are outdated and should be scheduled for replacement. Problems exist with the current shower water control systems. It is increasingly difficult to find replacement parts and experienced repairmen to service the equipment. This project includes the replacement of the shower water controllers, piping, valves, access panels, shower heads and all connections to the existing utilities. | HOUSING UNIT #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
2087PLM2 | CELL WATER CONTROL SYSTEMS REPLACEMENT | 2087 | This building is equipped with cell water control systems that are outdated and should be scheduled for replacement. Problems exist with the current water control systems. It is increasingly difficult to find replacement parts and experienced repairmen to service the equipment. It is recommended to replace the water control systems. This project includes the replacement of the water controllers, piping, valves, access panels and all connections to the existing utilities. | HOUSING UNIT #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 504000
2087INT2 | SHOWER UPGRADE | 2087 | There are twelve shower stalls in the building that are showing signs of failure and should be scheduled for repair or replacement. This project would provide for twelve stainless steel shower cabinets to be installed to provide shower facilities for the housing units. Removal and disposal of the existing materials is included in the estimate. | HOUSING UNIT #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 300000
2087ENR1 | LIGHTING UPGRADE | 2087 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | HOUSING UNIT #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 356000
2087HVA1 | EXHAUST FAN INSTALLATION | 2087 | The mechanical room within the housing unit has plumbing fixtures and drains. Due to moisture in this room, the humidity is very high and there is an increase probability for indoor air quality concern. This project would provide for the purchase and installation of a new commercial grade exhaust fan and the assemblies and will include the connections to utilities. | HOUSING UNIT #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 10000
2087SFT5 | ELECTRICAL OUTLET & CABLE UPGRADES | 2087 | At the time of the survey the building had residential and commercial cover plates over the electrical outlets and coaxial wires. This poses a safety hazard allowing inmates to remove them and use them as weapons. This could be a safety hazard to inmates and guards. This project would provide for the installation of new security grade cover plates throughout the entire housing unit. | HOUSING UNIT #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 74592
2087ADA4 | ADA SHOWER UPGRADE | 2087 | This project would provide for three ADA compliant stainless steel shower cabinets to be installed to provide shower facilities for the disabled. Included in this estimate is the installation of three stainless steel ADA compliant shower cabinet units complete with accessible plumbing fixtures, seats, etc. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | HOUSING UNIT #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 75000
2947EXT1 | EXTERIOR FINISHES | 2947 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT #10 | 9952 | Correct | HDSP |  | Indian Springs | 2009 | 51609 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 516090
2945HVA1 | EXHAUST FAN INSTALLATION | 2945 | The mechanical room within the housing unit has plumbing fixtures and drains. Due to moisture in this room, the humidity is very high and there is an increase probability for indoor air quality concern. This project would provide for the purchase and installation of a new commercial grade exhaust fan and the assemblies and will include the connections to utilities. | HOUSING UNIT #9 | 9952 | Correct | HDSP |  | Indian Springs | 2008 | 51609 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 10000
2091PLM1 | SUMP PUMP | 2091 | The sump pump in the mechanical room portion of the building is constantly failing. The ½ H.P. pump cannot handle all of the potential water that may flow into the pit. This project recommends the installation of 1H.P. sump pump to replace the existing pump. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | INMATE SERVICES/ CULINARY/ DINING | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 77005 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11500
2091PLM2 | GREASE WASTE INTERCEPTOR | 2091 | The automatic grease waste separator system for the Kitchen is failing to perform as intended. The system is constantly getting clogged with plastic kitchen utensils and other items disposed of by the inmates. The system has clogged and overflowed onto the floor creating a safety and health hazard. This project would provide for bypassing this equipment and having the waste go directly into the grease interceptor located below grade outside. The facility maintenance staff would have a third party vendor provide pumping services per a routine preventive maintenance schedule based on usage developed by staff to meet the demands of the system. The project cost represents an estimated yearly amount required for this service. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | INMATE SERVICES/ CULINARY/ DINING | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 77005 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
2091SFT1 | CATWALKS | 2091 | The mechanical room has equipment located about 20 feet above the finish floor that need to be monitored or serviced on a regular basis. Currently the maintenance staff is using ladders or climbing on the equipment. This project would provide for the installation of 100 feet long, 2 foot wide of catwalk with guard rails and one set of stairs. All required structural supports are included in this project. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | INMATE SERVICES/ CULINARY/ DINING | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 77005 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 130500
2091STR1 | STEAM PIPE BRACING/ SUPPORT | 2091 | During the visit to the bulk storage/ distribution area of this building, the high pressure steam pipes suspended from the ceiling were moving and shaking violently. It appears that there were surges of pressure in the steam lines that were causing a hammer-locking type condition. The pipes have vibrated badly enough that pieces of the FRP pipe insulation and the metal protective sleeves have fallen from the ceiling mounted pipes. This is a safety concern that needs to be addressed immediately. According to the original drawings, these high pressure steam pipes have 150 psig and there are special system design and inspection/ maintenance parameters and procedures that are required. This project would provide for a licensed Mechanical Engineer who specializes in steam boiler design to investigate this condition and provided a report on the conditions that are causing the condition mentioned above. Future projects would be based on this report. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | INMATE SERVICES/ CULINARY/ DINING | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 77005 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 5000
2086PLM2 | SHOWER WATER CONTROL SYSTEMS REPLACEMENT | 2086 | This building is equipped with shower water control systems that are outdated and should be scheduled for replacement. Problems exist with the current shower water control systems. It is increasingly difficult to find replacement parts and experienced repairmen to service the equipment. This project includes the replacement of the shower water controllers, piping, valves, access panels, shower heads and all connections to the existing utilities. | HOUSING UNIT #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
2086SFT5 | SPRINKLER HEAD REPLACEMENT | 2086 | The existing fire suppression sprinkler heads are an older style and are susceptible to damage and misuse by the inmates. Inmates have tied strings to the sprinkler heads and have broken them in the past. This project recommends that all of the fire sprinkler heads in all cells be removed and replaced with a new state of the art tamper-resistant sprinkler heads. | HOUSING UNIT #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 40000
2086INT3 | JANITORS CLOSET REPAIRS | 2086 | The mop sink in the Janitors Closet is mounted adjacent to CMU and is showing signs of water damage. This project would provide FRP to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | HOUSING UNIT #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
2093ELE1 | ELECTRICAL AND COMMUNICATIONS UPGRADE | 2093 | This building was constructed before the high demand for electrical services were needed for computers, communications systems and other electrical devices. As time has progressed, the buildings electrical demand and communications system has changed. The electrical system is utilized to its current maximum potential and the communications system is outdated. The electrical panels, switches and receptacles are at their limit. It is recommended to upgrade the entire electrical system and communications system to meet the evolving needs of the building. | VISITATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 11194 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 279850
2947PLM1 | FLOOR DRAIN REPAIR | 2947 | The floor drain in the building is clogged and water has pooled around it. The standing water will prematurely deteriorate the building components as well as create a slipping hazard. This project would provide for a licensed contractor to clear the drain and provide any necessary repairs to prevent future problems. | HOUSING UNIT #10 | 9952 | Correct | HDSP |  | Indian Springs | 2009 | 51609 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 2000
2945ENR1 | LIGHTING UPGRADE | 2945 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | HOUSING UNIT #9 | 9952 | Correct | HDSP |  | Indian Springs | 2008 | 51609 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 412872
2947HVA1 | EXHAUST FAN INSTALLATION | 2947 | The mechanical room within the housing unit has plumbing fixtures and drains. Due to moisture in this room, the humidity is very high and there is an increase probability for indoor air quality concern. This project would provide for the purchase and installation of a new commercial grade exhaust fan and the assemblies and will include the connections to utilities. | HOUSING UNIT #10 | 9952 | Correct | HDSP |  | Indian Springs | 2009 | 51609 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 10000
2947PLM5 | COMPUTER WATER CONTROL SYSTEM REPLACEMENT | 2947 | This building is equipped with a computer water control system that is outdated and should be scheduled for replacement. Problems exist with the current computer water control system. It is increasingly difficult to find software updates and experienced repairmen to service the equipment. This project recommends the installation of a new computer water control system for the building. This system will monitor and control the water for all fixtures throughout the building. New electronic sensors will be installed on each water control system. | HOUSING UNIT #10 | 9952 | Correct | HDSP |  | Indian Springs | 2009 | 51609 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 50000
2947SEC2 | CELL DOORS, LOCKS AND CONTROLS REPLACEMENT | 2947 | Housing Unit 10 was constructed in 2009. The cell doors, locks and controls are original to the building and have been problematic due to inmate abuse and age. This project would provide for installing new cell doors, locks and controls. A total of 168 doors were used for this estimate. Removal and disposal of the existing equipment is included in this estimate. | HOUSING UNIT #10 | 9952 | Correct | HDSP |  | Indian Springs | 2009 | 51609 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 421875
2947PLM4 | SHOWER WATER CONTROL SYSTEMS REPLACEMENT | 2947 | This building is equipped with shower water control systems that are outdated and should be scheduled for replacement. Problems exist with the current shower water control systems. It is increasingly difficult to find replacement parts and experienced repairmen to service the equipment. This project includes the replacement of the shower water controllers, piping, valves, access panels, shower heads and all connections to the existing utilities. | HOUSING UNIT #10 | 9952 | Correct | HDSP |  | Indian Springs | 2009 | 51609 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 15000
2091ELE1 | ELECTRICAL UPGRADE | 2091 | The electrical system within the building needs to have repairs made and an inspection on the main electrical distribution panel. Light switches are broken, electrical covers missing, and parts are missing out of the electrical distribution panel. The maintenance staff said the electrical distribution panel is at or over its rating capacity. This project recommends hiring a professional licensed electrician to make repairs and determine if the main electrical distribution panel is at or over its rated capacity. Future projects would be based on the information provided. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | INMATE SERVICES/ CULINARY/ DINING | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 77005 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
2091EXT4 | EXTERIOR FINISHES | 2091 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | INMATE SERVICES/ CULINARY/ DINING | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 77005 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 770050
2091HVA2 | HVAC EQUIPMENT REPLACEMENT | 2091 | The air handlers, fan coils and related equipment are original to the building, dating back to 2000. The equipment has consistent problems and has reached its expected life span. This project recommends replacement of the air handlers, fan coils, ventilation equipment and exhaust fans. It is recommended that this project be implemented in the next 2-3 years to avoid possible failure and emergency funding for replacement. | INMATE SERVICES/ CULINARY/ DINING | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 77005 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1155075
2091HVA1 | HOT WATER RE-USE ROOM REMODEL | 2091 | The hot water re-use room was designed to recycle hot final rinse water to be used as a pre-rinse and provide adequate pressure to laundry washers. During the time of the survey, the equipment required high maintenance, parts were obsolete, the holding tanks had failures and the system had been changed over to a cold wash and rinse system for energy savings. The hot water re-use area is due for a remodel to increase capacity and support the cold wash and rinse system. A mechanical engineer is needed to redesign the area and this project would provide for remodeling the existing area. | INMATE SERVICES/ CULINARY/ DINING | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 77005 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 250000
2947SFT3 | ROOF HATCH REPLACEMENT | 2947 | The roof hatch is original to the building and has reached the end of its useful life. The compression spring operators do not function properly, the latches and handles are worn and the seals and flashing have deteriorated. A faulty roof hatch is a safety hazard to anyone accessing the roof. This project would provide for removal and disposal of the existing roof hatch and purchase and installation of a new roof hatch. | HOUSING UNIT #10 | 9952 | Correct | HDSP |  | Indian Springs | 2009 | 51609 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 5000
2945EXT1 | EXTERIOR FINISHES | 2945 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT #9 | 9952 | Correct | HDSP |  | Indian Springs | 2008 | 51609 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 516090
2090INT3 | WASHING MACHINE REPLACEMENT | 2090 | One of the existing commercial washing machines appears to be a year 2000 model and has reached the end of its useful life. It is showing signs of age, and is constantly breaking down. This project would provide funding for the purchase and installation of one new 60lb. commercial washing machine. | INFIRMARY/ INTAKE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 32986 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
2090INT4 | DRYER REPLACEMENT | 2090 | The commercial tumbler dryer in the laundry area is original to the building and is troublesome and problematic to operate. Considering the age of the machine and the evolving needs of the facility it is recommended to be replaced. This project provides for the removal and disposal of the existing tumbler dryer and replacement with a new unit. A total of 1 dryer was used for this estimate. | INFIRMARY/ INTAKE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 32986 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
2090PLM3 | WATER HEATER REPLACEMENT | 2090 | There is a 40 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | INFIRMARY/ INTAKE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 32986 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
2090PLM2 | WATER TREATMENT SYSTEM REPLACEMENT | 2090 | The existing water softening/ treatment systems in the building are currently not operational. They are original to the building and approaching the end of their lifecycles. Failure of the equipment causes wear and tear on the domestic water supply lines, plumbing fixtures and HVAC equipment. This project would provide for the replacement of the existing water softeners/ treatment systems with new equipment. This project would also provide for a chemical treatment program including an updated chemicals control system, service and employee training provided by a qualified water treatment vendor. The annual maintenance fee charged by the water treatment vendor would be determined after an investigation of the water system is complete. These annual costs are not included in this project cost. For budgeting purposes, a $12,000 maintenance fee is suggested. | INFIRMARY/ INTAKE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 32986 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
2090ELE2 | PROVIDE CLEARANCE AT ELECTRICAL PANELS | 2090 | There are electrical panels in the building which do not have proper clear floor space around them. The 2012 IFC Section 605.3 states that, A working space of not less than 30 inches in width, 36 inches in depth and 78 inches in height shall be provided in front of electrical service equipment. Where the electrical service equipment is wider than 30 inches, the working space shall not be less than the width of the equipment. No storage of any materials shall be located within the designated working space. This project would provide funds to relocate the items currently blocking the working space. | INFIRMARY/ INTAKE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 32986 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 250
2090ELE4 | ELECTRICAL AND COMMUNICATIONS UPGRADE | 2090 | This building was constructed before the high demand for electrical services were needed for computers, communications systems and other electrical devices. As time has progressed, the buildings electrical demand and communications system has changed. The electrical system is utilized to its current maximum potential and the communications system is outdated. The electrical panels, switches and receptacles are at their limit. It is recommended to upgrade the entire electrical system and communications system to meet the evolving needs of the building. | INFIRMARY/ INTAKE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 32986 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 824650
2090INT5 | JANITORS CLOSET REPAIRS | 2090 | The mop sinks in the Janitor Closets are mounted adjacent to CMU walls and are showing signs of water damage. This project would provide FRP to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | INFIRMARY/ INTAKE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 32986 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2800
2946SFT1 | SPRINKLER HEAD REPLACEMENT | 2946 | The existing fire suppression sprinkler heads are an older style and are susceptible to damage and misuse by the inmates. Inmates have tied strings to the sprinkler heads and have broken them in the past. This project recommends that all of the fire sprinkler heads in all cells be removed and replaced with a new state of the art tamper-resistant sprinkler heads. | HOUSING UNIT #12 | 9952 | Correct | HDSP |  | Indian Springs | 2008 | 52096 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 16800
2945ELE2 | DOOR CONTROLS SYSTEM REPLACEMENT | 2945 | The control panel/ inmate movement and control system in the housing unit is not working properly. The cell door indicator lights on the control panel are falsely representing the actual status of the cell doors. The officer sometimes cannot tell if the cell door is open or closed. This project would replace the existing secured door control system with a programmable logic controlled system using touch screens for actuation and door status. This project would replace the existing door control system and the outdated wiring. Removal and disposal of the existing equipment is included in this estimate. | HOUSING UNIT #9 | 9952 | Correct | HDSP |  | Indian Springs | 2008 | 51609 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 1438241.25
2945PLM3 | CELL WATER CONTROL SYSTEMS REPLACEMENT | 2945 | This building is equipped with cell water control systems that are outdated and should be scheduled for replacement. Problems exist with the current water control systems. It is increasingly difficult to find replacement parts and experienced repairmen to service the equipment. It is recommended to replace the water control systems. This project includes the replacement of the water controllers, piping, valves, access panels and all connections to the existing utilities. | HOUSING UNIT #9 | 9952 | Correct | HDSP |  | Indian Springs | 2008 | 51609 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 504000
2945SFT3 | ROOF HATCH REPLACEMENT | 2945 | The roof hatch is original to the building and has reached the end of its useful life. The compression spring operators do not function properly, the latches and handles are worn and the seals and flashing have deteriorated. A faulty roof hatch is a safety hazard to anyone accessing the roof. This project would provide for removal and disposal of the existing roof hatch and purchase and installation of a new roof hatch. | HOUSING UNIT #9 | 9952 | Correct | HDSP |  | Indian Springs | 2008 | 51609 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 5000
2945PLM1 | FLOOR DRAIN REPAIR | 2945 | The floor drain in the building is clogged and water has pooled around it. The standing water will prematurely deteriorate the building components as well as create a slipping hazard. This project would provide for a licensed contractor to clear the drain and provide any necessary repairs to prevent future problems. | HOUSING UNIT #9 | 9952 | Correct | HDSP |  | Indian Springs | 2008 | 51609 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 2000
2091INT2 | INTERIOR FINISHES | 2091 | The Inmate Services/Culinary/Dining building has painted CMU walls. All flooring is sealed concrete and non-slip tile. It is recommended that the interior walls be painted and/or sealed at least once in the next 2-4 years. This also includes the sealing of the floor and floor tile maintenance in the kitchen and bakery area. Prior to painting or sealing, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | INMATE SERVICES/ CULINARY/ DINING | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 77005 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 770050
2086INT1 | INTERIOR FINISHES | 2086 | This project would provide funding to maintain the interior of the building. Included in the cost is painting the walls and ceilings, sealing the exposed masonry, repairing cracks in the masonry and replacing grout and caulk as needed. An epoxy-based paint should be utilized in wet areas for durability. It is recommended that the interior of the building be painted, sealed and repaired in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HOUSING UNIT #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 445000
2086EXT2 | EXTERIOR FINISHES | 2086 | It is important to maintain the finish, weather resistance and appearance of the building. The caulked control joints in the CMU of the exterior surface of this building are uniformly deteriorated and should be removed and the joints re-caulked. The metal doors and window frames should be sanded and painted on a cyclical basis. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HOUSING UNIT #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 445000
2086STR1 | WALKWAY RAILING | 2086 | The perimeter roof walkway guardrail is failing. The railing is loose or not attached and is posing a potential safety problem. This project recommends an assessment be performed by a Structural Engineer to determine the cause and provide a design solution. Future projects will be based on the design solution recommendation. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HOUSING UNIT #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 3000
2086ADA4 | ADA TABLE UPGRADE | 2086 | Per the United States Access Board and ICC ANSI-A117.1-2009, at least 5 percent of the seating spaces shall be, if fixed seating is provided, a loose seat or open space for a wheelchair. This project would provide funding to remove 3 of the fixed seats, which will allow access for wheel chairs. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HOUSING UNIT #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 3000
2945SFT2 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 2945 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT #9 | 9952 | Correct | HDSP |  | Indian Springs | 2008 | 51609 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 9000
2945SFT1 | SPRINKLER HEAD REPLACEMENT | 2945 | The existing fire suppression sprinkler heads are an older style and are susceptible to damage and misuse by the inmates. Inmates have tied strings to the sprinkler heads and have broken them in the past. This project recommends that all of the fire sprinkler heads in all cells be removed and replaced with a new state of the art tamper-resistant sprinkler heads. | HOUSING UNIT #9 | 9952 | Correct | HDSP |  | Indian Springs | 2008 | 51609 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 16800
2091INT1 | JANITORS CLOSET REPAIRS | 2091 | The mop sinks in the Janitors Closets are mounted adjacent to CMU walls and are showing signs of water damage. This project would provide FRP to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | INMATE SERVICES/ CULINARY/ DINING | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 77005 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2800
2945PLM4 | SHOWER WATER CONTROL SYSTEMS REPLACEMENT | 2945 | This building is equipped with shower water control systems that are outdated and should be scheduled for replacement. Problems exist with the current shower water control systems. It is increasingly difficult to find replacement parts and experienced repairmen to service the equipment. This project includes the replacement of the shower water controllers, piping, valves, access panels, shower heads and all connections to the existing utilities. | HOUSING UNIT #9 | 9952 | Correct | HDSP |  | Indian Springs | 2008 | 51609 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 15000
2092INT2 | JANITORS CLOSET REPAIRS | 2092 | The walls adjacent to and above the janitor's closet mop sink did not have a water resistant finish. This project recommends the installation of FRP on the walls adjacent to the mop sink to a height of 54" above the finish floor. | PROGRAM SERVICES/ EDUCATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 33652 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
2091EXT3 | ROOF REPLACEMENT | 2091 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2000. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. | INMATE SERVICES/ CULINARY/ DINING | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 77005 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1155075
2092INT3 | FLOORING REPLACEMENT | 2092 | The VCT and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the next 2-3 years. | PROGRAM SERVICES/ EDUCATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 33652 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 269216
2092ELE1 | GFCI OUTLETS | 2092 | The existing receptacle in the mechanical room is a standard duplex receptacle. The 2011 NEC 210.8 require this location to have GFCI protection. This project would provide for removing the standard receptacle and installing a GFCI receptacle. | PROGRAM SERVICES/ EDUCATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 33652 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 400
2086HVA3 | EXHAUST FAN INSTALLATION | 2086 | The mechanical room within the housing unit has plumbing fixtures and drains. Due to moisture in this room, the humidity is very high and there is an increase probability for indoor air quality concern. This project would provide for the purchase and installation of a new commercial grade exhaust fan and the assemblies and will include the connections to utilities. | HOUSING UNIT #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 10000
2086ENR1 | LIGHTING UPGRADE | 2086 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | HOUSING UNIT #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 356000
2086ADA1 | ADA SHOWER UPGRADE | 2086 | This project would provide for three ADA compliant stainless steel shower cabinets to be installed to provide shower facilities for the disabled. Included in this estimate is the installation of three stainless steel ADA compliant shower cabinet units complete with accessible plumbing fixtures, seats, etc. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | HOUSING UNIT #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 75000
2092HVA1 | HVAC EQUIPMENT REPLACEMENT | 2092 | The air handlers, fan coils and related equipment are original to the building, dating back to 2000. The equipment has consistent problems and has reached its expected life span. This project recommends replacement of the air handlers, fan coils, ventilation equipment and exhaust fans. It is recommended that this project be implemented in the next 2-3 years to avoid possible failure and emergency funding for replacement. | PROGRAM SERVICES/ EDUCATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 33652 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 504780
2092ELE2 | ELECTRICAL AND COMMUNICATIONS UPGRADE | 2092 | This building was constructed before the high demand for electrical services were needed for computers, communications systems and other electrical devices. As time has progressed, the buildings electrical demand and communications system has changed. The electrical system is utilized to its current maximum potential and the communications system is outdated. The electrical panels, switches and receptacles are at their limit. It is recommended to upgrade the entire electrical system and communications system to meet the evolving needs of the building. | PROGRAM SERVICES/ EDUCATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 33652 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 841300
2092LGT1 | ROOF REPLACEMENT | 2092 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2000. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. | PROGRAM SERVICES/ EDUCATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 33652 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 504870
2092ADA1 | ADA DOOR HARDWARE REPLACEMENT | 2092 | The 2010 ADA Standards for Accessible Design states that the force to activate operable parts shall be 5 pounds maximum. It is recommended that 5 pounds or less closers be installed on the men’s and woman’s ADA restroom doors. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and Sections 309.4 and 404.2.7 of the 2010 ADA Standards for Accessible Design were used as references for this project. | PROGRAM SERVICES/ EDUCATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 33652 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 2000
2092INT1 | INTERIOR FINISHES | 2092 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | PROGRAM SERVICES/ EDUCATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 33652 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 336520
2092PLM2 | WATER TREATMENT SYSTEM REPLACEMENT | 2092 | The existing water softening/ treatment systems in the building are currently not operational. They are original to the building and approaching the end of their lifecycles. Failure of the equipment causes wear and tear on the domestic water supply lines, plumbing fixtures and HVAC equipment. This project would provide for the replacement of the existing water softeners/ treatment systems with new equipment. This project would also provide for a chemical treatment program including an updated chemicals control system, service and employee training provided by a qualified water treatment vendor. The annual maintenance fee charged by the water treatment vendor would be determined after an investigation of the water system is complete. These annual costs are not included in this project cost. For budgeting purposes, a $12,000 maintenance fee is suggested. | PROGRAM SERVICES/ EDUCATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 33652 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
2092SFT1 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 2092 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | PROGRAM SERVICES/ EDUCATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 33652 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 9000
2092PLM1 | WATER HEATER REPLACEMENT | 2092 | There is a 40 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | PROGRAM SERVICES/ EDUCATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 33652 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
2093EXT1 | EXTERIOR FINISHES | 2093 | It is important to maintain the finish, weather resistance and appearance of the building. The caulked control joints in the CMU of the exterior surface of this building are uniformly deteriorated and should be removed and the joints re-caulked. The metal doors and window frames should be sanded and painted on a cyclical basis. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | VISITATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 11194 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 111940
2093INT1 | INTERIOR FINISHES | 2093 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | VISITATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 11194 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 111940
2093ADA1 | ADA TABLE UPGRADE | 2093 | Per the United States Access Board and ICC ANSI-A117.1-2009, at least 5 percent of the seating spaces shall be, if fixed seating is provided, a loose seat or open space for a wheelchair. This project would provide funding to remove 3 of the fixed seats, which will allow access for wheel chairs. | VISITATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 11194 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 3000
2093EXT3 | ROOF REPLACEMENT | 2093 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2000. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. | VISITATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 11194 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 134100
2093HVA1 | HVAC EQUIPMENT REPLACEMENT | 2093 | The air handlers, fan coils and related equipment are original to the building, dating back to 2000. The equipment has consistent problems and has reached its expected life span. This project recommends replacement of the air handlers, fan coils, ventilation equipment and exhaust fans. It is recommended that this project be implemented in the next 2-3 years to avoid possible failure and emergency funding for replacement. | VISITATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 11194 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 167910
2093PLM2 | WATER HEATER REPLACEMENT | 2093 | There is a 40 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | VISITATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 11194 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
2092SFT2 | FIRE ALARM SYSTEM REPLACEMENT | 2092 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and due to this the system no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | PROGRAM SERVICES/ EDUCATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 33652 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 269216
2945INT1 | INTERIOR FINISHES | 2945 | This project would provide funding to maintain the interior of the building. Included in the cost is painting the walls and ceilings, sealing the exposed masonry, repairing cracks in the masonry and replacing grout and caulk as needed. An epoxy-based paint should be utilized in wet areas for durability. It is recommended that the interior of the building be painted, sealed and repaired in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT #9 | 9952 | Correct | HDSP |  | Indian Springs | 2008 | 51609 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 516090
2095INT2 | JANITORS CLOSET REPAIRS | 2095 | The mop sink in the Janitors Closet is mounted adjacent to CMU and is showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the CMU walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | GATEHOUSE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 6165 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
2091CUL1 | DISHWASHER REPLACEMENT | 2091 | The commercial dishwashers in the kitchen appear to be original to the building and are troublesome and problematic to operate. Considering the age of the dishwashers and the evolving needs of the facility they are recommended to be replaced. This project provides for removal and disposal of the two existing dishwashers and replacement with two new units. | INMATE SERVICES/ CULINARY/ DINING | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 77005 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 350000
2086ADA3 | TDD INSTALLATION | 2086 | The Housing Unit is not equipped with a TDD. In order to comply with ADA requirements it is recommended to install a TDD system in the Housing Unit. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | HOUSING UNIT #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 60000
2086INT2 | SHOWER UPGRADE | 2086 | There are twelve shower stalls in the building that are showing signs of failure and should be scheduled for repair or replacement. This project would provide for twelve stainless steel shower cabinets to be installed to provide shower facilities for the housing units. Removal and disposal of the existing materials is included in the estimate. | HOUSING UNIT #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 300000
2086PLM3 | CELL WATER CONTROL SYSTEMS REPLACEMENT | 2086 | This building is equipped with cell water control systems that are outdated and should be scheduled for replacement. Problems exist with the current water control systems. It is increasingly difficult to find replacement parts and experienced repairmen to service the equipment. It is recommended to replace the water control systems. This project includes the replacement of the water controllers, piping, valves, access panels and all connections to the existing utilities. | HOUSING UNIT #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 504000
2086SEC2 | COMMUNICATIONS SYSTEM UPGRADE | 2086 | This building is equipped with a communications system that at the time of the survey was not working properly. The communications system provides paging, phone communications and communication to inmates. The communications system is an integral component of the notification and safety procedures for the inmates and staff. The system is problematic and replacement parts are no longer available. It is recommended that the communications system be upgraded. | HOUSING UNIT #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 222500
2945SEC1 | COMMUNICATIONS SYSTEM UPGRADE | 2945 | This building is equipped with a communications system that at the time of the survey was not working properly. The communications system provides paging, phone communications and communication to inmates. The communications system is an integral component of the notification and safety procedures for the inmates and staff. The system is problematic and replacement parts are no longer available. It is recommended that the communications system be upgraded. | HOUSING UNIT #9 | 9952 | Correct | HDSP |  | Indian Springs | 2008 | 51609 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 258045
2945ADA2 | TDD INSTALLATION | 2945 | The Housing Unit is not equipped with a TDD. In order to comply with ADA requirements it is recommended to install a TDD system in the Housing Unit. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | HOUSING UNIT #9 | 9952 | Correct | HDSP |  | Indian Springs | 2008 | 51609 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 60000
2092EXT1 | EXTERIOR FINISHES | 2092 | It is important to maintain the finish, weather resistance and appearance of the building. The caulked control joints in the CMU of the exterior surface of this building are uniformly deteriorated and should be removed and the joints re-caulked. The metal doors and window frames should be sanded and painted on a cyclical basis. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | PROGRAM SERVICES/ EDUCATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 33652 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 336520
2945ADA1 | ADA TABLE UPGRADE | 2945 | Per the United States Access Board and ICC ANSI-A117.1-2009, at least 5 percent of the seating spaces shall be, if fixed seating is provided, a loose seat or open space for a wheelchair. This project would provide funding to remove 3 of the fixed seats, which will allow access for wheel chairs. | HOUSING UNIT #9 | 9952 | Correct | HDSP |  | Indian Springs | 2008 | 51609 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 3000
2091PLM3 | WATER HEATER REPLACEMENT | 2091 | There are five electric on-demand water heaters that are 5-gallon capacity in the building. The average life span of the water heaters is eight to ten years. With the passage of time and constant use, these units are showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that 5 new 5-gallon on-demand electric water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. | INMATE SERVICES/ CULINARY/ DINING | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 77005 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12500
2945SEC2 | CELL DOORS, LOCKS AND CONTROLS REPLACEMENT | 2945 | Housing Unit 9 was constructed in 2008. The cell doors, locks and controls are original to the building and have been problematic due to inmate abuse and age. This project would provide for installing new cell doors, locks and controls. A total of 168 doors were used for this estimate. Removal and disposal of the existing equipment is included in this estimate. | HOUSING UNIT #9 | 9952 | Correct | HDSP |  | Indian Springs | 2008 | 51609 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 421875
2091SFT4 | PANIC HARDWARE IN ELECTRICAL ROOMS | 2091 | The electrical room with the uninterruptable power supply contains equipment that meets or exceeds 1,200 amps. It is recommended per the 2012 IBC 1008.1.10 that panic and fire exit hardware be installed. This equipment was not required when the building was constructed in 2000. When a remodel occurs, it is suggested to comply with current code. It is recommended that this project be completed within 1-2 years. The estimate is based on one door that requires panic hardware. | INMATE SERVICES/ CULINARY/ DINING | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 77005 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 3000
2091SFT2 | FIRE ALARM SYSTEM REPLACEMENT | 2091 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and due to this the system no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | INMATE SERVICES/ CULINARY/ DINING | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 77005 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 616040
2091ELE2 | ELECTRICAL AND COMMUNICATIONS UPGRADE | 2091 | This building was constructed before the high demand for electrical services were needed for computers, communications systems and other electrical devices. As time has progressed, the buildings electrical demand and communications system has changed. The electrical system is utilized to its current maximum potential and the communications system is outdated. The electrical panels, switches and receptacles are at their limit. It is recommended to upgrade the entire electrical system and communications system to meet the evolving needs of the building. | INMATE SERVICES/ CULINARY/ DINING | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 77005 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 1925125
2091SFT3 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 2091 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | INMATE SERVICES/ CULINARY/ DINING | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 77005 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 9000
2947SEC1 | COMMUNICATIONS SYSTEM UPGRADE | 2947 | This building is equipped with a communications system that at the time of the survey was not working properly. The communications system provides paging, phone communications and communication to inmates. The communications system is an integral component of the notification and safety procedures for the inmates and staff. The system is problematic and replacement parts are no longer available. It is recommended that the communications system be upgraded. | HOUSING UNIT #10 | 9952 | Correct | HDSP |  | Indian Springs | 2009 | 51609 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 258045
2091INT3 | FLOORING REPLACEMENT | 2091 | The tile in the building is damaged and reaching the end of its useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new culinary grade tile in the next 4-5 years. | INMATE SERVICES/ CULINARY/ DINING | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 77005 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 693045
2091PLM4 | WATER TREATMENT SYSTEM REPLACEMENT | 2091 | The existing water softening/ treatment systems in the building are currently not operational. They are original to the building and approaching the end of their lifecycles. Failure of the water softening/ treatment system causes additional wear and tear on the domestic water supply lines, water heaters and plumbing fixtures. This project would provide for the installation of a PRV (to be installed prior to the water softener/ treatment system) and the replacement of the existing water softeners/ treatment systems with new equipment. This project would also provide for a chemical treatment program to include an updated chemical control system, service and employee training to be provided by a qualified water treatment vendor. The annual maintenance fee charged by the water treatment vendor would be determined after an investigation of the water system is complete. These annual costs are not included in this project cost. For budgeting purposes, a $12,000 fee is suggested. | INMATE SERVICES/ CULINARY/ DINING | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 77005 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
2091ADA1 | ADA TABLE UPGRADE | 2091 | Per the United States Access Board Section 226.1 where dining surfaces are provided for the consumption of food or drink, at least 5 percent of the seating spaces and standing spaces at the dining surfaces shall comply with 902. ICC ANSI-A117.1-2009 Section 902 which says, if fixed seating is provided, a loose seat or open space for a wheelchair location must be available at those accessible tables. This project would provide funding to remove 4 of the fixed seats, which will allow access for seven wheel chairs. | INMATE SERVICES/ CULINARY/ DINING | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 77005 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 7000
2945PLM5 | COMPUTER WATER CONTROL SYSTEM REPLACEMENT | 2945 | This building is equipped with a computer water control system that is outdated and should be scheduled for replacement. Problems exist with the current computer water control system. It is increasingly difficult to find software updates and experienced repairmen to service the equipment. This project recommends the installation of a new computer water control system for the building. This system will monitor and control the water for all fixtures throughout the building. New electronic sensors will be installed on each water control system. | HOUSING UNIT #9 | 9952 | Correct | HDSP |  | Indian Springs | 2008 | 51609 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 50000
2099SEC2 | CELL DOORS, LOCKS AND CONTROLS REPLACEMENT | 2099 | Security/ Administration was constructed in 2000. The cell doors, locks and controls are original to the building and have been problematic due to inmate abuse and age. This project would provide for installing new cell doors, locks and controls. A total square footage of 13,241 was used for this estimate. Removal and disposal of the existing equipment is included in this estimate. | SECURITY/ ADMINISTRATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 13241 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 125790
2099EXT1 | EXTERIOR FINISHES | 2099 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | SECURITY/ ADMINISTRATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 13241 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 132410
2099PLM1 | WATER HEATER REPLACEMENT | 2099 | There is a 50 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 4-5 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | SECURITY/ ADMINISTRATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 13241 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 1500
2099SFT2 | FIRE ALARM SYSTEM REPLACEMENT | 2099 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and due to this, the system no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | SECURITY/ ADMINISTRATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 13241 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 105928
2099INT2 | JANITORS CLOSET REPAIRS | 2099 | The mop sink in the Janitors Closet is mounted adjacent to CMU and is showing signs of water damage. This project would provide FRP to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | SECURITY/ ADMINISTRATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 13241 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
2099ENR1 | LIGHTING UPGRADE | 2099 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | SECURITY/ ADMINISTRATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 13241 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 105928
2099HVA1 | HVAC EQUIPMENT REPLACEMENT | 2099 | The air handlers, fan coils and related equipment are original to the building, dating back to 2000. The equipment has consistent problems and has reached its expected life span. This project recommends replacement of the air handlers, fan coils, ventilation equipment and exhaust fans. It is recommended that this project be implemented in the next 2-3 years to avoid possible failure and emergency funding for replacement. | SECURITY/ ADMINISTRATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 13241 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 198615
2099SEC1 | DOORS CONTROL SYSTEM REPLACEMENT | 2099 | The control panel/ inmate movement and control system in the Security/ Administration is not working properly. The cell door indicator lights on the control panel are falsely representing the actual status of the cell doors. The officer sometimes cannot tell if the cell door is open or closed. This project would replace the existing secured door control system with a programmable logic controlled system using touch screens for actuation and door status. This project would replace the existing door control system and the outdated wiring. Removal and disposal of the existing equipment is included in this estimate. | SECURITY/ ADMINISTRATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 13241 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 423712
2099SFT3 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 2099 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SECURITY/ ADMINISTRATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 13241 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 9000
2100SFT2 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 2100 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | TOWER #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 9000
2099ELE1 | ELECTRICAL TRANSFORMER REPLACEMENT | 2099 | The 45 kVA electrical transformer that provides services to the building was damaged at the time of inspection and does not function properly. This project recommends replacing the electrical transformer. | SECURITY/ ADMINISTRATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 13241 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
2088EXT2 | ROOF REPLACEMENT | 2088 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2000. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. | HOUSING UNIT #4 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 667500
2100EXT0 | EXTERIOR FINISHES | 2100 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming, painting the metal panels and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended to paint the building in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | TOWER #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4550
2100INT1 | INTERIOR FINISHES | 2100 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | TOWER #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4550
2100ENR2 | CONDENSER DUCTING | 2100 | The condensing unit located in the middle level of the tower is missing the duct from the outside air intake louver to the condensing unit. This may be a cause for the overheating of the unit. This project would provide for replacing this missing duct and associated connections. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | TOWER #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
2100ENR3 | LIGHTING UPGRADE | 2100 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate | TOWER #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3640
2100EXT1 | SLIDING GLASS DOOR REPLACEMENT | 2100 | The sliding glass door is damaged from age and general wear and tear and has reached the end of its expected life. This project would provide for the replacement of the sliding glass door assembly with a new door, frame and hardware. Removal and disposal of the existing door is included in this estimate. | TOWER #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 2500
2100SFT1 | FIRE ALARM SYSTEM REPLACEMENT | 2100 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and due to this, the system no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | TOWER #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 3640
2100HVA1 | HVAC EQUIPMENT REPLACEMENT | 2100 | The HVAC unit was installed in 2000 and is not energy efficient. It has reached the end of its expected and useful life. This project would provide for the installation of a new HVAC unit and cleaning of the existing duct work and grilles. This project includes the removal and the disposal of the existing equipment and all required connections to the utilities. | TOWER #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11375
2100INT2 | FLOORING REPLACEMENT | 2100 | The VCT flooring in the tower is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. | TOWER #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4095
2946PLM3 | CELL WATER CONTROL SYSTEMS REPLACEMENT | 2946 | This building is equipped with cell water control systems that are outdated and should be scheduled for replacement. Problems exist with the current water control systems. It is increasingly difficult to find replacement parts and experienced repairmen to service the equipment. It is recommended to replace the water control systems. This project includes the replacement of the water controllers, piping, valves, access panels and all connections to the existing utilities. | HOUSING UNIT #12 | 9952 | Correct | HDSP |  | Indian Springs | 2008 | 52096 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 504000
2099ELE2 | ELECTRICAL AND COMMUNICATIONS UPGRADE | 2099 | This building was constructed before the high demand for electrical services were needed for computers, communications systems and other electrical devices. As time has progressed, the buildings electrical demand and communications system has changed. The electrical system is utilized to its current maximum potential and the communications system is outdated. The electrical panels, switches and receptacles are at their limit. It is recommended to upgrade the entire electrical system and communications system to meet the evolving needs of the building. | SECURITY/ ADMINISTRATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 13241 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 331025
2946PLM4 | SHOWER WATER CONTROL SYSTEMS REPLACEMENT | 2946 | This building is equipped with shower water control systems that are outdated and should be scheduled for replacement. Problems exist with the current shower water control systems. It is increasingly difficult to find replacement parts and experienced repairmen to service the equipment. This project includes the replacement of the shower water controllers, piping, valves, access panels, shower heads and all connections to the existing utilities. | HOUSING UNIT #12 | 9952 | Correct | HDSP |  | Indian Springs | 2008 | 52096 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 15000
2097HVA2 | BOILER BURNER REPLACEMENT | 2097 | The burners on the boilers were not working correctly at the time of the survey. This project recommends replacing all 6 boiler burners with energy-efficient boiler burners. This project would provide for the labor and materials to install 6 new boiler burners. | MAINTENANCE/ CENTRAL PLANT | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 30151 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 670000.02
2098EXT2 | EXTERIOR FINISHES | 2098 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | ARMORY/ EMERGENCY RESPONSE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 3405 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 34050
2098INT1 | INTERIOR FINISHES | 2098 | It is recommended that the interior walls and floors be painted or sealed at least once in the next 2-3 years. Prior to painting or sealing, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | ARMORY/ EMERGENCY RESPONSE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 3405 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 34050
2098PLM2 | WATER TREATMENT SYSTEM REPLACEMENT | 2098 | The existing water softening/ treatment systems in the building are currently not operational. They are original to the building and approaching the end of their lifecycles. Failure of the equipment causes wear and tear on the domestic water supply lines, plumbing fixtures and HVAC equipment. This project would provide for the replacement of the existing water softeners/ treatment systems with new equipment. This project would also provide for a chemical treatment program including an updated chemicals control system, service and employee training provided by a qualified water treatment vendor. The annual maintenance fee charged by the water treatment vendor would be determined after an investigation of the water system is complete. These annual costs are not included in this project cost. For budgeting purposes, a $12,000 maintenance fee is suggested. | ARMORY/ EMERGENCY RESPONSE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 3405 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 25000
2098SFT2 | FIRE ALARM SYSTEM REPLACEMENT | 2098 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and due to this, the system no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | ARMORY/ EMERGENCY RESPONSE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 3405 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 27240
2098ADA1 | BREAK ROOM REMODEL | 2098 | The kitchenette and associated cabinets in the employee break room are original to the building. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and countertops are delaminating and failing. This project recommends the replacement of the existing kitchen countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards for Accessible Design should be incorporated into the design such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. | ARMORY/ EMERGENCY RESPONSE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 3405 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 15000
2098SFT3 | BACKFLOW PREVENTER REPLACEMENT | 2098 | There is a backflow preventer for the fire suppression system in the building. It is leaking and should be scheduled for replacement. At the time of the survey the staff indicated they have rebuilt the backflow preventer several times, however it continues to leak. This project would provide for replacing the backflow preventer by a licensed fire suppression contractor. | ARMORY/ EMERGENCY RESPONSE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 3405 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 5000
2098ELE1 | ELECTRICAL TRANSFORMER REPLACEMENT | 2098 | The 30 kVA electrical transformer that provides services to the building was damaged at the time of inspection and does not function properly. This project recommends replacing the electrical transformer. | ARMORY/ EMERGENCY RESPONSE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 3405 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
2098HVA1 | HVAC EQUIPMENT REPLACEMENT | 2098 | The air handlers, fan coils and related HVAC equipment are original to the building, dating back to 2000. At the time of the survey the HVAC equipment was not working and the staff had indicated that it was very problematic and they had abandon the system and installed a mini split for the office location within the building. The equipment has reached its expected life span. This project recommends replacement of all the air handlers, fan coils, ventilation and related HVAC equipment and exhaust fans. It is recommended that this project be implemented in the next year. | ARMORY/ EMERGENCY RESPONSE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 3405 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 46600
2099INT1 | INTERIOR FINISHES | 2099 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | SECURITY/ ADMINISTRATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 13241 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 132410
2946PLM1 | FLOOR DRAIN REPAIR | 2946 | The floor drain in the building is clogged and water has pooled around it. The standing water will prematurely deteriorate the building components as well as create a slipping hazard. This project would provide for a licensed contractor to clear the drain and provide any necessary repairs to prevent future problems. | HOUSING UNIT #12 | 9952 | Correct | HDSP |  | Indian Springs | 2008 | 52096 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 2000
2088SFT2 | SPRINKLER HEAD REPLACEMENT | 2088 | The existing fire suppression sprinkler heads are an older style and are susceptible to damage and misuse by the inmates. Inmates have tied strings to the sprinkler heads and have broken them in the past. This project recommends that all of the fire sprinkler heads in all cells be removed and replaced with a new state of the art tamper-resistant sprinkler heads. | HOUSING UNIT #4 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 40000
2095SFT3 | FIRE ALARM SYSTEM REPLACEMENT | 2095 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and due to this, the system no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | GATEHOUSE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 6165 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 1536
2946SEC2 | CELL DOORS, LOCKS AND CONTROLS REPLACEMENT | 2946 | Housing Unit 12 was constructed in 2008. The cell doors, locks and controls are original to the building and have been problematic due to inmate abuse and age. This project would provide for installing new cell doors, locks and controls. A total of 168 doors were used for this estimate. Removal and disposal of the existing equipment is included in this estimate. | HOUSING UNIT #12 | 9952 | Correct | HDSP |  | Indian Springs | 2008 | 52096 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 421875
2946SEC1 | COMMUNICATIONS SYSTEM UPGRADE | 2946 | This building is equipped with a communications system that at the time of the survey was not working properly. The communications system provides paging, phone communications and communication to inmates. The communications system is an integral component of the notification and safety procedures for the inmates and staff. The system is problematic and replacement parts are no longer available. It is recommended that the communications system be upgraded. | HOUSING UNIT #12 | 9952 | Correct | HDSP |  | Indian Springs | 2008 | 52096 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 258045
2098ELE2 | ELECTRICAL AND COMMUNICATIONS UPGRADE | 2098 | This building was constructed before the high demand for electrical services were needed for computers, communications systems and other electrical devices. As time has progressed, the buildings electrical demand and communications system has changed. The electrical system is utilized to its current maximum potential and the communications system is outdated. The electrical panels, switches and receptacles are at their limit. It is recommended to upgrade the entire electrical system and communications system to meet the evolving needs of the building. | ARMORY/ EMERGENCY RESPONSE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 3405 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 85125
2098SFT4 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 2098 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | ARMORY/ EMERGENCY RESPONSE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 3405 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 9000
2098PLM1 | WATER HEATER REPLACEMENT | 2098 | There is a 50 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 4-5 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | ARMORY/ EMERGENCY RESPONSE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 3405 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 1500
2099LGT1 | ROOF REPLACEMENT | 2099 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2000. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. | SECURITY/ ADMINISTRATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 13241 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 198615
2088PLM4 | COMPUTER WATER CONTROL SYSTEM REPLACEMENT | 2088 | This building is equipped with a computer water control system that is outdated and should be scheduled for replacement. Problems exist with the current computer water control system. It is increasingly difficult to find software updates and experienced repairmen to service the equipment. This project recommends the installation of a new computer water control system for the building. This system will monitor and control the water for all fixtures throughout the building. New electronic sensors will be installed on each water control system. | HOUSING UNIT #4 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
2100SFT3 | BACKFLOW PREVENTER REPLACEMENT | 2100 | There is a backflow preventer for the fire suppression system in the building. It is leaking and should be scheduled for replacement. At the time of the survey the staff indicated they have rebuilt the backflow preventer several times, however it continues to leak. This project would provide for replacing the backflow preventer by a licensed fire suppression contractor. | TOWER #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 5000
2098EXT3 | ROOF REPLACEMENT | 2098 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2000. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. | ARMORY/ EMERGENCY RESPONSE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 3405 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 51075
2507ELE1 | ELECTRICAL AND COMMUNICATIONS UPGRADE | 2507 | This building was constructed before the high demand for electrical services were needed for computers, communications systems and other electrical devices. As time has progressed, the buildings electrical demand and communications system has changed. The electrical system is utilized to its current maximum potential and the communications system is outdated. The electrical panels, switches and receptacles are at their limit. It is recommended to upgrade the entire electrical system and communications system to meet the evolving needs of the building. | PRISON INDUSTRIES | 9952 | Correct | HDSP |  | Indian Springs | 2004 | 60000 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 900000
2102ENR2 | CONDENSER DUCTING | 2102 | The condensing unit located in the middle level of the tower is missing the duct from the outside air intake louver to the condensing unit. This may be a cause for the overheating of the unit. This project would provide for replacing this missing duct and associated connections. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | TOWER #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
2102PLM1 | WATER HEATER REPLACEMENT | 2102 | There is an on-demand electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new on-demand electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | TOWER #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
2088SEC4 | DOOR CONTROLS SYSTEM REPLACEMENT | 2088 | The control panel/ inmate movement and control system in the housing unit is not working properly. The cell door indicator lights on the control panel are falsely representing the actual status of the cell doors. The officer sometimes cannot tell if the cell door is open or closed. This project would replace the existing secured door control system with a programmable logic controlled system using touch screens for actuation and door status. This project would replace the existing door control system and the outdated wiring. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HOUSING UNIT #4 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 1438241.25
2507EXT2 | ROOF REPLACEMENT | 2507 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2004. It is recommended that this building be re-roofed in the next 6-7 years to be consistent with the roofing program and the end of the warranty period. | PRISON INDUSTRIES | 9952 | Correct | HDSP |  | Indian Springs | 2004 | 60000 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 720000
2507INT1 | INTERIOR FINISHES | 2507 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | PRISON INDUSTRIES | 9952 | Correct | HDSP |  | Indian Springs | 2004 | 60000 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 600000
2507SFT2 | FIRE ALARM SYSTEM REPLACEMENT | 2507 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and due to this the system no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | PRISON INDUSTRIES | 9952 | Correct | HDSP |  | Indian Springs | 2004 | 60000 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 480000
2507PLM0 | WATER HEATER REPLACEMENT | 2507 | There are six 30 gallon electric water heaters in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, these units are showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that new electric water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. | PRISON INDUSTRIES | 9952 | Correct | HDSP |  | Indian Springs | 2004 | 60000 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
2507ENR1 | LIGHTING UPGRADE | 2507 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | PRISON INDUSTRIES | 9952 | Correct | HDSP |  | Indian Springs | 2004 | 60000 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 480000
2100SFT5 | DOORS, LOCKS AND CONTROLS REPLACEMENT | 2100 | Tower #1 was constructed in 2000. The doors, locks and controls are original to the building and have been problematic due to age. This project would provide for installing new doors, locks and controls. Removal and disposal of the existing equipment is included in this estimate. | TOWER #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
2507EXT1 | EXTERIOR FINISHES | 2507 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete walls, painting the doors and trim and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | PRISON INDUSTRIES | 9952 | Correct | HDSP |  | Indian Springs | 2004 | 60000 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 600000
2101SEC1 | DOORS, LOCKS AND CONTROLS REPLACEMENT | 2101 | Tower #2 was constructed in 2000. The doors, locks and controls are original to the building and have been problematic due to age. This project would provide for installing new doors, locks and controls. Removal and disposal of the existing equipment is included in this estimate. | TOWER #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
2946EXT1 | EXTERIOR FINISHES | 2946 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT #12 | 9952 | Correct | HDSP |  | Indian Springs | 2008 | 52096 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 516090
2507HVA1 | HVAC EQUIPMENT REPLACEMENT | 2507 | The air handlers, fan coils and related equipment are original to the building, dating back to 2004. The equipment has consistent problems and has reached its expected life span. This project recommends replacement of the air handlers, fan coils, ventilation equipment and exhaust fans. It is recommended that this project be implemented in the next 6-7 years to avoid possible failure and emergency funding for replacement. | PRISON INDUSTRIES | 9952 | Correct | HDSP |  | Indian Springs | 2004 | 60000 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 900000
2947PLM3 | CELL WATER CONTROL SYSTEMS REPLACEMENT | 2947 | This building is equipped with cell water control systems that are outdated and should be scheduled for replacement. Problems exist with the current water control systems. It is increasingly difficult to find replacement parts and experienced repairmen to service the equipment. It is recommended to replace the water control systems. This project includes the replacement of the water controllers, piping, valves, access panels and all connections to the existing utilities. | HOUSING UNIT #10 | 9952 | Correct | HDSP |  | Indian Springs | 2009 | 51609 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 504000
2947SFT1 | SPRINKLER HEAD REPLACEMENT | 2947 | The existing fire suppression sprinkler heads are an older style and are susceptible to damage and misuse by the inmates. Inmates have tied strings to the sprinkler heads and have broken them in the past. This project recommends that all of the fire sprinkler heads in all cells be removed and replaced with a new state of the art tamper-resistant sprinkler heads. | HOUSING UNIT #10 | 9952 | Correct | HDSP |  | Indian Springs | 2009 | 51609 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 16800
2947SFT2 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 2947 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT #10 | 9952 | Correct | HDSP |  | Indian Springs | 2009 | 51609 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 9000
2947ADA1 | ADA TABLE UPGRADE | 2947 | Per the United States Access Board and ICC ANSI-A117.1-2009, at least 5 percent of the seating spaces shall be, if fixed seating is provided, a loose seat or open space for a wheelchair. This project would provide funding to remove 3 of the fixed seats, which will allow access for wheel chairs. | HOUSING UNIT #10 | 9952 | Correct | HDSP |  | Indian Springs | 2009 | 51609 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 3000
2947ENR1 | LIGHTING UPGRADE | 2947 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | HOUSING UNIT #10 | 9952 | Correct | HDSP |  | Indian Springs | 2009 | 51609 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 412872
2947INT1 | INTERIOR FINISHES | 2947 | This project would provide funding to maintain the interior of the building. Included in the cost is painting the walls and ceilings, sealing the exposed masonry, repairing cracks in the masonry and replacing grout and caulk as needed. An epoxy-based paint should be utilized in wet areas for durability. It is recommended that the interior of the building be painted, sealed and repaired in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT #10 | 9952 | Correct | HDSP |  | Indian Springs | 2009 | 51609 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 516090
2947ADA2 | TDD INSTALLATION | 2947 | The Housing Unit is not equipped with a TDD. In order to comply with ADA requirements it is recommended to install a TDD system in the Housing Unit. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | HOUSING UNIT #10 | 9952 | Correct | HDSP |  | Indian Springs | 2009 | 51609 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 60000
2507SFT3 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 2507 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | PRISON INDUSTRIES | 9952 | Correct | HDSP |  | Indian Springs | 2004 | 60000 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 9000
2101HVA1 | HVAC EQUIPMENT REPLACEMENT | 2101 | The HVAC unit was installed in 2000 and is not energy efficient. It has reached the end of its expected and useful life. This project would provide for the installation of a new HVAC unit and cleaning of the existing duct work and grilles. This project includes the removal and the disposal of the existing equipment and all required connections to the utilities. | TOWER #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11375
2100PLM1 | WATER HEATER REPLACEMENT | 2100 | There is an on-demand electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new on-demand electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | TOWER #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
2100EXT2 | WINDOW REPLACEMENT | 2100 | The existing windows in this building are of single pane wire mesh construction. They are not energy efficient. This project would provide for the removal and replacement of the windows with new dual pane security rated windows. | TOWER #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 19200
2100SFT4 | EGRESS LIGHTING REPLACEMENT | 2100 | The building does not currently have exit signs and emergency egress lighting is insufficient. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC 2012 Chapter 10 was referenced for this project. | TOWER #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 1000
2101EXT1 | EXTERIOR FINISHES | 2101 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming, painting the metal panels and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended to paint the building in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | TOWER #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4550
2101INT1 | INTERIOR FINISHES | 2101 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | TOWER #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4550
2101ENR2 | CONDENSER DUCTING | 2101 | The condensing unit located in the middle level of the tower is missing the duct from the outside air intake louver to the condensing unit. This may be a cause for the overheating of the unit. This project would provide for replacing this missing duct and associated connections. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | TOWER #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
2101EXT2 | WINDOW REPLACEMENT | 2101 | The existing windows in this building are of single pane wire mesh construction. They are not energy efficient. This project would provide for the removal and replacement of the windows with new dual pane security rated windows. | TOWER #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 19200
2088HVA1 | EXHAUST FAN INSTALLATION | 2088 | The mechanical room within the housing unit has plumbing fixtures and drains. Due to moisture in this room, the humidity is very high and there is an increase probability for indoor air quality concern. This project would provide for the purchase and installation of a new commercial grade exhaust fan and the assemblies and will include the connections to utilities. | HOUSING UNIT #4 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 10000
2088SEC3 | CELL DOORS, LOCKS AND CONTROLS REPLACEMENT | 2088 | The Housing Unit was constructed in 2000. The cell doors, locks and controls are original to the building and have been problematic due to inmate abuse and age. This project would provide for installing new cell doors, locks and controls. Removal and disposal of the existing equipment is included in this estimate. | HOUSING UNIT #4 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 421875
2102INT1 | INTERIOR FINISHES | 2102 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | TOWER #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4550
2088HVA3 | EVAPORATIVE COOLER REPLACEMENT | 2088 | There is a guard stationed on the roof to look out onto the yard. They have one overhead swamp cooler to keep them cool in the warmer months. At the time of the survey the swamp cooler was not working. It is severely scaled and has reached the end of its useful and expected life. This project would provide for a new evaporative cooler to be installed including all required connections to utilities. The estimate includes removal and disposal of the old cooler. | HOUSING UNIT #4 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 4000
2102EXT1 | EXTERIOR FINISHES | 2102 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming, painting the metal panels and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended to paint the building in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | TOWER #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4550
2101SFT4 | EGRESS LIGHTING REPLACEMENT | 2101 | There are older emergency egress lighting units in this building. These units have a finite lifespan, and this project recommends their replacement with new egress lights, and to also provide additional lights on the main exit routes and in individual rooms as needed. | TOWER #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 1000
2101PLM1 | WATER HEATER REPLACEMENT | 2101 | There is an on-demand electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new on-demand electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | TOWER #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
2101SFT3 | BACKFLOW PREVENTER REPLACEMENT | 2101 | There is a backflow preventer for the fire suppression system in the building. It is leaking and should be scheduled for replacement. At the time of the survey the staff indicated they have rebuilt the backflow preventer several times, however it continues to leak. This project would provide for replacing the backflow preventer by a licensed fire suppression contractor. | TOWER #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 5000
2101SFT2 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 2101 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | TOWER #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 9000
2101INT2 | FLOORING REPLACEMENT | 2101 | The VCT flooring in the tower is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. | TOWER #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4095
2101ENR3 | LIGHTING UPGRADE | 2101 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | TOWER #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3640
2101SFT1 | FIRE ALARM SYSTEM REPLACEMENT | 2101 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and due to this, the system no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | TOWER #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 3640
2101EXT3 | SLIDING GLASS DOOR REPLACEMENT | 2101 | The sliding glass door is damaged from age and general wear and tear and has reached the end of its expected life. This project would provide for the replacement of the sliding glass door assembly with a new door, frame and hardware. Removal and disposal of the existing door is included in this estimate. | TOWER #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 2500
2097PLM3 | WATER HEATER REPLACEMENT | 2097 | There is a 30 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | MAINTENANCE/ CENTRAL PLANT | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 30151 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
2088ADA4 | ADA SHOWER UPGRADE | 2088 | This project would provide for three ADA compliant stainless steel shower cabinets to be installed to provide shower facilities for the disabled. Included in this estimate is the installation of three stainless steel ADA compliant shower cabinet units complete with accessible plumbing fixtures, seats, etc. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | HOUSING UNIT #4 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 75000
2948SEC2 | CELL DOORS, LOCKS AND CONTROLS REPLACEMENT | 2948 | Housing Unit 11 was constructed in 2009. The cell doors, locks and controls are original to the building and have been problematic due to inmate abuse and age. This project would provide for installing new cell doors, locks and controls. A total of 168 doors were used for this estimate. Removal and disposal of the existing equipment is included in this estimate. | HOUSING UNIT #11 | 9952 | Correct | HDSP |  | Indian Springs | 2009 | 51609 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 421875
2088INT2 | SHOWER UPGRADE | 2088 | There are twelve shower stalls in the building that are showing signs of failure and should be scheduled for repair or replacement. This project would provide for twelve stainless steel shower cabinets to be installed to provide shower facilities for the housing units. Removal and disposal of the existing materials is included in the estimate. | HOUSING UNIT #4 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 300000
2088ADA2 | TDD INSTALLATION | 2088 | The Housing Unit is not equipped with a TDD. In order to comply with ADA requirements it is recommended to install a TDD system in the Housing Unit. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | HOUSING UNIT #4 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 60000
2088ADA1 | ADA TABLE UPGRADE | 2088 | Per the United States Access Board and ICC ANSI-A117.1-2009, at least 5 percent of the seating spaces shall be, if fixed seating is provided, a loose seat or open space for a wheelchair. This project would provide funding to remove 3 of the fixed seats, which will allow access for wheel chairs. | HOUSING UNIT #4 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 3000
2088PLM2 | CELL WATER CONTROL SYSTEMS REPLACEMENT | 2088 | This building is equipped with cell water control systems that are outdated and should be scheduled for replacement. Problems exist with the current water control systems. It is increasingly difficult to find replacement parts and experienced repairmen to service the equipment. It is recommended to replace the water control systems. This project includes the replacement of the water controllers, piping, valves, access panels and all connections to the existing utilities. | HOUSING UNIT #4 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 504000
2088PLM3 | SHOWER WATER CONTROL SYSTEMS REPLACEMENT | 2088 | The showers do not have water control systems in place. It is recommended to install new water control systems within the next 2-3 years. Installing water control systems will reduce the water usage in the building. This project includes the installation of new water controllers, piping, valves, access panels, shower heads and all connections to the existing utilities. | HOUSING UNIT #4 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
2948ENR1 | LIGHTING UPGRADE | 2948 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | HOUSING UNIT #11 | 9952 | Correct | HDSP |  | Indian Springs | 2009 | 51609 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 412872
2948SFT2 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 2948 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT #11 | 9952 | Correct | HDSP |  | Indian Springs | 2009 | 51609 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 9000
2948SFT1 | SPRINKLER HEAD REPLACEMENT | 2948 | The existing fire suppression sprinkler heads are an older style and are susceptible to damage and misuse by the inmates. Inmates have tied strings to the sprinkler heads and have broken them in the past. This project recommends that all of the fire sprinkler heads in all cells be removed and replaced with a new state of the art tamper-resistant sprinkler heads. | HOUSING UNIT #11 | 9952 | Correct | HDSP |  | Indian Springs | 2009 | 51609 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 16800
2097INT2 | JANITORS CLOSET REPAIRS | 2097 | The mop sink in the Janitors Closet is mounted adjacent to CMU and is showing signs of water damage. This project would provide FRP to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | MAINTENANCE/ CENTRAL PLANT | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 30151 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
2948INT1 | INTERIOR FINISHES | 2948 | This project would provide funding to maintain the interior of the building. Included in the cost is painting the walls and ceilings, sealing the exposed masonry, repairing cracks in the masonry and replacing grout and caulk as needed. An epoxy-based paint should be utilized in wet areas for durability. It is recommended that the interior of the building be painted, sealed and repaired in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT #11 | 9952 | Correct | HDSP |  | Indian Springs | 2009 | 51609 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 516090
2946HVA1 | EXHAUST FAN INSTALLATION | 2946 | The mechanical room within the housing unit has plumbing fixtures and drains. Due to moisture in this room, the humidity is very high and there is an increase probability for indoor air quality concern. This project would provide for the purchase and installation of a new commercial grade exhaust fan and the assemblies and will include the connections to utilities. | HOUSING UNIT #12 | 9952 | Correct | HDSP |  | Indian Springs | 2008 | 52096 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 10000
2948ELE2 | DOOR CONTROLS SYSTEM REPLACEMENT | 2948 | The control panel/ inmate movement and control system in the housing unit is not working properly. The cell door indicator lights on the control panel are falsely representing the actual status of the cell doors. The officer sometimes cannot tell if the cell door is open or closed. This project would replace the existing secured door control system with a programmable logic controlled system using touch screens for actuation and door status. This project would replace the existing door control system and the outdated wiring. Removal and disposal of the existing equipment is included in this estimate. | HOUSING UNIT #11 | 9952 | Correct | HDSP |  | Indian Springs | 2009 | 51609 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 1438241.25
2096INT1 | INTERIOR FINISHES | 2096 | It is recommended that the interior walls and floors be painted or sealed at least once in the next 2-3 years. Prior to painting or sealing, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | SALLYPORT | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 192 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1920
2096EXT1 | EXTERIOR FINISHES | 2096 | It is important to maintain the finish, weather resistance and appearance of the building. The metal exterior, doors and window frames should be sanded and painted on a cyclical basis. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | SALLYPORT | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 192 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1920
2096ELE2 | ELECTRICAL AND COMMUNICATIONS UPGRADE | 2096 | This building was constructed before the high demand for electrical services were needed for computers, communications systems and other electrical devices. As time has progressed, the buildings electrical demand and communications system has changed. The electrical system is utilized to its current maximum potential and the communications system is outdated. The electrical panels, switches and receptacles are at their limit. It is recommended to upgrade the entire electrical system and communications system to meet the evolving needs of the building. | SALLYPORT | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 192 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 4800
2096SFT3 | FIRE ALARM SYSTEM REPLACEMENT | 2096 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and due to this, the system no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | SALLYPORT | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 192 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 1536
2096ENR1 | LIGHTING UPGRADE | 2096 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | SALLYPORT | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 192 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1536
2097ENR2 | ENERGY MANAGEMENT SYSTEM INSTALLATION | 2097 | The Snider energy management system is original to the building and should be scheduled for replacement. Replacement parts for performing routine and emergency maintenance are not made any more. The system has had numerous failures and the staff no longer has some monitoring capabilities. In a facility of this type, it is imperative that the conditioned spaces are properly controlled at all times. This project would provide for the removal and disposal of the existing energy management system and replacement with new equipment including all required connections to utilities and equipment. | MAINTENANCE/ CENTRAL PLANT | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 30151 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
2096SFT1 | EXIT SIGN AND EGRESS LIGHTING INSTALLATION | 2096 | The building does not have emergency lighting or exit signs. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC 2012 Chapter 10 was referenced for this project. | SALLYPORT | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 192 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 960
2948ADA1 | ADA TABLE UPGRADE | 2948 | Per the United States Access Board and ICC ANSI-A117.1-2009, at least 5 percent of the seating spaces shall be, if fixed seating is provided, a loose seat or open space for a wheelchair. This project would provide funding to remove 3 of the fixed seats, which will allow access for wheel chairs. | HOUSING UNIT #11 | 9952 | Correct | HDSP |  | Indian Springs | 2009 | 51609 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 3000
2506EXT1 | EXTERIOR FINISHES | 2506 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete walls, painting the doors and trim and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | GYMNASIUM | 9952 | Correct | HDSP |  | Indian Springs | 2004 | 14620 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 146200
2948ADA2 | TDD INSTALLATION | 2948 | The Housing Unit is not equipped with a TDD. In order to comply with ADA requirements it is recommended to install a TDD system in the Housing Unit. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | HOUSING UNIT #11 | 9952 | Correct | HDSP |  | Indian Springs | 2009 | 51609 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 60000
2089ADA1 | ADA TABLE UPGRADE | 2089 | Per the United States Access Board and ICC ANSI-A117.1-2009, at least 5 percent of the seating spaces shall be, if fixed seating is provided, a loose seat or open space for a wheelchair. This project would provide funding to remove 3 of the fixed seats, which will allow access for wheel chairs. | HOUSING UNIT #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 3000
2089ADA2 | TDD INSTALLATION | 2089 | The Housing Unit is not equipped with a TDD. In order to comply with ADA requirements it is recommended to install a TDD system in the Housing Unit. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | HOUSING UNIT #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 60000
2088SFT3 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 2088 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT #4 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 9000
2088INT3 | JANITORS CLOSET REPAIRS | 2088 | The mop sink in the Janitors Closet is mounted adjacent to CMU and is showing signs of water damage. This project would provide FRP to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | HOUSING UNIT #4 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
2088SFT5 | ELECTRICAL OUTLET & CABLE UPGRADES | 2088 | At the time of the survey the building had residential and commercial cover plates over the electrical outlets and coaxial wires. This poses a safety hazard allowing inmates to remove them and use them as weapons. This could be a safety hazard to inmates and guards. This project would provide for the installation of new security grade cover plates throughout the entire housing unit. | HOUSING UNIT #4 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 74592
2089INT1 | INTERIOR FINISHES | 2089 | The interior finishes are in fair condition. It is recommended that the interior walls and floors be painted or sealed at least once in the next four to six years. Prior to painting or sealing, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HOUSING UNIT #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 445000
2089STR1 | WALKWAY RAILING | 2089 | The perimeter roof walkway guardrail is failing. The railing is loose or not attached and is posing a potential safety problem. This project recommends an assessment be performed by a Structural Engineer to determine the cause and provide a design solution. Future projects will be based on the design solution recommendation. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HOUSING UNIT #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 3000
2088SEC2 | COMMUNICATIONS SYSTEM UPGRADE | 2088 | This building is equipped with a communications system that at the time of the survey was not working properly. The communications system provides paging, phone communications and communication to inmates. The communications system is an integral component of the notification and safety procedures for the inmates and staff. The system is problematic and replacement parts are no longer available. It is recommended that the communications system be upgraded. | HOUSING UNIT #4 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 222500
2088ENR1 | LIGHTING UPGRADE | 2088 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | HOUSING UNIT #4 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 356000
2946INT1 | INTERIOR FINISHES | 2946 | This project would provide funding to maintain the interior of the building. Included in the cost is painting the walls and ceilings, sealing the exposed masonry, repairing cracks in the masonry and replacing grout and caulk as needed. An epoxy-based paint should be utilized in wet areas for durability. It is recommended that the interior of the building be painted, sealed and repaired in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT #12 | 9952 | Correct | HDSP |  | Indian Springs | 2008 | 52096 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 516090
2507SFT1 | INSTALL EMERGENCY EGRESS LIGHTING | 2507 | There is no emergency egress lighting in the warehouse sections. This project would provide for the purchase and installation of emergency egress lighting in each section. Connections to utilities are included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | PRISON INDUSTRIES | 9952 | Correct | HDSP |  | Indian Springs | 2004 | 60000 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 30000
2507ADA2 | ADA UPGRADES | 2507 | Section 4.13.9 of the ADAAG states that handles, pulls, latches, locks and other operating devices on accessible doors shall have a shape that is easy to grasp with one hand and does not require tight grasping, tight pinching, or twisting of the wrist to operate. Lever-operated mechanisms, push-type mechanisms, and U-shaped handles are acceptable designs. It is recommended that proper lever hardware be installed in this building to meet these requirements. | PRISON INDUSTRIES | 9952 | Correct | HDSP |  | Indian Springs | 2004 | 60000 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 1000
2946PLM5 | COMPUTER WATER CONTROL SYSTEM REPLACEMENT | 2946 | This building is equipped with a computer water control system that is outdated and should be scheduled for replacement. Problems exist with the current computer water control system. It is increasingly difficult to find software updates and experienced repairmen to service the equipment. This project recommends the installation of a new computer water control system for the building. This system will monitor and control the water for all fixtures throughout the building. New electronic sensors will be installed on each water control system. | HOUSING UNIT #12 | 9952 | Correct | HDSP |  | Indian Springs | 2008 | 52096 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 50000
2946ELE2 | DOOR CONTROLS SYSTEM REPLACEMENT | 2946 | The control panel/ inmate movement and control system in the housing unit is not working properly. The cell door indicator lights on the control panel are falsely representing the actual status of the cell doors. The officer sometimes cannot tell if the cell door is open or closed. This project would replace the existing secured door control system with a programmable logic controlled system using touch screens for actuation and door status. This project would replace the existing door control system and the outdated wiring. Removal and disposal of the existing equipment is included in this estimate. | HOUSING UNIT #12 | 9952 | Correct | HDSP |  | Indian Springs | 2008 | 52096 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 1438241.25
2946SFT2 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 2946 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT #12 | 9952 | Correct | HDSP |  | Indian Springs | 2008 | 52096 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 9000
2088SFT6 | ROOF HATCH REPLACEMENT | 2088 | The roof hatches are original to the building and have reached the end of their useful life. The compression spring operators do not function properly, the latches and handles are worn and the seals and flashing have deteriorated. A faulty roof hatch is a safety hazard to anyone accessing the roof. This project would provide for the removal and the disposal of the existing roof hatches and for the purchase and installation of new roof hatches. | HOUSING UNIT #4 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 10000
2174EXT1 | EXTERIOR FINISHES | 2174 | It is important to maintain the finish, weather resistance and appearance of the building. The caulked control joints in the CMU of the exterior surface of this building are uniformly deteriorated and should be removed and the joints re-caulked. The metal doors and window frames should be sanded and painted on a cyclical basis. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HOUSING UNIT #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 445000
2946ENR1 | LIGHTING UPGRADE | 2946 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | HOUSING UNIT #12 | 9952 | Correct | HDSP |  | Indian Springs | 2008 | 52096 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 412872
2096EXT2 | EXTERIOR DOOR REPLACEMENT | 2096 | The existing exterior metal doors and frames appear to be original to the building. They are damaged and showing signs of wear and deterioration from constant use. This project would provide for the removal and replacement of two new metal door assemblies including frames, locks, hardware and painting. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | SALLYPORT | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 192 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
2089EXT0 | EXTERIOR FINISHES | 2089 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide for caulking all control joints and penetrations on a cyclical basis. The metal doors and window frames should also be sanded and painted a on a cyclical basis. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HOUSING UNIT #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 445000
2097SFT4 | FIRE ALARM SYSTEM REPLACEMENT | 2097 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and due to this, the system no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | MAINTENANCE/ CENTRAL PLANT | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 30151 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 241208
2096HVA1 | HEAT PUMP REPLACEMENT | 2096 | The heat pumps in the building should be scheduled for replacement. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of new heat pump units and the cleaning of the existing ducting and grilles. This project includes removal and disposal of the existing heat pump units and all required connections to utilities. | SALLYPORT | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 192 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 2880
2096SFT2 | EGRESS DOOR UPGRADE | 2096 | The egress door located on south east side of the building was welded shut from the inside. IBC 2012 Section 1003.6 Obstructions shall not be placed in the required width of a means of egress. This project would provide for the removal of the welded angle iron and would cut any welds holding the door shut. This project should coincide with an Exterior Door Replacement project. | SALLYPORT | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 192 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 2000
2097ELE2 | ELECTRICAL AND COMMUNICATIONS UPGRADE | 2097 | This building was constructed before the high demand for electrical services were needed for computers, communications systems and other electrical devices. As time has progressed, the buildings electrical demand and communications system has changed. The electrical system is utilized to its current maximum potential and the communications system is outdated. The electrical panels, switches and receptacles are at their limit. It is recommended to upgrade the entire electrical system and communications system to meet the evolving needs of the building. | MAINTENANCE/ CENTRAL PLANT | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 30151 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 753775
2097HVA3 | HVAC EQUIPMENT REPLACEMENT | 2097 | The air handlers, fan coils and related equipment are original to the building, dating back to 2000. The equipment has consistent problems and has reached its expected life span. This project recommends replacement of the air handlers, fan coils, ventilation equipment and exhaust fans. It is recommended that this project be implemented in the next 2-3 years to avoid possible failure and emergency funding for replacement. | MAINTENANCE/ CENTRAL PLANT | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 30151 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 452265
2097PLM2 | WATER TREATMENT SYSTEM REPLACEMENT | 2097 | The existing water softening/ treatment systems in the building are currently not operational. They are original to the building and approaching the end of their lifecycles. Failure of the equipment causes wear and tear on the domestic water supply lines, plumbing fixtures and HVAC equipment. This project would provide for the replacement of the existing water softeners/ treatment systems with new equipment. This project would also provide for a chemical treatment program including an updated chemicals control system, service and employee training provided by a qualified water treatment vendor. The annual maintenance fee charged by the water treatment vendor would be determined after an investigation of the water system is complete. These annual costs are not included in this project cost. For budgeting purposes, a $12,000 maintenance fee is suggested. | MAINTENANCE/ CENTRAL PLANT | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 30151 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
2097EXT2 | ROOF REPLACEMENT | 2097 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2000. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. | MAINTENANCE/ CENTRAL PLANT | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 30151 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 452265
2097HVA1 | VARIABLE FREQUENCY DRIVE REPLACEMENT | 2097 | The Variable Frequency Drives (VLT 6000) for the hot water drives have been disabled. Staff reports that the hot water VFD's have been problematic and have purposely been by-passed from the HVAC system. This project would provide for purchase and installation of the VFD's for the hot water drives. | MAINTENANCE/ CENTRAL PLANT | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 30151 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35000
2097SFT1 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 2097 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MAINTENANCE/ CENTRAL PLANT | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 30151 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 9000
2097SFT2 | PANIC HARDWARE IN ELECTRICAL ROOMS | 2097 | The electrical room with the uninterruptable power supply contains equipment that meets or exceeds 1,200 amps. It is recommended per the 2012 IBC 1008.1.10 that panic and fire exit hardware be installed. This equipment was not required when the building was constructed in 2000. When a remodel occurs, it is suggested to comply with current code. It is recommended that this project be completed within the next year. The estimate is based on one door that requires panic hardware. | MAINTENANCE/ CENTRAL PLANT | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 30151 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 3000
2097ENR1 | LIGHTING UPGRADE | 2097 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | MAINTENANCE/ CENTRAL PLANT | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 30151 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 241208
2097INT3 | INTERIOR FINISHES | 2097 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | MAINTENANCE/ CENTRAL PLANT | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 30151 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 301510
2097PLM1 | EXPANSION TANKS | 2097 | The expansion tanks in the Central Plant Boiler Room are undersized for the system which has ruptured the bladders and blown out pump seals. They were not operational at the time of survey. The system was designed to have an acceptance volume/gallon of 3,964. The existing tanks are Wassels model number NLA7500 which has an acceptance volume/gallon number 1980. This project would provide for two expansion tanks, Wassels model number NLA-15000. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | MAINTENANCE/ CENTRAL PLANT | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 30151 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 350000
2096ADA2 | ADA UPGRADES | 2096 | Section 4.13.9 of the ADAAG states that handles, pulls, latches, locks and other operating devices on accessible doors shall have a shape that is easy to grasp with one hand and does not require tight grasping, tight pinching, or twisting of the wrist to operate. Lever-operated mechanisms, push-type mechanisms, and U-shaped handles are acceptable designs. It is recommended that proper lever hardware be installed in this building to meet these requirements. | SALLYPORT | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 192 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 10000
2946SFT3 | ROOF HATCH REPLACEMENT | 2946 | The roof hatch is original to the building and has reached the end of its useful life. The compression spring operators do not function properly, the latches and handles are worn and the seals and flashing have deteriorated. A faulty roof hatch is a safety hazard to anyone accessing the roof. This project would provide for removal and disposal of the existing roof hatch and purchase and installation of a new roof hatch. | HOUSING UNIT #12 | 9952 | Correct | HDSP |  | Indian Springs | 2008 | 52096 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 5000
2097EXT0 | EXTERIOR FINISHES | 2097 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | MAINTENANCE/ CENTRAL PLANT | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 30151 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 301510
3224INT1 | INTERIOR FINISHES | 3224 | It is important to maintain water quality, quantity and the interior finish of the water tank. This project would include hiring certified divers or draining the tank to inspect and clean the interior walls, and to weld, sandblast and perform repairs and add protective coatings, if needed. It is important to follow all ANSI, NSF and AWWA approved ways to disinfect and repair water tanks. The standard recommendation is to conduct a comprehensive inspection inside the water tank every 5 years, except for newly constructed tanks. Newly constructed water tanks should be inspected within 10 years of service and every 5 years thereafter. | HDSP WATER TANK #2 | 9952 | Correct | HDSP |  | Indian Springs | 1998 | 2952 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
3776SFT1 | EXTERIOR LANDING INSTALLATION | 3776 | There is an out-swinging exterior door from the building which swings out over a step and does not have a landing. IBC Section 1008 requires a landing to be not more than 1/2" below the threshold. This project would provide for the installation of a compliant landing for the door. | PUMP HOUSE #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 840 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 5000
3776INT1 | INTERIOR FINISHES | 3776 | It is recommended to repair and seal the interior concrete block walls at least once in the 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. | PUMP HOUSE #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 840 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8400
3776ELE1 | PANIC HARDWARE IN ELECTRICAL ROOMS | 3776 | The Pump House with the uninterruptable power supply contains equipment that meets or exceeds 1,200 amps. It is recommended per the 2012 IBC 1008.1.10 that panic and fire exit hardware be installed. This equipment was not required when the building was constructed. When a remodel occurs, it is suggested to comply with current code. It is recommended that this project be completed within 2-3 years. The estimate is based on one door that requires panic hardware. | PUMP HOUSE #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 840 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
3776EXT1 | CONCRETE APRON INSTALLATION | 3776 | There are two rollup doors that don’t have concrete aprons on the outside of the building. This project would provide for the installation of two new 120 square foot 4" thick concrete slab-on-grade aprons. | PUMP HOUSE #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 840 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2400
3775ELE1 | PANIC HARDWARE IN ELECTRICAL ROOMS | 3775 | The Pump House with the uninterruptable power supply contains equipment that meets or exceeds 1,200 amps. It is recommended per the 2012 IBC 1008.1.10 that panic and fire exit hardware be installed. This equipment was not required when the building was constructed. When a remodel occurs, it is suggested to comply with current code. It is recommended that this project be completed within 2-3 years. The estimate is based on one door that requires panic hardware. | PUMP HOUSE #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 840 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
3776EXT2 | EXTERIOR FINISHES | 3776 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | PUMP HOUSE #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 840 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8400
3776EXT3 | ROOF REPLACEMENT | 3776 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2000. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. | PUMP HOUSE #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 840 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12600
3225EXT1 | EXTERIOR FINISHES | 3225 | It is important to maintain the finish, weather resistance and appearance of the water tank. This project would provide for the painting of the water tank and caulking of the joints to maintain it in a good, weather tight condition. It is recommended that this project be implemented in the next 2-3 years and is recommended on a cyclical basis based on environmental conditions. | HDSP WATER TANK #3 | 9952 | Correct | HDSP |  | Indian Springs | 1998 | 1859 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18590
3223INT1 | INTERIOR FINISHES | 3223 | It is important to maintain water quality, quantity and the interior finish of the water tank. This project would include hiring certified divers or draining the tank to inspect and clean the interior walls, and to weld, sandblast and perform repairs and add protective coatings, if needed. It is important to follow all ANSI, NSF and AWWA approved ways to disinfect and repair water tanks. The standard recommendation is to conduct a comprehensive inspection inside the water tank every 5 years, except for newly constructed tanks. Newly constructed water tanks should be inspected within 10 years of service and every 5 years thereafter. | HDSP WATER TANK #1 | 9952 | Correct | HDSP |  | Indian Springs | 1978 | 2952 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 29520
9952ENV1 | PIGEON ABATEMENT | 9952 | The site and buildings have been inhabited by pigeons. The birds introduce a potential risk of disease, cause maintenance problems with the mechanical systems and cost labor time for general clean-up. This project provides for removal and disposal of pigeon debris, eggs and carcasses from the site and buildings by a licensed pest control business. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HIGH DESERT STATE PRISON SITE | 9952 | Correct | HDSP |  | Indian Springs | 2000 |  | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
9952SIT1 | SLURRY SEAL ASPHALT PAVING | 9952 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site wide including access roads and parking areas. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 504,110 square feet of asphalt area was used to generate this estimate. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HIGH DESERT STATE PRISON SITE | 9952 | Correct | HDSP |  | Indian Springs | 2000 |  | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 603138
9952SEC1 | SECURITY SYSTEM INSTALLATION | 9952 | The building does not have a security system. This project recommends installing video monitoring and recording equipment in every common inmate area and visitor area throughout the High Desert State Prison. This project would also include camera installation in all housing units. | HIGH DESERT STATE PRISON SITE | 9952 | Correct | HDSP |  | Indian Springs | 2000 |  | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 2417400
9952ELE2 | ELECTRICAL EQUIPMENT SURVEY | 9952 | The electrical systems are original to the site and should be evaluated to reduce possibility of a fire hazard, equipment down time or energy loss. There seems to be loose connections and electrical deficiencies and repairs needed. It is recommended to perform an infrared and ultrasonic inspection on all electrical site-wide and sample the oil in all oil filled transformers. This project would provide for an electrical engineer to conduct analysis of the current electrical and to recommend a preventative maintenance plan and necessary repairs. Other projects may arise from this survey. | HIGH DESERT STATE PRISON SITE | 9952 | Correct | HDSP |  | Indian Springs | 2000 |  | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 95000
9952ELE1 | HIGH MAST LAMP REPLACEMENT | 9952 | There are 45 high mast security light poles throughout the facility that have 10 security lamps each. Many of the lamps were burned out at the time of this survey and should be scheduled for replacement. This project would provide for the purchase and installation of 450 LEDs and retrofit the fixtures for the high mast security light poles. The cost includes the removal and the disposal of the existing lamps and fixtures. | HIGH DESERT STATE PRISON SITE | 9952 | Correct | HDSP |  | Indian Springs | 2000 |  | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 225000
9952PLM2 | WELL UPGRADE | 9952 | The construction of Well #6 was accomplished with CIP project (13-C04). This project would include construction of a well house with associated equipment and connection to the existing water distribution system at High Desert State Prison. | HIGH DESERT STATE PRISON SITE | 9952 | Correct | HDSP |  | Indian Springs | 2000 |  | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 240480
3774EXT1 | EXTERIOR FINISHES | 3774 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HAZMAT BUILDING | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 64 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 640
3223EXT1 | EXTERIOR FINISHES | 3223 | It is important to maintain the finish, weather resistance and appearance of the water tank. This project would provide for the painting of the water tank and caulking of the joints to maintain it in a good, weather tight condition. It is recommended that this project be implemented in the next 2-3 years and is recommended on a cyclical basis based on environmental conditions. | HDSP WATER TANK #1 | 9952 | Correct | HDSP |  | Indian Springs | 1978 | 2952 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 29520
3225EXT2 | GUARDRAIL INSTALLATION | 3225 | The water tank is used to store water for fire protection. It is an AWWA D100 tank. 360° guardrails should be installed per NFPA 22 standards which designate the requirements for water tanks used for private fire protection. This project would provide for the purchase and installation of new guardrails to be located at the top of the water tank. | HDSP WATER TANK #3 | 9952 | Correct | HDSP |  | Indian Springs | 1998 | 1859 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 12000
3775EXT2 | EXTERIOR FINISHES | 3775 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | PUMP HOUSE #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 840 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8400
3225INT1 | INTERIOR FINISHES | 3225 | It is important to maintain water quality, quantity and the interior finish of the water tank. This project would include hiring certified divers or draining the tank to inspect and clean the interior walls, and to weld, sandblast and perform repairs and add protective coatings, if needed. It is important to follow all ANSI, NSF and AWWA approved ways to disinfect and repair water tanks. The standard recommendation is to conduct a comprehensive inspection inside the water tank every 5 years, except for newly constructed tanks. Newly constructed water tanks should be inspected within 10 years of service and every 5 years thereafter. | HDSP WATER TANK #3 | 9952 | Correct | HDSP |  | Indian Springs | 1998 | 1859 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
3774EXT2 | ROOF REPLACEMENT | 3774 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2000. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. | HAZMAT BUILDING | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 64 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 960
3775EXT1 | CONCRETE APRON INSTALLATION | 3775 | There are two rollup doors that don’t have concrete aprons on the outside of the building. This project would provide for the installation of two new 120 square foot 4" thick concrete slab-on-grade aprons. | PUMP HOUSE #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 840 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2400
3775INT1 | INTERIOR FINISHES | 3775 | It is recommended to repair and seal the interior concrete block walls at least once in the 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. | PUMP HOUSE #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 840 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8400
3223EXT2 | GUARDRAIL INSTALLATION | 3223 | The water tank is used to store water for fire protection. It is an AWWA D100 tank. 360° guardrails should be installed per NFPA 22 standards which designate the requirements for water tanks used for private fire protection. This project would provide for the purchase and installation of new guardrails to be located at the top of the water tank. | HDSP WATER TANK #1 | 9952 | Correct | HDSP |  | Indian Springs | 1978 | 2952 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 12000
3224EXT1 | EXTERIOR FINISHES | 3224 | It is important to maintain the finish, weather resistance and appearance of the water tank. This project would provide for the painting of the water tank and caulking of the joints to maintain it in a good, weather tight condition. It is recommended that this project be implemented in the next 2-3 years and is recommended on a cyclical basis based on environmental conditions. | HDSP WATER TANK #2 | 9952 | Correct | HDSP |  | Indian Springs | 1998 | 2952 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 29520
3224EXT2 | GUARDRAIL INSTALLATION | 3224 | The water tank is used to store water for fire protection. It is an AWWA D100 tank. 360° guardrails should be installed per NFPA 22 standards which designate the requirements for water tanks used for private fire protection. This project would provide for the purchase and installation of new guardrails to be located at the top of the water tank. | HDSP WATER TANK #2 | 9952 | Correct | HDSP |  | Indian Springs | 1998 | 2952 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 12000
3775EXT3 | ROOF REPLACEMENT | 3775 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2000. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. | PUMP HOUSE #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 840 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12600
3775SFT1 | EXTERIOR LANDING INSTALLATION | 3775 | There is an out-swinging exterior door from the building which swings out over a step and does not have a landing. IBC Section 1008 requires a landing to be not more than 1/2" below the threshold. This project would provide for the installation of a compliant landing for the door. | PUMP HOUSE #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 840 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 5000
3774INT1 | INTERIOR FINISHES | 3774 | It is recommended to repair and seal the interior concrete block walls at least once in the 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. | HAZMAT BUILDING | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 64 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 640
1366EXT2 | EXTERIOR FINISHES | 1366 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | WALK-IN COOLER STORAGE | 9949 | Correct | PCC |  | Pioche | 1980 | 480 | 2017-03-02 | Four to Ten Years | Long-Term Needs | 3 | 4800
1364INT5 | DRYER REPLACEMENT | 1364 | The commercial tumbler dryer in the laundry area is original to the building and is troublesome and problematic to operate. Considering the age of the machine and the evolving needs of the facility it is recommended to replace it. This project provides for the removal and disposal of the existing tumbler dryer and would replace it with a new unit. | MULTI-PURPOSE/ SHOP | 9949 | Correct | PCC | Forestry | Pioche | 1987 | 7000 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
1364ADA2 | ADA SIGNAGE | 1364 | ADA regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with these criteria. This project will provide for compliant ADA signage. The 2012 IBC, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | MULTI-PURPOSE/ SHOP | 9949 | Correct | PCC | Forestry | Pioche | 1987 | 7000 | 2017-03-02 | Immediate to Two Years | Currently Critical | 1 | 1500
1364INT1 | INTERIOR FINISHES | 1364 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 04/11/2002 and 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | MULTI-PURPOSE/ SHOP | 9949 | Correct | PCC | Forestry | Pioche | 1987 | 7000 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 70000
1364ADA1 | ADA RESTROOM REMODEL | 1364 | The building does not have an accessible restroom. The existing restroom does not meet the ADA requirements. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom. Items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/11/2002 and 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | MULTI-PURPOSE/ SHOP | 9949 | Correct | PCC | Forestry | Pioche | 1987 | 7000 | 2017-03-02 | Immediate to Two Years | Currently Critical | 1 | 15000
1364SFT1 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 1364 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/11/2002 and 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | MULTI-PURPOSE/ SHOP | 9949 | Correct | PCC | Forestry | Pioche | 1987 | 7000 | 2017-03-02 | Immediate to Two Years | Currently Critical | 1 | 14000
1364EXT4 | EXTERIOR DOOR REPLACEMENT | 1364 | The existing exterior metal doors and frames are original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement and installation of two new metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | MULTI-PURPOSE/ SHOP | 9949 | Correct | PCC | Forestry | Pioche | 1987 | 7000 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
1364EXT1 | EXTERIOR FINISHES | 1364 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations and removing and replacing rusted metal panels as needed. It is recommended that the building be caulked, sealed and repaired in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/11/2002 and 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | MULTI-PURPOSE/ SHOP | 9949 | Correct | PCC | Forestry | Pioche | 1987 | 7000 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 70000
1364ENR1 | HEATING EQUIPMENT REPLACEMENT | 1364 | The existing heating system consists of a ceiling mounted propane heater (30,000 - 50,000 BTU). The heaters are inefficient and should be replaced with a propane fired heater 80% AFUE or higher units. This project would provide for disposal of the existing units and replacement with a new propane fired units including connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 04/11/2002 and 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | MULTI-PURPOSE/ SHOP | 9949 | Correct | PCC | Forestry | Pioche | 1987 | 7000 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
1364INT2 | VCT FLOORING REPLACEMENT | 1364 | The VCT flooring in the chapel, laundry, library and on the stairs is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. This project or a portion thereof was previously recommended in the FCA report dated 04/11/2002 and 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | MULTI-PURPOSE/ SHOP | 9949 | Correct | PCC | Forestry | Pioche | 1987 | 7000 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 56000
1355SFT1 | SAFETY CABINETS | 1355 | The building contains many different paints, stains, and other hazardous products located on open shelves and on the floor. This does not meet OSHA standards or IFC for hazardous materials containment. This project would provide a self-closing hazardous storage container in the building and install placards on the building exterior in accordance with OSHA 1910.106 (d) and IFC Chapter 57 Section 5704.3.2.1.3. | MAINTENANCE SHOP | 9949 | Correct | PCC |  | Pioche | 1980 | 720 | 2017-03-02 | Immediate to Two Years | Currently Critical | 1 | 5000
1364SFT4 | INTERIOR STAIR HANDRAIL REPLACEMENT | 1364 | The stair handrails are older and do not meet code for safety or accessibility. The gripping surfaces are incorrect and they are not continuous from the top to bottom landings. This project recommends the installation of handrails on both sides of the stairs, with proper returns and supports. Removal and disposal of the existing railing is included in this estimate. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | MULTI-PURPOSE/ SHOP | 9949 | Correct | PCC | Forestry | Pioche | 1987 | 7000 | 2017-03-02 | Immediate to Two Years | Currently Critical | 1 | 5000
1366SFT1 | EXTERIOR LANDING INSTALLATION | 1366 | There is an out-swinging exterior door from the building which swings out over a step and does not have a landing that complies with IBC 2012. IBC Section 1008 requires a landing to be not more than 1/2" below the threshold. This project would provide for the installation of a compliant landing for the door. | WALK-IN COOLER STORAGE | 9949 | Correct | PCC |  | Pioche | 1980 | 480 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
1364EXT2 | OVERHEAD DOOR REPLACEMENT | 1364 | There is a 16'x14' overhead coiling door which is damaged and does not function properly. It is original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead coiling door and replacement with a motorized door. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | MULTI-PURPOSE/ SHOP | 9949 | Correct | PCC | Forestry | Pioche | 1987 | 7000 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
1364SFT3 | OCCUPANCY SEPARATION UPGRADE | 1364 | The multipurpose building serves as a H-4 garage on one side (approximately 2600 s.f.) with office space and mezzanine storage above. A gymnasium, chapel, library and laundry is located on the other side. Per table 508.3.3 of the 2012 IBC, a 3 hour occupancy separation is required between the H-4 garage and the A-3 gymnasium. This will require demolition and new construction between the two portions of the building. his project or a portion thereof was previously recommended in the FCA report dated 04/11/2002 and 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | MULTI-PURPOSE/ SHOP | 9949 | Correct | PCC | Forestry | Pioche | 1987 | 7000 | 2017-03-02 | Immediate to Two Years | Currently Critical | 1 | 25000
1364INT4 | WASHING MACHINE REPLACEMENT | 1364 | The two existing commercial washing machines appear to have reached the end of their useful life. They show signs of age, and are constantly breaking down. This project would provide funding for the purchase and installation of two new 60lb. commercial washing machine units. | MULTI-PURPOSE/ SHOP | 9949 | Correct | PCC | Forestry | Pioche | 1987 | 7000 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18000
1364ENR2 | LIGHTING UPGRADE | 1364 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | MULTI-PURPOSE/ SHOP | 9949 | Correct | PCC | Forestry | Pioche | 1987 | 7000 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 56000
1355EXT1 | EXTERIOR FINISHES | 1355 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | MAINTENANCE SHOP | 9949 | Correct | PCC |  | Pioche | 1980 | 720 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7200
1364EXT3 | EXTERIOR SIDING REPLACEMENT | 1364 | The corrugated metal panels covering the building are original and should be scheduled for replacement. Many of the panels are damaged from general wear and tear. This project would provide for the removal and the disposal of the existing panels and the replacement with new pre-painted metal panels. This estimate is based on 700 linear feet of 4' wide panels at $17.00 per linear foot. | MULTI-PURPOSE/ SHOP | 9949 | Correct | PCC | Forestry | Pioche | 1987 | 7000 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11900
1355EXT2 | ROOF REPLACEMENT | 1355 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition shingle roof and new underlayment. This estimate includes the removal and the disposal of the old roof. | MAINTENANCE SHOP | 9949 | Correct | PCC |  | Pioche | 1980 | 720 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10800
1355ENR1 | LIGHTING UPGRADE | 1355 | The existing lighting fixtures are the older High Pressure Sodium, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | MAINTENANCE SHOP | 9949 | Correct | PCC |  | Pioche | 1980 | 720 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5760
1364SFT5 | EXTERIOR LANDING INSTALLATION | 1364 | There are two out-swinging exterior doors on the building, which swing out over a step that does not have a landing. This does not comply with 2012 IBC Section 1008.1, which requires a proper landing and for the landing to not be more than 1/2" below the threshold. This project would provide for the installation of compliant landings. | MULTI-PURPOSE/ SHOP | 9949 | Correct | PCC | Forestry | Pioche | 1987 | 7000 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
2210PLM3 | WATER TREATMENT SYSTEM INSTALLATION | 2210 | The existing plumbing and HVAC systems are not equipped with a water treatment system. Failure to treat the water causes wear and tear on the domestic water supply lines, plumbing fixtures and HVAC equipment. This project would provide for the purchase and installation of water softeners / treatment systems to serve all of the mechanical and plumbing equipment. This project would also provide for a chemical treatment program including an updated chemicals control system, service and employee training provided by a qualified water treatment vendor. The annual maintenance fee charged by the water treatment vendor would be determined after an investigation of the water system is complete. These annual costs are not included in this project cost. For budgeting purposes, a $12,000 fee is suggested. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | HOUSING ABC/ CULINARY UNIT | 9949 | Correct | PCC |  | Pioche | 1995 | 17669 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
2212SFT1 | EXTERIOR LANDING UPGRADES | 2212 | Chapter 10 of the 2012 IBC describes the requirements for doors including floor elevations, landings and handrails. The floor or landing shall be at the same elevation on each side of the door. The exterior landing shall not exceed a 2-percent slope and a length measured in the direction of travel of not less than 44 inches. Stairways shall have handrails on each side of the stairs. The landing and stairway at both exterior doors do not comply with this code and pose a safety hazard. This project would provide for the installation of two compliant landings and handrails for each door. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | PREFERRED HOUSING UNIT E | 9949 | Correct | PCC |  | Pioche | 1995 | 980 | 2017-03-02 | Immediate to Two Years | Currently Critical | 1 | 10000
2211SFT3 | FIRE ALARM SYSTEM INSTALLATION | 2211 | This building is lacking fire detection and an alarm system. It is recommended that fire detection and an alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2009 Section 7 and the 2012 International Fire Code. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | PREFERRED HOUSING UNIT D | 9949 | Correct | PCC |  | Pioche | 1995 | 980 | 2017-03-02 | Immediate to Two Years | Currently Critical | 1 | 3920
2211SFT2 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 2211 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | PREFERRED HOUSING UNIT D | 9949 | Correct | PCC |  | Pioche | 1995 | 980 | 2017-03-02 | Immediate to Two Years | Currently Critical | 1 | 4900
2211INT2 | RESTROOM REMODEL | 2211 | The restroom in the building is dated and in overall poor condition. The finishes, fixtures, cabinets, toilets, showers and exhaust fans are showing signs of wear and deterioration. This project would provide for a complete remodel of the restroom. The removal and disposal of the existing fixtures and finishes is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | PREFERRED HOUSING UNIT D | 9949 | Correct | PCC |  | Pioche | 1995 | 980 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
2211ENR2 | LIGHTING UPGRADE | 2211 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | PREFERRED HOUSING UNIT D | 9949 | Correct | PCC |  | Pioche | 1995 | 980 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7840
2211HVA1 | HEATER REPLACEMENT | 2211 | The heating system was installed in 1995. It consists of propane gas-fired furnaces. The system is not energy efficient and has reached the end of its expected and useful life. This project would provide for the installation of a new heating system and the cleaning of the existing duct work and grilles. The new system shall be designed to significantly reduce electrical and propane usage in order to comply with the 2012 IECC and ASHRAE 90.1 and to reduce utility costs. This project includes the removal and disposal of the existing heating units and all required connections to utilities. | PREFERRED HOUSING UNIT D | 9949 | Correct | PCC |  | Pioche | 1995 | 980 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
2211HVA2 | EVAPORATIVE COOLER REPLACEMENT | 2211 | There are two evaporative coolers mounted on the roof of the housing unit. They are severely scaled and have reached the end of their serviceable life. This project would provide for two new evaporative coolers to be installed, and includes the removal and disposal of the old evaporative coolers and utility connections to the new units. | PREFERRED HOUSING UNIT D | 9949 | Correct | PCC |  | Pioche | 1995 | 980 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
2211EXT2 | EXTERIOR FINISHES | 2211 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | PREFERRED HOUSING UNIT D | 9949 | Correct | PCC |  | Pioche | 1995 | 980 | 2017-03-02 | Four to Ten Years | Long-Term Needs | 3 | 9800
2211EXT3 | ROOF REPLACEMENT | 2211 | The standing seam metal roof on this building was in poor condition at the time of the survey and had active leaks. It is recommended that this building be re-roofed in the next 2-3 years with a new single-ply roofing system which will be installed directly over the existing metal roof. This will allow the roof to qualify for the statewide roofing program warranty and preventative maintenance agreement. | PREFERRED HOUSING UNIT D | 9949 | Correct | PCC |  | Pioche | 1995 | 980 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14700
2211INT3 | INTERIOR FINISHES | 2211 | The interior finishes are in fair condition. Some walls are covered by a fabric wall covering and some have been painted. It is recommended that the painted walls and ceilings be re-painted at least once in the next 4-5 years. This project should be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | PREFERRED HOUSING UNIT D | 9949 | Correct | PCC |  | Pioche | 1995 | 980 | 2017-03-02 | Four to Ten Years | Long-Term Needs | 3 | 9800
2211SFT5 | FLUE REPAIRS | 2211 | The flue vent in the building does not comply with UMC 2012 chapter 8, chimneys and vents. The flue vent was installed with an improper flue and per section 804 direct vent terminations vent terminals for direct vented appliances shall be installed in accordance with the manufacturer’s installation instructions. The flue vent is to close to combustibles, does not have the proper clearances and has a potential to leak CO. It is recommended that the furnace flue vent be replaced immediately. Replacements shall meet the manufacture’s specifications and UMC 2012. The flue vents should be installed by a licensed contractor. This project would provide funds to replace of the flue vent in the building. | PREFERRED HOUSING UNIT D | 9949 | Correct | PCC |  | Pioche | 1995 | 980 | 2017-03-02 | Immediate to Two Years | Currently Critical | 1 | 2000
2211ELE1 | WIRING CLEANUP | 2211 | The wiring in the housing unit is disorganized and not in proper electrical boxes. This creates a safety issue. This project would provide for organization, proper labeling and for the wiring to be placed in electrical boxes per NEC 2011. | PREFERRED HOUSING UNIT D | 9949 | Correct | PCC |  | Pioche | 1995 | 980 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
2211SFT1 | EXTERIOR LANDING UPGRADES | 2211 | Chapter 10 of the 2012 IBC describes the requirements for doors including floor elevations, landings and handrails. The floor or landing shall be at the same elevation on each side of the door. The exterior landing shall not exceed a 2-percent slope and a length measured in the direction of travel of not less than 44 inches. Stairways shall have handrails on each side of the stairs. The landing and stairway at both exterior doors do not comply with this code and pose a safety hazard. This project would provide for the installation of two compliant landings and handrails for each door. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | PREFERRED HOUSING UNIT D | 9949 | Correct | PCC |  | Pioche | 1995 | 980 | 2017-03-02 | Immediate to Two Years | Currently Critical | 1 | 10000
2212INT4 | FLOORING REPLACEMENT | 2212 | The floor coverings throughout this building are in generally poor condition and have reached the end of their serviceable lives. This project would provide funding to completely remove the existing flooring and replace with durable sheet vinyl. | PREFERRED HOUSING UNIT E | 9949 | Correct | PCC |  | Pioche | 1995 | 980 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11760
2212EXT3 | ROOF REPLACEMENT | 2212 | The standing seam metal roof on this building was in poor condition at the time of the survey and had active leaks. It is recommended that this building be re-roofed in the next 2-3 years with a new single-ply roofing system which will be installed directly over the existing metal roof. This will allow the roof to qualify for the statewide roofing program warranty and preventative maintenance agreement. | PREFERRED HOUSING UNIT E | 9949 | Correct | PCC |  | Pioche | 1995 | 980 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14700
2212INT2 | ADA RESTROOM UPGRADE | 2212 | The building does not have an accessible restroom. The existing restroom does not meet the ADA requirements. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom. Items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | PREFERRED HOUSING UNIT E | 9949 | Correct | PCC |  | Pioche | 1995 | 980 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
2212ENR1 | WINDOW REPLACEMENT | 2212 | The windows are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 4 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | PREFERRED HOUSING UNIT E | 9949 | Correct | PCC |  | Pioche | 1995 | 980 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
2212SFT2 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 2212 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | PREFERRED HOUSING UNIT E | 9949 | Correct | PCC |  | Pioche | 1995 | 980 | 2017-03-02 | Immediate to Two Years | Currently Critical | 1 | 4900
2212SFT4 | FIRE SUPPRESSION SYSTEM INSTALLATION | 2212 | This building does not have an automatic fire suppression system and should be retrofitted with fire sprinklers during the next remodel or addition. This project would provide funding for the installation of fire sprinklers including backflow prevention devices. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | PREFERRED HOUSING UNIT E | 9949 | Correct | PCC |  | Pioche | 1995 | 980 | 2017-03-02 | Immediate to Two Years | Currently Critical | 1 | 13720
2212SFT3 | FIRE ALARM SYSTEM INSTALLATION | 2212 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2009 Section 7 and the 2012 International Fire Code. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | PREFERRED HOUSING UNIT E | 9949 | Correct | PCC |  | Pioche | 1995 | 980 | 2017-03-02 | Immediate to Two Years | Currently Critical | 1 | 3920
2212EXT2 | EXTERIOR FINISHES | 2212 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is caulking and sealing the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | PREFERRED HOUSING UNIT E | 9949 | Correct | PCC |  | Pioche | 1995 | 980 | 2017-03-02 | Four to Ten Years | Long-Term Needs | 3 | 9800
2212ENR2 | LIGHTING UPGRADE | 2212 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | PREFERRED HOUSING UNIT E | 9949 | Correct | PCC |  | Pioche | 1995 | 980 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7840
2210ADA3 | ADA RESTROOM UPGRADE | 2210 | The building does not have accessible restrooms. The existing restrooms do not meet the ADA requirements. A complete retrofit is necessary. This project would provide funding for remodeling the restrooms per ADA regulations. Items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | HOUSING ABC/ CULINARY UNIT | 9949 | Correct | PCC |  | Pioche | 1995 | 17669 | 2017-03-02 | Immediate to Two Years | Currently Critical | 1 | 160000
2212ELE1 | WIRING CLEANUP | 2212 | The wiring in the housing unit is disorganized and not in proper electrical boxes. This creates a safety issue. This project would provide for organization, proper labeling and for the wiring to be placed in electrical boxes per NEC 2011. | PREFERRED HOUSING UNIT E | 9949 | Correct | PCC |  | Pioche | 1995 | 980 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
2212INT3 | INTERIOR FINISHES | 2212 | The interior finishes are in fair condition. Some walls are covered by a fabric wall covering and some have been painted. It is recommended that the painted walls and ceilings be re-painted at least once in the next 4-5 years. This project should be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | PREFERRED HOUSING UNIT E | 9949 | Correct | PCC |  | Pioche | 1995 | 980 | 2017-03-02 | Four to Ten Years | Long-Term Needs | 3 | 9800
2212PLM1 | WATER HEATER REPLACEMENT | 2212 | There is a 40 gallon propane-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, the water heater and the floor below the water heater are showing signs of wear and deterioration. It is recommended that the floor be replaced and a new propane-fired water heater be installed immediately. Removal and disposal of the existing equipment is included in this estimate. | PREFERRED HOUSING UNIT E | 9949 | Correct | PCC |  | Pioche | 1995 | 980 | 2017-03-02 | Immediate to Two Years | Currently Critical | 1 | 1750
2212HVA1 | HEATER REPLACEMENT | 2212 | The heating system was installed in 1995. It consists of propane gas-fired furnaces. The system is not energy efficient and has reached the end of its expected and useful life. This project would provide for the installation of new heating systems and cleaning of the existing duct work and grilles. The new systems shall be designed to significantly reduce electrical and propane usage in order to comply with the 2012 IECC and ASHRAE 90.1 and to reduce utility costs. This project includes the removal and disposal of the existing heating units and all required connections to the utilities. | PREFERRED HOUSING UNIT E | 9949 | Correct | PCC |  | Pioche | 1995 | 980 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
2211PLM1 | WATER HEATER REPLACEMENT | 2211 | There is a 50 gallon propane-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new propane-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | PREFERRED HOUSING UNIT D | 9949 | Correct | PCC |  | Pioche | 1995 | 980 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1750
2210EXT2 | LOADING DOCK REPAIRS | 2210 | The loading dock behind the Culinary area is worn and damaged and in need of replacement. The concrete has heaved and has extensive cracks and the entire structure is pulling away from the building. This project will provide for the removal and the replacement of the concrete and the installation of new hardware for the truck guards. This project or a portion thereof was previously recommended in the FCA report dated 04/11/2002 and 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | HOUSING ABC/ CULINARY UNIT | 9949 | Correct | PCC |  | Pioche | 1995 | 17669 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 200000
2212HVA2 | EVAPORATIVE COOLER REPLACEMENT | 2212 | There are two evaporative coolers mounted on the roof of the housing unit. They are severely scaled and have reached the end of their serviceable life. This project would provide for two new evaporative coolers to be installed, and will include the removal and disposal of the old evaporative coolers and the utility connections to the new units. | PREFERRED HOUSING UNIT E | 9949 | Correct | PCC |  | Pioche | 1995 | 980 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
2209EXT2 | ROOF REPLACEMENT | 2209 | The asphalt composition shingle roof on this building was in fair to poor condition at the time of the survey. It is recommended that this building be re-roofed in the next year with a new 50 year asphalt composition shingle roof and new underlayment. This estimate includes removal and disposal of the old roof. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | GARDEN SHED | 9949 | Correct | PCC |  | Pioche | 1987 | 64 | 2017-03-02 | Four to Ten Years | Long-Term Needs | 3 | 960
2209SFT1 | SAFETY CABINETS | 2209 | The building contains many different paints, stains, and other hazardous products located on open shelves and on the floor. This does not meet OSHA standards or IFC for hazardous materials containment. This project would provide a self-closing hazardous storage container in the building and install placards on the building’s exterior in accordance with OSHA 1910.106 (d) and IFC Chapter 57 Section 5704.3.2.1.3. | GARDEN SHED | 9949 | Correct | PCC |  | Pioche | 1987 | 64 | 2017-03-02 | Immediate to Two Years | Currently Critical | 1 | 5000
2209ELE1 | WIRING CLEANUP | 2209 | The wiring in the building is disorganized and not in proper electrical boxes. This creates a safety issue when making repairs or upgrades. This project would provide for cleanup and labeling of the wiring. | GARDEN SHED | 9949 | Correct | PCC |  | Pioche | 1987 | 64 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
2211SFT4 | FIRE SUPPRESSION SYSTEM INSTALLATION | 2211 | This building does not have an automatic fire suppression system. It should be retrofitted with fire sprinklers during the next remodel or addition. This project would provide funding for the installation of fire sprinklers including backflow prevention devices. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | PREFERRED HOUSING UNIT D | 9949 | Correct | PCC |  | Pioche | 1995 | 980 | 2017-03-02 | Immediate to Two Years | Currently Critical | 1 | 13720
2209ENR1 | LIGHTING UPGRADE | 2209 | The existing lighting fixtures are the older incandescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | GARDEN SHED | 9949 | Correct | PCC |  | Pioche | 1987 | 64 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 512
2209EXT1 | EXTERIOR FINISHES | 2209 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | GARDEN SHED | 9949 | Correct | PCC |  | Pioche | 1987 | 64 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 640
2210ELE2 | ELECTRICAL UPGRADE | 2210 | This building was constructed before the high demand for electrical services were needed for computers and other electrical devices. As time has progressed, the buildings electrical demand and system has changed. It is utilized to its current maximum potential. In the commissary and several of the office areas, the receptacles are at their limit. It is recommended that additional capacity be provided in the main core to meet the evolving demands of the building. This project or a portion thereof was previously recommended in the FCA report dated 04/11/2002 and 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | HOUSING ABC/ CULINARY UNIT | 9949 | Correct | PCC |  | Pioche | 1995 | 17669 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 441725
2210EXT3 | ROOF REPLACEMENT | 2210 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition shingle roof and new underlayment. This estimate includes the removal and the disposal of the old roof. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | HOUSING ABC/ CULINARY UNIT | 9949 | Correct | PCC |  | Pioche | 1995 | 17669 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 265035
2210PLM2 | EVAPORATIVE COOLER REPLACEMENT | 2210 | There are 13 evaporative coolers installed on the roof of this building. They are severely scaled and have reached the end of their useful and expected life. They do not have overflow drains and the excess water is damaging roof materials. This project would provide for new evaporative coolers to be installed, including all required connections to utilities. The estimate includes the removal and the disposal of the old coolers. This project or a portion thereof was previously recommended in the FCA report dated 04/11/2002 and 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | HOUSING ABC/ CULINARY UNIT | 9949 | Correct | PCC |  | Pioche | 1995 | 17669 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 52000
2210INT2 | JANITORS CLOSET REPAIRS | 2210 | The mop sink in one of the Janitors Closets is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide FRP to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | HOUSING ABC/ CULINARY UNIT | 9949 | Correct | PCC |  | Pioche | 1995 | 17669 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
2211INT4 | FLOORING REPLACEMENT | 2211 | The floor coverings throughout this building are in generally poor condition and have reached the end of their serviceable lives. This project would provide funding to completely remove the existing flooring and replace with durable sheet viny | PREFERRED HOUSING UNIT D | 9949 | Correct | PCC |  | Pioche | 1995 | 980 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11760
2210ADA1 | ADA SIGNAGE | 2210 | ADA regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with these criteria. This project or a portion thereof was previously recommended in the FCA report dated 04/11/2002 and 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | HOUSING ABC/ CULINARY UNIT | 9949 | Correct | PCC |  | Pioche | 1995 | 17669 | 2017-03-02 | Immediate to Two Years | Currently Critical | 1 | 3000
2210HVA3 | BOILER REPLACEMENT | 2210 | The hot water boilers, controls and mixing valves servicing the building are original dating back to 1995. The life expectancy of these units is 20 to 25 years with proper maintenance and with a water treatment program in place. Replacement parts for performing routine and emergency maintenance are hard to find for this old equipment. This project would provide for the removal and the disposal of the existing boilers, controls and mixing valves and will replace with all new equipment. This estimate includes all required connections to utilities and equipment. The estimate is based on 505 MBH output hot water boilers. The existing chemical water treatment system will need to be tested and adjusted once equipment is operational. $2,000 is included in this estimate for testing of the chemical water treatment system. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | HOUSING ABC/ CULINARY UNIT | 9949 | Correct | PCC |  | Pioche | 1995 | 17669 | 2017-03-02 | Immediate to Two Years | Currently Critical | 1 | 100000
2210HVA4 | AIR CONDITIONER INSTALLATION | 2210 | The server room is not sufficiently cooled by the existing HVAC system. If the room is too warm, the computer equipment will prematurely age and may fail due to overheating. It is recommended to install an air conditioning system in the room to ensure that the temperature is properly regulated. This project would provide for the purchase and installation of an air conditioner and includes all required connections to existing utilities. | HOUSING ABC/ CULINARY UNIT | 9949 | Correct | PCC |  | Pioche | 1995 | 17669 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
2210INT3 | FLOORING REPLACEMENT | 2210 | The floor coverings throughout this building are in generally poor condition and have reached the end of their serviceable lives. At the present time, most of the floor surfaces have been removed in the cafeteria and culinary area. This presents health and sanitation issues. The remaining floor covering has 12" VCT floor covering. This project would provide funding to replace the entire floor with non-slip sheet vinyl, and includes removing and installing the Culinary preparation and cooking equipment, tables and chairs. | HOUSING ABC/ CULINARY UNIT | 9949 | Correct | PCC |  | Pioche | 1995 | 17669 | 2017-03-02 | Four to Ten Years | Long-Term Needs | 3 | 159021
2210CUL1 | CULINARY EQUIPMENT REPLACEMENT | 2210 | The kitchen cooking equipment is original to the building and has reached the end of its useful life. It is recommended that the equipment be scheduled for replacement in the next 2-3 years, including ovens and hoods, grills, sinks and dishwashers. This project provides for the removal and disposal of the existing equipment and replacement with new equipment. | HOUSING ABC/ CULINARY UNIT | 9949 | Correct | PCC |  | Pioche | 1995 | 17669 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 150000
2210ADA4 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 2210 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | HOUSING ABC/ CULINARY UNIT | 9949 | Correct | PCC |  | Pioche | 1995 | 17669 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
2210ADA5 | ADA TABLE UPGRADE | 2210 | Per the USAB Section 226.1 where dining surfaces are provided for the consumption of food or drink, at least 5 percent of the seating spaces and standing spaces at the dining surfaces shall comply with 902. ICC ANSI-A117.1-2009 which says, if fixed seating is provided, a loose seat or open space for a wheelchair location must be available at those accessible tables. This project would provide funding to remove 4 of the fixed seats, which will allow access for four wheel chairs. | HOUSING ABC/ CULINARY UNIT | 9949 | Correct | PCC |  | Pioche | 1995 | 17669 | 2017-03-02 | Immediate to Two Years | Currently Critical | 1 | 4000
2210HVA5 | HVAC EQUIPMENT REPLACEMENT | 2210 | The HVAC system is original to the building and should be scheduled for replacement. It is not energy efficient and has reached the end of its expected and useful life. The R-22 refrigerant in the cooling system is no longer EPA complaint and it's production is mandated to be phased out completely by January 1, 2020. This project would provide for installation of a new HVAC system and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC system and all required connections to utilities. | HOUSING ABC/ CULINARY UNIT | 9949 | Correct | PCC |  | Pioche | 1995 | 17669 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
2211ENR1 | WINDOW REPLACEMENT | 2211 | The windows are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 4 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | PREFERRED HOUSING UNIT D | 9949 | Correct | PCC |  | Pioche | 1995 | 980 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
2209SFT2 | PROPANE TANK RELOCATION | 2209 | There are above ground propane storage tanks stored next to the building. According to Table 3504.2.1 of the 2012 International Fire Code, flammable gases must be stored at least 5 feet away from a building of non-rated construction. This project would provide for relocating the propane storage tanks to comply with the code. | GARDEN SHED | 9949 | Correct | PCC |  | Pioche | 1987 | 64 | 2017-03-02 | Immediate to Two Years | Currently Critical | 1 | 3500
9949PLM1 | SEWER SYSTEM REPLACEMENT | 9949 | The sanitary wastewater system and the lift station are showing signs of deterioration and the system is not working to its full potential. The sewer and leach field lines are original to the site and are in poor condition. Deposits within the pipes are causing them to be restricted, which is slowing the flow of water. The passage of time and constant heavy use are contributing factors to problems that arise. This project would provide for the complete replacement of the sanitary sewer system and the lift station. | PIOCHE CONSERVATION CAMP SITE | 9949 | Correct | PCC |  | Pioche | 1980 | 0 | 2017-03-02 | Immediate to Two Years | Currently Critical | 1 | 2500000
9949ADA1 | ADA PARKING AND PATH OF TRAVEL | 9949 | The ADA provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the office are necessary to comply with ADA accessibility requirements. This project would provide for a concrete van accessible ADA parking and loading space and concrete walkway to the existing sidewalk. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. 750 square feet of concrete was used for this estimate. It is recommended that this project coincide with the paving project. This project or a portion thereof was previously recommended in the FCA report dated 04/11/2002 and 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | PIOCHE CONSERVATION CAMP SITE | 9949 | Correct | PCC |  | Pioche | 1980 | 0 | 2017-03-02 | Immediate to Two Years | Currently Critical | 1 | 30000
9949SEC1 | FENCE UPGRADE | 9949 | The chain link perimeter fence is currently 7 feet high. For security purposes the staff has requested to raise the fence to 12 feet high. This project would provide for adding 5 feet of fencing and razor wire to the existing perimeter fence. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | PIOCHE CONSERVATION CAMP SITE | 9949 | Correct | PCC |  | Pioche | 1980 | 0 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 75000
9949ENR1 | EXTERIOR LIGHTING REPLACEMENT | 9949 | The 13 perimeter light poles that surround the site have a total of 52 light fixtures. These light fixtures are metal halide and are not energy efficient. This project would provide for the replacement of the exterior light fixtures with new LED light fixtures and will utilize the existing wiring. | PIOCHE CONSERVATION CAMP SITE | 9949 | Correct | PCC |  | Pioche | 1980 | 0 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19500
9949SIT2 | SITE DRAINAGE IMPROVEMENTS | 9949 | The grade does not slope away effectively from the buildings. This allows water to pool against the foundation. In the winter months, the water freezes against the foundation, and over time, this can cause damage to the foundation. It is recommended per IBC 1804.3 Site Grading that the ground immediately adjacent to the foundation shall be sloped away from the building at a slope of not less than one vertical in 20 units horizontal (5-percent slope) for a minimum distance of 10 feet (3048 mm) measured perpendicular to the face of the wall. This project would create a 5% slope away from the buildings. Additional drainage swales shall be installed, as needed. It is recommended that the grading be completed within 4-10 years. | PIOCHE CONSERVATION CAMP SITE | 9949 | Correct | PCC |  | Pioche | 1980 | 0 | 2017-03-02 | Four to Ten Years | Long-Term Needs | 3 | 5000
1388EXT3 | REPLACE ROOF | 1388 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. The extreme temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof, and constant exposure to the sun are contributing factors to wear and deterioration. The roof has many patches on it and is a constant maintenance problem. It is recommended that this building be re-roofed in the next two to four years with a 50 year asphalt composition roofing shingle and new underlayments. This project or a portion thereof was previously recommended in the FCA report dated 08/21/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/20/2007. | ADMINISTRATION/HOUSING/CULINARY | 9976 | Correct | ECC |  | Ely | 1984 | 13968 | 2017-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 140000
1388HVA4 | REPLACE EXPANSION TANK BLADDERS | 1388 | At the time of the 2007 survey, the maintenance staff reported that the bladders in the two expansion tanks had failed. It is assumed that the age of the equipment is the cause of the failure. This project provides funding for removal of the existing bladders and installation of two new bladders in the existing expansion tanks. | ADMINISTRATION/HOUSING/CULINARY | 9976 | Correct | ECC |  | Ely | 1984 | 13968 | 2017-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
1389ADA1 | ADA RESTROOM REMODEL | 1389 | The restroom does not meet the Americans with Disabilities Act (ADA) regulations. A retrofit is necessary to comply with ICC/ANSI A117.1-1998 Sections 603 - 604 and 2018 ICC Chapter 11. Given the current configuration of the restroom, the work will include the installation of a new toilet, sink, grab bars, faucet, mirror, dispensers, and door hardware. Some minor design work will be required and may impact the final cost estimate. This estimate is for one Men's restroom facility. The removal and disposal of the old restroom fixtures is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 08/21/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/20/2007. | MULTI-PURPOSE/GYMNASIUM | 9976 | Correct | ECC |  | Ely | 1987 | 6743 | 2017-05-24 | Immediate to Two Years | Currently Critical | 1 | 50000
1388HVA2 | REPLACE AIR CONDITIONING UNITS | 1388 | The building has four window-mounted air conditioning units. These units have a life span of 10 years under normal operating conditions. From a visual assessment it appears they will be reaching the end of their useful life within a few years. This project provides funding for removal and disposal of the existing units and replacement with new units. This project or a portion thereof was previously recommended in the FCA report dated 08/21/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/20/2007. | ADMINISTRATION/HOUSING/CULINARY | 9976 | Correct | ECC |  | Ely | 1984 | 13968 | 2017-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
1388ADA1 | ADA RESTROOM REMODEL | 1388 | The restroom does not meet the Americans with Disabilities Act (ADA) regulations. A retrofit is necessary to comply with ICC/ANSI A117.1-1998 Sections 603 - 604, 2018 IBC Chapter 11 and the Americans with Disabilities Act Accessibility Guidelines (ADAAG). Given the current configuration of the restroom, the work will include the installation of a new toilet, sink, grab bars, faucets, mirrors, dispensers, hardware and an accessible shower stall. Some minor design work will be required and may impact the final cost estimate. This estimate is for one Men's restroom facility. The removal and disposal of the old restroom fixtures is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 08/21/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/20/2007. | ADMINISTRATION/HOUSING/CULINARY | 9976 | Correct | ECC |  | Ely | 1984 | 13968 | 2017-05-24 | Immediate to Two Years | Currently Critical | 1 | 60000
1388HVA1 | BATHROOM EXHAUST FAN REPLACEMENT | 1388 | The exhaust fans in the showers and restroom areas are inoperative and/ or insufficient, contributing to moisture accumulation and possible mold infiltration. After the moisture issues are mitigated and wall repairs and repainting occur, the exhaust fans should be replaced. This project would provide for the removal of the existing exhaust fan assemblies and the purchase and installation of new exhaust fan assemblies including ducting and connections to utilities. This report recommends the installation of high efficiency exhaust fans with humidity detection and delayed shut-off to exhaust all moisture and prevent future accumulation issues. This project or a portion thereof was previously recommended in the FCA report dated 08/21/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/20/2007. | ADMINISTRATION/HOUSING/CULINARY | 9976 | Correct | ECC |  | Ely | 1984 | 13968 | 2017-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
1388EXT2 | REPLACE EXTERIOR WINDOWS | 1388 | The windows are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 52 units. This project or a portion thereof was previously recommended in the FCA report dated 08/21/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/20/2007. | ADMINISTRATION/HOUSING/CULINARY | 9976 | Correct | ECC |  | Ely | 1984 | 13968 | 2017-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 52000
1388SEC1 | EXTERIOR DOOR REPLACEMENT | 1388 | The existing exterior commercial grade metal door assemblies appear to be original to the building. They are showing signs of wear and deterioration from constant use and abuse. Due security concerns and the condition of the doors, this project recommends the installation of new metal doors, frames and hardware and includes the disposal of the existing door assemblies. This project or a portion thereof was previously recommended in the FCA report dated 08/21/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/20/2007. | ADMINISTRATION/HOUSING/CULINARY | 9976 | Correct | ECC |  | Ely | 1984 | 13968 | 2017-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 40000
1388INT1 | INTERIOR FINISHES | 1388 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 08/21/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/20/2007. | ADMINISTRATION/HOUSING/CULINARY | 9976 | Correct | ECC |  | Ely | 1984 | 13968 | 2017-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 69840
1388EXT1 | EXTERIOR FINISHES | 1388 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. This project or a portion thereof was previously recommended in the FCA report dated 08/21/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/20/2007. | ADMINISTRATION/HOUSING/CULINARY | 9976 | Correct | ECC |  | Ely | 1984 | 13968 | 2017-05-24 | Four to Ten Years | Long-Term Needs | 3 | 139680
1388INT2 | REPAIR JANITORS CLOSET | 1388 | The mop sink in the Janitors Closet is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. This project or a portion thereof was previously recommended in the FCA report dated 08/21/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/20/2007. | ADMINISTRATION/HOUSING/CULINARY | 9976 | Correct | ECC |  | Ely | 1984 | 13968 | 2017-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
1389ADA2 | SIGNAGE FOR ADA COMPLIANCE | 1389 | The building is lacking ADA signage. Americans with Disabilities Act (ADA) regulations pertaining to parking, building access, route of travel and restrooms has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances, route of travel inside the building and restrooms. IBC - 2018, ICC/ANSI A117.1 - 2003 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2003 were referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 08/21/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/20/2007. | MULTI-PURPOSE/GYMNASIUM | 9976 | Correct | ECC |  | Ely | 1987 | 6743 | 2017-05-24 | Immediate to Two Years | Currently Critical | 1 | 2000
1389SFT1 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 1389 | The existing exit signs in this building are older types and should be replaced with new self-illuminated or LED style signs with battery-backed internal systems. Emergency exit lighting should be installed and/or replaced to provide illumination along the egress route. This project or a portion thereof was previously recommended in the FCA report dated 08/21/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/20/2007. | MULTI-PURPOSE/GYMNASIUM | 9976 | Correct | ECC |  | Ely | 1987 | 6743 | 2017-05-24 | Immediate to Two Years | Currently Critical | 1 | 1500
1388ENR1 | LIGHTING UPGRADE | 1388 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 08/21/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/20/2007. | ADMINISTRATION/HOUSING/CULINARY | 9976 | Correct | ECC |  | Ely | 1984 | 13968 | 2017-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 41904
1388SFT4 | GFCI DUPLEX OUTLET REPLACEMENT | 1388 | There are 6 GFCI outlets in the restrooms which are not GFCI protected outlets. These outlets are near sinks requiring the outlets to be protected. This project would provide for the purchase and installation of 6 new GFCI duplex outlets. | ADMINISTRATION/HOUSING/CULINARY | 9976 | Correct | ECC |  | Ely | 1984 | 13968 | 2017-05-24 | Immediate to Two Years | Currently Critical | 1 | 1500
1388PLM2 | REPLACE DOMESTIC WATER PIPING | 1388 | The domestic water piping under the building are original to the building and are beginning to fail. At the time of the survey, staff reported that the lines are continuously developing leaks. The maintenance time and loss of water is enough to warrant an entire replacement of the piping. This project would provide funding for the removal and disposal of the existing domestic water lines and installation domestic water supply piping. | ADMINISTRATION/HOUSING/CULINARY | 9976 | Correct | ECC |  | Ely | 1984 | 13968 | 2017-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 75000
1388CUL1 | REPLACE KITCHEN EQUIPMENT | 1388 | The kitchen cooking equipment is original to the building and is reaching the end of its lifetime. It is recommended that the equipment be scheduled for replacement in the next two to three years, including ovens, grills and the dishwasher. This project provides for the removal and disposal of the existing equipment and replacement with new equipment. This estimate is a lump some for budgeting purposes. | ADMINISTRATION/HOUSING/CULINARY | 9976 | Correct | ECC |  | Ely | 1984 | 13968 | 2017-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
1388SFT3 | INSTALL FIRE SUPPRESSION SYSTEM | 1388 | This building does not have an automatic fire suppression system. Nevada State Fire Marshal NRS 477.915 (c) requires buildings having a floor area exceeding 12,000 s.f. on any floor or 24,000 s.f. on all floors, or which contain a B or R-1 occupancy, be scheduled for installation of an automatic fire suppression system during the next remodeling of, or addition to the building. Backflow prevention is included in this estimate. This building exceeds 12,000 s.f. and is partially classified as a B occupancy. This project or a portion thereof was previously recommended in the FCA report dated 08/21/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/20/2007. | ADMINISTRATION/HOUSING/CULINARY | 9976 | Correct | ECC |  | Ely | 1984 | 13968 | 2017-05-24 | Immediate to Two Years | Currently Critical | 1 | 69840
1388HVA5 | REPLACE WATER TREATMENT SYSTEMS | 1388 | The existing water softening/ treatment systems in the building are currently operational, but are original to the building and approaching the end of their lifecycles. Failure of the equipment would cause wear and tear on the domestic water supply lines, plumbing fixtures and HVAC equipment. This project would provide for the replacement of the existing water softeners/ treatment systems with new equipment. This project would also provide for a chemical treatment program including an updated chemicals control system, service and employee training provided by a qualified water treatment vendor. The annual maintenance fee charged by the water treatment vendor would be determined after an investigation of the water system is complete. These annual costs are not included in this project cost. For budgeting purposes, a $12,000 fee is suggested. | ADMINISTRATION/HOUSING/CULINARY | 9976 | Correct | ECC |  | Ely | 1984 | 13968 | 2017-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 40000
1388INT6 | RESTROOM REMODEL | 1388 | The bathroom and shower rooms are in overall poor condition. The countertops in each wing show signs of wear and deterioration. Extensive use, combined with repetitive water being spilled, has caused the laminate top to separate from the wooden underlayment and should be replaced. The tile on the floors and walls of the bathrooms are damaged and worn and should be replaced. This project provides for a complete remodel of the bathrooms and shower rooms. Given the current configuration of the restrooms, the work will include the installation of a new toilet, sink, grab bars, faucets, mirrors, dispensers, hardware and an accessible shower stall. Some minor design work will be required and may impact the final cost estimate. This estimate is for three Men's restroom facilities, one in each residential wing. The removal and disposal of the old restroom fixtures is included in this estimate. This project should be coordinated with the ADA restroom project and water line replacement project. This will also address the issue with the floor not properly sloping to the drains. This project or a portion thereof was previously recommended in the FCA report dated 12/01/2001. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2007. | ADMINISTRATION/HOUSING/CULINARY | 9976 | Correct | ECC |  | Ely | 1984 | 13968 | 2017-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500000
1388PLM1 | REPLACE WATER HEATERS | 1388 | The average life span of a water heater is eight to ten years. The three existing 100 gallon propane water heaters in the building have reached the end of their expected life and are not energy efficient. This project would provide for the removal and disposal of the old water heaters and installation of three new 100 gallon propane water heaters. This project or a portion thereof was previously recommended in the FCA report dated 08/21/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/20/2007. | ADMINISTRATION/HOUSING/CULINARY | 9976 | Correct | ECC |  | Ely | 1984 | 13968 | 2017-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
1388ADA2 | SIGNAGE FOR ADA COMPLIANCE | 1388 | The building is lacking ADA signage. Americans with Disabilities Act (ADA) regulations pertaining to parking, building access, route of travel and restrooms has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances, route of travel inside the building and restroom. IBC - 2018, ICC/ANSI A117.1 - 2003 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2003 were referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 08/21/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/20/2007. | ADMINISTRATION/HOUSING/CULINARY | 9976 | Correct | ECC |  | Ely | 1984 | 13968 | 2017-05-24 | Immediate to Two Years | Currently Critical | 1 | 2000
1388HVA3 | HEATING CONTROLS REPLACEMENT AND UPGRADE | 1388 | The existing heating system controls are malfunctioning or inoperative. This project will provide a new master panel with remote monitoring, pulling new wire, associated controls and thermostats. This project or a portion thereof was previously recommended in the FCA report dated 08/21/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/20/2007. | ADMINISTRATION/HOUSING/CULINARY | 9976 | Correct | ECC |  | Ely | 1984 | 13968 | 2017-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
1389HVA1 | REPLACE CEILING MOUNTED HEATERS | 1389 | The building is heated by three ceiling mounted gas unit heaters. They are original to the building and are reaching the end of their useful life. This project provides for disposal of the existing units and replacement of the existing units and associated utility connections. | MULTI-PURPOSE/GYMNASIUM | 9976 | Correct | ECC |  | Ely | 1987 | 6743 | 2017-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
1389EXT2 | REPLACE OVERHEAD COILING DOOR | 1389 | There is a 12'x12' overhead coiling door which is damaged and does not function properly. It is original to the building and should be scheduled for replacement. This project would provide for the removal and replacement of the manually operated overhead coiling door. | MULTI-PURPOSE/GYMNASIUM | 9976 | Correct | ECC |  | Ely | 1987 | 6743 | 2017-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
1388INT5 | NONABSORBANT FINISHES | 1388 | 2018 IBC Section 1210 requires the installation of smooth, hard, nonabsorbent surfaces in the following restroom areas: on floors in toilet and bathing rooms that extend upward onto the walls at least 6 inches, within 2 feet of the sides of urinals and water closets to a height of 4 feet above the floor and in shower compartments to a height not less than 70 inches above the drain inlet. This project recommends the installation of Fiberglass Reinforced Panel (FRP) or an equal material to comply with this code section. | ADMINISTRATION/HOUSING/CULINARY | 9976 | Correct | ECC |  | Ely | 1984 | 13968 | 2017-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7000
1389ENR1 | LIGHTING UPGRADE | 1389 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 08/21/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/20/2007. | MULTI-PURPOSE/GYMNASIUM | 9976 | Correct | ECC |  | Ely | 1987 | 6743 | 2017-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20229
1389INT1 | INTERIOR FINISHES | 1389 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 08/21/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/20/2007. | MULTI-PURPOSE/GYMNASIUM | 9976 | Correct | ECC |  | Ely | 1987 | 6743 | 2017-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 33715
1389EXT1 | EXTERIOR FINISHES | 1389 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | MULTI-PURPOSE/GYMNASIUM | 9976 | Correct | ECC |  | Ely | 1987 | 6743 | 2017-05-24 | Four to Ten Years | Long-Term Needs | 3 | 33715
1389SFT3 | REBUILD HANDRAILS / GUARDRAILS | 1389 | The handrails and guardrails at the stairway and storage mezzanine do not meet the building code requirements in their current configuration. This project would provide for the removal of the existing wood framed railing and replacement with new wood framed handrails and guardrail that will meet the 2018 IBC code Chapter 10, Section 1012 and 1013. | MULTI-PURPOSE/GYMNASIUM | 9976 | Correct | ECC |  | Ely | 1987 | 6743 | 2017-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3500
1389SFT2 | LAUNDRY ROOM REPAIRS | 1389 | The Laundry Room has a base board heater installed in the wall due to the inadequate heating of the building. When the ceiling mounted heating units are replaced, this base board heater should be removed and the gypsum board repaired. The base board heater poses a fire risk as it is currently installed and is not an acceptable solution to the heating inefficiencies. | MULTI-PURPOSE/GYMNASIUM | 9976 | Correct | ECC |  | Ely | 1987 | 6743 | 2017-05-24 | Immediate to Two Years | Currently Critical | 1 | 1000
1389HVA2 | REPLACE WATER HEATER | 1389 | The average life span of a water heater is eight to ten years. The existing 100 gallon propane water heater will be reaching the end of its expected life and should be scheduled for replacement. This project would provide for the removal of the existing water heater and the replacement with a new water heater including required connections to utilities. | MULTI-PURPOSE/GYMNASIUM | 9976 | Correct | ECC |  | Ely | 1987 | 6743 | 2017-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
2728EXT1 | EXTERIOR FINISHES | 2728 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | MAINTENANCE SHOP | 9976 | Correct | ECC |  | Ely | 0 | 352 | 2017-05-24 | Four to Ten Years | Long-Term Needs | 3 | 4410
2727EXT1 | EXTERIOR FINISHES | 2727 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | PHONE RAMADA | 9976 | Correct | ECC |  | Ely | 0 | 352 | 2017-05-24 | Four to Ten Years | Long-Term Needs | 3 | 704
2130EXT1 | EXTERIOR FINISHES | 2130 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | TOOL SHED | 9976 | Correct | ECC |  | Ely |  | 102 | 2017-05-24 | Four to Ten Years | Long-Term Needs | 3 | 1020
2129EXT1 | EXTERIOR FINISHES | 2129 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | STORAGE SHED | 9976 | Correct | ECC |  | Ely |  | 80 | 2017-05-24 | Four to Ten Years | Long-Term Needs | 3 | 800
2131EXT1 | EXTERIOR FINISHES | 2131 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | WEIGHT ROOM BUILDING | 9976 | Correct | ECC |  | Ely |  | 590 | 2017-05-24 | Four to Ten Years | Long-Term Needs | 3 | 2950
9976PLM1 | INSTALL NEW SEPTIC SYSTEM | 9976 | The existing septic system backs-up frequently and requires frequent pumping. Visual inspection of the septic tanks and leach field piping at the time of the survey showed that the system was virtually inoperable. This project provides funding for abandonment of the existing system and installation of new septic tanks and leach fields for the facility. The system must comply with local, State and Federal environmental laws. | ELY CONSERVATION CAMP SITE | 9976 | Correct | ECC |  | Ely | 1984 |  | 2017-05-24 | Immediate to Two Years | Currently Critical | 1 | 100000
9976SIT2 | PATCH / SLURRY SEAL ASPHALT PAVING | 9976 | It is important to maintain the asphalt concrete paving on the site. This project would provide for patching, minor crack filling and slurry sealing of the paving site wide including loading zones, access roads and parking areas. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. This project should coincide with the ADA parking project. | ELY CONSERVATION CAMP SITE | 9976 | Correct | ECC |  | Ely | 1984 |  | 2017-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 40000
9976SEC1 | INSTALL POLE LIGHTING AROUND PARKING LOT | 9976 | The entrance road and parking area have insufficient lighting. Considering the environment of the site, this area needs to be well lit. This project would provide funding for purchase and installation of twelve 30 foot tall light poles including 30" diameter raised concrete bases, electrical trenching, conduit, wiring and connections to existing utilities. This project or a portion thereof was previously recommended in the FCA report dated 08/21/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/20/2007. | ELY CONSERVATION CAMP SITE | 9976 | Correct | ECC |  | Ely | 1984 |  | 2017-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 110448
9976ADA1 | ADA PARKING SPACE | 9976 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. A concrete parking area and passenger loading area are necessary to comply with ADA requirements. This project would provide for a concrete van accessible ADA parking and loading space and walkway to the existing sidewalk. 1,000 square feet of concrete was used for this estimate. Signage and striping is included. IBC - 2018, ICC/ANSI A117.1 - 2009 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2009 were referenced for this project. | ELY CONSERVATION CAMP SITE | 9976 | Correct | ECC |  | Ely | 1984 |  | 2017-05-24 | Immediate to Two Years | Currently Critical | 1 | 25000
2457HVA7 | CULINARY MAKE-UP AIR REPLACEMENT | 2457 | There are two roof mounted make-up air units for the culinary equipment that are reaching the end of their useful life and should be scheduled for replacement. This project would provide for the installation of two new roof mounted make-up air units including variable frequency drive fan motors for energy efficiency. Removal and disposal of the old equipment and connections to existing utility and ductwork is included in this estimate. | ADMINISTRATION/HOUSING UNITS | 9893 | Correct | FMWCC |  | North Las Vegas | 1997 | 199212 | 2018-12-11 | Immediate to Two Years | Currently Critical | 1 | 40000
2786EXT1 | EXTERIOR FINISHES | 2786 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units, painting of the doors, window frames and other painted metal surfaces and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | FMWCC DORM HOUSING UNIT #9 | 9893 | Correct | FMWCC |  | North Las Vegas | 2008 | 23780 | 2018-12-11 | Four to Ten Years | Long-Term Needs | 3 | 118900
2786INT1 | INTERIOR FINISHES | 2786 | The interior finishes are in fair condition. It is recommended that the interior CMU and gypsum board walls be sealed and painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | FMWCC DORM HOUSING UNIT #9 | 9893 | Correct | FMWCC |  | North Las Vegas | 2008 | 23780 | 2018-12-11 | Four to Ten Years | Long-Term Needs | 3 | 47560
2512EXT1 | EXTERIOR FINISHES | 2512 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete walls and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | FMWCC ARMORY | 9893 | Correct | FMWCC |  | North Las Vegas | 1997 | 320 | 2018-12-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1600
2512INT1 | INTERIOR FINISHES | 2512 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. | FMWCC ARMORY | 9893 | Correct | FMWCC |  | North Las Vegas | 1997 | 320 | 2018-12-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1600
2512SFT1 | EXIT SIGN AND EGRESS LIGHTING INSTALLATION | 2512 | The building does not have an exit sign or emergency lighting. This project would provide for the purchase and installation of a self-illuminated or LED style exit sign with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2006 Chapter 10 was referenced for this project. | FMWCC ARMORY | 9893 | Correct | FMWCC |  | North Las Vegas | 1997 | 320 | 2018-12-11 | Immediate to Two Years | Currently Critical | 1 | 800
2512HVA1 | HVAC EQUIPMENT REPLACEMENT | 2512 | The packaged roof top unit was installed in 1997. It is not energy efficient and has reached the end of its expected and useful life. This project would provide for installation of a new packaged unit and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC unit and all required connections to utilities. | FMWCC ARMORY | 9893 | Correct | FMWCC |  | North Las Vegas | 1997 | 320 | 2018-12-11 | Four to Ten Years | Long-Term Needs | 3 | 3500
2513EXT1 | EXTERIOR FINISHES | 2513 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SHADE RAMADA 1 | 9893 | Correct | FMWCC |  | North Las Vegas | 2004 | 484 | 2018-12-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
2514EXT1 | EXTERIOR FINISHES | 2514 | It is important to maintain the finish, weather resistance and appearance of the structure. This project recommends work to protect the exterior building envelope including repairs to the exterior polycarbonate panels and caulking around the panels, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 3-4 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | FMWCC GREENHOUSE | 9893 | Correct | FMWCC |  | North Las Vegas | 1997 | 360 | 2018-12-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 720
2457EXT4 | ROOF REPLACEMENT | 2457 | The roof on the 1997 portion of the building was in fair to poor condition at the time of the survey. The built-up ballasted roof system is 15 years old and numerous leaks have occurred recently. It is recommended that this older ballasted roof be replaced with a single-ply membrane system in the next 2-3 years. The new membrane will have a 20 year warranty with a preventative maintenance agreement to ensure that any future leaks will be repaired by the manufacturer. | ADMINISTRATION/HOUSING UNITS | 9893 | Correct | FMWCC |  | North Las Vegas | 1997 | 199212 | 2018-12-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1706544
2457ELE1 | TRANSFORMER REPLACEMENT | 2457 | There is an electrical transformer located inside the main electrical room. The transformer is original to the building dating to 1997 and creates excessive heat. This project recommends replacing the transformer with a new 225 kVA three phase power transformer. | ADMINISTRATION/HOUSING UNITS | 9893 | Correct | FMWCC |  | North Las Vegas | 1997 | 199212 | 2018-12-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
2457SFT1 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 2457 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 05/05/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/02/2011. | ADMINISTRATION/HOUSING UNITS | 9893 | Correct | FMWCC |  | North Las Vegas | 1997 | 199212 | 2018-12-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
2457HVA6 | HVAC REPLACEMENT | 2457 | The existing HVAC system in the original 1997 portion of the building consists of (6) 1,281 MBH output Lochinvar hot water boilers and approximately 38 roof top evaporative coolers and packaged units. They are not energy efficient and have reached the end of their expected and useful life. This equipment is original to the building and should be scheduled for replacement. This project would provide for replacing the boilers, the boiler controls, mixing valves, evaporative coolers and packaged units with new equipment and includes removal and disposal of the existing HVAC units and all required connections to utilities. | ADMINISTRATION/HOUSING UNITS | 9893 | Correct | FMWCC |  | North Las Vegas | 1997 | 199212 | 2018-12-11 | Four to Ten Years | Long-Term Needs | 3 | 2000000
2457HVA5 | AIR CONDITIONER INSTALLATION | 2457 | The main electrical room is not sufficiently cooled by the existing HVAC system. If the room is too warm, the electrical equipment will prematurely age and may fail due to overheating. It is recommended to install an air conditioning system in the room to ensure that the temperature is properly regulated. This project would provide for the purchase and installation of an air conditioner including all required connections to existing utilities. | ADMINISTRATION/HOUSING UNITS | 9893 | Correct | FMWCC |  | North Las Vegas | 1997 | 199212 | 2018-12-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
2457HVA4 | REPLACE FREEZER COMPRESSORS | 2457 | There are two low velocity unit compressors servicing the culinary freezer. They are original to the building dating back to 1997. Replacement parts for performing routine and emergency maintenance are hard to find for this old equipment. This project would provide for the removal and disposal of the existing compressors with new equipment including all required connections to utilities and equipment. The estimate is based on two 13,400 BTUH low velocity unit compressors. | ADMINISTRATION/HOUSING UNITS | 9893 | Correct | FMWCC |  | North Las Vegas | 1997 | 199212 | 2018-12-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
2457PLM3 | DRYER EXHAUST DUCT UPGRADE | 2457 | Each of the four clothes dryers are vented with one 90 degree elbow and goes vertically 25’ through the roof and protrudes above the ceiling by another 2 feet. The IMC 504.6.1 states the maximum length of a clothes dryer exhaust duct shall not exceed 25 ft from the dryer location to the outlet terminal. The maximum length of duct shall be reduced 2 ½ feet for each 45-degree bend and 5 feet for each 90-degree bend. This project recommends the installation of a booster fan installed on each of the four exhaust ducts per manufacture’s specifications to insure proper exhaust is obtained. This project or a portion thereof was previously recommended in the FCA report dated 05/05/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/02/2011. | ADMINISTRATION/HOUSING UNITS | 9893 | Correct | FMWCC |  | North Las Vegas | 1997 | 199212 | 2018-12-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
2457INT2 | CARPET REPLACEMENT | 2457 | The carpet in the Administration/ Office wing is showing signs of extreme wear. It is recommended that the carpet be replaced with heavy duty commercial grade carpet in the next 2-3 years. This project or a portion thereof was previously recommended in the FCA report dated 05/05/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/02/2011. | ADMINISTRATION/HOUSING UNITS | 9893 | Correct | FMWCC |  | North Las Vegas | 1997 | 199212 | 2018-12-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14000
2457SFT2 | FIRE ALARM SYSTEM UPGRADE | 2457 | This building, excluding the recent addition, is equipped with an automatic fire detection and alarm system that no longer complies with current requirements. At the time of the survey, the main fire alarm panel had a "trouble" status and staff indicated that they could not remedy the problem. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 "If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure". When completed, the new system will provide visual, as well as audible notification, in accordance with the 2006 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. This project or a portion thereof was previously recommended in the FCA report dated 05/05/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/02/2011. | ADMINISTRATION/HOUSING UNITS | 9893 | Correct | FMWCC |  | North Las Vegas | 1997 | 199212 | 2018-12-11 | Immediate to Two Years | Currently Critical | 1 | 568848
2457SEC2 | SECURITY EQUIPMENT UPGRADES | 2457 | This building is equipped with a security system including monitoring equipment, door controls, video surveillance and communications. The new touch screen controls in the original building were installed in 2010. They were connected to the existing 1980's CCTV and Intercom electronics racks. This has caused problems with security because the new technology does not function properly with the old technology. Also, the new touch screen controls installed in 2010 have different functionality than the touch screen controls installed in the addition in 2008. This causes confusion with the operators who move from one system to the other on a day to day basis. This project would provide for the purchase and installation of CCTV and Intercom equipment to replace the original 1980's racks and upgrading the 2008 touch screen software to match the newer 2010 controls. Removal and disposal of the existing equipment and all required connections to existing utilities are included in this project.0 | ADMINISTRATION/HOUSING UNITS | 9893 | Correct | FMWCC |  | North Las Vegas | 1997 | 199212 | 2018-12-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 250000
2457INT6 | SHOWER REPLACEMENT | 2457 | The shower ceilings, walls, floors and fixtures in Housing Units A & B are in poor condition and should be scheduled for replacement. The gypsum board ceiling has been removed and the ceramic tile walls and painted concrete flooring are damaged and failing. The exposed pipes at the ceiling are rusting and should not be exposed to the wet environment and is also a safety concern for inmates. This project would provide for removing the walls, ceilings, flooring and fixtures and replacing them with a uniform ceramic tile finish or stainless steel units. Removal and disposal of the existing materials is included in the estimate. | ADMINISTRATION/HOUSING UNITS | 9893 | Correct | FMWCC |  | North Las Vegas | 1997 | 199212 | 2018-12-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 170000
2457INT5 | INTERIOR FINISHES | 2457 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | ADMINISTRATION/HOUSING UNITS | 9893 | Correct | FMWCC |  | North Las Vegas | 1997 | 199212 | 2018-12-11 | Four to Ten Years | Long-Term Needs | 3 | 996060
2457EXT3 | EXTERIOR FINISHES | 2457 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete walls and caulking of the control joints, windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | ADMINISTRATION/HOUSING UNITS | 9893 | Correct | FMWCC |  | North Las Vegas | 1997 | 199212 | 2018-12-11 | Four to Ten Years | Long-Term Needs | 3 | 996060
2457PLM4 | WASHER / EXTRACTORS & DRYER REPLACEMENT | 2457 | Two of the four commercial washer / extractors and tumbler dryers in the laundry are original to the building and are troublesome and problematic to operate. Considering the age of the machines and the evolving needs of the facility, it is recommended to replace them. This project provides for removal and disposal of the existing washer / extractors and tumbler dryers with new units. A total of 2 washers and 2 dryers was used for this estimate. | ADMINISTRATION/HOUSING UNITS | 9893 | Correct | FMWCC |  | North Las Vegas | 1997 | 199212 | 2018-12-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 76000
2457PLM1 | WATER SHUT OFF VALVES | 2457 | The original building has a 2" domestic water line that circles the interior of the building. There is no way to shut off the water supply to the individual wings without shutting off water service to the whole building. This project will provide four 2" brass gate valves to be installed in 4 strategic locations recommended by facility staff. This project or a portion thereof was previously recommended in the FCA report dated 05/05/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/02/2011. | ADMINISTRATION/HOUSING UNITS | 9893 | Correct | FMWCC |  | North Las Vegas | 1997 | 199212 | 2018-12-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
2457ADA1 | ADA SIGNAGE | 2457 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | ADMINISTRATION/HOUSING UNITS | 9893 | Correct | FMWCC |  | North Las Vegas | 1997 | 199212 | 2018-12-11 | Immediate to Two Years | Currently Critical | 1 | 3500
2457CUL1 | SERVING TRAY REPLACEMENT | 2457 | The hot and cold serving trays in the culinary are original to the building and are no longer operating. Considering the age of the equipment and the evolving needs of the facility it is recommended to replace them. This project provides for removal and disposal of the 6-well steam table and the 6-well cold table with new equipment. | ADMINISTRATION/HOUSING UNITS | 9893 | Correct | FMWCC |  | North Las Vegas | 1997 | 199212 | 2018-12-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
2457PLM5 | WATER TREATMENT SYSTEM REPLACEMENT | 2457 | The existing water softening/ treatment systems in the building are currently not operational. They are original to the building and approaching the end of their lifecycles. Failure of the equipment causes wear and tear on the domestic water supply lines, plumbing fixtures and HVAC equipment. This project would provide for the replacement of the existing water softeners/ treatment systems with new equipment. This project would also provide for a chemical treatment program including an updated chemicals control system, service and employee training provided by a qualified water treatment vendor. The annual maintenance fee charged by the water treatment vendor would be determined after an investigation of the water system is complete. These annual costs are not included in this project cost. For budgeting purposes, a $12,000 fee is suggested. | ADMINISTRATION/HOUSING UNITS | 9893 | Correct | FMWCC |  | North Las Vegas | 1997 | 199212 | 2018-12-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 90000
9893SIT4 | SLURRY SEAL ASPHALT PAVING | 9893 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site wide including access roads, parking areas and the maintenance yard. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 90,000 square feet of asphalt area was used to generate this estimate. | FMWCC SITE | 9893 | Correct | FMWCC |  | North Las Vegas | 1997 |  | 2018-12-11 | Four to Ten Years | Long-Term Needs | 3 | 67500
3107INT1 | INTERIOR FINISHES | 3107 | The interior finishes are in fair condition. It is recommended that the interior walls and ceiling be painted at least once in the next 5-6 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. | SALLY PORT GUARD STATION | 9893 | Correct | FMWCC |  | North Las Vegas | 2008 | 128 | 2018-12-11 | Four to Ten Years | Long-Term Needs | 3 | 640
3107EXT1 | EXTERIOR FINISHES | 3107 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the metal siding and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SALLY PORT GUARD STATION | 9893 | Correct | FMWCC |  | North Las Vegas | 2008 | 128 | 2018-12-11 | Four to Ten Years | Long-Term Needs | 3 | 640
3108EXT1 | EXTERIOR FINISHES | 3108 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SHADE RAMADA 2 | 9893 | Correct | FMWCC |  | North Las Vegas | 2010 | 240 | 2018-12-11 | Four to Ten Years | Long-Term Needs | 3 | 300
9893PLM1 | SEWAGE GRINDER INSTALLATION | 9893 | The main sewage line exiting the facility is connected to the city sewer system. There is a lift station before the connection to the city line, but no sewage grinder. This has caused blockages and clogging of the lift station and piping requiring costly maintenance and repairs. It is recommended to install a sewage grinder on the main line before it reaches the lift station to remedy this problem. This project would provide for the purchase and installation of a sewage grinder on the existing sewer line. | FMWCC SITE | 9893 | Correct | FMWCC |  | North Las Vegas | 1997 |  | 2018-12-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0431ADA2 | ADA RESTROOM REMODEL | 0431 | The designated unisex ADA accessible restroom is not fully compliant. There is no pipe protection, the toilet paper dispenser is not in the correct location, and the flush handle is on the wrong side. A partial retrofit is necessary. This project would provide funding to bring the restroom into full ADA compliance. The 2018 IBC, ICC/ANSI A117.1, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #089 ADMINISTRATION (NDOC) | 9971 | Correct | B&G |  | Stewart | 1931 | 17545 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 2400
0431ADA4 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0431 | This building contains a water fountain that is not ADA compliant. The 2018 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA require This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #089 ADMINISTRATION (NDOC) | 9971 | Correct | B&G |  | Stewart | 1931 | 17545 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 2700
0431ADA3 | BREAK ROOM REMODEL | 0431 | The employee lounge does not meet the Americans with Disabilities Act (ADA) requirements. It is recommended to upgrade some of the features of the room for compliance with accessibility standards for employees. This project would provide funding for construction of an accessible sink and faucet and an accessible path of travel throughout the room. The 2018 IBC, ICC/ANSI A117.1, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #089 ADMINISTRATION (NDOC) | 9971 | Correct | B&G |  | Stewart | 1931 | 17545 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 2400
0431SFT2 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0431 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems, as well as emergency egress lighting, to provide illumination along the egress route. IBC - 2018 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #089 ADMINISTRATION (NDOC) | 9971 | Correct | B&G |  | Stewart | 1931 | 17545 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 10400
0431SFT5 | CONCRETE STAIRS REPLACEMENT | 0431 | The concrete stairs that access the building and the wood stairs in the courtyard are not code compliant and many areas of the concrete are spalling and cracking. It appears these stairs are original to the building and should be scheduled for replacement. This project would provide for removal and disposal of the existing concrete and wood stairs and handrails and installation of new compliant stairs and handrails. The estimate is for the replacement of 6 separate stairs. 2018 IBC Chapter 10 was used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #089 ADMINISTRATION (NDOC) | 9971 | Correct | B&G |  | Stewart | 1931 | 17545 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 45000
0431INT1 | INTERIOR FINISHES | 0431 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | #089 ADMINISTRATION (NDOC) | 9971 | Correct | B&G |  | Stewart | 1931 | 17545 | 2020-02-07 | Four to Ten Years | Long-Term Needs | 3 | 105000
0431SIT1 | REMOVE SPRINKLERED LAWN WITHIN 3' OF BUILDING | 0431 | The building has some damage to the stone exterior from lawn sprinklers wetting the walls. The water has stained the stone and caused premature cracking to the mortar. This project would create drip irrigated planters within three feet of the building and relocate sprinklers so they do not wet the building. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #089 ADMINISTRATION (NDOC) | 9971 | Correct | B&G |  | Stewart | 1931 | 17545 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 17000
0431INT3 | RESTROOM REMODELS | 0431 | The large Men's and Women's restrooms are in overall poor condition and should be scheduled for a remodel. The finishes, fixtures, partitions, water closets, urinals and exhaust fans are showing signs of wear and deterioration. This project would provide for a complete remodel of the restrooms. The removal and disposal of the existing fixtures and finishes is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #089 ADMINISTRATION (NDOC) | 9971 | Correct | B&G |  | Stewart | 1931 | 17545 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 84000
0431EXT2 | EXTERIOR FINISHES | 0431 | The exterior finishes appear to be in good condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting the wood finishes, re-pointing the stone where needed, and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | #089 ADMINISTRATION (NDOC) | 9971 | Correct | B&G |  | Stewart | 1931 | 17545 | 2020-02-07 | Four to Ten Years | Long-Term Needs | 3 | 105000
0438EXT2 | EXTERIOR FINISHES | 0438 | The exterior finishes are in poor condition with some of the masonry appears loose with grout falling out. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting the wood finishes, re-pointing the stone where needed, and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2 - 3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | #018 OFFICE (NDOC) | 9971 | Correct | B&G |  | Stewart | 1936 | 3700 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 22000
0438SFT5 | ADA ACCESSIBLE PATH OF TRAVEL | 0438 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the office entrance are necessary to comply with ADA accessibility requirements. This project would provide for a concrete van accessible ADA parking and loading space and concrete walkway to the entrance. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2018 IBC, ICC/ANSI A117.1, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #018 OFFICE (NDOC) | 9971 | Correct | B&G |  | Stewart | 1936 | 3700 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 36000
0438ADA1 | ADA RESTROOM UPGRADE | 0438 | The building does not have an accessible restroom. The existing restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for remodeling the Men's and Women's restrooms into ADA compliant restrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2018 IBC, ICC/ANSI A117.1, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #018 OFFICE (NDOC) | 9971 | Correct | B&G |  | Stewart | 1936 | 3700 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 30000
0438PLM1 | WATER HEATER REPLACEMENT | 0438 | There is a 15 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #018 OFFICE (NDOC) | 9971 | Correct | B&G |  | Stewart | 1936 | 3700 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1200
0438SFT1 | EXIT SIGN & EGRESS LIGHTING | 0438 | The building does not have any emergency lighting and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2018 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #018 OFFICE (NDOC) | 9971 | Correct | B&G |  | Stewart | 1936 | 3700 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 11000
0438SFT7 | SEISMIC RETROFIT ROOF STRUCTURE | 0438 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current codes. Visual analysis during the survey found no indication of seismic strengthening of the roof structure. The roof structure should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #018 OFFICE (NDOC) | 9971 | Correct | B&G |  | Stewart | 1936 | 3700 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 173900
0438ENR3 | WINDOW REPLACEMENT | 0438 | The windows are original, dual pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 22 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #018 OFFICE (NDOC) | 9971 | Correct | B&G |  | Stewart | 1936 | 3700 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24200
0433EXT3 | ROOF REPLACEMENT | 0433 | The statewide roofing program has set the useful life of an average roof at 15 years. The roof warranty expires at the end of the same time frame. This roof was installed in 2005 and should be scheduled for replacement. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next 5 years to be consistent with the roofing program and the end of the warranty period. | #017 SCHOOL (NDOC) | 9971 | Correct | B&G |  | Stewart | 1964 | 41826 | 2020-02-07 | Four to Ten Years | Long-Term Needs | 3 | 395000
0433EXT1 | EXTERIOR FINISHES | 0433 | The exterior on the south side is in poor condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are painting the concrete walls, cleaning and sealing the brick masonry, and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2 - 3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | #017 SCHOOL (NDOC) | 9971 | Correct | B&G |  | Stewart | 1964 | 41826 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 249000
0433INT1 | INTERIOR FINISHES | 0433 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | #017 SCHOOL (NDOC) | 9971 | Correct | B&G |  | Stewart | 1964 | 41826 | 2020-02-07 | Four to Ten Years | Long-Term Needs | 3 | 249000
0431ELE1 | ELECTRICAL UPGRADE | 0431 | GFCI receptacles are not installed in all wet locations. A standard receptacle was noted near a toilet. This project would fund a review and replacement of standard outlets with GFCI receptacles in all wet locations by a qualified electrician. | #089 ADMINISTRATION (NDOC) | 9971 | Correct | B&G |  | Stewart | 1931 | 17545 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 1000
0431SFT6 | SEISMIC RETROFIT WALLS | 0431 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current code. Visual analysis during the survey found no indication of seismic strengthening of the URM walls. The walls should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #089 ADMINISTRATION (NDOC) | 9971 | Correct | B&G |  | Stewart | 1931 | 17545 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 1315000
0431HVA1 | CHILLER REPLACEMENT | 0431 | The building is cooled by a 50 ton air-cooled chiller system using R-22 refrigerant. The chiller is reaching the end of its useful life. In addition, it utilizes a refrigerant that is no longer manufactured. It is recommended to schedule replacement of the chiller in the next 3-4 years. This project provides for disposal of the existing unit and replacement with a new 50 ton water cooled chiller including connections to utilities. | #089 ADMINISTRATION (NDOC) | 9971 | Correct | B&G |  | Stewart | 1931 | 17545 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
0431SFT7 | SEISMIC RETROFIT ROOF STRUCTURE | 0431 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current codes. Visual analysis during the survey found no indication of seismic strengthening of the roof structure. The roof structure should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #089 ADMINISTRATION (NDOC) | 9971 | Correct | B&G |  | Stewart | 1931 | 17545 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 825000
0431SFT4 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0431 | The building is a B occupancy per the 2018 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 or R-2 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #089 ADMINISTRATION (NDOC) | 9971 | Correct | B&G |  | Stewart | 1931 | 17545 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 290000
0438INT2 | INTERIOR DOOR REPLACEMENT | 0438 | The interior doors in this building are hollow core units and most are damaged. This project would provide for the installation of new solid core interior doors including frames, lever action door handles, hardware and paint. Removal and disposal of the existing doors is included in this cost estimate. A total of 6 interior doors was used in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #018 OFFICE (NDOC) | 9971 | Correct | B&G |  | Stewart | 1936 | 3700 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7200
0438INT1 | INTERIOR FINISHES | 0438 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | #018 OFFICE (NDOC) | 9971 | Correct | B&G |  | Stewart | 1936 | 3700 | 2020-02-07 | Four to Ten Years | Long-Term Needs | 3 | 22000
0438SFT6 | SEISMIC RETROFIT WALLS | 0438 | This building is an unreinforced masonry (URM) structure which requires seismic strengthening to comply with current code. Visual analysis during the survey found no indication of seismic strengthening of the URM walls. The walls should be seismically retrofitted during the next remodel or change of occupancy. The estimate is for construction costs only. | #018 OFFICE (NDOC) | 9971 | Correct | B&G |  | Stewart | 1936 | 3700 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 277500
1481SFT7 | SPRINKLER HEAD REPLACEMENT | 1481 | The existing fire suppression sprinkler heads are an older style and are susceptible to damage and misuse by the inmates. Inmates have tied strings to them and have broken them in the past. This project recommends that all of the fire sprinkler heads in all cells be removed and replaced with tamper-resistant sprinkler heads. This project or a portion thereof was previously recommended in the FCA report dated 12/13/2016. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC HOUSING UNIT 8 | 9970 | Correct | SDCC |  | Indian Springs | 1988 | 32000 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 44000
1481PLM2 | PLUMBING REPLACEMENT | 1481 | The plumbing and waste system is older and in poor condition. Most of the system appears to be original to the building and should be scheduled for replacement. The sewer lines are rusted and failing especially underground. This project recommends replacing all of the water and sewer lines in the building. This estimate includes removal and disposal of the existing system as required. This project or a portion thereof was previously recommended in the FCA report dated 12/13/2016. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC HOUSING UNIT 8 | 9970 | Correct | SDCC |  | Indian Springs | 1988 | 32000 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 880000
1481INT1 | INTERIOR FINISHES | 1481 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next 8 - 9 year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SDCC HOUSING UNIT 8 | 9970 | Correct | SDCC |  | Indian Springs | 1988 | 32000 | 2020-02-11 | Four to Ten Years | Long-Term Needs | 3 | 384000
1481EXT4 | ROOF REPLACEMENT | 1481 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expired on 05/20/2017. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt onto the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 05/20/2002. It is recommended that this building be re-roofed in the next 3 - 4 years. This project or a portion thereof was previously recommended in the FCA report dated 12/13/2016. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC HOUSING UNIT 8 | 9970 | Correct | SDCC |  | Indian Springs | 1988 | 32000 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 360000
1481EXT3 | WINDOW REPLACEMENT | 1481 | The existing windows in this building are of single pane wire mesh construction. Some are broken and all are not energy efficient. This project would provide for the removal and replacement of the windows with new dual pane security rated windows. This project or a portion thereof was previously recommended in the FCA report dated 12/13/2016. It has been amended accordingly to reflect conditions observed during the most recent survey date of 2/11/2020. | SDCC HOUSING UNIT 8 | 9970 | Correct | SDCC |  | Indian Springs | 1988 | 32000 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 528000
1482EXT1 | EXTERIOR FINISHES | 1482 | The exterior is in very poor condition. It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the 1 - 2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SDCC GUN POST 1 AT GYM BUILDING | 9970 | Correct | SDCC |  | Indian Springs | 1987 | 80 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 1600
1482INT2 | FLOORING AND SUBFLOORING REPLACEMENT | 1482 | The VCT (vinyl composite tile) flooring and subfloor are damaged and reaching the end of their useful life. It is recommended to replace the VCT flooring and plywood subfloor. This project would provide for the removal and disposal of the old flooring and subfloor, and installation of new plywood subfloor and new 12x12 VCT flooring with a 6" base. | SDCC GUN POST 1 AT GYM BUILDING | 9970 | Correct | SDCC |  | Indian Springs | 1987 | 80 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2400
1482EXT4 | EXTERIOR DOOR REPLACEMENT | 1482 | The existing exterior metal door and frame appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement and installation of a new metal door, frame and hardware. Removal and disposal of the existing door and painting of the new door is included in this estimate. | SDCC GUN POST 1 AT GYM BUILDING | 9970 | Correct | SDCC |  | Indian Springs | 1987 | 80 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 2500
1481EXT6 | ROOF DRAIN DOWNSPOUT INSTALLATION | 1481 | The rain gutters are in need of full length downspouts and extensions. The downspouts currently terminate within inches of the rain gutter with no continuous drainage away from the building. This is causing the water to run down the building and pool next to the foundation and damage the foundation and stucco walls. This project would provide for full length downspouts to grade and extensions to approximately 5'-0" away from the perimeter of the building to prevent pooling and damage to the building. This project or a portion thereof was previously recommended in the FCA report dated 12/13/2016. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC HOUSING UNIT 8 | 9970 | Correct | SDCC |  | Indian Springs | 1988 | 32000 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 10400
1482INT1 | INTERIOR FINISHES | 1482 | The interior finishes are in very poor condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SDCC GUN POST 1 AT GYM BUILDING | 9970 | Correct | SDCC |  | Indian Springs | 1987 | 80 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1200
1481ADA4 | TDD INSTALLATION | 1481 | Housing Unit 8 is not equipped with a telecommunications device for the deaf (TDD). In order to comply with ADA requirements it is recommended to install a TDD system in Housing Unit 8. The 2018 IBC, ICC/ANSI A117.1, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 12/13/2016. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC HOUSING UNIT 8 | 9970 | Correct | SDCC |  | Indian Springs | 1988 | 32000 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 66000
1482EXT5 | EXTERIOR SIDING REPLACEMENT | 1482 | The metal siding panels covering the building are original. One panel has been replaced by plywood and should be scheduled for replacement. This project would provide for the removal and the disposal of the existing wood panel and the replacement with a new pre-finished metal panel. | SDCC GUN POST 1 AT GYM BUILDING | 9970 | Correct | SDCC |  | Indian Springs | 1987 | 80 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 750
1482HVA1 | WINDOW UNIT A/C REPLACEMENT | 1482 | The existing window unit air condition is in poor condition and in need of replacement. In addition, it does not have a proper wall sleeve. This project would provide for the installation of a wall sleeve, framing, insulation, and replacing the existing unit with a new, more efficient unit. | SDCC GUN POST 1 AT GYM BUILDING | 9970 | Correct | SDCC |  | Indian Springs | 1987 | 80 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 7500
1482EXT3 | ROOF REPLACEMENT | 1482 | The corrugated metal roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next year with a new single-ply roofing system. This estimate includes removal and disposal of the old roof. This project should be implemented concurrently with the ROOF REPLACEMENT project for the Gymnasium Building. | SDCC GUN POST 1 AT GYM BUILDING | 9970 | Correct | SDCC |  | Indian Springs | 1987 | 80 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 2400
1482EXT2 | WINDOW REPLACEMENT | 1482 | The windows are original, single pane construction in metal frames. Some of the glass is missing and replaced with plywood. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 20 units. Removal and disposal of the existing windows is included in this estimate. | SDCC GUN POST 1 AT GYM BUILDING | 9970 | Correct | SDCC |  | Indian Springs | 1987 | 80 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 3500
1481SEC2 | VIDEO SECURITY SYSTEM UPGRADE | 1481 | The video security system is outdated and some of the cameras do not function consistently. This project addresses replacement of the cameras and controls in the building with all digital equipment as well as sufficient storage capacity. This project or a portion thereof was previously recommended in the FCA report dated 12/13/2016. It has been amended accordingly to reflect conditions observed during the most recent survey date of 2/11/2020. | SDCC HOUSING UNIT 8 | 9970 | Correct | SDCC |  | Indian Springs | 1988 | 32000 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 275000
1481ADA3 | ADA TABLE UPGRADE | 1481 | Per the United States Access Board and ICC ANSI-A117.1, at least 5 percent of the seating spaces shall be, if fixed seating is provided, a loose seat or open space for a wheelchair. This project would provide funding to remove 3 of the fixed seats, which will allow access for wheel chairs. This project or a portion thereof was previously recommended in the FCA report dated 12/13/2016. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC HOUSING UNIT 8 | 9970 | Correct | SDCC |  | Indian Springs | 1988 | 32000 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 3600
1481EXT2 | EXTERIOR FINISHES | 1481 | The building exterior is in good condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is repairing damaged areas of stucco, power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be repaired and painted in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SDCC HOUSING UNIT 8 | 9970 | Correct | SDCC |  | Indian Springs | 1988 | 32000 | 2020-02-11 | Four to Ten Years | Long-Term Needs | 3 | 320000
2183EXT5 | EXTERIOR SIDING REPLACEMENT | 2183 | The corrugated metal panels covering the building are original and should be scheduled for replacement. Many of the panels are damaged from general wear and tear. This project would provide for the removal and the disposal of the existing panels and the replacement with new pre-painted metal panels. The estimate is based on 120 linear feet of 4' wide panels at $60 per linear foot. | SDCC UPHOLSTERY BUILDING | 9970 | Correct | SDCC |  | Indian Springs |  | 800 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
2707PLM1 | REPLACE SEWER / WASTE WATER LINES | 2707 | The waste line from the wash sink is not connected to the sanitary sewer. This project would connect the 1 1/2" sink waste line to the 3" sanitary waste line outside of the building. | SDCC TOWER 1 SALLY PORT | 9970 | Correct | SDCC |  | Indian Springs |  | 144 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 1000
2721INT1 | INTERIOR FINISHES | 2721 | The interior finishes are in fair condition considering the function of the building. It is recommended that the interior pre-finished metal panel walls and ceilings be inspected for signs of corrosion at least once in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. All surfaces should be inspected and repaired and re-coated. | SDCC P. I. SANDBLASTING SHED 2 | 9970 | Correct | SDCC |  | Indian Springs |  | 320 | 2020-02-11 | Four to Ten Years | Long-Term Needs | 3 | 1600
2710INT1 | INTERIOR FINISHES | 2710 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SDCC P. I. SANDBLASTING SHED 1 | 9970 | Correct | SDCC |  | Indian Springs |  | 120 | 2020-02-11 | Four to Ten Years | Long-Term Needs | 3 | 600
2710EXT1 | EXTERIOR FINISHES | 2710 | The building exterior is in poor condition. It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2 - 3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project should be implemented concurrently with EXTERIOR SIDING REPLACEMENT. | SDCC P. I. SANDBLASTING SHED 1 | 9970 | Correct | SDCC |  | Indian Springs |  | 120 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1200
2710EXT2 | EXTERIOR DOOR REPLACEMENT | 2710 | The existing exterior wood door and frame appear to be original to the building. They are damaged and showing signs of wear and deterioration from constant use and weather damage. This project would provide for the removal and replacement with a new wood door assembly including frames, locks, hardware, and painting. Removal and disposal of the existing door and painting of the new door is included in this estimate. | SDCC P. I. SANDBLASTING SHED 1 | 9970 | Correct | SDCC |  | Indian Springs |  | 120 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
2710EXT3 | EXTERIOR SIDING REPLACEMENT | 2710 | The building has painted T1-11 siding that is due for replacement. The existing siding is in poor condition and will no longer hold paint. This project recommends removing the T1-11 siding and replacing it with new T1-11 siding and window trim, finished with an oil-based stain or paint. | SDCC P. I. SANDBLASTING SHED 1 | 9970 | Correct | SDCC |  | Indian Springs |  | 120 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2400
2709EXT1 | EXTERIOR FINISHES | 2709 | The pre-finished metal panel exterior is in fair condition. It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SDCC P. I. PAINT BOOTH | 9970 | Correct | SDCC |  | Indian Springs |  | 704 | 2020-02-11 | Four to Ten Years | Long-Term Needs | 3 | 704
2709INT1 | INTERIOR FINISHES | 2709 | The interior pre-finished metal panel finishes are in fair condition. It is recommended that the interior walls and ceilings be checked for signs of corrosion issues in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the interior of the building. As part of the inspection, all surfaces should be repaired and re-painted as necessary. | SDCC P. I. PAINT BOOTH | 9970 | Correct | SDCC |  | Indian Springs |  | 704 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3520
2708EXT1 | EXTERIOR FINISHES | 2708 | The building exterior is in poor condition. It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2 - 3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project should be implemented concurrently with EXTERIOR SIDING REPLACEMENT. | SDCC K GATE GUARD SHACK | 9970 | Correct | SDCC |  | Indian Springs |  | 48 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 960
2708EXT4 | EXTERIOR DOOR REPLACEMENT | 2708 | The existing exterior wood door and frame appear to be original to the building. They are damaged and showing signs of wear and deterioration from constant use and weather damage. This project would provide for the removal and replacement with a new metal door assembly including frames, locks, hardware, and painting. Removal and disposal of the existing door and painting of the new door is included in this estimate. | SDCC K GATE GUARD SHACK | 9970 | Correct | SDCC |  | Indian Springs |  | 48 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3500
2708EXT2 | EXTERIOR SIDING REPLACEMENT | 2708 | The guard shack has painted T1-11 siding that is due for replacement. The existing siding is in poor condition and will no longer hold paint. This project recommends removing the T1-11 siding and to replace it with new T1-11 siding and window trim, finished with an oil-based stain or paint. | SDCC K GATE GUARD SHACK | 9970 | Correct | SDCC |  | Indian Springs |  | 48 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2400
2707HVA1 | AIR CONDITIONER REPLACEMENT | 2707 | A small air conditioner is installed on the side of this building. It is original to the building and has reached the end of its useful and expected life. This project would provide for a new air conditioner to be installed including all required connections to utilities. The estimate includes removal and disposal of the old unit. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC TOWER 1 SALLY PORT | 9970 | Correct | SDCC |  | Indian Springs |  | 144 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
2707INT1 | INTERIOR FINISHES | 2707 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SDCC TOWER 1 SALLY PORT | 9970 | Correct | SDCC |  | Indian Springs |  | 144 | 2020-02-11 | Four to Ten Years | Long-Term Needs | 3 | 1440
2721EXT1 | EXTERIOR FINISHES | 2721 | The building exterior is in poor condition showing multiple locations of corrosion and deterioration of the pre-finished metal panels. It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2 - 3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SDCC P. I. SANDBLASTING SHED 2 | 9970 | Correct | SDCC |  | Indian Springs |  | 320 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4800
2707INT2 | FLOORING AND SUBFLOORING REPLACEMENT | 2707 | The VCT (vinyl composite tile) flooring and subfloor are damaged and reaching the end of their useful life. It is recommended to replace the VCT flooring and plywood subfloor. This project would provide for removal and disposal of the VCT and plywood and installation of new plywood subfloor and new 12x12 VCT with a 6" base. | SDCC TOWER 1 SALLY PORT | 9970 | Correct | SDCC |  | Indian Springs |  | 144 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4300
2708INT1 | INTERIOR FINISHES | 2708 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SDCC K GATE GUARD SHACK | 9970 | Correct | SDCC |  | Indian Springs |  | 48 | 2020-02-11 | Four to Ten Years | Long-Term Needs | 3 | 480
2706INT2 | INTERIOR DRAINAGE REPAIRS | 2706 | The building has a drainage problem inside where the slope of the floor does not carry water towards the floor drain. The water accumulates in several areas inside the building and pools up against the exterior walls. This is causing severe damage to the CMU walls and concrete foundation from the water leaching into the concrete at the Southwest corner of the building. This is visually apparent on the building exterior where the CMU corner block has crumbled and potentially corroding the steel rebar reinforcement in the walls. This project would provide for a structural review and structural testing of the wall, and either installing additional floor drains or pouring a new concrete floor with proper slopes. In addition, once floor is repaired, to install an epoxy floor coating to protect floor. | SDCC PUMP HOUSE 1 | 9970 | Correct | SDCC |  | Indian Springs |  | 800 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 15000
2706EXT1 | EXTERIOR FINISHES | 2706 | The building exterior is in good condition - except SW corner at foundation which is addressed in a separate project. It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SDCC PUMP HOUSE 1 | 9970 | Correct | SDCC |  | Indian Springs |  | 800 | 2020-02-11 | Four to Ten Years | Long-Term Needs | 3 | 4000
2706INT1 | INTERIOR FINISHES | 2706 | The interior finishes are in fair condition. Rollup door tracks should be refinished to treat the surface corrosion. It is recommended to repair and seal the interior concrete block walls at least once in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. | SDCC PUMP HOUSE 1 | 9970 | Correct | SDCC |  | Indian Springs |  | 800 | 2020-02-11 | Four to Ten Years | Long-Term Needs | 3 | 4000
2180EXT3 | ROOF REPLACEMENT | 2180 | The corrugated metal roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 1 - 2 years. This estimate includes removal and disposal of the old roof. | SDCC P.I. QUONSET HUT | 9970 | Correct | SDCC |  | Indian Springs | 2001 | 1000 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 18800
2181INT1 | INTERIOR FINISHES | 2181 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SDCC P.I. LUNCH ROOM | 9970 | Correct | SDCC |  | Indian Springs |  | 600 | 2020-02-11 | Four to Ten Years | Long-Term Needs | 3 | 3600
2553HVA2 | EVAPORATIVE COOLER REPLACEMENT | 2553 | An evaporative cooler is installed on the side of this building. It is severely scaled and has reached the end of its useful and expected life. This project would provide for a new evaporative cooler to be installed including all required connections to utilities. The estimate includes removal and disposal of the old cooler. | SDCC PRISON INDUSTRIES SPRUNG BLDG | 9970 | Correct | SDCC |  | Indian Springs | 2004 | 20000 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
2553HVA1 | HVAC EQUIPMENT REPLACEMENT | 2553 | There is a ground mounted rooftop packaged HVAC unit that is original to the building and is not energy efficient. The packaged HVAC unit utilizes R-22 refrigerant that has been phased out. The unit has reached the end of its expected and useful life. This project would provide for the installation of one new 25 ton unit. Also included in this estimate is new duct adapters, support stand modifications, crane and rigging removal and installation and all required connections to utilities. | SDCC PRISON INDUSTRIES SPRUNG BLDG | 9970 | Correct | SDCC |  | Indian Springs | 2004 | 20000 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
2553SFT2 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 2553 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC 2018 Chapter 10 was referenced for this project. | SDCC PRISON INDUSTRIES SPRUNG BLDG | 9970 | Correct | SDCC |  | Indian Springs | 2004 | 20000 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 25000
2553ADA10 | ADA RESTROOM UPGRADE | 2553 | The men's and women's designated ADA restrooms do not meet the ADA requirements. A complete retrofit is necessary. This project would provide funding for construction of two unisex accessible restrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2018 IBC, ICC/ANSI A117.1, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as a reference for this project. | SDCC PRISON INDUSTRIES SPRUNG BLDG | 9970 | Correct | SDCC |  | Indian Springs | 2004 | 20000 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 31000
2553INT1 | INTERIOR FINISHES | 2553 | The interior finishes are in fair condition. It is recommended that the interior gypsum walls and ceilings be painted at least once in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SDCC PRISON INDUSTRIES SPRUNG BLDG | 9970 | Correct | SDCC |  | Indian Springs | 2004 | 20000 | 2020-02-11 | Four to Ten Years | Long-Term Needs | 3 | 10000
2553EXT1 | EXTERIOR FINISHES | 2553 | The building exterior is in good condition. It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building including the roof. Included in the cost is cleaning the wall panels and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be cleaned and caulked in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SDCC PRISON INDUSTRIES SPRUNG BLDG | 9970 | Correct | SDCC |  | Indian Springs | 2004 | 20000 | 2020-02-11 | Four to Ten Years | Long-Term Needs | 3 | 10000
2553SFT1 | RECOMMISSION BUILDING SYSTEMS | 2553 | The fire suppression system, fire alarm system, and electricity have been turned off in the building; however, the building is currently used to store boxes of playing cards on pallets. During the survey, inmates were bringing the pallets of cards into and out of the building. This poses a safety risk since the life safety systems are turned off. There should be no occupants in the building at any time. This project would provide for recommissioning the building systems before any activities are resumed inside the building. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC PRISON INDUSTRIES SPRUNG BLDG | 9970 | Correct | SDCC |  | Indian Springs | 2004 | 20000 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 15000
2707EXT1 | EXTERIOR FINISHES | 2707 | The exterior finish is in good condition. It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SDCC TOWER 1 SALLY PORT | 9970 | Correct | SDCC |  | Indian Springs |  | 144 | 2020-02-11 | Four to Ten Years | Long-Term Needs | 3 | 1440
2180EXT1 | EXTERIOR FINISHES | 2180 | The exterior finishes are in poor condition. It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2 - 3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SDCC P.I. QUONSET HUT | 9970 | Correct | SDCC |  | Indian Springs | 2001 | 1000 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
2787EXT1 | EXTERIOR FINISHES | 2787 | The exterior finishes are in good condition. It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SDCC DORM HOUSING UNIT #11 | 9970 | Correct | SDCC |  | Indian Springs | 2008 | 23780 | 2020-02-11 | Four to Ten Years | Long-Term Needs | 3 | 118900
2183EXT3 | EXTERIOR DOOR REPLACEMENT | 2183 | The exterior metal man doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the double door assembly with new metal doors, frames and hardware. Removal and disposal of the existing doors is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC UPHOLSTERY BUILDING | 9970 | Correct | SDCC |  | Indian Springs |  | 800 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3600
2788INT1 | INTERIOR FINISHES | 2788 | The interior finishes are in fair condition. The restroom and shower areas need to be repainted with an epoxy based paint. It is recommended that the interior walls and ceilings be painted or sealed at least once in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SDCC DORM HOUSING UNIT #12 | 9970 | Correct | SDCC |  | Indian Springs | 2008 | 23780 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 118900
2183PLM1 | RESTROOM REMODEL | 2183 | The restroom in the building was out of service at the time of the survey. It is original to the building and is due for a complete remodel. This project would provide for a complete remodel of the restroom fixtures, hardware, floor and wall finishes. | SDCC UPHOLSTERY BUILDING | 9970 | Correct | SDCC |  | Indian Springs |  | 800 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 15000
2788EXT1 | EXTERIOR FINISHES | 2788 | The exterior finishes are in good condition. It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SDCC DORM HOUSING UNIT #12 | 9970 | Correct | SDCC |  | Indian Springs | 2008 | 23780 | 2020-02-11 | Four to Ten Years | Long-Term Needs | 3 | 118900
2184EXT1 | EXTERIOR FINISHES | 2184 | The pre-finished metal panel exterior is in fair condition. It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SDCC AUTOMOTIVE SHOP | 9970 | Correct | SDCC |  | Indian Springs |  | 1200 | 2020-02-11 | Four to Ten Years | Long-Term Needs | 3 | 6000
2184INT1 | INTERIOR FINISHES | 2184 | The interior pre-finished metal panel finishes are in good condition. It is recommended that the interior walls and ceilings be checked for signs of corrosion issues in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the interior of the building. In addition, a small amount of corrosion on the inside of the large metal rolling doors should be treated. As part of the inspection, all surfaces should be repaired and re-painted as necessary. | SDCC AUTOMOTIVE SHOP | 9970 | Correct | SDCC |  | Indian Springs |  | 1200 | 2020-02-11 | Four to Ten Years | Long-Term Needs | 3 | 6000
2787INT1 | INTERIOR FINISHES | 2787 | The interior finishes are in fair condition. The restroom and shower areas need to be repainted with an epoxy based paint. It is recommended that the interior walls and ceilings be painted or sealed at least once in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SDCC DORM HOUSING UNIT #11 | 9970 | Correct | SDCC |  | Indian Springs | 2008 | 23780 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 118900
2183ENR1 | WINDOW REPLACEMENT | 2183 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 6 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC UPHOLSTERY BUILDING | 9970 | Correct | SDCC |  | Indian Springs |  | 800 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
2788PLM2 | PLUMBING LEAKS | 2788 | Pooling water on the floor in the maintenance areas behind the restroom and shower pods indicates water leaks in the plumbing and / or the seals are broken in the shower enclosures. These leaks need to be addressed in order to prevent further damage and corrosion to the modular metal pods. | SDCC DORM HOUSING UNIT #12 | 9970 | Correct | SDCC |  | Indian Springs | 2008 | 23780 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
2708EXT3 | ROOF REPLACEMENT | 2708 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2 - 3 years with a new 50 year asphalt composition roofing shingle and new underlayment. This estimate includes removal and disposal of the old roof. | SDCC K GATE GUARD SHACK | 9970 | Correct | SDCC |  | Indian Springs |  | 48 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
2180INT1 | INTERIOR FINISHES | 2180 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SDCC P.I. QUONSET HUT | 9970 | Correct | SDCC |  | Indian Springs | 2001 | 1000 | 2020-02-11 | Four to Ten Years | Long-Term Needs | 3 | 10000
2183INT1 | INTERIOR FINISHES | 2183 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SDCC UPHOLSTERY BUILDING | 9970 | Correct | SDCC |  | Indian Springs |  | 800 | 2020-02-11 | Four to Ten Years | Long-Term Needs | 3 | 4800
2180EXT2 | EXTERIOR DOOR REPLACEMENT | 2180 | The exterior metal doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the two door assemblies with new metal doors, frames and hardware. Removal and disposal of the existing doors is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC P.I. QUONSET HUT | 9970 | Correct | SDCC |  | Indian Springs | 2001 | 1000 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3600
2180HVA1 | EVAPORATIVE COOLER REPLACEMENT | 2180 | An evaporative cooler is installed on the side of this building. It is severely scaled and has reached the end of its useful and expected life. This project would provide for a new evaporative cooler to be installed including all required connections to utilities. The estimate includes removal and disposal of the old cooler. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC P.I. QUONSET HUT | 9970 | Correct | SDCC |  | Indian Springs | 2001 | 1000 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3500
2181EXT2 | EXTERIOR FINISHES | 2181 | The building exterior is in poor condition. It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2 - 3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SDCC P.I. LUNCH ROOM | 9970 | Correct | SDCC |  | Indian Springs |  | 600 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3600
2183HVA1 | HVAC REPLACEMENT | 2183 | An air conditioning unit is installed on the roof of this building. It is original to the building and has reached the end of its useful and expected life. This project would provide for a new air conditioner to be installed including all required connections to utilities. The estimate includes removal and disposal of the old unit. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC UPHOLSTERY BUILDING | 9970 | Correct | SDCC |  | Indian Springs |  | 800 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5700
2183EXT2 | EXTERIOR FINISHES | 2183 | The exterior finishes are in very poor condition. It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2 - 3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project should be implemented concurrently with EXTERIOR SIDING REPLACEMENT. | SDCC UPHOLSTERY BUILDING | 9970 | Correct | SDCC |  | Indian Springs |  | 800 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4800
2787PLM1 | PLUMBING LEAKS | 2787 | Pooling water on the floor in the maintenance areas behind the restroom and shower pods indicates water leaks in the plumbing and / or the seals are broken in the shower enclosures. These leaks need to be addressed in order to prevent further damage and corrosion to the modular metal pods. | SDCC DORM HOUSING UNIT #11 | 9970 | Correct | SDCC |  | Indian Springs | 2008 | 23780 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 5000
2788PLM1 | WATER HEATER REPLACEMENT | 2788 | There are two 125 gallon gas-fired water heaters in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, these units are showing signs of wear and should be scheduled for replacement in the next 2 - 3 years. It is recommended that two new gas-fired water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC DORM HOUSING UNIT #12 | 9970 | Correct | SDCC |  | Indian Springs | 2008 | 23780 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
3160EXT1 | EXTERIOR FINISHES | 3160 | The building exterior is in poor condition. It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2 - 3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SDCC CARD SORTING BUILDING | 9970 | Correct | SDCC |  | Indian Springs | 2008 | 2000 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
3160ADA1 | ADA RESTROOM UPGRADE | 3160 | The building does not have an accessible restroom. The existing restroom does not meet the ADA requirements. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom. Items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2018 IBC, ICC/ANSI A117.1, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as a reference for this project. | SDCC CARD SORTING BUILDING | 9970 | Correct | SDCC |  | Indian Springs | 2008 | 2000 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 31100
3160INT2 | INTERIOR FINISHES | 3160 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SDCC CARD SORTING BUILDING | 9970 | Correct | SDCC |  | Indian Springs | 2008 | 2000 | 2020-02-11 | Four to Ten Years | Long-Term Needs | 3 | 10000
3160HVA1 | HVAC EQUIPMENT REPLACEMENT | 3160 | The three HVAC sidewall units and one evaporative cooler appear to be original to the building. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of three new HVAC packaged units, an evaporative cooler and cleaning of the existing grilles. This project includes removal and disposal of the existing equipment and all required connections to utilities. | SDCC CARD SORTING BUILDING | 9970 | Correct | SDCC |  | Indian Springs | 2008 | 2000 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
3160EXT2 | ROOF REPLACEMENT | 3160 | It appears the corrugated metal roof on this building was in poor condition at the time of the survey due to eveidence of multiple water stains on the interior roof insulation. It is recommended that this building be re-roofed in the next 2-3 years with a standing seam metal roofing system. This estimate includes removal and disposal of the old roofing. This project should be implemented concurrently with EXPOSED INSULATION REPAIRS. | SDCC CARD SORTING BUILDING | 9970 | Correct | SDCC |  | Indian Springs | 2008 | 2000 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 37600
3097EXT1 | EXTERIOR FINISHES | 3097 | The exterior finishes are in good condition. It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SDCC POWER/GENERATOR BUILDING | 9970 | Correct | SDCC |  | Indian Springs | 2010 | 4004 | 2020-02-11 | Four to Ten Years | Long-Term Needs | 3 | 12000
3097INT1 | INTERIOR FINISHES | 3097 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SDCC POWER/GENERATOR BUILDING | 9970 | Correct | SDCC |  | Indian Springs | 2010 | 4004 | 2020-02-11 | Four to Ten Years | Long-Term Needs | 3 | 20000
3096EXT1 | EXTERIOR FINISHES | 3096 | The exterior finishes are in good condition. It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SDCC INFIRMARY | 9970 | Correct | SDCC |  | Indian Springs | 2010 | 11724 | 2020-02-11 | Four to Ten Years | Long-Term Needs | 3 | 58620
3096INT1 | INTERIOR FINISHES | 3096 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SDCC INFIRMARY | 9970 | Correct | SDCC |  | Indian Springs | 2010 | 11724 | 2020-02-11 | Four to Ten Years | Long-Term Needs | 3 | 58620
3095INT1 | INTERIOR FINISHES | 3095 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SDCC CULINARY/DINING/CHAPEL/LAUNDRY | 9970 | Correct | SDCC |  | Indian Springs | 2010 | 44049 | 2020-02-11 | Four to Ten Years | Long-Term Needs | 3 | 220245
3095PLM1 | HEAT EXCHANGER REPAIR | 3095 | Two plate and frame heat exchangers are leaking or show evidence of past leaks. It is unknown whether one or both heat exchangers are plugged. These units need to be completely disassembled and rebuilt to ensure continuous supply of domestic hot water and prevent further damage to the equipment, piping, and concrete bases. | SDCC CULINARY/DINING/CHAPEL/LAUNDRY | 9970 | Correct | SDCC |  | Indian Springs | 2010 | 44049 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 5000
9970ELE2 | CONSOLIDATE GENERATOR BACKUP POWER | 9970 | Extend site utility power to Dorm Units 11 & 12. This will enable the existing redundant backup power generators to supply backup power to the entire site. The added electrical load to the main utility circuit is not expected to exceed the generating standby power capacity of one generator and therefore preserving 100% generator redundancy. In addition to substantially increasing backup power reliability, it will eliminate the operational costs of maintaining the older, smaller independent generator and also remove utility fees associated with separate metering. This project includes removal and disposal of abandoned generator and associated equipment, installation of a transformer, trenching, conduit, cable and all labor for installation and testing. | SOUTHERN DESERT CORRECTIONAL CENTER SITE | 9970 | Correct | SDCC |  | Indian Springs | 1980 |  | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 600000
9970SIT5 | SLIDING GATE REPLACEMENT | 9970 | The sliding K gate on the west side of Control/Visitation has completely failed and has been removed. This project would fund the replacement of the sliding gate, controls and repair of approximately 100' of security fencing. | SOUTHERN DESERT CORRECTIONAL CENTER SITE | 9970 | Correct | SDCC |  | Indian Springs | 1980 |  | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
9970SIT3 | SLURRY SEAL ASPHALT PAVING | 9970 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site wide including access roads, parking areas and paving around the old Culinary and Laundry building. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 265,000 square feet of asphalt area was used to generate this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SOUTHERN DESERT CORRECTIONAL CENTER SITE | 9970 | Correct | SDCC |  | Indian Springs | 1980 |  | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 240000
9970ADA2 | ADA ACCESSIBLE PATH OF TRAVEL | 9970 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. 7 concrete parking spaces, passenger loading areas and a path of travel to the office are necessary to comply with ADA accessibility requirements. This project would provide for 7 total accessible parking spaces, of which at least 2 shall be van accessible spaces and an accessible concrete walkway from each space to the existing sidewalk. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2018 IBC, ICC/ANSI A117.1, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. 3,000 square feet of concrete was used for this estimate. It is recommended that this project coincide with the paving project. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020 | SOUTHERN DESERT CORRECTIONAL CENTER SITE | 9970 | Correct | SDCC |  | Indian Springs | 1980 |  | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 90000
9970ENV1 | PIGEON ABATEMENT | 9970 | The site and buildings have been inhabited by pigeons. The birds introduce a potential risk of disease, cause maintenance problems with the mechanical systems and cost labor time for general clean-up. This project provides for removal and disposal of pigeon debris, eggs, and carcasses from the site and buildings by a licensed pest control business. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SOUTHERN DESERT CORRECTIONAL CENTER SITE | 9970 | Correct | SDCC |  | Indian Springs | 1980 |  | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 36000
3160INT3 | EXPOSED INSULATION REPAIRS | 3160 | Exposed insulation in an occupied space is not recommended and should be covered. Disturbing fiberglass insulation can send particles into the air that act as lung, eye and skin irritants. This project would provide for the installation of a ceiling grid system below the insulation. It does not appear that any routine operations disturb the fiberglass so risk of exposure is low. Project scope should be included in the next remodel or change in occupancy. | SDCC CARD SORTING BUILDING | 9970 | Correct | SDCC |  | Indian Springs | 2008 | 2000 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
9970ENR2 | ENERGY MANAGEMENT SYSTEM UPGRADE | 9970 | The existing energy management system is older and is not connected to all of the equipment. In a facility of this type, it is imperative that the conditioned spaces and lighting are properly controlled at all times. This project would provide for the removal and disposal of the existing energy management system and replacement with new equipment including all required connections to utilities and equipment. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SOUTHERN DESERT CORRECTIONAL CENTER SITE | 9970 | Correct | SDCC |  | Indian Springs | 1980 |  | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 595000
9970SIT4 | SITE DRAINAGE UPGRADES | 9970 | Recent heavy rains exposed drainage problems around the site. The grade does not slope away from the buildings effectively which allowed water to infiltrate several of the housing units. This project would create positive flow away from the buildings by regrading, paving and/ or installing additional drainage swales as needed. This is particularly troublesome on the north side of the Gym Building #0166. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SOUTHERN DESERT CORRECTIONAL CENTER SITE | 9970 | Correct | SDCC |  | Indian Springs | 1980 |  | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 75000
3095EXT1 | EXTERIOR FINISHES | 3095 | The exterior finishes are in good condition. It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SDCC CULINARY/DINING/CHAPEL/LAUNDRY | 9970 | Correct | SDCC |  | Indian Springs | 2010 | 44049 | 2020-02-11 | Four to Ten Years | Long-Term Needs | 3 | 220245
0173INT1 | FLOORING AND SUBFLOORING REPLACEMENT | 0173 | The VCT (vinyl composite tile) flooring and subfloor are damaged and reaching the end of their useful life. It is recommended to replace the VCT flooring and plywood subfloor. This project would provide for the removal and disposal of the old flooring and subfloor, and installation of new plywood subfloor and new 12x12 VCT flooring with a 6" base. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC GUARD TOWER 5 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3600
0172SFT1 | EXIT SIGN AND EGRESS LIGHTING INSTALLATION | 0172 | There are no exit signs or emergency egress lights in the guard tower. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2018 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC GUARD TOWER 4 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 1100
0172EXT1 | ROOF REPLACEMENT | 0172 | The rolled asphalt roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roof. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC GUARD TOWER 4 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3600
0172EXT3 | EXTERIOR SIDING REPLACEMENT | 0172 | The tower has a painted T1-11 siding that is due for replacement. The existing siding is in poor condition and is missing some trim pieces. This project recommends removing the T1-11 siding, inspecting the exposed building structural elements and replacing it with new T1-11 siding including priming and painting. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC GUARD TOWER 4 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35800
0173ELE0 | EXTERIOR LIGHTING REPLACEMENT | 0173 | The building has perimeter HPS lighting on the exterior of the building, but the light fixtures are old and not energy efficient. This project would provide for the replacement of the exterior lighting fixtures with new LED light fixtures, using existing wiring. | SDCC GUARD TOWER 5 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0173EXT2 | EXTERIOR FINISHES | 0173 | The building exterior is in poor condition. The paint is severely sun damaged and flaking at the window trim and the southern exposure. It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2 - 3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project should be implemented concurrently with EXTERIOR SIDING REPLACEMENT. | SDCC GUARD TOWER 5 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
0173INT3 | REPAIR DAMAGED CEILING | 0173 | The gypsum board ceiling is severely damaged from a plumbing leak below the toilet and sink. This project would provide for the removal of the damaged gypsum board ceiling and installation of new 5/8" type X gypsum board. This estimate includes tape, texture and paint. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC GUARD TOWER 5 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 1200
0173SFT1 | EXIT SIGN AND EGRESS LIGHTING INSTALLATION | 0173 | There are no exit signs or emergency egress lights in the guard tower. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2018 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC GUARD TOWER 5 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 1100
0173EXT1 | ROOF REPLACEMENT | 0173 | The rolled asphalt roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roof. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC GUARD TOWER 5 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3600
0173INT2 | INTERIOR FINISHES | 0173 | The interior finishes are in poor condition. It is recommended that the interior walls and ceiling be repaired and painted at least once in the next 2 - 3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. Additional costs have been added for repairing large areas of damaged drywall. | SDCC GUARD TOWER 5 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2400
0173EXT4 | WINDOW REPLACEMENT | 0173 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 8 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC GUARD TOWER 5 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14300
0173EXT3 | EXTERIOR SIDING REPLACEMENT | 0173 | The tower has a painted T1-11 siding that is due for replacement. The existing siding is in poor condition and is missing some trim pieces. This project recommends removing the T1-11 siding, inspecting the exposed building structural elements and replacing it with new T1-11 siding including priming and painting. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC GUARD TOWER 5 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35800
0172EXT4 | WINDOW REPLACEMENT | 0172 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 8 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC GUARD TOWER 4 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14300
0172INT1 | FLOORING AND SUBFLOORING REPLACEMENT | 0172 | The VCT (vinyl composite tile) flooring and subfloor are damaged and reaching the end of their useful life. It is recommended to replace the VCT flooring and plywood subfloor. This project would provide for the removal and disposal of the old flooring and subfloor, and installation of new plywood subfloor and new 12x12 VCT flooring with a 6" base. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC GUARD TOWER 4 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3600
0171INT2 | INTERIOR FINISHES | 0171 | The interior finishes are in poor condition. It is recommended that the interior walls and ceiling be repaired and painted at least once in the next 2 - 3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. Additional costs have been added for repairing large areas of damaged drywall. | SDCC GUARD TOWER 3 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2400
0171EXT1 | ROOF REPLACEMENT | 0171 | The rolled asphalt roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roof. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC GUARD TOWER 3 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3600
0171INT1 | FLOORING AND SUBFLOORING REPLACEMENT | 0171 | The VCT (vinyl composite tile) flooring and subfloor are damaged and reaching the end of their useful life. It is recommended to replace the VCT flooring and plywood subfloor. This project would provide for the removal and disposal of the old flooring and subfloor, and installation of new plywood subfloor and new 12x12 VCT flooring with a 6" base. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC GUARD TOWER 3 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3600
0171EXT2 | EXTERIOR FINISHES | 0171 | The building exterior is in poor condition. The paint is severely sun damaged and flaking at the window trim and the southern exposure. It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2 - 3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project should be implemented concurrently with EXTERIOR SIDING REPLACEMENT. | SDCC GUARD TOWER 3 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
0171SFT1 | EXIT SIGN AND EGRESS LIGHTING INSTALLATION | 0171 | There are no exit signs or emergency egress lights in the guard tower. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2018 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC GUARD TOWER 3 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 1100
0171EXT4 | WINDOW REPLACEMENT | 0171 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 8 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC GUARD TOWER 3 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14300
0171EXT3 | EXTERIOR SIDING REPLACEMENT | 0171 | The tower has a painted T1-11 siding that is due for replacement. The existing siding is in poor condition and is missing some trim pieces. This project recommends removing the T1-11 siding, inspecting the exposed building structural elements and replacing it with new T1-11 siding including priming and painting. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC GUARD TOWER 3 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 17900
0170EXT2 | EXTERIOR FINISHES | 0170 | The building exterior is in poor condition. The paint is severely sun damaged and flaking at the window trim and the southern exposure. It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2 - 3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project should be implemented concurrently with EXTERIOR SIDING REPLACEMENT. | SDCC GUARD TOWER 2 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
0172EXT2 | EXTERIOR FINISHES | 0172 | The building exterior is in poor condition. The paint is severely sun damaged and flaking at the window trim and the southern exposure. It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2 - 3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project should be implemented concurrently with EXTERIOR SIDING REPLACEMENT. | SDCC GUARD TOWER 4 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
0170INT2 | INTERIOR FINISHES | 0170 | The interior finishes are in poor condition. It is recommended that the interior walls and ceiling be repaired and painted at least once in the next 2 - 3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. Additional costs have been added for repairing large areas of damaged drywall. | SDCC GUARD TOWER 2 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2400
0172INT2 | INTERIOR FINISHES | 0172 | The interior finishes are in poor condition. It is recommended that the interior walls and ceiling be repaired and painted at least once in the next 2 -3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. Additional costs have been added for repairing large areas of damaged drywall. | SDCC GUARD TOWER 4 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2400
0170SFT2 | EXIT SIGN AND EGRESS LIGHTING INSTALLATION | 0170 | There are no exit signs or emergency egress lights in the guard tower. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2018 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC GUARD TOWER 2 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 1100
0170EXT1 | ROOF REPLACEMENT | 0170 | The rolled asphalt roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roof. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC GUARD TOWER 2 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3600
0170INT1 | FLOORING AND SUBFLOORING REPLACEMENT | 0170 | The VCT (vinyl composite tile) flooring and subfloor are damaged and reaching the end of their useful life. It is recommended to replace the VCT flooring and plywood subfloor. This project would provide for the removal and disposal of the old flooring and subfloor, and installation of new plywood subfloor and new 12x12 VCT flooring with a 6" base. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC GUARD TOWER 2 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3600
0167EXT1 | EXTERIOR FINISHES | 0167 | The building exterior is in good condition. It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SDCC REINJECTION BUILDING | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 624 | 2020-02-11 | Four to Ten Years | Long-Term Needs | 3 | 3120
0170EXT3 | EXTERIOR SIDING REPLACEMENT | 0170 | The tower has a painted T1-11 siding that is due for replacement. The existing siding is in poor condition and is missing some trim pieces. This project recommends removing the T1-11 siding, inspecting the exposed building structural elements and replacing it with new T1-11 siding including priming and painting. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC GUARD TOWER 2 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 17900
0170EXT4 | WINDOW REPLACEMENT | 0170 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 8 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC GUARD TOWER 2 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14300
0171ELE2 | EXTERIOR LIGHTING REPLACEMENT | 0171 | The building has perimeter HPS lighting on the exterior of the building, but the light fixtures are old and not energy efficient. This project would provide for the replacement of the exterior lighting fixtures with new LED light fixtures, using existing wiring. | SDCC GUARD TOWER 3 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0172ELE0 | EXTERIOR LIGHTING REPLACEMENT | 0172 | The building has perimeter HPS lighting on the exterior of the building, but the light fixtures are old and not energy efficient. This project would provide for the replacement of the exterior lighting fixtures with new LED light fixtures, using existing wiring. | SDCC GUARD TOWER 4 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0159PLM4 | REPAIR WATER SOFTENING SYSTEM | 0159 | The water softeners were not operational at the time of the 2020 survey and require additional rehabilitation. It is important to properly maintain these systems to provide quality water for the templifier / hot water heat pump system located in the penthouse and to prevent premature failure of the equipment. This project would provide for the necessary repairs of the water softening system including all connections to utilities. This project should be implemented concurrently with the REPLACE HEAT PUMP WATER HEATING SYSTEM project. | SDCC HOUSING UNIT 3 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 3000
0158HVA2 | EXHAUST FAN REPLACEMENT | 0158 | The existing exhaust fans that serve restroom and shower areas were replaced in 1999 and are not providing adequate ventilation. This project would provide for the removal of the existing exhaust fan assemblies and the purchase and installation of new exhaust fan assemblies including ducting and connections to utilities. Due to excessive humidity concerns, high volume commercial units are recommended. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC HOUSING UNIT 2 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 10800
0159EXT3 | EXTERIOR FINISHES | 0159 | Since the previous FCA visit in 2013, the exterior painted stucco and window frames have been refreshed with a new color scheme and is in good condition. It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is repairing the broken fluted blocks, power washing, priming and painting the stucco, cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SDCC HOUSING UNIT 3 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2020-02-11 | Four to Ten Years | Long-Term Needs | 3 | 119889
0159INT1 | INTERIOR FINISHES | 0159 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SDCC HOUSING UNIT 3 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2020-02-11 | Four to Ten Years | Long-Term Needs | 3 | 170100
0159EXT4 | ROOF REPLACEMENT | 0159 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1995. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC HOUSING UNIT 3 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 321900
0159SFT3 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0159 | This building does not have an automatic fire suppression system. This building exceeds 12,000 square feet on a single floor. Pursuant to the Nevada State Fire Marshal Regulation NAC 477.915 1.(c)(1) states that every building owned or occupied by the state regardless of occupancy having a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors, must have fire sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC HOUSING UNIT 3 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 301000
0159SEC2 | EXTERIOR DOOR REPLACEMENT | 0159 | The existing exterior doors and locks appear to be original to the building. They are showing signs of wear and deterioration from constant use and inmate abuse. It was noted that maintenance problems are occurring often. Because of security concerns and the condition of the doors, it is recommended they be replaced in the next two years. This project includes doors, frames, hardware, painting and disposal of the old doors. A total of 6 solid metal security-grade doors was used for this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC HOUSING UNIT 3 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 29000
0160PLM6 | REPLACE HEAT PUMP WATER HEATING SYSTEM | 0160 | Housing units 1-7 have their hot water provided by a heat pump system. There is one of these heat pump systems located in the penthouse of each housing unit 1-7. These systems were replaced once back in the 1990's as were the water softeners. But due to the lack of maintenance of the water softeners, the heat pumps are beginning to fail again or in some cases, have already failed. This project would provide for a new domestic water heating heat pump system. Removal and disposal of the old equipment is included in this estimate. This project should be implemented concurrently with the REPAIR WATER SOFTENING SYSTEM project. | SDCC HOUSING UNIT 4 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 83000
0159HVA2 | EXHAUST FAN REPLACEMENT | 0159 | The existing exhaust fans that serve restroom and shower areas were replaced in 1999 and are not providing adequate ventilation. This project would provide for the removal of the existing exhaust fan assemblies and the purchase and installation of new exhaust fan assemblies including ducting and connections to utilities. Due to excessive humidity concerns, high volume commercial units are recommended. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC HOUSING UNIT 3 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 10800
0160PLM5 | REPAIR WATER SOFTENING SYSTEM | 0160 | The water softeners were not operational at the time of the 2020 survey and require additional rehabilitation. It is important to properly maintain these systems to provide quality water for the templifier / hot water heat pump system located in the penthouse and to prevent premature failure of the equipment. This project would provide for the necessary repairs of the water softening system including all connections to utilities. This project should be implemented concurrently with the REPLACE HEAT PUMP WATER HEATING SYSTEM project. | SDCC HOUSING UNIT 4 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 3000
0159PLM5 | REPLACE HEAT PUMP WATER HEATING SYSTEM | 0159 | Housing units 1-7 have their hot water provided by a heat pump system. There is one of these heat pump systems located in the penthouse of each housing unit 1-7. These systems were replaced once back in the 1990's as were the water softeners. But due to the lack of maintenance of the water softeners, the heat pumps are beginning to fail again or in some cases, have already failed. This project would provide for a new domestic water heating heat pump system. Removal and disposal of the old equipment is included in this estimate. This project should be implemented concurrently with the REPAIR WATER SOFTENING SYSTEM project. | SDCC HOUSING UNIT 3 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 83000
0158ENR2 | WINDOW REPLACEMENT | 0158 | The existing windows in this building are of single pane wire mesh construction. These older windows are drafty and not energy efficient. Some of the windows and louver mechanisms are broken. This project would provide for the removal and replacement of the windows with new dual pane security rated window systems. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC HOUSING UNIT 2 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 165000
0158EXT5 | EXTERIOR DOOR REPLACEMENT | 0158 | The existing exterior doors and locks appear to be original to the building. They are showing signs of wear and deterioration from constant use and inmate abuse. It was noted that maintenance problems are occurring often. Because of security concerns and the condition of the doors, it is recommended they be replaced in the next two years. This project includes doors, frames, hardware, painting and disposal of the old doors. A total of 6 solid metal security-grade doors was used for this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC HOUSING UNIT 2 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 29000
0158SFT3 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0158 | This building does not have an automatic fire suppression system. This building exceeds 12,000 square feet on a single floor. Pursuant to the Nevada State Fire Marshal Regulation NAC 477.915 1.(c)(1) states that every building owned or occupied by the state regardless of occupancy having a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors, must have fire sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC HOUSING UNIT 2 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 301000
0158PLM2 | TOILET AND LAVATORY REPLACEMENT | 0158 | The existing toilets and lavatories in each of the 102 inmate cells are made of vitreous china. These types of fixtures are damaged and broken frequently. Weapons can be made from the broken pieces which creates a security risk. Stainless steel units are more durable and are recommended to be installed. This project would provide for replacing the existing toilets and lavatories with a stainless steel combination toilet with lavatory unit that is suicide resistant. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC HOUSING UNIT 2 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 668000
0168HVA5 | COOLING TOWER REPLACEMENT | 0168 | There are three cooling towers on site whose function is to remove heat from the sitewide water source heat pump (WSHP) loop. The equipment is in poor condition and should be scheduled for replacement in the next 1 - 2 years. This project would provide for removal and disposal of the existing equipment and installation of new cooling towers. | SDCC CENTRAL PLANT/WAREHOUSE | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 21122 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 650000
0159PLM1 | TOILET AND LAVATORY REPLACEMENT | 0159 | The existing toilets and lavatories in each of the 102 inmate cells are made of vitreous china. These types of fixtures are damaged and broken frequently. Weapons can be made from the broken pieces which creates a security risk. Stainless steel units are more durable and are recommended to be installed. This project would provide for replacing the existing toilets and lavatories with a stainless steel combination toilet with lavatory unit that is suicide resistant. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC HOUSING UNIT 3 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 668000
0160EXT3 | EXTERIOR FINISHES | 0160 | The exterior facade has not been refreshed with the new color scheme however it is in fair condition. It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is repairing the broken fluted blocks, power washing, priming and painting the stucco, cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SDCC HOUSING UNIT 4 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2020-02-11 | Four to Ten Years | Long-Term Needs | 3 | 119889
0161SFT3 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0161 | This building does not have an automatic fire suppression system. This building exceeds 12,000 square feet on a single floor. Pursuant to the Nevada State Fire Marshal Regulation NAC 477.915 1.(c)(1) states that every building owned or occupied by the state regardless of occupancy having a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors, must have fire sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC HOUSING UNIT 5 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 301000
0161HVA2 | EXHAUST FAN REPLACEMENT | 0161 | The existing exhaust fans that serve restroom and shower areas are original equipment and are not providing adequate ventilation. This project would provide for the removal of the existing exhaust fan assemblies and the purchase and installation of new exhaust fan assemblies including ducting and connections to utilities. Due to excessive humidity concerns, high volume commercial units are recommended. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC HOUSING UNIT 5 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 10800
0161PLM1 | TOILET AND LAVATORY REPLACEMENT | 0161 | The existing toilets and lavatories in each of the 102 inmate cells are made of vitreous china. These types of fixtures are damaged and broken frequently. Weapons can be made from the broken pieces which creates a security risk. Stainless steel units are more durable and are recommended to be installed. This project would provide for replacing the existing toilets and lavatories with a stainless steel combination toilet with lavatory unit that is suicide resistant. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC HOUSING UNIT 5 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 668000
0161EXT3 | EXTERIOR FINISHES | 0161 | The exterior facade has not been refreshed with the new color scheme however it is in fair condition. It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is repairing the broken fluted blocks, power washing, priming and painting the stucco, cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SDCC HOUSING UNIT 5 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2020-02-11 | Four to Ten Years | Long-Term Needs | 3 | 119889
0161EXT4 | ROOF REPLACEMENT | 0161 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1995. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC HOUSING UNIT 5 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 321900
0161PLM6 | REPLACE HEAT PUMP WATER HEATING SYSTEM | 0161 | Housing units 1-7 have their hot water provided by a heat pump system. There is one of these heat pump systems located in the penthouse of each housing unit 1-7. These systems were replaced once back in the 1990's as were the water softeners. But due to the lack of maintenance of the water softeners, the heat pumps are beginning to fail again or in some cases, have already failed. This project would provide for a new domestic water heating heat pump system. Removal and disposal of the old equipment is included in this estimate. This project should be implemented concurrently with the REPAIR WATER SOFTENING SYSTEM project. | SDCC HOUSING UNIT 5 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 83000
0159ENR2 | WINDOW REPLACEMENT | 0159 | The existing windows in this building are of single pane wire mesh construction. These older windows are drafty and not energy efficient. Some of the windows and louver mechanisms are broken. This project would provide for the removal and replacement of the windows with new dual pane security rated window systems. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC HOUSING UNIT 3 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 165000
0160ENR2 | WINDOW REPLACEMENT | 0160 | The existing windows in this building are of single pane wire mesh construction. These older windows are drafty and not energy efficient. Some of the windows and louver mechanisms are broken. This project would provide for the removal and replacement of the windows with new dual pane security rated window systems. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC HOUSING UNIT 4 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 165000
0158EXT3 | EXTERIOR FINISHES | 0158 | Since the previous FCA visit in 2013, the exterior painted stucco and window frames have been refreshed with a new color scheme and are in good condition. It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is repairing the broken fluted blocks, power washing, priming and painting the stucco, cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SDCC HOUSING UNIT 2 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2020-02-11 | Four to Ten Years | Long-Term Needs | 3 | 119889
0160HVA2 | EXHAUST FAN REPLACEMENT | 0160 | The existing exhaust fans that serve restroom and shower areas are original equipment and are not providing adequate ventilation. This project would provide for the removal of the existing exhaust fan assemblies and the purchase and installation of new exhaust fan assemblies including ducting and connections to utilities. Due to excessive humidity concerns, high volume commercial units are recommended. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC HOUSING UNIT 4 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 10800
0160INT1 | INTERIOR FINISHES | 0160 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SDCC HOUSING UNIT 4 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2020-02-11 | Four to Ten Years | Long-Term Needs | 3 | 170100
0160SFT3 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0160 | This building does not have an automatic fire suppression system. This building exceeds 12,000 square feet on a single floor. Pursuant to the Nevada State Fire Marshal Regulation NAC 477.915 1.(c)(1) states that every building owned or occupied by the state regardless of occupancy having a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors, must have fire sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC HOUSING UNIT 4 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 301000
0160EXT4 | ROOF REPLACEMENT | 0160 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1995. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC HOUSING UNIT 4 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 321900
0160SEC2 | EXTERIOR DOOR REPLACEMENT | 0160 | The existing exterior doors and locks appear to be original to the building. They are showing signs of wear and deterioration from constant use and inmate abuse. It was noted that maintenance problems are occurring often. Because of security concerns and the condition of the doors, it is recommended they be replaced in the next two years. This project includes doors, frames, hardware, painting and disposal of the old doors. A total of 6 solid metal security-grade doors was used for this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC HOUSING UNIT 4 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 29000
0160PLM2 | TOILET AND LAVATORY REPLACEMENT | 0160 | The existing toilets and lavatories in each of the 102 inmate cells are made of vitreous china. These types of fixtures are damaged and broken frequently. Weapons can be made from the broken pieces which creates a security risk. Stainless steel units are more durable and are recommended to be installed. This project would provide for replacing the existing toilets and lavatories with a stainless steel combination toilet with lavatory unit that is suicide resistant. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC HOUSING UNIT 4 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 668000
0161PLM4 | REPAIR WATER SOFTENING SYSTEM | 0161 | The water softeners were not operational at the time of the 2020 survey and require additional rehabilitation. It is important to properly maintain these systems to provide quality water for the templifier / hot water heat pump system located in the penthouse and to prevent premature failure of the equipment. This project would provide for the necessary repairs of the water softening system including all connections to utilities. This project should be implemented concurrently with the REPLACE HEAT PUMP WATER HEATING SYSTEM project. | SDCC HOUSING UNIT 5 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 3000
0155ADA2 | ADA RESTROOM UPGRADE | 0155 | The existing Men's and Women's restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for remodeling the Men's and Women's restrooms into ADA compliant restrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2018 IBC, ICC/ANSI A117.1, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC ADMINISTRATION A | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 9895 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 35700
0158INT1 | INTERIOR FINISHES | 0158 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SDCC HOUSING UNIT 2 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2020-02-11 | Four to Ten Years | Long-Term Needs | 3 | 170100
0156SEC1 | VISITOR CENTER SECURITY UPGRADES | 0156 | The visitor center serves as the primary access for friends and families visiting inmates. The potential for the introduction of contraband into the prison via visitors remains a problem, and this project addresses general security and related issues in this portion of the building. Included in the alterations are the installation of fixed covers for the restroom lavatory drains and replacing hollow stall components with solid materials. In the no-contact visitors room, there are line of sight issues for the correction officers, and the phone systems are outdated and in need of replacement. This project will include the installation of a full-view window in this area, a new correctional type phone system, and the installation of outlets and communications equipment for deaf and hearing impaired inmates and visitors. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC CONTROL/VISITATION | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 27669 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 77400
0156INT1 | INTERIOR FINISHES | 0156 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SDCC CONTROL/VISITATION | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 27669 | 2020-02-11 | Four to Ten Years | Long-Term Needs | 3 | 276700
0156EXT1 | EXTERIOR FINISHES | 0156 | The interior finishes are in good condition. It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting the stucco, cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SDCC CONTROL/VISITATION | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 27669 | 2020-02-11 | Four to Ten Years | Long-Term Needs | 3 | 276700
0156ADA3 | ADA DOOR HARDWARE REPLACEMENT | 0156 | The ADA Standards for Accessible Design states that handles, pulls, latches, locks and other operable parts on doors and gates shall be operable with one hand and shall not require tight grasping, pinching, or twisting of the wrist. The force to activate operable parts shall be 5 pounds maximum. It is recommended that proper lever hardware be installed on all of the interior and exterior doors in this building to meet these requirements. The 2018 IBC, ICC/ANSI A117.1, NRS 338.180 and sections 309.4 and 404.2.7 of the ADA Standards For Accessible Design were used as a reference for this project. | SDCC CONTROL/VISITATION | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 27669 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 72000
0155ADA4 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0155 | This building contains a water fountain that is not ADA compliant. The 2018 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC ADMINISTRATION A | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 9895 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 4800
0156ENR2 | WINDOW REPLACEMENT | 0156 | The windows are original, single pane construction in metal frames. These older windows are not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 53 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC CONTROL/VISITATION | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 27669 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 63000
0155ADA3 | BREAK ROOM REMODEL | 0155 | The kitchenette and associated cabinets in the employee break room are original to the building. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and countertops are delaminating and failing. This project recommends the replacement of the existing kitchen countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2018, ICC/ANSI A117.1 and the most current version of the ADA Standards for Accessible Design should be incorporated into the design such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC ADMINISTRATION A | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 9895 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 19500
0156ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0156 | This building contains a water fountain that is not ADA compliant. The 2018 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC CONTROL/VISITATION | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 27669 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 4800
0155ADA1 | ADA DOOR HARDWARE REPLACEMENT | 0155 | The ADA Standards for Accessible Design states that handles, pulls, latches, locks and other operable parts on doors and gates shall be operable with one hand and shall not require tight grasping, pinching, or twisting of the wrist. The force to activate operable parts shall be 5 pounds maximum. It is recommended that proper lever hardware be installed on all the interior and exterior doors in this building to meet these requirements. The 2018 IBC, ICC/ANSI A117.1, NRS 338.180 and sections 309.4 and 404.2.7 of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC ADMINISTRATION A | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 9895 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 9000
0155ENR2 | WINDOW REPLACEMENT | 0155 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 35 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC ADMINISTRATION A | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 9895 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 49000
0155INT1 | INTERIOR FINISHES | 0155 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SDCC ADMINISTRATION A | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 9895 | 2020-02-11 | Four to Ten Years | Long-Term Needs | 3 | 49475
0155EXT3 | ROOF REPLACEMENT | 0155 | The roof on this building was in fair to poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1995. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC ADMINISTRATION A | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 9895 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 186000
0155EXT1 | EXTERIOR FINISHES | 0155 | The exterior is in good condition and was refinished since the previous FCA Survey. It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting the stucco, cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. . | SDCC ADMINISTRATION A | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 9895 | 2020-02-11 | Four to Ten Years | Long-Term Needs | 3 | 59800
0155EXT2 | INVESTIGATE/ REPAIR WATERPROOFING | 0155 | The grade on the southeast side of the building has built up over time to the extent that it is higher than the grade originally designed. The result is that the waterproofing membrane is below grade and there are reports of water seeping into the interior of the building. This project recommends excavating the excess dirt to the grade originally designed and inspecting and repairing the waterproof membrane. The estimated depth of excavation is about two feet. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC ADMINISTRATION A | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 9895 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 10200
0155INT2 | JANITORS CLOSET REPAIRS | 0155 | The mop sink in the Janitors Closet is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC ADMINISTRATION A | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 9895 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1700
0157PLM1 | TOILET AND LAVATORY REPLACEMENT | 0157 | The existing toilets and lavatories in each of the 102 inmate cells are made of vitreous china. These types of fixtures are damaged and broken frequently. Weapons can be made from the broken pieces which creates a security risk. Stainless steel units are more durable and are recommended to be installed. This project would provide for replacing the existing toilets and lavatories with a stainless steel combination toilet with lavatory unit that is suicide resistant. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC HOUSING UNIT 1 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 668000
0158EXT4 | ROOF REPLACEMENT | 0158 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1995. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC HOUSING UNIT 2 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 321900
0158PLM5 | REPLACE HEAT PUMP WATER HEATING SYSTEM | 0158 | Housing units 1-7 have their hot water provided by a heat pump system. There is one of these heat pump systems located in the penthouse of each housing unit 1-7. These systems were replaced once back in the 1990's as were the water softeners. But due to the lack of maintenance of the water softeners, the heat pumps are beginning to fail again or in some cases, have already failed. This project would provide for a new domestic water heating heat pump system. Removal and disposal of the old equipment is included in this estimate. This project should be implemented concurrently with the REPAIR WATER SOFTENING SYSTEM project. | SDCC HOUSING UNIT 2 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 83000
0158PLM6 | REPAIR WATER SOFTENING SYSTEM | 0158 | The water softeners were not operational at the time of the 2020 survey and require additional rehabilitation. It is important to properly maintain these systems to provide quality water for the templifier / hot water heat pump system located in the penthouse and to prevent premature failure of the equipment. This project would provide for the necessary repairs of the water softening system including all connections to utilities. This project should be implemented concurrently with the REPLACE HEAT PUMP WATER HEATING SYSTEM project. | SDCC HOUSING UNIT 2 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 3000
0157ENR2 | WINDOW REPLACEMENT | 0157 | The existing windows in this building are of single pane wire mesh construction. These older windows are drafty and not energy efficient. Some of the windows and louver mechanisms are broken. This project would provide for the removal and replacement of the windows with new dual pane security rated window systems. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC HOUSING UNIT 1 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 165000
0157SEC3 | SECURITY GLAZING UPGRADE AT CENTRAL CONTROL | 0157 | The central control area in the housing unit is encased in an expanded metal lath and plexiglass. This arrangement protects the correctional officers, but causes line of sight issues, blind spots, and is damaged from abuse. The plexiglass is scratched and hazy making it difficult to see through. This project recommends replacing the expanded metal lath and plexiglass with a high-impact resistant glazing product, new frames and operable expanded metal protection (for cleaning purposes). A total of 6 glazing panel systems were used for this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC HOUSING UNIT 1 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 45000
0157EXT3 | EXTERIOR FINISHES | 0157 | Since the previous FCA visit in 2013, the exterior painted stucco and window frames have been refreshed with a new color scheme and is in good condition. It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is repairing the broken fluted blocks, power washing, priming and painting the stucco, cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SDCC HOUSING UNIT 1 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2020-02-11 | Four to Ten Years | Long-Term Needs | 3 | 119889
0156ADA1 | ADA RESTROOM UPGRADE | 0156 | There are 10 small restrooms, 2 large restrooms, and locker rooms for the staff. The locker rooms have recently been remodeled and are ADA compliant, but none of the other restrooms meet the Americans with Disabilities Act (ADA) requirements. Per 2018 IBC 1109.2, a complete retrofit of each restroom is necessary. This project would provide funding for remodeling the restrooms into ADA compliant restrooms. These items may include new sinks, toilets, hardware, mirrors, fixtures, flooring and paint. The 2018 IBC, ICC/ANSI A117.1, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC CONTROL/VISITATION | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 27669 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 59500
0157SEC2 | CELL DOORS, LOCKS AND MECHANISMS REPLACEMENT | 0157 | Housing Unit 1 was constructed in 1981. The cell door locks and mechanisms are original to the building and have been problematic due to inmate abuse and age. This project would provide for installing new cell doors, locks and mechanisms. A total of 102 doors was used for this estimate. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC HOUSING UNIT 1 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 1685000
0161SEC2 | EXTERIOR DOOR REPLACEMENT | 0161 | The existing exterior doors and locks appear to be original to the building. They are showing signs of wear and deterioration from constant use and inmate abuse. It was noted that maintenance problems are occurring often. Because of security concerns and the condition of the doors, it is recommended they be replaced in the next two years. This project includes doors, frames, hardware, painting and disposal of the old doors. A total of 6 solid metal security-grade doors was used for this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC HOUSING UNIT 5 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 29000
0157INT1 | INTERIOR FINISHES | 0157 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SDCC HOUSING UNIT 1 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 170100
0157SEC1 | EXTERIOR DOOR REPLACEMENT | 0157 | The existing exterior doors and locks appear to be original to the building. They are showing signs of wear and deterioration from constant use and inmate abuse. It was noted that maintenance problems are occurring often. Because of security concerns and the condition of the doors, it is recommended they be replaced in the next two years. This project includes doors, frames, hardware, painting and disposal of the old doors. A total of 6 solid metal security-grade doors was used for this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC HOUSING UNIT 1 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 29000
0157EXT4 | ROOF REPLACEMENT | 0157 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1995. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC HOUSING UNIT 1 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 321900
0157SFT1 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0157 | This building does not have an automatic fire suppression system. This building exceeds 12,000 square feet on a single floor. Pursuant to the Nevada State Fire Marshal Regulation NAC 477.915 1.(c)(1) states that every building owned or occupied by the state regardless of occupancy having a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors, must have fire sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC HOUSING UNIT 1 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 301000
0157PLM5 | REPLACE HEAT PUMP WATER HEATING SYSTEM | 0157 | Housing units 1-7 have their hot water provided by a heat pump system. There is one of these heat pump systems located in the penthouse of each housing unit 1-7. These systems were replaced once back in the 1990's as were the water softeners. But due to the lack of maintenance of the water softeners, the heat pumps are beginning to fail again or in some cases, have already failed. This project would provide for a new domestic water heating heat pump system. Removal and disposal of the old equipment is included in this estimate. This project should be implemented concurrently with the REPAIR WATER SOFTENING SYSTEM project. | SDCC HOUSING UNIT 1 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 83000
0157PLM4 | REPAIR WATER SOFTENING SYSTEM | 0157 | The water softeners were not operational at the time of the 2020 survey and require additional rehabilitation. It is important to properly maintain these systems to provide quality water for the templifier / hot water heat pump system located in the penthouse and to prevent premature failure of the equipment. This project would provide for the necessary repairs of the water softening system including all connections to utilities. This project should be implemented concurrently with the REPLACE HEAT PUMP WATER HEATING SYSTEM project. | SDCC HOUSING UNIT 1 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 3000
0157HVA2 | EXHAUST FAN REPLACEMENT | 0157 | The existing exhaust fans that serve restroom and shower areas were replaced in 1999 and are not providing adequate ventilation. This project would provide for the removal of the existing exhaust fan assemblies and the purchase and installation of new exhaust fan assemblies including ducting and connections to utilities. Due to excessive humidity concerns, high volume commercial units are recommended. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC HOUSING UNIT 1 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 10800
0166SIT2 | SITE DRAINAGE UPGRADES | 0166 | The grade does not slope away effectively from the buildings. Water has pooled against the foundation. In the winter months, as the water freezes against the foundation, over time, this can cause damage to the foundation. It is recommended per IBC 1804.3 Site Grading the ground immediately adjacent to the foundation shall be sloped away from the building at a slope of not less than one vertical in 20 units horizontal (5-percent slope) for a minimum distance of 10 feet (3048 mm) measured perpendicular to the face of the wall. This project would create a 5% slope away from the buildings. An additional retaining wall shall be installed as needed. It is recommended that the grading be completed within 2-3 years. | SDCC GYM/RECREATION BUILDING | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 16324 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0161SEC1 | CELL DOORS, LOCKS AND MECHANISMS REPLACEMENT | 0161 | Housing Unit 5 was constructed in 1981. The cell door locks and mechanisms are original to the building and have been problematic due to inmate abuse and age. This project would provide for installing new cell doors, locks and mechanisms. A total of 102 doors was used for this estimate. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC HOUSING UNIT 5 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1685000
0166INT5 | FLOORING REPLACEMENT | 0166 | The VCT (vinyl composite tile) flooring in the building is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for the removal and disposal of the old flooring, and installation of new 12x12 VCT flooring with a 6" base. The wood gymnasium flooring is addressed in a separate project. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC GYM/RECREATION BUILDING | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 16324 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 100800
0166INT6 | GYMNASIUM FLOOR REPLACEMENT | 0166 | The existing wood flooring in the gymnasium is reaching the end of its useful life. This project would provide for the removal of the existing flooring and installation of a new wood floor. A 25/32" thick maple on a sleeper system was used for this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC GYM/RECREATION BUILDING | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 16324 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 123400
0166ADA2 | ADA RESTROOM REPLACEMENT | 0166 | The building does not have an accessible restroom. The existing restrooms on the upper level and lower level do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom on each level. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2018 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC GYM/RECREATION BUILDING | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 16324 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 36000
0166ADA1 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0166 | This building contains water fountains on each floor that are not ADA compliant. The 2018 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of four drinking fountains to meet the ADA requirements, two on each floor. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC GYM/RECREATION BUILDING | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 16324 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 9600
0166EXT2 | ROOF REPLACEMENT | 0166 | The roof on this building was in poor condition at the time of the survey. Additionally, the roof is a walking surface for security personnel. This requirement needs consideration when determining a re-roofing solution. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1995. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. This project should be implemented concurrently with the ROOF REPLACEMENT project for the Gun Post at Gym Building. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC GYM/RECREATION BUILDING | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 16324 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 306900
0166INT4 | INTERIOR DOOR REPLACEMENT | 0166 | The existing interior doors in the building are original to the building and are damaged from abuse and age. This project would provide for the removal of the existing doors and the purchase and installation of new metal doors. All hardware and painting is included in this estimate. Hardware to include security keys and fusible locks. This estimate is for 22 interior doors. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC GYM/RECREATION BUILDING | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 16324 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 52400
0166SIT3 | SIDEWALK REPLACEMENT | 0166 | The concrete sidewalk and recreation area on the north side of the building is in need of replacement. They have cracks and are spalling. This project would provide for the removal and replacement of the concrete flatwork. 1000 SF of 4" thick concrete was used for this estimate. This project addresses removal and replacement of existing sidewalks as needed. | SDCC GYM/RECREATION BUILDING | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 16324 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18000
0166INT3 | INTERIOR FINISHES | 0166 | The interior finishes are in poor condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2 - 3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SDCC GYM/RECREATION BUILDING | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 16324 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 81620
0166SFT5 | GYPSUM BOARD CEILING REPAIRS | 0166 | The gypsum board ceiling on the 2nd floor in the southwest corner and located below the gun post on the roof appears to have structurally failed and is sagging significantly. The cause appears to be roof leaks and should be repaired. This project would provide for repairs to structure supporting the hard lid ceiling and a new gypsum board ceiling. Taping, texture and paint are included in this estimate. This project should be implemented concurrently with the ROOF REPLACEMENT project. | SDCC GYM/RECREATION BUILDING | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 16324 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 9750
0165EXT4 | OVERHEAD DOOR REPLACEMENT | 0165 | There are eight 12'x12' overhead coiling doors which are damaged and do not function properly. Exposure and wind have caused the doors to bend, crack and lose their finish. They are original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead coiling doors and replacement with new manually operated overhead coiling doors. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC INDUSTRIAL/CULINARY/P.I. | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 76309 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 48000
0165INT6 | INTERIOR DOOR REPLACEMENT | 0165 | The existing interior doors in the Industrial/Vocational side of the building are original to the building and are damaged from abuse and age. This project would provide for the removal of the existing doors and the purchase and installation of new metal doors. All hardware and painting is included in this estimate. Hardware is to include security keys and fusible locks. This estimate is for 44 interior doors, not including the Laundry/Culinary side of the building. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC INDUSTRIAL/CULINARY/P.I. | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 76309 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 105100
0165INT7 | FLOORING REPLACEMENT | 0165 | The VCT (vinyl composite tile), painted concrete, and ceramic tile in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for the removal and disposal of the existing flooring and installation of new 12x12 VCT flooring with a 6" base, painting or sealing the concrete as needed and replacing the ceramic tile in the next 2-3 years. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC INDUSTRIAL/CULINARY/P.I. | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 76309 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 57100
0165INT2 | INTERIOR FINISHES | 0165 | The interior finishes are in poor condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SDCC INDUSTRIAL/CULINARY/P.I. | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 76309 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 457800
0165EXT3 | ROOF REPLACEMENT | 0165 | The roof on this building was in fair to poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1995. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC INDUSTRIAL/CULINARY/P.I. | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 76309 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1434600
0166INT2 | FIRE RATED CEILING ASSEMBLY REPAIRS | 0166 | The gypsum board ceilings are damaged in several areas. It appears that these locations are a one-hour fire rated ceiling assembly and need to be repaired immediately. This project would provide for repairs to the ceiling with a fire rated gypsum board assembly. Taping, texture and paint are included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC GYM/RECREATION BUILDING | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 16324 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 3000
0168EXT1 | EXTERIOR FINISHES | 0168 | The exterior is in fair condition. It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting the stucco, cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SDCC CENTRAL PLANT/WAREHOUSE | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 21122 | 2020-02-11 | Four to Ten Years | Long-Term Needs | 3 | 105610
0169SFT3 | EXIT SIGN AND EGRESS LIGHTING INSTALLATION | 0169 | There are no exit signs or emergency egress lights in the guard tower. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2018 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC GUARD TOWER 1 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 200 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 1100
0169INT3 | FLOORING INSTALLATION | 0169 | The VCT (vinyl composite tile) flooring in the tower has been removed and the concrete is exposed. It is recommended to install new VCT flooring. This project would provide for the installation of new 12x12 VCT flooring with a 6" base. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC GUARD TOWER 1 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 200 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0169INT2 | INTERIOR FINISHES | 0169 | The interior finishes, including the stair tower are in poor condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SDCC GUARD TOWER 1 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 200 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0169EXT2 | EXTERIOR FINISHES | 0169 | The stucco finish is in good condition; however, all metal surfaces are showing signs of corrosion and need re-finishing. It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the exterior metal surfaces be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SDCC GUARD TOWER 1 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 200 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
0169INT4 | INTERIOR STAIRWAY REFURBISHMENT | 0169 | The interior metal stairs are showing signs of corrosion at the structural connections between the stair treads and side structural channels. At least one solid toe-kick has corroded through in multiple locations. This project would provide funding to remove and replace damaged toe-kicks, remove the corrosion at the stair tread connections, inspect and repair as required, and refinish the stairway and handrail. | SDCC GUARD TOWER 1 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 200 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0168INT2 | INTERIOR FINISHES | 0168 | The interior finishes are in good condition. It is recommended to repair and seal the interior concrete block walls at least once in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. | SDCC CENTRAL PLANT/WAREHOUSE | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 21122 | 2020-02-11 | Four to Ten Years | Long-Term Needs | 3 | 24000
0166EXT1 | EXTERIOR FINISHES | 0166 | Since the previous FCA visit in 2013, the exterior painted stucco and window frames have been refreshed with a new color scheme and is in good condition. It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting the stucco, cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SDCC GYM/RECREATION BUILDING | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 16324 | 2020-02-11 | Four to Ten Years | Long-Term Needs | 3 | 81620
0168EXT2 | OVERHEAD DOOR REPLACEMENT | 0168 | There are two 12'x15' overhead coiling doors and five 12'x10' overhead coiling doors which are damaged and do not function properly. Exposure and wind have caused the doors to bend, and the door tracks to pull away from the structure. They are original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead coiling doors and replacement with new manually operated overhead coiling doors. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC CENTRAL PLANT/WAREHOUSE | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 21122 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 52500
0165EXT1 | EXTERIOR FINISHES | 0165 | The exterior facade is in good condition. It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting the stucco, cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 8 -9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SDCC INDUSTRIAL/CULINARY/P.I. | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 76309 | 2020-02-11 | Four to Ten Years | Long-Term Needs | 3 | 381545
0168SFT2 | STORAGE RACK SEISMIC BRACING | 0168 | This project would provide for the installation of seismic bracing for the steel storage racks in the Warehouse. Section 15.5.3 of ASCE 7 describes the provisions required for seismic bracing of steel storage racks including connections to the floor, connections between back to back racks and protections for lower portions of posts from forklifts or other equipment. This project would provide for installing seismic bracing as required. The assessment and design of seismic bracing requirements by a licensed structural or civil engineer are not included in the estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC CENTRAL PLANT/WAREHOUSE | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 21122 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 41650
0168HVA4 | EVAPORATIVE COOLER REPLACEMENT | 0168 | The 4 roof top evaporative cooling units were installed in 1989. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of 4 new evaporative coolers and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing equipment and all required connections to utilities. | SDCC CENTRAL PLANT/WAREHOUSE | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 21122 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 14400
0168SFT3 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0168 | It appears that the Central Plant and Central Stores areas (approximately 9,100 square feet) are without fire suppression while the north end (approximately 12,000 square feet) of the building is protected. This building exceeds 12,000 square feet on a single floor. Pursuant to the Nevada State Fire Marshal Regulation NAC 477.915 1.(c)(1) states that every building owned or occupied by the state regardless of occupancy having a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors, must have fire sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. | SDCC CENTRAL PLANT/WAREHOUSE | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 21122 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 160300
0167INT1 | INTERIOR FINISHES | 0167 | The interior finishes are in fair condition. It is recommended to repair and seal the interior concrete block walls at least once in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. | SDCC REINJECTION BUILDING | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 624 | 2020-02-11 | Four to Ten Years | Long-Term Needs | 3 | 3120
0166SFT3 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0166 | This building does not have an automatic fire suppression system. This building exceeds 12,000 square feet on a single floor. Pursuant to the Nevada State Fire Marshal Regulation NAC 477.915 1.(c)(1) states that every building owned or occupied by the state regardless of occupancy having a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors, must have fire sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC GYM/RECREATION BUILDING | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 16324 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 286600
0166PLM1 | WATER HEATER REPLACEMENT | 0166 | There is a 100 gallon gas-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC GYM/RECREATION BUILDING | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 16324 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3570
0168EXT4 | EXTERIOR STUCCO FINISH REPAIRS | 0168 | The exterior walls have a stucco finish. Some of the areas have cracked and the stucco and underlying block have been damaged. Some damage was caused by forklifts and large delivery trucks. This project would provide for the repair of the damaged areas and repainting with an elastomeric paint. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC CENTRAL PLANT/WAREHOUSE | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 21122 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 17850
0162INT1 | INTERIOR FINISHES | 0162 | The interior finishes are in poor condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2 - 3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SDCC HOUSING UNIT 6 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 170100
0162ENR2 | WINDOW REPLACEMENT | 0162 | The existing windows in this building are of single pane wire mesh construction. These older windows are drafty and not energy efficient. Some of the windows and louver mechanisms are broken. This project would provide for the removal and replacement of the windows with new dual pane security rated window systems. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC HOUSING UNIT 6 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 165000
0162EXT3 | EXTERIOR FINISHES | 0162 | The exterior facade has not been refreshed with the new color scheme however it is in fair condition. It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is repairing the broken fluted blocks, power washing, priming and painting the stucco, cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SDCC HOUSING UNIT 6 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2020-02-11 | Four to Ten Years | Long-Term Needs | 3 | 119889
0162SEC2 | EXTERIOR DOOR REPLACEMENT | 0162 | The existing exterior doors and locks appear to be original to the building. They are showing signs of wear and deterioration from constant use and inmate abuse. It was noted that maintenance problems are occurring often. Because of security concerns and the condition of the doors, it is recommended they be replaced in the next two years. This project includes doors, frames, hardware, painting and disposal of the old doors. A total of 6 solid metal security-grade doors was used for this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC HOUSING UNIT 6 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 29000
0162PLM2 | TOILET AND LAVATORY REPLACEMENT | 0162 | The existing toilets and lavatories in each of the 102 inmate cells are made of vitreous china. These types of fixtures are damaged and broken frequently. Weapons can be made from the broken pieces which creates a security risk. Stainless steel units are more durable and are recommended to be installed. This project would provide for replacing the existing toilets and lavatories with a stainless steel combination toilet with lavatory unit that is suicide resistant. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC HOUSING UNIT 6 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 668000
0162EXT4 | ROOF REPLACEMENT | 0162 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1995. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC HOUSING UNIT 6 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 321900
0162SEC1 | CELL DOORS, LOCKS AND MECHANISMS REPLACEMENT | 0162 | Housing Unit 6 was constructed in 1981. The cell door locks and mechanisms are original to the building and have been problematic due to inmate abuse and age. This project would provide for installing new cell doors, locks and mechanisms. A total of 102 doors was used for this estimate. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC HOUSING UNIT 6 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1685000
0165HVA3 | EVAPORATIVE COOLER REPLACEMENT | 0165 | The 14 roof top evaporative cooling units were installed in 1989. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of 14 new evaporative coolers and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing equipment and all required connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | SDCC INDUSTRIAL/CULINARY/P.I. | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 76309 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50400
0162SEC3 | SECURITY GLAZING UPGRADE AT CENTRAL CONTROL | 0162 | The central control area in the housing unit is encased in an expanded metal lath and plexiglass. This arrangement protects the correctional officers, but causes line of sight issues, blind spots, and is damaged from abuse. The plexiglass is scratched and hazy making it difficult to see through. This project recommends replacing the expanded metal lath and plexiglass with a high-impact resistant glazing product, new frames and reinforcement to support the new glazing systems. A total of 6 glazing panels was used for this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC HOUSING UNIT 6 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 45000
0163HVA2 | EXHAUST FAN REPLACEMENT | 0163 | The existing exhaust fans that serve restroom and shower areas are original equipment and are not providing adequate ventilation. This project would provide for the removal of the existing exhaust fan assemblies and the purchase and installation of new exhaust fan assemblies including ducting and connections to utilities. Due to excessive humidity concerns, high volume commercial units should be installed. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC HOUSING UNIT 7 | 9970 | Correct | SDCC |  | Indian Springs | 1981 | 17127 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 10800
0162HVA2 | EXHAUST FAN REPLACEMENT | 0162 | The existing exhaust fans that serve restroom and shower areas are original equipment and are not providing adequate ventilation. This project would provide for the removal of the existing exhaust fan assemblies and the purchase and installation of new exhaust fan assemblies including ducting and connections to utilities. Due to excessive humidity concerns, high volume commercial units are recommended. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC HOUSING UNIT 6 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 10800
0162PLM6 | REPLACE HEAT PUMP WATER HEATING SYSTEM | 0162 | Housing units 1-7 have their hot water provided by a heat pump system. There is one of these heat pump systems located in the penthouse of each housing unit 1-7. These systems were replaced once back in the 1990's as were the water softeners. But due to the lack of maintenance of the water softeners, the heat pumps are beginning to fail again or in some cases, have already failed. This project would provide for a new domestic water heating heat pump system. Removal and disposal of the old equipment is included in this estimate. This project should be implemented concurrently with the REPAIR WATER SOFTENING SYSTEM project. | SDCC HOUSING UNIT 6 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 83000
0162PLM5 | REPAIR WATER SOFTENING SYSTEM | 0162 | The water softeners were not operational at the time of the 2020 survey and require additional rehabilitation. It is important to properly maintain these systems to provide quality water for the templifier / hot water heat pump system located in the penthouse and to prevent premature failure of the equipment. This project would provide for the necessary repairs of the water softening system including all connections to utilities. This project should be implemented concurrently with the REPLACE HEAT PUMP WATER HEATING SYSTEM project. | SDCC HOUSING UNIT 6 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 3000
0161ENR2 | WINDOW REPLACEMENT | 0161 | The existing windows in this building are of single pane wire mesh construction. These older windows are drafty and not energy efficient. Some of the windows and louver mechanisms are broken. This project would provide for the removal and replacement of the windows with new dual pane security rated window systems. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC HOUSING UNIT 5 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 165000
0161INT1 | INTERIOR FINISHES | 0161 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SDCC HOUSING UNIT 5 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2020-02-11 | Four to Ten Years | Long-Term Needs | 3 | 170100
0170ELE1 | EXTERIOR LIGHTING REPLACEMENT | 0170 | The building has perimeter HPS lighting on the exterior of the building, but the light fixtures are old and not energy efficient. This project would provide for the replacement of the exterior lighting fixtures with new LED light fixtures, using existing wiring. | SDCC GUARD TOWER 2 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0162SFT3 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0162 | This building does not have an automatic fire suppression system. This building exceeds 12,000 square feet on a single floor. Pursuant to the Nevada State Fire Marshal Regulation NAC 477.915 1.(c)(1) states that every building owned or occupied by the state regardless of occupancy having a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors, must have fire sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC HOUSING UNIT 6 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 301000
0163SEC3 | SECURITY GLAZING UPGRADE AT CENTRAL CONTROL | 0163 | The central control area in the housing unit is encased in an expanded metal lath and plexiglass. This arrangement protects the correctional officers, but causes line of sight issues, blind spots, and is damaged from abuse. The plexiglass is scratched and hazy making it difficult to see through. This project recommends replacing the expanded metal lath and plexiglass with a high-impact resistant glazing product, new frames and reinforcement to support the new glazing systems. A total of 6 glazing panels was used for this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC HOUSING UNIT 7 | 9970 | Correct | SDCC |  | Indian Springs | 1981 | 17127 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 45000
0161SEC3 | SECURITY GLAZING UPGRADE AT CENTRAL CONTROL | 0161 | The central control area in the housing unit is encased in an expanded metal lath and plexiglass. This arrangement protects the correctional officers, but causes line of sight issues, blind spots, and is damaged from abuse. The plexiglass is scratched and hazy making it difficult to see through. This project recommends replacing the expanded metal lath and plexiglass with a high-impact resistant glazing product, new frames and reinforcement to support the new glazing systems. A total of 6 glazing panels was used for this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC HOUSING UNIT 5 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 45000
0164INT3 | INTERIOR FINISHES | 0164 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SDCC EDUCATION BUILDING | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 19824 | 2020-02-11 | Four to Ten Years | Long-Term Needs | 3 | 138000
0164ENR2 | WINDOW REPLACEMENT | 0164 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 98 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC EDUCATION BUILDING | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 19824 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 117600
0164ADA1 | ADA RESTROOM UPGRADE | 0164 | The unisex restroom and the inmate restroom have been upgraded for ADA accessibility compliance, but they are not fully compliant. There is no pipe protection, the toilet paper dispenser is not in the correct location, and the accessories are not all within reach ranges. A partial retrofit is necessary. This project would provide funding to bring the restrooms into full ADA compliance. The 2018 IBC, ICC/ANSI A117.1, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC EDUCATION BUILDING | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 19824 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 7700
0164EXT2 | EXTERIOR FINISHES | 0164 | The building exterior is in good condition. It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is repairing the broken stucco areas, power washing, priming and painting the stucco, cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SDCC EDUCATION BUILDING | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 19824 | 2020-02-11 | Four to Ten Years | Long-Term Needs | 3 | 138768
0164PLM2 | JANITORS CLOSET REPAIRS | 0164 | The mop sink in the Janitors Closet has several cracks in the concrete and is leaking. This could lead to mold growth if not addressed. This project would provide for a new fiberglass mop sink and FRP to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | SDCC EDUCATION BUILDING | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 19824 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 3500
0163PLM3 | REPAIR WATER SOFTENING SYSTEM | 0163 | The water softeners were not operational at the time of the 2020 survey and require additional rehabilitation. It is important to properly maintain these systems to provide quality water for the templifier / hot water heat pump system located in the penthouse and to prevent premature failure of the equipment. This project would provide for the necessary repairs of the water softening system including all connections to utilities. This project should be implemented concurrently with the REPLACE HEAT PUMP WATER HEATING SYSTEM project. | SDCC HOUSING UNIT 7 | 9970 | Correct | SDCC |  | Indian Springs | 1981 | 17127 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 3000
0163SFT3 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0163 | This building does not have an automatic fire suppression system. This building exceeds 12,000 square feet on a single floor. Pursuant to the Nevada State Fire Marshal Regulation NAC 477.915 1.(c)(1) states that every building owned or occupied by the state regardless of occupancy having a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors, must have fire sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC HOUSING UNIT 7 | 9970 | Correct | SDCC |  | Indian Springs | 1981 | 17127 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 301000
0163PLM4 | REPLACE HEAT PUMP WATER HEATING SYSTEM | 0163 | Housing units 1-7 have their hot water provided by a heat pump system. There is one of these heat pump systems located in the penthouse of each housing unit 1-7. These systems were replaced once back in the 1990's as were the water softeners. But due to the lack of maintenance of the water softeners, the heat pumps are beginning to fail again or in some cases, have already failed. This project would provide for a new domestic water heating heat pump system. Removal and disposal of the old equipment is included in this estimate. This project should be implemented concurrently with the REPAIR WATER SOFTENING SYSTEM project. | SDCC HOUSING UNIT 7 | 9970 | Correct | SDCC |  | Indian Springs | 1981 | 17127 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 83000
0163EXT3 | EXTERIOR FINISHES | 0163 | Since the previous FCA visit in 2013, the exterior painted stucco and window frames have been refreshed with a new color scheme and are in good condition. It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is repairing the broken fluted blocks, power washing, priming and painting the stucco, cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SDCC HOUSING UNIT 7 | 9970 | Correct | SDCC |  | Indian Springs | 1981 | 17127 | 2020-02-11 | Four to Ten Years | Long-Term Needs | 3 | 119889
0163INT1 | INTERIOR FINISHES | 0163 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SDCC HOUSING UNIT 7 | 9970 | Correct | SDCC |  | Indian Springs | 1981 | 17127 | 2020-02-11 | Four to Ten Years | Long-Term Needs | 3 | 170100
0163SEC2 | CELL DOORS, LOCKS AND MECHANISMS REPLACEMENT | 0163 | Housing Unit 7 was constructed in 1981. The cell door locks and mechanisms are original to the building and have been problematic due to inmate abuse and age. This project would provide for installing new cell doors, locks and mechanisms. A total of 102 doors was used for this estimate. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC HOUSING UNIT 7 | 9970 | Correct | SDCC |  | Indian Springs | 1981 | 17127 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 1685000
0163EXT4 | ROOF REPLACEMENT | 0163 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1995. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC HOUSING UNIT 7 | 9970 | Correct | SDCC |  | Indian Springs | 1981 | 17127 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 321900
0163SEC1 | EXTERIOR DOOR REPLACEMENT | 0163 | The existing exterior doors and locks appear to be original to the building. They are showing signs of wear and deterioration from constant use and inmate abuse. It was noted that maintenance problems are occurring often. Because of security concerns and the condition of the doors, it is recommended they be replaced in the next two years. This project includes doors, frames, hardware, painting and disposal of the old doors. A total of 6 solid metal security-grade doors was used for this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC HOUSING UNIT 7 | 9970 | Correct | SDCC |  | Indian Springs | 1981 | 17127 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 29000
0163PLM1 | TOILET AND LAVATORY REPLACEMENT | 0163 | The existing toilets and lavatories in each of the 102 inmate cells are made of vitreous china. These types of fixtures are damaged and broken frequently. Weapons can be made from the broken pieces which creates a security risk. Stainless steel units are more durable and are recommended to be installed. This project would provide for replacing the existing toilets and lavatories with a stainless steel combination toilet with lavatory unit that is suicide resistant. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC HOUSING UNIT 7 | 9970 | Correct | SDCC |  | Indian Springs | 1981 | 17127 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 668000
0165SFT2 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0165 | An estimated 50% of this building (38,000 ft2) does not have an automatic fire suppression system. Nevada State Fire Marshal NRS 477.915 (c) requires buildings having a floor area exceeding 12,000 s.f. on any floor or 24,000 s.f. on all floors, or which contain an R occupancy, be scheduled for installation of an automatic fire suppression system during the next remodeling of, or addition to the building. Backflow prevention is included in this estimate. There is currently an outdated Ansul system in the culinary area. This system was not operational at the time of this survey and must be replaced with the most current and appropriate system. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC INDUSTRIAL/CULINARY/P.I. | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 76309 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 670300
0163ENR2 | WINDOW REPLACEMENT | 0163 | The existing windows in this building are of single pane wire mesh construction. These older windows are drafty and not energy efficient. Some of the windows and louver mechanisms are broken. This project would provide for the removal and replacement of the windows with new dual pane security rated window systems. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/11/2020. | SDCC HOUSING UNIT 7 | 9970 | Correct | SDCC |  | Indian Springs | 1981 | 17127 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 165000
0365SFT2 | EXIT SIGN AND EGRESS LIGHTING INSTALLATION | 0365 | The building does not have emergency lighting or exit signs. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC 2018 Chapter 10 and IFC 2018 Chapter 11 was referenced for this project. | SDCC WELDING SHOP | 9970 | Correct | SDCC |  | Indian Springs |  | 400 | 2020-02-11 | Immediate to Two Years | Currently Critical | 1 | 2500
0624SIT1 | CRACK FILL & SEAL ASPHALT PAVING | 0624 | It is important to maintain the asphalt concrete paving around the Water Tank. This project would provide for minor crack filling and sealing of the paving around the tank, including minor erosion repairs at tank overflow. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 4,000 square feet of asphalt area was used to generate this estimate. | SDCC WATER TANK | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 2551 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
0365EXT1 | EXTERIOR FINISHES | 0365 | The pre-finished metal panel exterior is in fair condition. It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SDCC WELDING SHOP | 9970 | Correct | SDCC |  | Indian Springs |  | 400 | 2020-02-11 | Four to Ten Years | Long-Term Needs | 3 | 2000
0365INT1 | INTERIOR FINISHES | 0365 | The interior pre-finished metal panel finishes are in good condition. It is recommended that the interior walls and ceilings be checked for signs of corrosion issues in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the interior of the building. As part of the inspection, all surfaces should be repaired and re-painted as necessary. | SDCC WELDING SHOP | 9970 | Correct | SDCC |  | Indian Springs |  | 400 | 2020-02-11 | Four to Ten Years | Long-Term Needs | 3 | 2000
0624EXT1 | EXTERIOR FINISHES | 0624 | There are signs of corrosion at the ladder attachment points and also the external lighting poles. It is important to maintain the finish, weather resistance and appearance of the water tank. This project would provide funding for the painting of the water tank and caulking of the joints to maintain it in a good, weather tight condition. It is recommended that this project be implemented in the next 2 - 3 years and that this project be scheduled on a cyclical basis based on environmental conditions. | SDCC WATER TANK | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 2551 | 2020-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 51100
2302SFT2 | FIRE ALARM SYSTEM UPGRADE | 2302 | This building is equipped with an automatic fire detection and alarm system that is no longer operable. According to 2018 IFC 907.8.5 Inspection, testing and maintenance, the building owner shall be responsible to maintain the fire and life safety systems in an operable condition at all times. It is recommended the fire alarm AHJ (Authority Having Jurisdiction) be notified and make a determination on the disposition of the existing system, whether to demolish / decommission or upgrade and make operational. This estimate includes the cost of replacing the existing system with a new system that will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1 Section 7 and the 2018 International Fire Code. | MODULAR STORAGE #1-NORTH | 9916 | Educ | B&G |  | Carson City | 1960 | 1440 | 2020-10-07 | Immediate to Two Years | Currently Critical | 1 | 7200
2308SFT3 | FIRE ALARM SYSTEM UPGRADE | 2308 | This building is equipped with an automatic fire detection and alarm system that is no longer operable. According to 2018 IFC 907.8.5 Inspection, testing and maintenance, the building owner shall be responsible to maintain the fire and life safety systems in an operable condition at all times. It is recommended the fire alarm AHJ (Authority Having Jurisdiction) be notified and make a determination on the disposition of the existing system, whether to demolish / decommission or upgrade and make operational. This estimate includes the cost of replacing the existing system with a new system that will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1 Section 7 and the 2018 International Fire Code. | EDUCATION MODULAR OFFICE-WEST | 9916 | Educ | B&G |  | Carson City | 1960 | 1152 | 2020-10-07 | Immediate to Two Years | Currently Critical | 1 | 5800
2308HVA1 | HVAC EQUIPMENT REPLACEMENT | 2308 | The building is heated and cooled by several separate pieces of equipment including electric baseboard heaters, wall-mounted evaporative coolers, and a portable air conditioning unit. These units are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of a new HVAC packaged unit and ductwork to provide conditioning for the entire building. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 03/31/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/07/2020. | EDUCATION MODULAR OFFICE-WEST | 9916 | Educ | B&G |  | Carson City | 1960 | 1152 | 2020-10-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 46000
2308EXT3 | WINDOW REPLACEMENT | 2308 | The windows are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 4 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 03/31/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/07/2020. | EDUCATION MODULAR OFFICE-WEST | 9916 | Educ | B&G |  | Carson City | 1960 | 1152 | 2020-10-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
2308INT1 | INTERIOR FINISHES | 2308 | The interior finishes are in good condition. It is recommended that the interior walls be painted at least once in the next 8 - 9 years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | EDUCATION MODULAR OFFICE-WEST | 9916 | Educ | B&G |  | Carson City | 1960 | 1152 | 2020-10-07 | Four to Ten Years | Long-Term Needs | 3 | 6900
2308EXT1 | EXTERIOR FINISHES | 2308 | The exterior finishes are in good condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding, priming, painting, caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | EDUCATION MODULAR OFFICE-WEST | 9916 | Educ | B&G |  | Carson City | 1960 | 1152 | 2020-10-07 | Four to Ten Years | Long-Term Needs | 3 | 8000
2308SFT4 | STRENGTHEN GUARDRAIL | 2308 | The guardrail supporting the ADA handrails appears to be inadequately supported. The guardrail can be easily moved horizontally perpendicular to the path of travel. It is recommended that the guardrail and handrail be strengthened to meet 2018 IBC Chapter 1607.8 requirements. | EDUCATION MODULAR OFFICE-WEST | 9916 | Educ | B&G |  | Carson City | 1960 | 1152 | 2020-10-07 | Immediate to Two Years | Currently Critical | 1 | 1500
2302EXT1 | EXTERIOR FINISHES | 2302 | The exterior finishes are in good condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding, priming, painting, and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MODULAR STORAGE #1-NORTH | 9916 | Educ | B&G |  | Carson City | 1960 | 1440 | 2020-10-07 | Four to Ten Years | Long-Term Needs | 3 | 7200
2302INT1 | INTERIOR FINISHES | 2302 | The interior finishes were not examined and access not provided. The building is not occupied and is used for storage. It is recommended that the interior walls be painted at least once in the next 8 - 9 years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | MODULAR STORAGE #1-NORTH | 9916 | Educ | B&G |  | Carson City | 1960 | 1440 | 2020-10-07 | Four to Ten Years | Long-Term Needs | 3 | 7200
2302ADA1 | REPLACE ACCESSIBLE ENTRANCE RAMP / ENTRY DECK | 2302 | This facility has a wood ramp and entry deck located on the south side of the building which is the only entrance and exit to the building. The ramp and deck are deteriorating and do not have proper landings, guardrails or handrails. This project would provide for an upgrade to the ramp to make it fully ADA compliant including new decking, handrails, guardrails, signage, and landings. The 2018 IBC Chapter 10 and 11, ICC/ANSI A117.1 and the most current version of the Americans With Disabilities Act Accessible Guidelines (ADAAG) was used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 03/31/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/07/2020. | MODULAR STORAGE #1-NORTH | 9916 | Educ | B&G |  | Carson City | 1960 | 1440 | 2020-10-07 | Immediate to Two Years | Currently Critical | 1 | 22000
0202EXT5 | CONCRETE STAIR REPLACEMENT | 0202 | The concrete stairs that access the east end of the building are deteriorating. Spalling and cracking have occurred. Exposure to the elements is a contributing factor. It appears these stairs are original to the building. A replacement of the stairs, landing, and guardrail system is recommended. | DEPARTMENT OF EDUCATION OFFICE | 9916 | Educ | B&G |  | Carson City | 1965 | 27500 | 2020-10-07 | Immediate to Two Years | Currently Critical | 1 | 7500
0202PLM2 | SEWER SYSTEM REPLACEMENT | 0202 | The sewer / wastewater infrastructure in the building is over 50 years old and has caused maintenance problems. This project would provide for the removal of the existing infrastructure and installation of a new sewer / waste water infrastructure in the building. 300 linear feet of cast iron pipe was used to generate this estimate. | DEPARTMENT OF EDUCATION OFFICE | 9916 | Educ | B&G |  | Carson City | 1965 | 27500 | 2020-10-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 90000
0202ENR2 | EXTERIOR LIGHTING REPLACEMENT | 0202 | The building has perimeter lighting on the exterior of the building, but the light fixtures are old and not energy efficient. This project would provide for the replacement of the exterior lighting fixtures with new LED light fixtures using existing wiring. This estimate is based on replacing 25 fixtures. | DEPARTMENT OF EDUCATION OFFICE | 9916 | Educ | B&G |  | Carson City | 1965 | 27500 | 2020-10-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0202EXT4 | EXTERIOR DOOR REPLACEMENT | 0202 | The existing west facing exterior metal doors and frame located on the north side of the building appear to be original to the building. The hinges and doors are damaged and showing signs of wear and deterioration from constant use. This project would provide for the removal of the existing doors and replacement with a new metal door assembly including frames, locks, hardware, and painting. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | DEPARTMENT OF EDUCATION OFFICE | 9916 | Educ | B&G |  | Carson City | 1965 | 27500 | 2020-10-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0202INT2 | REPLACE CARPETING | 0202 | The carpeted flooring was installed during the remodel of 1995. It is reaching the end of its expected life and should be scheduled for replacement. This project would provide for the removal of the existing carpet and installation of new commercial grade carpet tiles and new rubber base. This project or a portion thereof was previously recommended in the FCA report dated 03/31/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/07/2020. | DEPARTMENT OF EDUCATION OFFICE | 9916 | Educ | B&G |  | Carson City | 1965 | 27500 | 2020-10-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 131700
0202INT1 | INTERIOR FINISHES | 0202 | The interior finishes are in good condition. It is recommended that the interior walls be painted at least once in the next 8 - 9 years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | DEPARTMENT OF EDUCATION OFFICE | 9916 | Educ | B&G |  | Carson City | 1965 | 27500 | 2020-10-07 | Four to Ten Years | Long-Term Needs | 3 | 82500
0202EXT1 | EXTERIOR FINISHES | 0202 | The exterior finishes are in good condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including cleaning and sealing the brick masonry, painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures and other penetrations. It is recommended that the building be sealed, painted, and caulked in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Also included is repairs to the damaged brick masonry columns and damaged infill CMU / concrete slab areas where doors were once located. | DEPARTMENT OF EDUCATION OFFICE | 9916 | Educ | B&G |  | Carson City | 1965 | 27500 | 2020-10-07 | Four to Ten Years | Long-Term Needs | 3 | 192500
1935EXT2 | REPLACE ROOF | 1935 | The existing roof is due for replacement and is the subject of a 2005 CIP project request. | FALLON ETR OFFICE | 9827 | ETR | ESD |  | Fallon | 1978 | 4000 | 2004-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 28000
1935HVA0 | REPLACE HVAC SYSTEM AND CONTROLS | 1935 | The existing HVAC system is not able to effectively heat and cool the office spaces, handicapped restrooms, and the phone/server room. The rooftop units are reaching the end of their useful lives and should be replaced. Ductwork should be redesigned, installed, and balanced to effectively distribute the air in the spaces. New electric supplemental heating should be added to the two handicapped bathrooms, which are on exterior walls. An exhaust fan should be installed in the store room (phone and server room) to remove heat from the server. | FALLON ETR OFFICE | 9827 | ETR | ESD |  | Fallon | 1978 | 4000 | 2004-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 61000
1935EXT1 | REFINISH SOFFITS | 1935 | The building soffits are starting to show signs of weathering. This project would cover the existing wood soffit with an aluminum cover and install soffit vents. | FALLON ETR OFFICE | 9827 | ETR | ESD |  | Fallon | 1978 | 4000 | 2004-06-04 | Four to Ten Years | Long-Term Needs | 3 | 3000
1935SIT1 | SEAL AND STRIPE PARKING LOT | 1935 | The existing parking lot has numerous cracks, in which weeds are growing. This project would seal the cracks, seal the entire lot, restripe, and relocate the handicapped parking sign. | FALLON ETR OFFICE | 9827 | ETR | ESD |  | Fallon | 1978 | 4000 | 2004-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 17500
1935HVA2 | INSTAL ROOF ACCESS HATCH AND LADDER | 1935 | The existing building has no permanent access to the rooftop equipment. The shape of the Mansard roof makes using a ladder to access the roof unsafe. The Uniform Mechanical Code (1997 307.5 and 2003 904.10.3) require roof access for equipment servicing. This project would install a lockable roof access hatch and permanent fixed ladder in the Janitor's Closet or Store Room. | FALLON ETR OFFICE | 9827 | ETR | ESD |  | Fallon | 1978 | 4000 | 2004-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
1935LGT1 | LONG-TERM NEEDS | 1935 | Projects in this category address possible long term needs of the facility. This does not represent a cost for all future maintenance but is a budgetary number for future Capital Improvement projects related to maintenance. The cyclical treatment of the building exterior and interior is very important to help maintain the finish, weather proofing, integrity and appearance of the building. This treatment should include everything that has to do with water proofing the building envelope including painting or staining, sealing, repair, and sealant where applicable; for example, around all windows, flashing, fixtures, sills, etc. This also includes interior applied finishes such as paint, grout, caulking, etc. Special attention should be paid to areas that are exposed to moisture. This project also accounts for possible system replacements. | FALLON ETR OFFICE | 9827 | ETR | ESD |  | Fallon | 1978 | 4000 | 2004-06-04 | Four to Ten Years | Long-Term Needs | 3 | 20000
1935ADA1 | INSTALL POWER DOOR OPENER AND HARDWARE | 1935 | The main entrance to this building is a pair of aluminum storefront doors arranged in a vestibule configuration. This project recommends the installation of a power-assisted door opener for the main entrance and includes the installation, related wiring and hardware. | FALLON ETR OFFICE | 9827 | ETR | ESD |  | Fallon | 1978 | 4000 | 2004-06-04 | Immediate to Two Years | Currently Critical | 1 | 7000
1935INT1 | BUILDING INTERIOR REFINISHING | 1935 | The building exterior walls are bare Concrete Masonry Units (CMU) and should be furred and insulated to conserve energy and improve comfort. Floor coverings, VCT and carpet are well worn and in need of replacement. The kitchen cabinets are in need of refinishing. The interior walls are in need of repainting. In numerous locations, sheetrock fasteners in partition walls are working loose and are protruding. Both doors to the handicapped restrooms have improper door stops that will damage the doors. the rear door is in need of weather strip, a door stop, repairs to the exit device. This project would furr the exterior walls, paint all interior walls, grind and fill the floor slab cracks, replace the VCT, replace the carpet with carpet tile, refinish the kitchen cabinets, install overhead stops on both handicapped restroom doors and the rear door, repair the rear door exit device, and install new brush type weather seal at the rear door. | FALLON ETR OFFICE | 9827 | ETR | ESD |  | Fallon | 1978 | 4000 | 2004-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 52500
0398EXT2 | INSTALL RIGID INSULATION | 0398 | The East side of the basement has an air intake louver currently covered by Masonite. This project would replace the Masonite with rigid insulation to prevent the possibility of freezing water lines. | STATE ADMINISTRATIVE OFFICE | 9853 | ETR | ESD |  | Carson City | 1960 | 30920 | 2004-09-28 | Immediate to Two Years | Currently Critical | 1 | 2500
0398SFT1 | RELOCATE BICYCLE RACK | 0398 | The existing bicycle rack is immediately adjacent to the building gas service. The service has a seismic gas shutoff valve to protect the facility from gas leakage after an earthquake. These valves are sensitive to vibration and impact and there is the possibility that personnel using the bicycle rack can trip the valve and cause a nuisance shut down of gas to the building. This project would relocate the bicycle rack to the East side of the building. | STATE ADMINISTRATIVE OFFICE | 9853 | ETR | ESD |  | Carson City | 1960 | 30920 | 2004-09-28 | Immediate to Two Years | Currently Critical | 1 | 550
0398EXT3 | REPLACE SIDE WALKS | 0398 | The existing concrete side walks are cracked and present a trip hazard to pedestrians. | STATE ADMINISTRATIVE OFFICE | 9853 | ETR | ESD |  | Carson City | 1960 | 30920 | 2004-09-28 | Immediate to Two Years | Currently Critical | 1 | 5800
0398INT2 | REPLACE CEILING TILE | 0398 | Ceiling tile in the computer room and in the first floor hall is damaged, dirty, or mismatched. This project would replace the tile in the computer room with a smooth face tile not subject to holding dirt. The project would also replace tile in the first floor hall to provide matching tile throughout. | STATE ADMINISTRATIVE OFFICE | 9853 | ETR | ESD |  | Carson City | 1960 | 30920 | 2004-09-28 | Four to Ten Years | Long-Term Needs | 3 | 3500
0398EXT1 | REPLACE FLASHING OVER GENERATOR ROOM | 0398 | Existing flashing allows wind driven rain to enter the building. This project would replace the flashing with a mastic sealed flashing to protect the building. | STATE ADMINISTRATIVE OFFICE | 9853 | ETR | ESD |  | Carson City | 1960 | 30920 | 2004-09-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
0398INT1 | REPLACE CARPET | 0398 | Carpet throughout the facility is worn and stained. This project would replace the existing broadloom carpet with carpet tile. | STATE ADMINISTRATIVE OFFICE | 9853 | ETR | ESD |  | Carson City | 1960 | 30920 | 2004-09-28 | Four to Ten Years | Long-Term Needs | 3 | 87500
0398INT4 | PAINT INTERIOR FINISHES | 0398 | Based on building use and the passage of time, the interior walls and ceilings of this building should have a new application of paint for proper upkeep and maintenance. | STATE ADMINISTRATIVE OFFICE | 9853 | ETR | ESD |  | Carson City | 1960 | 30920 | 2004-09-28 | Four to Ten Years | Long-Term Needs | 3 | 77300
0398SIT1 | REPAIR AND RESEAL ASPHALT PARKING AREAS | 0398 | The existing paving is in fair condition. Climate and constant use will accelerate deterioration. For proper maintenance it is recommended the entire parking area and driveway be resealed. | STATE ADMINISTRATIVE OFFICE | 9853 | ETR | ESD |  | Carson City | 1960 | 30920 | 2004-09-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 40000
0398EXT5 | TREATMENT OF EXTERIOR FINISHES | 0398 | It is important to maintain the finish, weather resistance and appearance of the building. This project includes items to protect the exterior building envelope other than the roof, including painting, staining, or other applied finishes, and sealant and gaskets in and around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. | STATE ADMINISTRATIVE OFFICE | 9853 | ETR | ESD |  | Carson City | 1960 | 30920 | 2004-09-28 | Four to Ten Years | Long-Term Needs | 3 | 54110
0398EXT4 | INSTALL DOCK BUMPERS AND LIGHTING | 0398 | The loading dock does not have bumpers to protect the building from impact. This project would install rubber bumpers and a loading dock light. | STATE ADMINISTRATIVE OFFICE | 9853 | ETR | ESD |  | Carson City | 1960 | 30920 | 2004-09-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5500
0398PLM1 | INSTALL BACKFLOW PREVENTION DEVICES | 0398 | State Health law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of back siphonage or backpressure. This project allows for the installation of a reduced pressure principle backflow preventer on the building service and vacuum breakers at all hose bibs and janitor's sinks. Costs include an above ground vault for the backflow preventer, and allowance for 200 feet of 1" conduit to provide power for freeze protection. | STATE ADMINISTRATIVE OFFICE | 9853 | ETR | ESD |  | Carson City | 1960 | 30920 | 2004-09-28 | Immediate to Two Years | Currently Critical | 1 | 15000
0398ENR1 | INSTALL LIGHTING CONTROL | 0398 | The existing entry lights do not shut off during daylight hours. This project would repair an existing or install a new photocell control for the lights. | STATE ADMINISTRATIVE OFFICE | 9853 | ETR | ESD |  | Carson City | 1960 | 30920 | 2004-09-28 | Four to Ten Years | Long-Term Needs | 3 | 500
2565EXT1 | EXTERIOR FINISHES | 2565 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. This project will protect the building envelope and is recommended on a cyclical basis based on environmental conditions. | DETR LAS VEGAS OFFICE | 9837 | ETR | ETR |  | Las Vegas | 2006 | 59874 | 2013-06-05 | Four to Ten Years | Long-Term Needs | 3 | 179622
2565INT1 | INTERIOR FINISHES | 2565 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next four to six years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | DETR LAS VEGAS OFFICE | 9837 | ETR | ETR |  | Las Vegas | 2006 | 59874 | 2013-06-05 | Four to Ten Years | Long-Term Needs | 3 | 299370
9837SIT1 | CRACK FILL / SEAL ASPHALT PAVING | 9837 | The existing asphalt concrete paving on site is in good condition. This project would provide for crack filling as needed and sealing and striping the pavement in the next three to four years. This project should be completed on a cyclical basis based on environmental conditions and use. | DETR LAS VEGAS OFFICE SITE | 9837 | ETR | ETR |  | Las Vegas | 0 |  | 2013-06-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 46300
1476INT6 | JANITORS CLOSET REPAIRS | 1476 | The mop sink in the Janitors Closet is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide Fiberglass Reinforced Panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | NEVADA JOB CONNECT - ELKO OFFICE | 9823 | ETR | ESD |  | Elko | 1985 | 4000 | 2016-07-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
1476EXT6 | WINDOW REPLACEMENT | 1476 | The windows are original, double pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 20 units. Removal and disposal of the existing windows is included in this estimate. | NEVADA JOB CONNECT - ELKO OFFICE | 9823 | ETR | ESD |  | Elko | 1985 | 4000 | 2016-07-05 | Four to Ten Years | Long-Term Needs | 3 | 30000
1476ENR2 | LIGHTING UPGRADE | 1476 | The existing lighting fixtures are the older fluorescent type and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | NEVADA JOB CONNECT - ELKO OFFICE | 9823 | ETR | ESD |  | Elko | 1985 | 4000 | 2016-07-05 | Four to Ten Years | Long-Term Needs | 3 | 32000
1476PLM1 | WATER HEATER REPLACEMENT | 1476 | There are two electric water heaters in the building. One water heater is a 12 gallon and the other is a 19 gallon. The average lifespan of a water heater is eight to ten years. The units were installed in 1992. It is recommended that 2 new electric water heaters, seismic straps, braided steel hose, expansion tanks, ball valves, hardwire electric lines and pans be installed in the next 2-3 years. Removal and disposal of the existing equipment is included in this estimate. | NEVADA JOB CONNECT - ELKO OFFICE | 9823 | ETR | ESD |  | Elko | 1985 | 4000 | 2016-07-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
1476ELE2 | ELECTRICAL REPAIRS | 1476 | Heat tape was installed in the roof drains and the power cords were plugged into outlets on the roof. The electrical outlets were installed in such a way that the face is on top allowing rain and snow to fall directly into the plug. The conduit is not screwed together in some areas exposing the wires inside to the elements. These issues create a fire and safety hazard and will at the very least cause premature failure of the equipment. This project would provide for reworking the conduits, outlets and wiring by a licensed electrician. This project or a portion thereof was previously recommended in the FCA report dated 07/23/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/05/2016. | NEVADA JOB CONNECT - ELKO OFFICE | 9823 | ETR | ESD |  | Elko | 1985 | 4000 | 2016-07-05 | Immediate to Two Years | Currently Critical | 1 | 1500
1476EXT5 | ROOF REPLACEMENT | 1476 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time-frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next 4-5 years to be consistent with the roofing program and the end of the warranty period. | NEVADA JOB CONNECT - ELKO OFFICE | 9823 | ETR | ESD |  | Elko | 1985 | 4000 | 2016-07-05 | Four to Ten Years | Long-Term Needs | 3 | 48000
1476EXT3 | EXTERIOR FINISHES | 1476 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NEVADA JOB CONNECT - ELKO OFFICE | 9823 | ETR | ESD |  | Elko | 1985 | 4000 | 2016-07-05 | Four to Ten Years | Long-Term Needs | 3 | 40000
1476INT5 | INTERIOR FINISHES | 1476 | It is recommended to paint the interior walls and ceilings at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and adequately prepared to receive the coating. An epoxy-based paint should be utilized in wet areas for durability. | NEVADA JOB CONNECT - ELKO OFFICE | 9823 | ETR | ESD |  | Elko | 1985 | 4000 | 2016-07-05 | Four to Ten Years | Long-Term Needs | 3 | 40000
1476ELE3 | ELECTRICAL PANEL UPGRADES | 1476 | The electrical panel in the building does not have an inside cover (dead panel) that properly protects individuals from touching the bus bar and the interior of the panel. This does not comply with NEC 2011 or OSHA 1910. This project would provide funds to fabricate and install a new dead panel in accordance with NEC 2011 and OSHA 1910. | NEVADA JOB CONNECT - ELKO OFFICE | 9823 | ETR | ESD |  | Elko | 1985 | 4000 | 2016-07-05 | Immediate to Two Years | Currently Critical | 1 | 2000
1476ADA2 | BREAK ROOM REMODEL | 1476 | The kitchenette and associated cabinets in the employee break room are in good condition but don’t comply with ADA requirements. This project recommends changes to the kitchenette and associated break room for ADA compliance. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards for Accessible Design should be incorporated into the design. This estimate includes removal and disposal of the necessary existing materials. | NEVADA JOB CONNECT - ELKO OFFICE | 9823 | ETR | ESD |  | Elko | 1985 | 4000 | 2016-07-05 | Immediate to Two Years | Currently Critical | 1 | 15000
1476ADA4 | ADA RESTROOM UPGRADE | 1476 | The Men's and Women's designated ADA restrooms do not entirely meet the ADA requirements. A complete retrofit is necessary. This project would provide funding for remodeling the Men's and Women's restrooms per ADA regulations. Items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | NEVADA JOB CONNECT - ELKO OFFICE | 9823 | ETR | ESD |  | Elko | 1985 | 4000 | 2016-07-05 | Immediate to Two Years | Currently Critical | 1 | 40000
1476ADA3 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 1476 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. This project or a portion thereof was previously recommended in the FCA report dated 07/23/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/05/2016. | NEVADA JOB CONNECT - ELKO OFFICE | 9823 | ETR | ESD |  | Elko | 1985 | 4000 | 2016-07-05 | Immediate to Two Years | Currently Critical | 1 | 4000
9823ENR1 | EXTERIOR LIGHTING REPLACEMENT | 9823 | The building has perimeter lighting on the exterior of the building, but the light fixtures are old, failing and not energy efficient. This project would provide for the replacement of the exterior lighting fixtures with new LED light fixtures, using existing wiring. | ELKO DETR OFFICE SITE | 9823 | ETR | ESD |  | Elko | 0 |  | 2016-07-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
9823ADA1 | ADA ACCESSIBLE PATH OF TRAVEL | 9823 | The ADA provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the office are necessary to comply with ADA accessibility requirements. This project would provide for a concrete van accessible ADA parking and loading space and concrete walkway to the existing sidewalk. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. 750 square feet of concrete was used for this estimate. It is recommended that this project coincide with the paving project. | ELKO DETR OFFICE SITE | 9823 | ETR | ESD |  | Elko | 0 |  | 2016-07-05 | Immediate to Two Years | Currently Critical | 1 | 30000
9823SFT1 | EXTERIOR STAIR HANDRAIL REPLACEMENT | 9823 | The handrail on the concrete stairs on the north side of the site is older and does not meet current code for safety. The gripping surfaces are incorrect, they do not have proper extensions and they are installed on only one side of the stairs. This project recommends the installation of handrails in accordance with 2012 IBC Section 1012. Removal and disposal of the existing materials are included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 07/23/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/05/2016. | ELKO DETR OFFICE SITE | 9823 | ETR | ESD |  | Elko | 0 |  | 2016-07-05 | Immediate to Two Years | Currently Critical | 1 | 7500
9823SIT2 | CRACK FILL & SEAL ASPHALT PAVING | 9823 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the paving site wide including access roads and parking areas. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 10,000 square feet of asphalt area was used to generate this estimate. | ELKO DETR OFFICE SITE | 9823 | ETR | ESD |  | Elko | 0 |  | 2016-07-05 | Four to Ten Years | Long-Term Needs | 3 | 14000
1473INT2 | JANITORS CLOSET REPAIRS | 1473 | The mop sink in the Janitors Closet is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | WASHOE CASUAL LABOR OFFICE | 9847 | ETR | ESD |  | Sparks | 1985 | 2400 | 2016-10-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
1473INT1 | INTERIOR FINISHES | 1473 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | WASHOE CASUAL LABOR OFFICE | 9847 | ETR | ESD |  | Sparks | 1985 | 2400 | 2016-10-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24000
1473HVA1 | EXHAUST FAN REPLACEMENT | 1473 | The exhaust fans in the restrooms were inoperative and/or damaged at the time of the survey. Due to building code requirements and excessive humidity concerns, this project would provide funding for the purchase and installation of high volume commercial exhaust fans. | WASHOE CASUAL LABOR OFFICE | 9847 | ETR | ESD |  | Sparks | 1985 | 2400 | 2016-10-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
1473ADA4 | ADA RESTROOM UPGRADE | 1473 | The building does not have fully accessible restrooms and do not meet the ADA requirements. A retrofit is necessary. This project would provide funding for remodeling the Men's and Women's restrooms per ADA regulations. Items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | WASHOE CASUAL LABOR OFFICE | 9847 | ETR | ESD |  | Sparks | 1985 | 2400 | 2016-10-26 | Immediate to Two Years | Currently Critical | 1 | 30000
1473SFT3 | EGRESS LIGHTING UPGRADE | 1473 | The emergency egress lighting is insufficient. This project would provide for the purchase and installation of emergency egress lighting to provide illumination along the egress route. IBC 2012 Chapter 10 was referenced for this project. | WASHOE CASUAL LABOR OFFICE | 9847 | ETR | ESD |  | Sparks | 1985 | 2400 | 2016-10-26 | Immediate to Two Years | Currently Critical | 1 | 1200
1473ENR2 | LIGHTING UPGRADE | 1473 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | WASHOE CASUAL LABOR OFFICE | 9847 | ETR | ESD |  | Sparks | 1985 | 2400 | 2016-10-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19200
1473ENR3 | EXTERIOR LIGHTING REPLACEMENT | 1473 | The building has perimeter lighting on the exterior of the building, but the light fixtures are old and not energy efficient. This project would provide for the replacement of the exterior lighting fixtures with new LED light fixtures, using existing wiring. | WASHOE CASUAL LABOR OFFICE | 9847 | ETR | ESD |  | Sparks | 1985 | 2400 | 2016-10-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18000
1473SFT2 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 1473 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. | WASHOE CASUAL LABOR OFFICE | 9847 | ETR | ESD |  | Sparks | 1985 | 2400 | 2016-10-26 | Immediate to Two Years | Currently Critical | 1 | 4000
1473PLM1 | WATER HEATER REPLACEMENT | 1473 | There are two natural gas fired water heaters in the building. One is a 50 gallon and the other is a 40 gallon water heater. The average life span of a water heater is eight to ten years. With the passage of time and constant use, these units are showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that the new natural gas fired water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. | WASHOE CASUAL LABOR OFFICE | 9847 | ETR | ESD |  | Sparks | 1985 | 2400 | 2016-10-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3500
1473EXT2 | EXTERIOR FINISHES | 1473 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | WASHOE CASUAL LABOR OFFICE | 9847 | ETR | ESD |  | Sparks | 1985 | 2400 | 2016-10-26 | Four to Ten Years | Long-Term Needs | 3 | 24000
1473EXT3 | WINDOW REPLACEMENT | 1473 | The windows are original, double pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 7 units. Removal and disposal of the existing windows is included in this estimate. | WASHOE CASUAL LABOR OFFICE | 9847 | ETR | ESD |  | Sparks | 1985 | 2400 | 2016-10-26 | Four to Ten Years | Long-Term Needs | 3 | 10500
9847ADA1 | ADA ACCESSIBLE PATH OF TRAVEL | 9847 | The ADA provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the office are necessary to comply with ADA accessibility requirements. This project would provide for a concrete van accessible ADA parking and loading space and concrete walkway to the existing sidewalk. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. 750 square feet of concrete was used for this estimate. It is recommended that this project coincide with the paving project. | WASHOE CASUAL LABOR OFFICE SITE | 9847 | ETR | ESD |  | Sparks | 0 |  | 2016-10-26 | Immediate to Two Years | Currently Critical | 1 | 30000
9847SIT1 | SITE DRAINAGE UPGRADES | 9847 | The grade does not slope away effectively from the buildings. Water has pooled against the foundation. In the winter months, as the water freezes against the foundation, over time, this can cause damage to the foundation. It is recommended per IBC 1804.3 Site Grading the ground immediately adjacent to the foundation shall be sloped away from the building at a slope of not less than one vertical in 20 units horizontal (5-percent slope) for a minimum distance of 10 feet (3048 mm) measured perpendicular to the face of the wall. This project would create a 5% slope away from the buildings. Additional drainage swales shall be installed, as needed. It is recommended that the grading be completed within 2-3 years. | WASHOE CASUAL LABOR OFFICE SITE | 9847 | ETR | ESD |  | Sparks | 0 |  | 2016-10-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
9833ADA1 | ADA SIGNAGE | 9833 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2003 were referenced for this project. | LAS VEGAS CASUAL LABOR SITE | 9833 | ETR | ESD |  | Las Vegas | 0 |  | 2017-12-12 | Immediate to Two Years | Currently Critical | 1 | 2500
9833SIT1 | ASPHALT PARKING LOT REPLACEMENT | 9833 | The asphalt parking lots are failing, with significant alligatoring, settling and general deterioration observed. The settling on the south side has caused drainage problems with standing water in the middle of the parking lot. This project covers the removal and replacement of the existing asphalt for parking and site access. Striping for safety, parking and loading zones is included in this estimate as well as perimeter curbing and parking curbs as needed. 18,000 square feet was used to generate this estimate. | LAS VEGAS CASUAL LABOR SITE | 9833 | ETR | ESD |  | Las Vegas | 0 |  | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 180000
9833SIT2 | CHAIN LINK FENCE REPLACEMENT | 9833 | The chain link perimeter fence does not keep vagrants out and has several areas that are in need of repair. This project recommends the installation of a 6 foot high 6 gauge wire perimeter chain link fence around the entire site and two vehicle gates with hardware. A three wire barbed fence is also recommended to be installed along the top of the chain link fence to prevent vagrants from entering the property. The cost estimate includes demolition and disposal of the existing fence. | LAS VEGAS CASUAL LABOR SITE | 9833 | ETR | ESD |  | Las Vegas | 0 |  | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 42000
0257EXT5 | HVAC STRUCTURE REPLACEMENT | 0257 | The HVAC units on the roof are surrounded by a wood framed structure. The structure partially protects the equipment from the elements and serves an architectural function by blocking the equipment from view. The wood framing and plywood walls have deteriorated and should be scheduled for replacement. This project would provide for removal and disposal of the existing materials and replacement with a new wood structure. | LAS VEGAS CASUAL LABOR OFFICE | 9833 | ETR | ESD |  | Las Vegas | 1975 | 2400 | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0257ADA1 | EMPLOYEE ADA RESTROOM REPAIRS | 0257 | The employee ADA restroom does not entirely meet the current accessibility requirements. The sign on the wall adjacent to the door is blocked by chairs. A person must be able to approach within 3 inches of the sign without encountering protruding objects. The clear floor space inside the restroom is blocked by storage items which impede on the required turning radius as well as access to the lavatory. This project provides for removing the chairs and storage items in order to maintain the restroom in a compliant status. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2003 were referenced for this project. | LAS VEGAS CASUAL LABOR OFFICE | 9833 | ETR | ESD |  | Las Vegas | 1975 | 2400 | 2017-12-12 | Immediate to Two Years | Currently Critical | 1 | 500
0257SFT4 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0257 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. | LAS VEGAS CASUAL LABOR OFFICE | 9833 | ETR | ESD |  | Las Vegas | 1975 | 2400 | 2017-12-12 | Immediate to Two Years | Currently Critical | 1 | 4000
0257INT2 | INTERIOR FINISHES | 0257 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 5-6 years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | LAS VEGAS CASUAL LABOR OFFICE | 9833 | ETR | ESD |  | Las Vegas | 1975 | 2400 | 2017-12-12 | Four to Ten Years | Long-Term Needs | 3 | 12000
0257ADA3 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0257 | This building contains a water fountain. The 2006 IBC Section 1109.5 states where a water fountain is provided, at least half should be accessible. This project would provide funding for the purchase and installation of a new accessible fixed high/ low ADA drinking fountain. | LAS VEGAS CASUAL LABOR OFFICE | 9833 | ETR | ESD |  | Las Vegas | 1975 | 2400 | 2017-12-12 | Immediate to Two Years | Currently Critical | 1 | 4000
0257EXT4 | EXTERIOR DOOR REPLACEMENT | 0257 | Two of the exterior metal doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the north and south single door assemblies with new metal doors, frames and hardware. The storefront system on the east elevation has been replaced recently. Removal and disposal of the existing doors is included in this estimate. | LAS VEGAS CASUAL LABOR OFFICE | 9833 | ETR | ESD |  | Las Vegas | 1975 | 2400 | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0257ENR1 | WINDOW REPLACEMENT | 0257 | The windows are original, single pane construction in a metal frame. There is also a clerestory row of plexiglass windows on two sides of the building. These older windows are drafty and not energy efficient. This project recommends replacing all of the windows with dual pane, higher efficiency units. This estimate is for the replacement of 12 glass units and 16 plexiglass units. Removal and disposal of the existing windows is included in this estimate. | LAS VEGAS CASUAL LABOR OFFICE | 9833 | ETR | ESD |  | Las Vegas | 1975 | 2400 | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24000
0257PLM1 | WATER HEATER REPLACEMENT | 0257 | There is a 20 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. The water heater is located in the attic. It cannot be converted to a gas-fired unit due to limited space and access. Removal and disposal of the existing equipment is included in this estimate. | LAS VEGAS CASUAL LABOR OFFICE | 9833 | ETR | ESD |  | Las Vegas | 1975 | 2400 | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
0257PLM2 | BACKFLOW PREVENTION | 0257 | State Health Law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of back siphonage or backpressure. This project allows for the installation of double check valves or reduced pressure principle backflow preventers as appropriate to the hazard and in appropriate locations near the potential source of contamination. Costs include an above ground vault, and allowance for 200 feet of 1" conduit to provide power for freeze protection. | LAS VEGAS CASUAL LABOR OFFICE | 9833 | ETR | ESD |  | Las Vegas | 1975 | 2400 | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0257SFT2 | EXIT SIGN AND EGRESS LIGHTING INSTALLATION | 0257 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2006 Chapter 10 was referenced for this project. | LAS VEGAS CASUAL LABOR OFFICE | 9833 | ETR | ESD |  | Las Vegas | 1975 | 2400 | 2017-12-12 | Immediate to Two Years | Currently Critical | 1 | 5000
0257SFT1 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0257 | The building is a B occupancy per the 2006 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. | LAS VEGAS CASUAL LABOR OFFICE | 9833 | ETR | ESD |  | Las Vegas | 1975 | 2400 | 2017-12-12 | Immediate to Two Years | Currently Critical | 1 | 33600
0257ADA2 | PUBLIC ADA RESTROOM REMODEL | 0257 | The Men's and Women's designated ADA restrooms in the Job Seeker Room do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for construction of two unisex accessible restrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2003 were referenced for this project. | LAS VEGAS CASUAL LABOR OFFICE | 9833 | ETR | ESD |  | Las Vegas | 1975 | 2400 | 2017-12-12 | Immediate to Two Years | Currently Critical | 1 | 50000
0257EXT3 | REPAIR/ REPLACE FASCIA AND SOFFITS | 0257 | The metal fascia and the soffits around the building are weather beaten, peeling, and are showing signs of considerable wear. This project would provide funding to repair the fascia and soffits. Repairs include: replacing if necessary, sanding, scrapping, priming and painting. | LAS VEGAS CASUAL LABOR OFFICE | 9833 | ETR | ESD |  | Las Vegas | 1975 | 2400 | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18750
0257EXT2 | EXTERIOR FINISHES | 0257 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 6-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | LAS VEGAS CASUAL LABOR OFFICE | 9833 | ETR | ESD |  | Las Vegas | 1975 | 2400 | 2017-12-12 | Four to Ten Years | Long-Term Needs | 3 | 24000
0257ENR2 | LIGHTING UPGRADE | 0257 | The lighting fixtures are the older mercury vapor type in the employee office and fluorescent T-12's in the Job Seeker Room which are not energy efficient. This project will upgrade the mercury vapor lamps to current standards and the T-12 lamps to T-8 lamps with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination and HVAC load. Occupancy sensors will be installed in restrooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | LAS VEGAS CASUAL LABOR OFFICE | 9833 | ETR | ESD |  | Las Vegas | 1975 | 2400 | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
1994SIT3 | GATE OPERATOR REPLACEMENT | 1994 | The site has an automatic vehicle access gate to control access into the maintenance yard. The gate operator has been malfunctioning and has difficulty opening and closing the gate and is usually left open due to its problematic operation. This project recommends replacing the gate operator with a high quality operator that can handle heavy traffic as well as servicing the gates and related hardware to ensure prolonged operation. The new gate operator is required to meet UL Standard 325, per NRS 405.270. | #17 DESERT WILLOW TREATMENT CENTER | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1998 | 58400 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
1993ADA2 | ADA RESTROOM UPGRADE | 1993 | The designated unisex ADA accessible restroom is not fully compliant. The flush handle is on the wrong side, the faucet controls are not compliant and the sink location is not compliant. A partial retrofit is necessary. This project would provide funding to bring the restroom into full ADA compliance. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | #15 WEST NEIGHBORHOOD FAMILY SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 6580 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 2000
1993SFT5 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 1993 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. | #15 WEST NEIGHBORHOOD FAMILY SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 6580 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 3290
1995EXT2 | WINDOW REPLACEMENT | 1995 | The windows are original, single pane construction in metal frames. These older windows are drafty and at least one of them is broken. This project recommends replacing the windows with dual pane units. This estimate is for the replacement of 4 units. Removal and disposal of the existing windows is included in this estimate. | POOLHOUSE/STORAGE | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 836 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
1995EXT1 | EXTERIOR FINISHES | 1995 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 02/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | POOLHOUSE/STORAGE | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 836 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4180
1993EXT1 | EXTERIOR FINISHES | 1993 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA reports dated 06/19/1998 and 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #15 WEST NEIGHBORHOOD FAMILY SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 6580 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 32900
1993INT3 | RESTROOM REMODEL | 1993 | The non-ADA restroom in the building has older fixtures, finishes and cabinets. It is original to the building and is due for a complete remodel. This project would provide for a complete remodel of the restroom fixtures, cabinets, hardware, floor and wall finishes. | #15 WEST NEIGHBORHOOD FAMILY SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 6580 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
1993SFT4 | FIRE SUPPRESSION SYSTEM INSTALLATION | 1993 | The building is a B occupancy per the 2012 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 or R-2 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #15 WEST NEIGHBORHOOD FAMILY SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 6580 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 92120
1994SIT4 | COURTYARD IMPROVEMENTS | 1994 | The building and courtyard walls have considerable damage to the concrete masonry units (CMU) from lawn sprinklers wetting the CMU and poor drainage. Four of the five courtyards are due to be re-worked in order to prevent further damage. This project would remove the turf within three feet of the CMU walls, adjust the sprinklers so they do not wet the walls and re-grade or install French drains to ensure proper drainage out of the courtyards. | #17 DESERT WILLOW TREATMENT CENTER | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1998 | 58400 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
1994EXT1 | EXTERIOR FINISHES | 1994 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #17 DESERT WILLOW TREATMENT CENTER | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1998 | 58400 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 292000
1994SFT1 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 1994 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #17 DESERT WILLOW TREATMENT CENTER | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1998 | 58400 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 4000
1991SFT4 | FIRE RATED CEILING REPAIRS | 1991 | The fire rated ceilings in the two mechanical equipment closets are damaged and should be scheduled for immediate repairs. Penetrations have been made in the one hour fire rated assemblies when new equipment or utility lines are installed which compromises the fire protection design of the building. This project would provide for the removal of the remaining gypsum board ceiling and installation of new 5/8" type X fire rated gypsum board including taping and fire proofing all ceiling penetrations to provide a one hour fire rated ceiling assembly. Taping, texture and paint are included in this estimate. | #13 RESIDENTIAL UNIT | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 4610 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 5000
1994ENR1 | DIRECT DIGITAL CONTROL SYSTEM FOR HVAC UPGRADE | 1994 | Presently the building has an older direct digital control (DDC) system for the HVAC system. The current Schneider system was an upgrade from the original Yamas system. The original Yamas equipment is failing and does not integrate well with the new Schneider software. A new comprehensive system of software and equipment is due to be installed. The new system should allow starting of equipment, monitoring of status, monitoring of space temperatures, monitoring and control of hot and chilled water temperatures, and similar typical centrally controlled elements. Detailed control of the individual elements of the buildings systems can yield tremendous benefits based upon the reported operating hours coupled with varying occupancy loads. The system should include a microprocessor control center which monitors and manages all components of the buildings HVAC system. The system should also have the capability of controlling other building systems (such as lighting, alarms, etc.) and of communicating with the central management system for the campus. | #17 DESERT WILLOW TREATMENT CENTER | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1998 | 58400 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 85000
1993EXT3 | EXTERIOR DOOR REPLACEMENT | 1993 | The existing exterior door in the storefront entrance is original to the building. It is damaged from age and general wear and tear and does not function properly. This project would provide for the replacement and installation of a new metal door, frame and ADA compliant hardware. Removal and disposal of the existing door is included in this estimate. | #15 WEST NEIGHBORHOOD FAMILY SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 6580 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 4000
1994INT1 | INTERIOR FINISHES | 1994 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #17 DESERT WILLOW TREATMENT CENTER | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1998 | 58400 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 292000
1993ADA3 | ACCESSIBLE ENTRANCE RAMP | 1993 | The building is lacking an accessible entrance into the building. The building offers a program to the public. This building is required to have an accessible entrance per the Americans with Disabilities Act (ADA) regulations. This project would provide for an accessible ramp to access the building. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | #15 WEST NEIGHBORHOOD FAMILY SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 6580 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 35000
1993EXT4 | ROOF REPLACEMENT | 1993 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1993. It is recommended that the single-ply membrane on this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. The clay tile roofing is not included in this estimate. | #15 WEST NEIGHBORHOOD FAMILY SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 6580 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 66000
1994HVA2 | WATER TREATMENT | 1994 | The chemical water treatment systems for the cooling tower, the chillers and the boilers were not operating at the time of the survey. This project would provide for a chemical treatment program including an updated chemicals control system, service and employee training provided by a qualified water treatment vendor. The annual maintenance fee charged by the water treatment vendor would be determined after an investigation of the water system is complete. These annual costs are not included in this project cost. For budgeting purposes, a $12,000 fee is suggested. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #17 DESERT WILLOW TREATMENT CENTER | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1998 | 58400 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 12000
1994SEC1 | SECURITY CARD ACCESS UPGRADE | 1994 | This building is equipped with a security control system that is outdated and should be scheduled for immediate replacement. Problems exist with the door control panel and door access readers for the client rooms and access doors. The "Checkpoint" system is over ten years old and it is increasingly difficult to find replacement parts and experienced repairmen to service the equipment. Due to the security level of the facility it is imperative that a new system is installed for the safety of the staff, clients and the public. This project addresses replacement of the control panels, computer software and approximately 35 door access card readers. | #17 DESERT WILLOW TREATMENT CENTER | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1998 | 58400 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 87500
1994SIT2 | SITE DRAINAGE UPGRADES | 1994 | The building has drainage problems mainly on the north side where grade does not properly slope away from the building and drain pipes get clogged. The rain accumulates in several areas adjacent to the building, creating a water problem which infiltrates the interior during inclement weather. It is unknown where the drainage pipes attached to the downspouts lead to after they leave the building, but they get backed up and overflow near the building. This project would create positive flow away from the buildings by re-grading, paving, installing additional drainage swales as needed and scoping the drain pipes to determine why they back up. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #17 DESERT WILLOW TREATMENT CENTER | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1998 | 58400 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
1995INT1 | INTERIOR FINISHES | 1995 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 02/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | POOLHOUSE/STORAGE | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 836 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4180
1992INT3 | INTERIOR FINISHES | 1992 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | #14 RESIDENTIAL UNIT | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 4610 | 2012-10-17 | Four to Ten Years | Long-Term Needs | 3 | 23050
1991EXT7 | ROOF / CAP FLASHING MAINTENANCE | 1991 | It is important to maintain the finish, weather resistance and appearance of the roof's cap flashing, caulking and penetrations. This project recommends work to protect these elements, including re-caulking and painting the metal roof cap flashing to maintain it in a good, weather-tight condition. This project should be completed within the next one to two years. | #13 RESIDENTIAL UNIT | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 4610 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 1200
1991SIT2 | ROOF DRAIN DOWNSPOUT MODIFICATIONS | 1991 | The roof drain downspouts currently terminate within inches of the building with no continuous drainage away from the foundation. This is causing the water to pool next to the foundation and damage the foundation and walls. This project would provide for the extension of the roof drains from the downspouts to approximately 5'-0" away from the perimeter of the building to prevent pooling and damage to the building. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #13 RESIDENTIAL UNIT | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 4610 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
1991SFT6 | EXTERIOR STAIR HANDRAIL INSTALLATION | 1991 | The concrete exterior stairs at the entry are lacking a handrail as required in the 2012 IBC Chapter 10, Section 1012. This project would provide for a tubular steel framed handrail to be installed. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #13 RESIDENTIAL UNIT | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 4610 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 5000
1991EXT6 | ROOF REPLACEMENT | 1991 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1992. It is recommended that the single-ply membrane on this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. The clay tile roofing is not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #13 RESIDENTIAL UNIT | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 4610 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 42000
1991INT4 | INTERIOR FINISHES | 1991 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | #13 RESIDENTIAL UNIT | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 4610 | 2012-10-17 | Four to Ten Years | Long-Term Needs | 3 | 23050
1991ADA3 | ADA KITCHEN REMODEL | 1991 | The two kitchens in the building are original to the building. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and countertops are delaminating and failing. This project recommends the replacement of the existing kitchen countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards For Accessible Design should be incorporated into the design such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. | #13 RESIDENTIAL UNIT | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 4610 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 30000
1991ADA4 | ADA RESTROOM REMODEL | 1991 | The building does not have an accessible restroom. The existing restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit of two restrooms is necessary. This project would provide funding for construction of two unisex accessible restrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #13 RESIDENTIAL UNIT | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 4610 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 40000
1991EXT2 | EXTERIOR FINISHES | 1991 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA reports dated 06/22/1998 and 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #13 RESIDENTIAL UNIT | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 4610 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 23050
1991SFT3 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 1991 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #13 RESIDENTIAL UNIT | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 4610 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 4000
1991ADA2 | ADA DOOR HARDWARE REPLACEMENT | 1991 | The 2010 ADA Standards for Accessible Design states that handles, pulls, latches, locks and other operable parts on doors and gates shall be operable with one hand and shall not require tight grasping, pinching, or twisting of the wrist. The force to activate operable parts shall be 5 pounds maximum. It is recommended that proper lever hardware be installed on all of the interior and exterior doors in this building to meet these requirements. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and sections 309.4 and 404.2.7 of the 2010 ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #13 RESIDENTIAL UNIT | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 4610 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 9600
1991ADA5 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 1991 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | #13 RESIDENTIAL UNIT | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 4610 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 2000
1992SFT5 | FIRE RATED CEILING REPAIRS | 1992 | The fire rated ceilings in the two mechanical equipment closets are damaged and should be scheduled for immediate repairs. Penetrations have been made in the one hour fire rated assemblies when new equipment or utility lines are installed which compromises the fire protection design of the building. This project would provide for the removal of the remaining gypsum board ceiling and installation of new 5/8" type X fire rated gypsum board including taping and fire proofing all ceiling penetrations to provide a one hour fire rated ceiling assembly. Taping, texture and paint are included in this estimate. | #14 RESIDENTIAL UNIT | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 4610 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 5000
1991PLM2 | WATER TREATMENT SYSTEM INSTALLATION | 1991 | The existing plumbing and HVAC systems are not equipped with a water treatment system. Failure to treat the water causes wear and tear on the domestic water supply lines, plumbing fixtures and HVAC equipment. This project would provide for the purchase and installation of water softeners/ treatment systems to serve all of the mechanical and plumbing equipment. This project would also provide for a chemical treatment program including an updated chemicals control system, service and employee training provided by a qualified water treatment vendor. The annual maintenance fee charged by the water treatment vendor would be determined after an investigation of the water system is complete. These annual costs are not included in this project cost. For budgeting purposes, a $12,000 fee is suggested. | #13 RESIDENTIAL UNIT | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 4610 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
1993INT1 | INTERIOR FINISHES | 1993 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | #15 WEST NEIGHBORHOOD FAMILY SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 6580 | 2012-10-17 | Four to Ten Years | Long-Term Needs | 3 | 32900
1994EXT3 | EXTERIOR DOOR REPLACEMENT | 1994 | Some of the exterior metal doors are damaged from age and general wear and tear and have reached the end of their expected life. They are warped and do not open and close smoothly and have problems with the locking mechanisms. This project would provide for the replacement of five door assemblies with new metal doors, frames and hardware. Removal and disposal of the existing doors is included in this estimate. | #17 DESERT WILLOW TREATMENT CENTER | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1998 | 58400 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
1992ADA5 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 1992 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | #14 RESIDENTIAL UNIT | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 4610 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 2000
1992SFT3 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 1992 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #14 RESIDENTIAL UNIT | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 4610 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 4000
1992ADA6 | ADA KITCHEN REMODEL | 1992 | The two kitchens in the building are original to the building. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and countertops are delaminating and failing. This project recommends the replacement of the existing kitchen countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards For Accessible Design should be incorporated into the design such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. | #14 RESIDENTIAL UNIT | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 4610 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 30000
1992ADA4 | ADA RESTROOM REMODEL | 1992 | The building does not have an accessible restroom. The existing restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit of two restrooms is necessary. This project would provide funding for construction of two unisex accessible restrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #14 RESIDENTIAL UNIT | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 4610 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 40000
1992ADA3 | ADA SIGNAGE | 1992 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #14 RESIDENTIAL UNIT | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 4610 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 3000
1992ADA2 | ADA DOOR HARDWARE REPLACEMENT | 1992 | The 2010 ADA Standards for Accessible Design states that handles, pulls, latches, locks and other operable parts on doors and gates shall be operable with one hand and shall not require tight grasping, pinching, or twisting of the wrist. The force to activate operable parts shall be 5 pounds maximum. It is recommended that proper lever hardware be installed on all of the interior and exterior doors in this building to meet these requirements. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and sections 309.4 and 404.2.7 of the 2010 ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #14 RESIDENTIAL UNIT | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 4610 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 9600
1992EXT7 | ROOF REPLACEMENT | 1992 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1992. It is recommended that the single-ply membrane on this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. The clay tile roofing is not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #14 RESIDENTIAL UNIT | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 4610 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 42000
1992PLM2 | WATER TREATMENT SYSTEM INSTALLATION | 1992 | The existing plumbing and HVAC systems are not equipped with a water treatment system. Failure to treat the water causes wear and tear on the domestic water supply lines, plumbing fixtures and HVAC equipment. This project would provide for the purchase and installation of water softeners/ treatment systems to serve all of the mechanical and plumbing equipment. This project would also provide for a chemical treatment program including an updated chemicals control system, service and employee training provided by a qualified water treatment vendor. The annual maintenance fee charged by the water treatment vendor would be determined after an investigation of the water system is complete. These annual costs are not included in this project cost. For budgeting purposes, a $12,000 fee is suggested. | #14 RESIDENTIAL UNIT | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 4610 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
1992EXT2 | EXTERIOR FINISHES | 1992 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA reports dated 06/22/1998 and 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #14 RESIDENTIAL UNIT | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 4610 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 23050
1993ENR2 | HVAC EQUIPMENT REPLACEMENT | 1993 | Four of the HVAC roof top units were recently replaced, the remaining four are more than 20 years old and should be scheduled for replacement. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of four new HVAC packaged units and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #15 WEST NEIGHBORHOOD FAMILY SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 6580 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 48000
1993SFT3 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 1993 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #15 WEST NEIGHBORHOOD FAMILY SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 6580 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 4000
9991ADA2 | SIDEWALK REPAIRS | 9991 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The concrete sidewalks around the site do not meet ADA requirements and are in need of repairs. Settling, spalling and cracking have created elevation changes or gaps that are non-ADA compliant. This project would provide for removing the damaged sections of concrete and replacing them with new concrete. 500 SF of 4" thick P.C. concrete sidewalk was used for this estimate. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | SNCAS SITE | 9991 | HHS | DCFS | SNCAS | Las Vegas |  |  | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 7500
9991ENV1 | PEST CONTROL | 9991 | There are numerous stray rabbits that have taken up residence throughout the site. The rabbits cause many problems including digging holes that people trip in, damaging the landscaping including eating the plants, leaving droppings all over the campus and possibly spreading diseases. Due to these issues, this project provides for removal of the rabbits and clean up of the droppings by a licensed pest control business. | SNCAS SITE | 9991 | HHS | DCFS | SNCAS | Las Vegas |  |  | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
9991SEC1 | DOOR HARDWARE REPLACEMENT | 9991 | The door handles and locking mechanisms on the interior and exterior doors across the site are due for replacement. Staff has had continuous problems with the hardware and there is no common system between the buildings which requires an enormous number of keys to access all of the buildings. This project would provide for the replacement of the hardware on all of the doors. Removal and disposal of the existing hardware is included in this estimate. The estimate was provided by the maintenance staff who have procured a quote for this work. | SNCAS SITE | 9991 | HHS | DCFS | SNCAS | Las Vegas |  |  | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 300000
9991SIT1 | CRACK FILL & SEAL ASPHALT PAVING | 9991 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the parking lot east of Building #15. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 40,000 square feet of asphalt area was used to generate this estimate. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | SNCAS SITE | 9991 | HHS | DCFS | SNCAS | Las Vegas |  |  | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24000
0355ENR2 | WINDOW REPLACEMENT | 0355 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 14 units. Removal and disposal of the existing windows is included in this estimate. | #9 FISCAL/PAYROLL SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1974 | 4000 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14000
0355SFT2 | EXTERIOR LANDING REPLACEMENT | 0355 | The landing outside the main door into 4B is lower than allowed by the 2012 International Building Code and the Americans with Disabilities Act (ADA). This report recommends modifying the concrete flatwork outside this door to provide a landing no more than ½" lower than the threshold. This project would provide for the removal and replacement of a section of the flatwork to provide a code compliant landing and transition to the remaining flatwork. This project or a portion thereof was previously recommended in the FCA reports dated 06/19/1998 and 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #9 FISCAL/PAYROLL SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1974 | 4000 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 2500
0355SFT3 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0355 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #9 FISCAL/PAYROLL SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1974 | 4000 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 4000
0355SIT1 | ROOF DRAIN DOWNSPOUT MODIFICATIONS | 0355 | The roof drain downspouts currently terminate within inches of the building with no continuous drainage away from the foundation. This is causing the water to pool next to the foundation and damage the foundation and walls. This project would provide for the extension of the roof drains from the downspouts to approximately 5'-0" away from the perimeter of the building to prevent pooling and damage to the building. | #9 FISCAL/PAYROLL SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1974 | 4000 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0355SFT4 | SAFETY GLAZING INSTALLATION | 0355 | There are four windows around the building which have an exposed bottom edge less than 18 inches above the floor. This condition requires safety glazing according to 2012 IBC Section 2406.4.3. This project would provide for the removal and replacement of the windows with safety glazing. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #9 FISCAL/PAYROLL SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1974 | 4000 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 5000
0356SFT5 | WINDOW REPLACEMENT | 0356 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. There are four windows around the building which have an exposed bottom edge less than 18 inches above the floor. This condition requires safety glazing according to 2003 IBC Section 2406.3. This project recommends replacing the windows with dual pane, higher efficiency units including safety glazing where required. This estimate is for the replacement of 15 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #10 WRAPAROUND | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1974 | 4000 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 15000
0355SFT5 | EXIT SIGN INSTALLATION | 0355 | The building does not have any exit signs which does not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems. IBC - 2012 Chapter 10 was referenced for this project. | #9 FISCAL/PAYROLL SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1974 | 4000 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 1800
0358ADA3 | ADA RESTROOM UPGRADE | 0358 | The building does not have an accessible restroom. The existing restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit of two restrooms is necessary. This project would provide funding for construction of two unisex accessible restrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #12 RESIDENTIAL PROGRAMS SOCIAL SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 9265 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 40000
0354EXT4 | EXTERIOR FINISHES | 0354 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the brick masonry and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | #7 WEST NBHD FAMILY SERVICES CENTER | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1974 | 12500 | 2012-10-17 | Four to Ten Years | Long-Term Needs | 3 | 62500
0354EXT5 | ROOF REPLACEMENT | 0354 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1981. It is recommended that the single-ply membrane on this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. The asphalt composition shingle roofing is not included in this estimate. | #7 WEST NBHD FAMILY SERVICES CENTER | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1974 | 12500 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 60000
0359ADA4 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0359 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | #8 ADMINISTRATION/OFFICE FACILITY | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 5200 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 2000
0355EXT1 | EXTERIOR FINISHES | 0355 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the brick masonry and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA reports dated 06/19/1998 and 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #9 FISCAL/PAYROLL SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1974 | 4000 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0355INT4 | INTERIOR FINISHES | 0355 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA reports dated 06/19/1998 and 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #9 FISCAL/PAYROLL SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1974 | 4000 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0354HVA4 | CHILLER AND COOLING TOWER REPLACEMENT | 0354 | The building is cooled by a chiller and cooling tower system. The equipment is original to the building and is reaching the end of its useful life. It is recommended to schedule replacement of the chiller and cooling tower in the next 2-3 years. This project provides for disposal of the existing units and replacement with a new water cooled centrifugal chiller and cooling tower including connections to utilities. The new system shall be designed to significantly reduce electrical usage in order to comply with the 2009 IECC and ASHRAE 90.1 and to reduce utility costs. This project includes removal and disposal of the existing equipment and all required connections to utilities. | #7 WEST NBHD FAMILY SERVICES CENTER | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1974 | 12500 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 150000
0363EXT3 | EXTERIOR DOOR REPLACEMENT | 0363 | The exterior metal doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the two door assemblies with new metal doors, frames and hardware. Removal and disposal of the existing doors is included in this estimate. | #16 EARLY CHILDHOOD SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1995 | 3024 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0356SFT3 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0356 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #10 WRAPAROUND | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1974 | 4000 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 4000
0359SFT3 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0359 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #8 ADMINISTRATION/OFFICE FACILITY | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 5200 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 4000
0358EXT4 | ROOF REPLACEMENT | 0358 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1981. It is recommended that the single-ply membrane on this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. The asphalt composition shingle roofing is not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #12 RESIDENTIAL PROGRAMS SOCIAL SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 9265 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 14400
0359INT2 | INTERIOR FINISHES | 0359 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA reports dated 06/19/1998 and 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #8 ADMINISTRATION/OFFICE FACILITY | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 5200 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 26000
0359ENR2 | WINDOW REPLACEMENT | 0359 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 39 units. Removal and disposal of the existing windows is included in this estimate. | #8 ADMINISTRATION/OFFICE FACILITY | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 5200 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 29250
0354PLM3 | PLUMBING REPLACEMENT | 0354 | The plumbing and waste system is older and in poor condition. All of the pipes are original to the building and should be scheduled for replacement. The piping that supports the HVAC system has mineral build-up and corrosion throughout as do the domestic water lines. The sewer pipes also have considerable build up inside the pipes and get clogged often causing back ups and flooding in the building. This project recommends replacing all of the water, HVAC and sewer lines in the building. This estimate includes removal and disposal of the existing system as required. | #7 WEST NBHD FAMILY SERVICES CENTER | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1974 | 12500 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 250000
0354ENR2 | WINDOW REPLACEMENT | 0354 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 52 units. Removal and disposal of the existing windows is included in this estimate. | #7 WEST NBHD FAMILY SERVICES CENTER | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1974 | 12500 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 52000
0354SFT4 | INTERIOR HANDRAIL REPLACEMENT | 0354 | The interior stair handrails are older and do not meet code for safety or accessibility. The gripping surfaces are incorrect and they are not continuous from the top to bottom landings. This project recommends the installation of handrails on both sides of the stairs, with proper returns and supports. Removal and disposal of the existing railing is included. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | #7 WEST NBHD FAMILY SERVICES CENTER | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1974 | 12500 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 4000
0354ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0354 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | #7 WEST NBHD FAMILY SERVICES CENTER | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1974 | 12500 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 2000
0354INT5 | INTERIOR FINISHES | 0354 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA reports dated 06/19/1998 and 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #7 WEST NBHD FAMILY SERVICES CENTER | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1974 | 12500 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 62500
0354SFT3 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0354 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #7 WEST NBHD FAMILY SERVICES CENTER | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1974 | 12500 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 4000
0358ADA4 | ADA DOOR HARDWARE REPLACEMENT | 0358 | The 2010 ADA Standards for Accessible Design states that handles, pulls, latches, locks and other operable parts on doors and gates shall be operable with one hand and shall not require tight grasping, pinching, or twisting of the wrist. The force to activate operable parts shall be 5 pounds maximum. It is recommended that proper lever hardware be installed on all of the interior and exterior doors in this building to meet these requirements. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and sections 309.4 and 404.2.7 of the 2010 ADA Standards For Accessible Design were used as a reference for this project. | #12 RESIDENTIAL PROGRAMS SOCIAL SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 9265 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 54750
0363ENR2 | WINDOW REPLACEMENT | 0363 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 12 units. Removal and disposal of the existing windows is included in this estimate. | #16 EARLY CHILDHOOD SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1995 | 3024 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
0359SFT2 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0359 | The building is a B occupancy per the 2006 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 or R-2 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. This project or a portion thereof was previously recommended in the FCA reports dated 06/19/1998 and 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #8 ADMINISTRATION/OFFICE FACILITY | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 5200 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 72800
0363INT3 | INTERIOR DOOR REPLACEMENT | 0363 | The interior doors in this building are hollow core units and most are damaged. This project would provide for the installation of new solid core interior doors including lever action door handles, hardware and paint. Frames are not included in this estimate. Removal and disposal of the existing doors is included in this cost estimate. A total of 6 interior doors was used in this estimate. | #16 EARLY CHILDHOOD SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1995 | 3024 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0363INT4 | CEILING SYSTEM REPLACEMENT | 0363 | The majority of the building has a suspended acoustical tile ceiling system. The t-bar framing is old, bent and rusted in some areas and many ceiling tiles are damaged and stained. This project would provide for the replacement of the suspended acoustical tile ceiling system including the framing, acoustical tile and seismic bracing assemblies. Removal and disposal of the existing ceiling system is included in this estimate. | #16 EARLY CHILDHOOD SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1995 | 3024 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
0363INT2 | CARPET REPLACEMENT | 0363 | The carpet in the building is showing signs of extreme wear and should be scheduled for replacement. It is recommended that the carpet be replaced with heavy duty commercial grade carpet in the next 2-3 years. | #16 EARLY CHILDHOOD SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1995 | 3024 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14000
0363EXT1 | EXTERIOR FINISHES | 0363 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #16 EARLY CHILDHOOD SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1995 | 3024 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15120
0363SFT3 | ELECTRICAL EQUIPMENT REPLACEMENT | 0363 | The existing XFMR (transformer) and electrical panel located on the exterior of this building is not NEMA 3R rated and the workspace in front of the panel is about plus or minus 24 inches; 30 inches is required by code. This project would provide for the removal and replacement of these two items with a NEMA 3R rated transformer and electrical panel and provide for 30 inches of workspace in front of the electrical panel. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #16 EARLY CHILDHOOD SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1995 | 3024 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 10000
0363SFT1 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0363 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #16 EARLY CHILDHOOD SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1995 | 3024 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 4000
0363SFT2 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0363 | The building is a B occupancy per the 2012 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 or R-2 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #16 EARLY CHILDHOOD SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1995 | 3024 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 42336
0363INT1 | INTERIOR FINISHES | 0363 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #16 EARLY CHILDHOOD SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1995 | 3024 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15120
0359INT3 | JANITORS CLOSET REPAIRS | 0359 | The mop sink in the Janitors Closet is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | #8 ADMINISTRATION/OFFICE FACILITY | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 5200 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
0359EXT2 | ROOF REPLACEMENT | 0359 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1981. It is recommended that the single-ply membrane on this building be re-roofed in the next 1-2 years to be consistent with the roofing program and the end of the warranty period. The asphalt composition shingle roofing is not included in this estimate. | #8 ADMINISTRATION/OFFICE FACILITY | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 5200 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 36000
0359ADA3 | ADA RESTROOM REMODEL | 0359 | The Men's and Women's designated ADA restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit of both restrooms is necessary. This project would provide funding for remodeling the Men's and Women's restrooms into ADA compliant restrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | #8 ADMINISTRATION/OFFICE FACILITY | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 5200 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 30000
0363ENR1 | HVAC EQUIPMENT REPLACEMENT | 0363 | The four HVAC packaged units were installed in 1995. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of four new HVAC packaged units and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | #16 EARLY CHILDHOOD SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1995 | 3024 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
0357ELE2 | GFCI DUPLEX OUTLET REPLACEMENT | 0357 | There are several outlets in the restrooms and kitchens throughout the building which are not GFCI protected. These outlets should be changed to GFCI type outlets per the 2011 NEC. There are also several GFCI outlets throughout the building which are damaged and not working properly. This project would provide for the purchase and installation of GFCI duplex outlets. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #11 RESIDENTIAL UNIT | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 9265 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 1500
0356INT4 | INTERIOR FINISHES | 0356 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA reports dated 06/19/1998 and 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #10 WRAPAROUND | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1974 | 4000 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0356INT5 | FIRE RATED CEILING REPAIRS | 0356 | The fire rated ceiling in the telecommunications closet is damaged and should be scheduled for immediate repairs. Penetrations have been made in the one hour fire rated assemblies when new equipment or utility lines are installed which compromises the fire protection design of the building. This project would provide for the removal of the remaining gypsum board ceiling and installation of new 5/8" type X fire rated gypsum board including taping and fire proofing all ceiling penetrations to provide a one hour fire rated ceiling assembly. Taping, texture and paint are included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #10 WRAPAROUND | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1974 | 4000 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 2500
0356EXT1 | EXTERIOR FINISHES | 0356 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the brick masonry and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA reports dated 06/19/1998 and 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #10 WRAPAROUND | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1974 | 4000 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0356ADA3 | ADA KITCHEN REMODELS | 0356 | The two kitchens in the building are in fair to poor condition. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and countertops are delaminating and failing. This project recommends the replacement of the existing kitchen countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards For Accessible Design should be incorporated into the design such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. | #10 WRAPAROUND | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1974 | 4000 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 40000
0356SFT6 | EXIT SIGN UPGRADE | 0356 | The existing exit signs in this building are older types and should be replaced with new self-illuminated or LED style signs with battery-backed internal systems. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #10 WRAPAROUND | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1974 | 4000 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 1800
0356PLM3 | WATER HEATER REPLACEMENT | 0356 | There is a 40 gallon gas-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | #10 WRAPAROUND | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1974 | 4000 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0357SFT2 | EGRESS WINDOWS | 0357 | After this building was built, residential sleeping room emergency egress requirements came into the International Building Code. Part of these requirements included a maximum sill height of 44" above the finished floor. The window sill height currently is 47" above finished floor. This project recommends replacing the existing windows with 48" x 48" dual pane horizontal sliders, installed to meet minimum safety standard for emergency egress. Project based on 2012 IBC Chapter 10 Section 1029.3, This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #11 RESIDENTIAL UNIT | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 9265 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 16000
0357EXT4 | ROOF REPLACEMENT | 0357 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1981. It is recommended that the single-ply membrane on this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. The asphalt composition shingle roofing is not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #11 RESIDENTIAL UNIT | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 9265 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14400
0357EXT2 | EXTERIOR FINISHES | 0357 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA reports dated 06/22/1998 and 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #11 RESIDENTIAL UNIT | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 9265 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 46325
0357INT4 | INTERIOR DOOR REPLACEMENT | 0357 | The interior doors in this building are hollow core units and most are damaged. This project would provide for the installation of new solid core interior doors including lever action door handles, hardware and paint. Frames are not included in this estimate. Removal and disposal of the existing doors is included in this cost estimate. A total of 40 interior doors was used in this estimate. This project or a portion thereof was previously recommended in the FCA reports dated 6/19/1998 and 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #11 RESIDENTIAL UNIT | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 9265 | 2012-10-17 | Four to Ten Years | Long-Term Needs | 3 | 20000
0357INT3 | INTERIOR FINISHES | 0357 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA reports dated 6/19/1998 and 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #11 RESIDENTIAL UNIT | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 9265 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 46325
0357SFT5 | FIRE RATED CEILING REPAIRS | 0357 | The fire rated ceilings in the two mechanical equipment closets are damaged and should be scheduled for immediate repairs. Penetrations have been made in the one hour fire rated assemblies when new equipment or utility lines are installed which compromises the fire protection design of the building. This project would provide for the removal of the remaining gypsum board ceiling and installation of new 5/8" type X fire rated gypsum board including taping and fire proofing all ceiling penetrations to provide a one hour fire rated ceiling assembly. Taping, texture and paint are included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #11 RESIDENTIAL UNIT | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 9265 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 5000
0359EXT1 | EXTERIOR FINISHES | 0359 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA reports dated 06/19/1998 and 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #8 ADMINISTRATION/OFFICE FACILITY | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 5200 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 26000
0357SFT3 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0357 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #11 RESIDENTIAL UNIT | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 9265 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 4000
0358SFT3 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0358 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #12 RESIDENTIAL PROGRAMS SOCIAL SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 9265 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 4000
0358SFT4 | FIRE RATED CEILING REPAIRS | 0358 | The fire rated ceilings in the two mechanical equipment closets are damaged and should be scheduled for immediate repairs. Penetrations have been made in the one hour fire rated assemblies when new equipment or utility lines are installed which compromises the fire protection design of the building. This project would provide for the removal of the remaining gypsum board ceiling and installation of new 5/8" type X fire rated gypsum board including taping and fire proofing all ceiling penetrations to provide a one hour fire rated ceiling assembly. Taping, texture and paint are included in this estimate. | #12 RESIDENTIAL PROGRAMS SOCIAL SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 9265 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 5000
0358INT3 | INTERIOR FINISHES | 0358 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA reports dated 06/22/1998 and 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #12 RESIDENTIAL PROGRAMS SOCIAL SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 9265 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 46325
0358EXT3 | EXTERIOR FINISHES | 0358 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA reports dated 06/22/1998 and 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #12 RESIDENTIAL PROGRAMS SOCIAL SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 9265 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 46325
0357ENR1 | WINDOW REPLACEMENT | 0357 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 27 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #11 RESIDENTIAL UNIT | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 9265 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 27000
0358ENR1 | WINDOW REPLACEMENT | 0358 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 40 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #12 RESIDENTIAL PROGRAMS SOCIAL SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 9265 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
0358ADA5 | ADA KITCHEN REMODEL | 0358 | The two kitchens in the building are original to the building. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and countertops are delaminating and failing. This project recommends the replacement of the existing kitchen countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards For Accessible Design should be incorporated into the design such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. | #12 RESIDENTIAL PROGRAMS SOCIAL SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 9265 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 30000
0358SIT1 | ROOF DRAIN DOWNSPOUT MODIFICATIONS | 0358 | The roof drain downspouts currently terminate within inches of the building with no continuous drainage away from the foundation. This is causing the water to pool next to the foundation and damage the foundation and walls. This project would provide for the extension of the roof drains from the downspouts to approximately 5'-0" away from the perimeter of the building to prevent pooling and damage to the building. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #12 RESIDENTIAL PROGRAMS SOCIAL SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 9265 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0358PLM3 | WATER HEATER REPLACEMENT | 0358 | There are two 40 gallon gas-fired water heaters in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, these units are showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that two new gas-fired water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #12 RESIDENTIAL PROGRAMS SOCIAL SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 9265 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0357ADA2 | ADA RESTROOM UPGRADE | 0357 | The building does not have an accessible restroom. The existing restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit of four of the first floor restrooms is necessary. This project would provide funding for construction of four unisex accessible restrooms on the first floor. These items may include new sinks, toilets, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | #11 RESIDENTIAL UNIT | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 9265 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 20000
0357ADA3 | ADA KITCHEN REMODELS | 0357 | The five kitchens in the building are in fair to poor condition. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and countertops are delaminating and failing. This project recommends the replacement of the existing kitchen countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards For Accessible Design should be incorporated into the design such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. | #11 RESIDENTIAL UNIT | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 9265 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 50000
0357SFT6 | EXIT SIGN UPGRADE | 0357 | The existing exit signs in this building are older types and should be replaced with new self-illuminated or LED style signs with battery-backed internal systems. There are also missing signs at some of the exit doors. IBC - 2012 Chapter 10 was referenced for this project. | #11 RESIDENTIAL UNIT | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 9265 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 5400
1954ENV1 | RELOCATE IRRIGATION SYSTEM | 1954 | The existing irrigation system along the south side of the building appears to be spraying water on the side of the building. This has led to extreme damage to the exterior stucco and there are water stains on the interior gypsum board. This could lead to mold growth if not addressed soon. This project would provide for the relocation of the sprinklers away from the building as well as repairing damaged lines which were exposed in the southwest corner. This project should be completed prior to replacing the damaged stucco addressed in another project. This project or a portion thereof was previously recommended in the FCA report dated 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2013. | #6 STORAGE/SHOP | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1981 | 5300 | 2012-10-18 | Immediate to Two Years | Currently Critical | 1 | 1000
1950EXT3 | EXTERIOR DOORS | 1950 | The existing exterior hollow metal door systems are damaged from age and abuse. This project would provide for 9 new exterior door assemblies to be installed including hardware and painting. Removal and disposal of the existing doors are included in this estimate. | #3 INPATIENT HOSPITAL | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1988 | 37800 | 2012-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 29700
1949SFT1 | INSTALL FIRE SPRINKLER SYSTEM | 1949 | Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 occupancy, must have sprinklers installed when the building is remodeled or has an addition. The building in this report is currently classified as a B occupancy. This project would provide for a fire sprinkler system to be installed including backflow prevention and monitoring. This project or a portion thereof was previously recommended in the FCA report dated 6/25/1998 and 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. | #1 ADMINISTRATION/OUTPATIENT SERVICES | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1969 | 30000 | 2012-10-18 | Immediate to Two Years | Currently Critical | 1 | 210000
1950SFT3 | REPLACE EXERCISE YARD CONCRETE | 1950 | A secured exercise area surrounds the exterior of the building. Patients are allowed in this area. Much of the concrete flatwork is irregularly surfaced or broken and presents a hazard. This project would provide for the removal and replacement of the concrete slab in the exercise area. This project or a portion thereof was previously recommended in the FCA report dated 6/23/1998 and 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. | #3 INPATIENT HOSPITAL | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1988 | 37800 | 2012-10-18 | Immediate to Two Years | Currently Critical | 1 | 25000
1950PLM5 | REPLACE BOILERS / UPGRADE HVAC SYSTEM | 1950 | The two 1987 Hydrotherm boilers are original to the building, and are about 20 years old. The boilers are reaching the end of their serviceable life span, and should be scheduled for replacement. Two 500 MBH steam boilers were used for this cost estimate. This project should be implemented at the same time as the water treatment system project to ensure proper operation and care of the boilers. This project also includes monies for upgrades and work to existing equipment including but not limited to new VAV terminal units, exhaust fans on roof, diffusers, 2 scroll compressors, temperature controls and commissioning. This project or a portion thereof was previously recommended in the FCA report dated 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. | #3 INPATIENT HOSPITAL | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1988 | 37800 | 2012-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 225000
1950INT7 | REPAIR ELEVATOR | 1950 | This building has a passenger elevator and a cargo elevator. The cargo elevator is out of service. This project would provide funding to repair the elevator to facilitate maintenance and control of the building. This project or a portion thereof was previously recommended in the FCA report dated 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. | #3 INPATIENT HOSPITAL | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1988 | 37800 | 2012-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
1954EXT1 | EXTERIOR FINISHES | 1954 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. This project or a portion thereof was previously recommended in the FCA report dated 6/18/1998 and 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2013. | #6 STORAGE/SHOP | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1981 | 5300 | 2012-10-18 | Immediate to Two Years | Currently Critical | 1 | 26500
1950PLM3 | PLUMBING FIXTURES / IMPROVEMENTS | 1950 | At the nurses stations in rooms 146, 232, and 265, the sinks and faucets should be replaced. Room 211 has a sink which should be removed and the pipes capped off. In medical exam room 127, the faucet should be replaced. The drain piping from the dishwasher in kitchen 214 requires an air gap fitting. Also, this project would provide for the installation of new toilets, sinks, faucets and casework, shower pans, tubs, toilet partitions and drinking fountains for lower and upper level. This project or a portion thereof was previously recommended in the FCA report dated 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. | #3 INPATIENT HOSPITAL | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1988 | 37800 | 2012-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 180000
1954ENR2 | HVAC REPLACEMENT | 1954 | There are two evaporative coolers and one packaged unit on the roof which have reached the end of their expected life. This project would provide for two new evaporative coolers and one packaged unit to be installed on the roof. Roof curb modifications and connections to existing utilities are included in this estimate. | #6 STORAGE/SHOP | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1981 | 5300 | 2012-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
1951ADA2 | REPAIR SIDEWALK | 1951 | Tree roots have damaged the sidewalk around the south side of the building causing uplift and cracking. The damage is enough to cause the accessible path of travel to no longer meet ADA requirements. This project makes allowance for cutting the roots back to prevent further damage and repairing the sidewalks to meet ADA requirements and eliminate a tripping hazard. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 6/16/1998 and 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. | #3A CRISIS OBSERVATION UNIT | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1972 | 10700 | 2012-10-18 | Immediate to Two Years | Currently Critical | 1 | 1200
1951EXT3 | EXTERIOR DOOR REPLACEMENT | 1951 | There are 5 single leaf exterior metal doors and 3 exterior storefront systems in need of replacement. They are damaged from age and abuse. This project would provide for the installation of new door systems including frames and hardware. Removal and disposal of the old units is included in this estimate. | #3A CRISIS OBSERVATION UNIT | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1972 | 10700 | 2012-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 32000
1951INT5 | REPAIR WOMEN'S SHOWER | 1951 | The Women's restroom has an active leak in the shower area and has caused damage to the gypsum board of the adjacent room. If the leak and gypsum board is not repaired, the moisture may cause mold and dry-rot. This project would provide for the repair to the shower. This may include removal of the ceramic tile shower pan and 2 courses of wall tile, waterproofing the shower pan and reinstall tile, grout and seal. Removal and replacement of the gypsum board in the adjacent room will be required if it has been damaged. This project or a portion thereof was previously recommended in the FCA report dated 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. | #3A CRISIS OBSERVATION UNIT | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1972 | 10700 | 2012-10-18 | Immediate to Two Years | Currently Critical | 1 | 2000
1951INT2 | INTERIOR FINISHES | 1951 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 6/16/1998 and 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. | #3A CRISIS OBSERVATION UNIT | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1972 | 10700 | 2012-10-18 | Four to Ten Years | Long-Term Needs | 3 | 53500
1951INT7 | INTERIOR DOOR ASSEMBLY REPLACEMENT | 1951 | The existing interior door assemblies are damaged from abuse and age. This project would provide for the removal of the existing door assemblies and the purchase and installation of new metal door assemblies. All hardware and painting is included in this estimate. Hardware is to include security keys and fusible links (for one-hour door assemblies) or where applicable. A total of 25 doors was used for this estimate. This project or a portion thereof was previously recommended in the FCA report dated 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. | #3A CRISIS OBSERVATION UNIT | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1972 | 10700 | 2012-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 100000
1950INT8 | NURSES STATION UPGRADE | 1950 | There are 4 nurses stations that are in need of upgrades. The casework is worn from age and use and they should be scheduled for replacement. This project would provide for the removal of the existing casework and installation of new casework at the nurse's station. Removal and re-installation of existing glazing is included in the estimate. | #3 INPATIENT HOSPITAL | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1988 | 37800 | 2012-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 32000
1951ENR1 | REPLACE WINDOWS | 1951 | The windows in the building are original, not energy efficient and in need of replacement. This project would provide for the installation of new dual pane insulated window units. Safety glazing of window units is recommended due to the use of this facility. Removal and disposal of the old units is included in this estimate. | #3A CRISIS OBSERVATION UNIT | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1972 | 10700 | 2012-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 38400
1951SFT2 | INSTALL SEISMIC GAS SHUT-OFF VALVE | 1951 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel brace. This project or a portion thereof was previously recommended in the FCA report dated 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. | #3A CRISIS OBSERVATION UNIT | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1972 | 10700 | 2012-10-18 | Immediate to Two Years | Currently Critical | 1 | 3000
1950INT9 | REPLACE IINTERIOR DOORS | 1950 | The existing interior doors are worn from age and abuse. Many of the locking mechanisms do not operate properly and should be replaced. This project would provide for the installation of new hollow metal doors, frames, and hardware. Painting is included in this estimate Removal and disposal of the old doors and frames is included in this estimate. | #3 INPATIENT HOSPITAL | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1988 | 37800 | 2012-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 253000
1950ADA5 | ADA BUILDING SIGNAGE | 1950 | The building is lacking ADA compliant signage to identify spaces, restrooms and offices. This project would provide for the installation of ADA compliant signage throughout the building. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | #3 INPATIENT HOSPITAL | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1988 | 37800 | 2012-10-18 | Immediate to Two Years | Currently Critical | 1 | 8000
1950HVA3 | REPAIR WATER TREATMENT SYSTEM | 1950 | The chemical water treatment system was not operating at the time of the survey. This project would provide for a chemical treatment program including an updated chemicals control system, service and employee training provided by a qualified water treatment vendor. The annual maintenance fee charged by the water treatment vendor would be determined after an investigation of the water system is complete. This project should coincide with the HVAC replacement project. These annual costs are not included in this project cost. For budgeting purposes, a $12,000 fee is suggested. This project or a portion thereof was previously recommended in the FCA report dated 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. | #3 INPATIENT HOSPITAL | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1988 | 37800 | 2012-10-18 | Immediate to Two Years | Currently Critical | 1 | 12000
1949INT5 | INTERIOR DOOR ASSEMBLY REPLACEMENT | 1949 | The existing interior door assemblies are damaged from abuse and age. This project would provide for the removal of the existing door assemblies and the purchase and installation of new metal door assemblies. All hardware and painting is included in this estimate. Hardware is to include security keys and fusible links (for one-hour door assemblies) or where applicable. A total of 89 doors was used for this estimate. Removal and disposal of the existing door assemblies is also included in the estimate. This project or a portion thereof was previously recommended in the FCA report dated 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. | #1 ADMINISTRATION/OUTPATIENT SERVICES | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1969 | 30000 | 2012-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 195800
1949EXT3 | CONCRETE FLATWORK | 1949 | The concrete slab outside Rooms 111 and 139 has been broken and lifted up by tree roots. These areas should be repaired. At the exterior door to Room 122, there is a step down to the landing. This presents a hazard and is not in compliance with the International Building Code. This project recommends replacing the slab so the threshold is not more than ½" higher than the exterior concrete landing and changing the door swing so it does not swing out over the step. This project or a portion there of was previously recommended in the FCA report dated 06/23/1998 and 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012 | #1 ADMINISTRATION/OUTPATIENT SERVICES | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1969 | 30000 | 2012-10-18 | Four to Ten Years | Long-Term Needs | 3 | 1500
1949INT6 | VINYL COMPOSITION TILE (VCT) REPLACEMENT | 1949 | The existing vinyl composition tile (VCT) is in poor condition and should be scheduled for replacement. This project would provide for the installation of new VCT in the facility. Removal and disposal of the old tile is included in this estimate. A $2,500 allowance for an asbestos survey is included in this estimate. | #1 ADMINISTRATION/OUTPATIENT SERVICES | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1969 | 30000 | 2012-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 132100
1949ADA2 | INSTALL HIGH LOW DRINKING FOUNTAIN | 1949 | This building contains a water fountain. The 2012 IBC Section 1109.5 states where a water fountain is provided, at least half should be accessible. This project would provide funding for the purchase and installation of a new accessible fixed high/ low ADA drinking fountain. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | #1 ADMINISTRATION/OUTPATIENT SERVICES | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1969 | 30000 | 2012-10-18 | Immediate to Two Years | Currently Critical | 1 | 4000
1949INT4 | INTERIOR FINISHES | 1949 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next five to six years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 6/25/1998 and 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. | #1 ADMINISTRATION/OUTPATIENT SERVICES | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1969 | 30000 | 2012-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 150000
1949INT3 | STORAGE ROOM RAMP | 1949 | The door into Room 128, a storage room, swings out over a set of stairs. This step down is a violation of the International Building Code. This project recommends building a wooden landing inside the door and a ramp down to the lower floor, to make the space more usable. Steel prefabricated handrails should be provided. This project or a portion thereof was previously recommended in the FCA report dated 6/25/1998 and 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012 | #1 ADMINISTRATION/OUTPATIENT SERVICES | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1969 | 30000 | 2012-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
1949EXT4 | EXTERIOR FINISHES | 1949 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented within the next 2 years and is recommended on a cyclical basis based on environmental conditions. The wood outriggers are in need of sanding, sealing and painting as soon as possible to prevent further damage. This project or a portion thereof was previously recommended in the FCA report dated 6/16/1998 and 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. | #1 ADMINISTRATION/OUTPATIENT SERVICES | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1969 | 30000 | 2012-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 210000
1949EXT5 | WINDOW / DOOR GLAZING REPLACEMENT | 1949 | There are ten windows that face onto the patio. They are single pane glazed units and should be replaced with dual-pane glass. This project would provide for the removal and replacement of these windows. Safety glazing will be used in areas required by the 2012 IBC. Also, the remaining 70 windows are single pane and original to the facility. This project also would provide for the installation of new windows throughout the building. Removal and disposal of the existing windows is included in this estimate. 6 glass double doors are also included in the estimate. This project or a portion thereof was previously recommended in the FCA report dated 6/25/1998 and 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. | #1 ADMINISTRATION/OUTPATIENT SERVICES | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1969 | 30000 | 2012-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 330420
1949SFT3 | INSTALL SEISMIC GAS SHUT-OFF VALVE | 1949 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel brace. This project or a portion thereof was previously recommended in the FCA report dated 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. | #1 ADMINISTRATION/OUTPATIENT SERVICES | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1969 | 30000 | 2012-10-18 | Immediate to Two Years | Currently Critical | 1 | 3500
1951EXT6 | INSTALL EXTERIOR HANDRAILS | 1951 | The 2012 IBC Chapter 1009.15 requires handrails be installed on stairs with two or more risers. The exterior stairs do not meet these requirements. This project would provide for two 1-1/2 inch diameter steel handrails, one on each side of the stairway to meet the 2003 IBC code requirements. Painting of the railing is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. | #3A CRISIS OBSERVATION UNIT | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1972 | 10700 | 2012-10-18 | Immediate to Two Years | Currently Critical | 1 | 2500
1954STR1 | STRUCTURAL ASSESSMENT OF STORAGE FLOOR | 1954 | An upper level storage mezzanine has been constructed inside of the Storage Building. The 2012 IBC Table 1607.1 has a minimum load requirement of 125p.s.f. for light storage in non-residential spaces. There is no record of a CIP project or structural plans for this construction and it could be a potential safety issue due to collapse. This project recommends that a licensed engineer perform a structural investigation to assess the load carrying capacity of this area. Future projects would be based on this report. This project or a portion thereof was previously recommended in the FCA report dated 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2013. | #6 STORAGE/SHOP | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1981 | 5300 | 2012-10-18 | Immediate to Two Years | Currently Critical | 1 | 1500
1954EXT3 | REROOF BUILDING | 1954 | The statewide roofing program has set the useful life of an average roof at 15-20 years. The roof warranty expires at the end of the same time frame. This roof was installed in 1995. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next two years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2013. | #6 STORAGE/SHOP | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1981 | 5300 | 2012-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 53000
1950PLM6 | REPAIR SEWER LINES | 1950 | The existing sanitary sewer system in the building is failing in numerous areas. This project would provide for saw cutting, excavation and installation of new sanitary waste lines in the building. This project includes removal of the existing piping and fittings as required. | #3 INPATIENT HOSPITAL | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1988 | 37800 | 2012-10-18 | Immediate to Two Years | Currently Critical | 1 | 300000
1954SFT4 | OSHA SAFETY CABINETS | 1954 | Flammable or combustible liquids in drums or other containers (including flammable aerosols) not exceeding 60 gallons individual capacity and those portable tanks not exceeding 660 gallons individual capacity, shall have a proper storage container, OSHA Chapter 1910.106 (7) (d). This project would provide two OSHA approved storage cabinets for gasoline, aerosol cans and other flammable items. This project or a portion thereof was previously recommended in the FCA report dated 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2013. | #6 STORAGE/SHOP | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1981 | 5300 | 2012-10-18 | Immediate to Two Years | Currently Critical | 1 | 6000
1954ENR1 | WINDOW REPLACEMENT | 1954 | There are two old aluminum windows which should be scheduled for replacement. This project would provide for two new dual pane window units to be installed.. Removal and disposal of the old windows is included in this estimate. | #6 STORAGE/SHOP | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1981 | 5300 | 2012-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
1954EXT2 | REPLACE DAMAGED WOOD / STUCCO | 1954 | The existing wood and stucco finish along the loading dock and the south side is damaged and is in need of replacement. This project would provide for the removal of the existing stucco and wood exterior finish and installation of a new exterior stucco finish on the south side. Disposal of the old stucco and wood is included in this estimate. This project should be implemented concurrent with or after the irrigation system project has been completed. This project or a portion thereof was previously recommended in the FCA report dated 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2013. | #6 STORAGE/SHOP | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1981 | 5300 | 2012-10-18 | Immediate to Two Years | Currently Critical | 1 | 4320
1954SFT6 | MEZZANINE STORAGE STAIRS GUARDRAILS | 1954 | The existing stairs and guardrails that access the mezzanine storage area do not meet current building code requirements. This project would provide for the removal of the existing stairs and rails and installation of new wood framed stairs and guardrails. | #6 STORAGE/SHOP | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1981 | 5300 | 2012-10-18 | Immediate to Two Years | Currently Critical | 1 | 1200
1954INT1 | INTERIOR FINISHES | 1954 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next four to six years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2013. | #6 STORAGE/SHOP | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1981 | 5300 | 2012-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 26500
1954SFT3 | INSTALL SEISMIC GAS SHUT-OFF VALVE | 1954 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel brace. This project or a portion thereof was previously recommended in the FCA report dated 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2013. | #6 STORAGE/SHOP | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1981 | 5300 | 2012-10-18 | Immediate to Two Years | Currently Critical | 1 | 3000
1954SFT5 | INSTALL FIRE ALARM SYSTEM | 1954 | This building is lacking an automatic fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements. This project or a portion thereof was previously recommended in the FCA report dated 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2013. | #6 STORAGE/SHOP | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1981 | 5300 | 2012-10-18 | Immediate to Two Years | Currently Critical | 1 | 21200
1950ADA4 | LOBBY CASEWORK ADA UPGRADE | 1950 | The existing entry / lobby reception area is not ADA compliant. This project would provide for new ADA compliant casework to be installed in the lobby area. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | #3 INPATIENT HOSPITAL | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1988 | 37800 | 2012-10-18 | Immediate to Two Years | Currently Critical | 1 | 4500
1950SFT2 | INSTALL SEISMIC GAS SHUT-OFF VALVE | 1950 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel brace. This project or a portion thereof was previously recommended in the FCA report dated 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. | #3 INPATIENT HOSPITAL | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1988 | 37800 | 2012-10-18 | Immediate to Two Years | Currently Critical | 1 | 3500
1950EXT2 | EXTERIOR FINISHES | 1950 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented within the next 2-3 years and is recommended on a cyclical basis based on environmental conditions. Painting and / or sealing of the exterior metal security cages is included as part of this project. This project or a portion thereof was previously recommended in the FCA report dated 6/16/1998 and 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012 | #3 INPATIENT HOSPITAL | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1988 | 37800 | 2012-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 189000
1950SFT1 | FIRE ALARM UPGRADE | 1950 | This building is equipped with an automatic fire detection and alarm system, but the system has reached the end of it's serviceable life. It is recommended that the fire detection and alarm system be upgraded. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements. | #3 INPATIENT HOSPITAL | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1988 | 37800 | 2012-10-18 | Immediate to Two Years | Currently Critical | 1 | 30000
1950INT6 | FLOORING REPLACEMENT | 1950 | Approximately one-third of the floor covering in this building is carpet, in poor condition. It is recommended that the carpet be replaced with heavy duty institutional grade carpet in the next one to two years. The remainder is a vinyl composition tile (VCT) except for the restrooms which is ceramic tile. This is also in poor condition. This project would provide for the removal and replacement of the carpet ceramic tile and VCT in this building. This project or a portion there of was previously recommended in the FCA report dated 06/23/1998 and 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012 | #3 INPATIENT HOSPITAL | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1988 | 37800 | 2012-10-18 | Immediate to Two Years | Currently Critical | 1 | 340200
1952SFT0 | INSTALL SEISMIC GAS SHUT-OFF VALVE | 1952 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel brace. This project or a portion there of was previously recommended in the FCA report dated 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. | #4 FOOD SERVICE CENTER | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1972 | 3400 | 2012-10-18 | Immediate to Two Years | Currently Critical | 1 | 3000
1951EXT1 | EXTERIOR FINISHES | 1951 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented within the next 2 years and is recommended on a cyclical basis based on environmental conditions. Painting and / or sealing of the exposed outriggers is included as part of this project. This project or a portion thereof was previously recommended in the FCA report dated 6/16/1998 and 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. | #3A CRISIS OBSERVATION UNIT | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1972 | 10700 | 2012-10-18 | Immediate to Two Years | Currently Critical | 1 | 53500
1951INT1 | CARPET AND TILE REPLACEMENT | 1951 | The interior floor covering is vinyl tile, in poor condition. The carpet is stained, and repeated cleanings have failed to eliminate the stains. The flooring in the building should be replaced. This project would provide for the removal and replacement of the carpet and vinyl tile throughout the building. This project does not include the ceramic floor tile in the restrooms. This project or a portion thereof was previously recommended in the FCA report dated 6/16/1998 and 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. | #3A CRISIS OBSERVATION UNIT | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1972 | 10700 | 2012-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 74900
1952EXT3 | EXTERIOR FINISHES | 1952 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented within the next 2 to 3 years and is recommended on a cyclical basis based on environmental conditions. This project or a portion there of was previously recommended in the FCA report dated 6/16/1998 and 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. | #4 FOOD SERVICE CENTER | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1972 | 3400 | 2012-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 17000
1952ADA2 | ADA UPGRADES | 1952 | There is an ADA restroom located in the facility which is in need of some minor improvements. Also, the existing drinking fountain is non-ADA compliant. This project would provide for a new high-low ADA compliant drinking fountain and minor modifications to the restroom which may include flush handle modifications and some fixture location improvements. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 6/16/1998 and 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. | #4 FOOD SERVICE CENTER | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1972 | 3400 | 2012-10-18 | Immediate to Two Years | Currently Critical | 1 | 6000
1950INT5 | INTERIOR FINISHES | 1950 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 6/16/1998 and 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. | #3 INPATIENT HOSPITAL | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1988 | 37800 | 2012-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 189000
1952INT2 | INTERIOR FINISHES | 1952 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA report dated 6/16/1998 and 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. | #4 FOOD SERVICE CENTER | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1972 | 3400 | 2012-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 17000
1950INT4 | RESTROOM WALL TILE REPLACEMENT | 1950 | Throughout the facility, the ceramic tile wall covering in the restrooms are cracked and failing. This project recommends replacement of the ceramic tile wall coverings. This project should be coordinated with the accessibility upgrade, which includes ADA restroom remodeling if they have not been completed. Demolition of the existing tile is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 6/23/1998 and 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. | #3 INPATIENT HOSPITAL | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1988 | 37800 | 2012-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35000
1953EXT3 | EXTERIOR FINISHES | 1953 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented within the next 2 years and is recommended on a cyclical basis based on environmental conditions. Painting and / or sealing of the exposed outriggers is included as part of this project. | #5 FOOD SERVICE CENTER STORAGE | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1972 | 1458 | 2012-10-18 | Immediate to Two Years | Currently Critical | 1 | 7290
1953SFT2 | INSTALL SEISMIC GAS SHUT-OFF VALVE | 1953 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel brace. This project or a portion thereof was previously recommended in the FCA report dated 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012 | #5 FOOD SERVICE CENTER STORAGE | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1972 | 1458 | 2012-10-18 | Immediate to Two Years | Currently Critical | 1 | 3000
1953INT1 | INTERIOR FINISHES | 1953 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012 | #5 FOOD SERVICE CENTER STORAGE | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1972 | 1458 | 2012-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7290
1953SFT1 | REPLACE LOADING DOCK STAIRS | 1953 | The 2003 IBC Chapter 1009.5.1 requires the horizontal slope of stair treads in any direction not to exceed 2 percent. Chapter 1009.11 requires handrails be installed on stairs with two or more risers and a landing is required at the top and bottom of the stairs. The stairs next to the loading dock do not meet these requirements. This project would provide for the rebuilding of the concrete stairway to meet the 2012 IBC code requirements. Two handrails, one on each side of the stairway are included in this cost estimate. This project or a portion there of was previously recommended in the FCA report dated 6/18/1998 and 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2013. | #5 FOOD SERVICE CENTER STORAGE | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1972 | 1458 | 2012-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
1954PLM3 | REPLACE WATER HEATER | 1954 | The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear. It is recommended that a new gas-fired water heater be installed for more efficient use of energy. This estimate includes: 100 feet of gas pipe, fittings, couplers, and labor for installation. Removal and disposal of the old electric water heater is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2013. | #6 STORAGE/SHOP | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1981 | 5300 | 2012-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
1954INT2 | REPLACE VCT IN OFFICE | 1954 | The existing vinyl composition tile (VCT) is damaged from age and use. This project would provide for the installation of new VCT in the office area. Removal of the existing tile is included in this estimate. This cost does NOT include any monies for asbestos containing material testing or removal if it is present. 400 square feet was used for this estimate. | #6 STORAGE/SHOP | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1981 | 5300 | 2012-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2800
9992SIT2 | CRACK FILL AND SEAL ASPHALT PAVING | 9992 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the parking lot and access roads on the site. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 70,000 square feet of asphalt area was used to generate this estimate. | SNAMHS SITE | 9992 | HHS | DPBH | SNAMHS | Las Vegas |  |  | 2012-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 42000
9992SIT3 | CONCRETE SIDEWALK REPAIRS | 9992 | There are some areas of damaged concrete walkways that are in need of replacement due to large cracks and heaving / settling. This project would provide for the removal and replacement of the damaged concrete walkways as needed. 1,000 square feet was used to generate this estimate. | SNAMHS SITE | 9992 | HHS | DPBH | SNAMHS | Las Vegas |  |  | 2012-10-18 | Immediate to Two Years | Currently Critical | 1 | 10000
9992ADA1 | ADA SIGNAGE | 9992 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established signage criteria for permanent spaces in buildings and accessible route of travel from parking to building(s). The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. This project would provide for directional signage along the accessible route of travel from the ADA accessible parking to each building and public space. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards For Accessible Design were used for reference on this project. This project or a portion there of was previously recommended in the FCA report dated 02/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. | SNAMHS SITE | 9992 | HHS | DPBH | SNAMHS | Las Vegas |  |  | 2012-10-18 | Immediate to Two Years | Currently Critical | 1 | 5000
0243INT1 | VINYL COMPOSITION TILE (VCT) REPLACEMENT | 0243 | The majority of the interior floor covering is vinyl composition tile (VCT) in poor condition. The VCT flooring in the building should be replaced. This project would provide for the removal and replacement of the VCT throughout the building. A $2,500 asbestos survey allowance is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 6/16/1998 and 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. | #2 PHARMACY/LABORATORY BUILDING | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1972 | 7600 | 2012-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 58500
0243SFT3 | INSTALL SEISMIC GAS SHUT-OFF VALVE | 0243 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel brace. This project or a portion thereof was previously recommended in the FCA report dated 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. | #2 PHARMACY/LABORATORY BUILDING | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1972 | 7600 | 2012-10-18 | Immediate to Two Years | Currently Critical | 1 | 3500
0243EXT5 | EXTERIOR DOOR REPLACEMENT | 0243 | The existing exterior doors and frames are damaged from age and use. This project would provide for the installation of 4 new door assemblies including frames hardware and paint, Removal and disposal of the existing doors is included in this estimate. | #2 PHARMACY/LABORATORY BUILDING | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1972 | 7600 | 2012-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
0243EXT6 | REPLACE WINDOWS AND FRAMES | 0243 | The existing wood framed window systems are damaged from age and exposure. This project would provide for the removal of the existing wood window systems and replacement with new aluminum storefront window systems. The remainder of the windows are old single pane and should be scheduled for replacement. This project would also provide for the installation of new dual pane window systems. Removal and disposal of the old window systems are included in this estimate. A total of 32 units was used for this estimate. This project or a portion thereof was previously recommended in the FCA report dated 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. | #2 PHARMACY/LABORATORY BUILDING | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1972 | 7600 | 2012-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 38400
0243INT4 | INTERIOR DOOR ASSEMBLY REPLACEMENT | 0243 | The existing interior door assemblies are damaged from abuse and age. This project would provide for the removal of the existing door assemblies and the purchase and installation of new metal door assemblies. All hardware and painting is included in this estimate. Hardware is to include security keys and fusible links (for one-hour door assemblies) or where applicable. A total of 32 doors was used for this estimate. This project or a portion thereof was previously recommended in the FCA report dated 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. | #2 PHARMACY/LABORATORY BUILDING | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1972 | 7600 | 2012-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 80000
0243ADA1 | ADA MODIFICATIONS | 0243 | The restroom has been retrofitted for ADA accessibility but is not 100% ADA compliant. Also, the facility is lacking ADA direction signage. This project would provide for an ADA sign package and minor modifications to the existing ADA designated restroom. A new high low drinking fountain and casework modifications to the public reception area are also included in this estimate. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards For Accessible Design were used for reference on this project This project or a portion there of was previously recommended in the FCA report dated 06/23/1998 and 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. | #2 PHARMACY/LABORATORY BUILDING | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1972 | 7600 | 2012-10-18 | Immediate to Two Years | Currently Critical | 1 | 20000
0243INT2 | INTERIOR FINISHES | 0243 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next four to six years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 6/23/1998 and 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. | #2 PHARMACY/LABORATORY BUILDING | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1972 | 7600 | 2012-10-18 | Four to Ten Years | Long-Term Needs | 3 | 38000
0243EXT3 | EXTERIOR FINISHES | 0243 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented within the next 2 years and is recommended on a cyclical basis based on environmental conditions. Painting and / or sealing of the exposed outriggers is included as part of this project. This project or a portion thereof was previously recommended in the FCA report dated 6/16/1998 and 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. | #2 PHARMACY/LABORATORY BUILDING | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1972 | 7600 | 2012-10-18 | Immediate to Two Years | Currently Critical | 1 | 53200
0243SIT2 | TREE REMOVAL | 0243 | There is a deciduous tree growing next to the building. The tree in time will cause damage to the foundation and structure. It should be removed before damage occurs. This project would provide funding to remove the tree. Debris removal is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. | #2 PHARMACY/LABORATORY BUILDING | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1972 | 7600 | 2012-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0243ADA2 | REPAIR SIDEWALKS | 0243 | Tree roots have damaged the sidewalks around the building causing uplift and cracking. In several areas, the damage is enough to cause the path of travel to no longer meet ADA accessibility requirements and is a tripping hazard. This project makes allowance for cutting the roots back to prevent further damage and repairing the sidewalks to meet the ADA requirements. This project or a portion thereof was previously recommended in the FCA report dated 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. | #2 PHARMACY/LABORATORY BUILDING | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1972 | 7600 | 2012-10-18 | Immediate to Two Years | Currently Critical | 1 | 2500
0360EXT1 | EXTERIOR FINISHES | 0360 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented within the next 2-3 years and is recommended on a cyclical basis based on environmental conditions. This project or a portion there of was previously recommended in the FCA report dated 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. Reassigned to other projects. | #6A STORAGE BUILDING | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 2005 | 800 | 2012-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0360INT1 | INTERIOR FINISHES | 0360 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next four to six years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA report dated 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. Reassigned to other projects. | #6A STORAGE BUILDING | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 2005 | 800 | 2012-10-18 | Four to Ten Years | Long-Term Needs | 3 | 4000
1671INT4 | INTERIOR FINISHES | 1671 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1309 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1992 | 2650 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 13250
1671ADA4 | KITCHEN REMODEL | 1671 | The kitchen in the building is in fair to poor condition. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and countertops are delaminating and failing. This project recommends the replacement of the existing kitchen countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards For Accessible Design should be incorporated into the design such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1309 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1992 | 2650 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 15000
1672ADA3 | ADA SIGNAGE | 1672 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1308 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1992 | 2650 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 1000
1672ADA4 | KITCHEN REMODEL | 1672 | The kitchen in the building is in fair to poor condition. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and countertops are delaminating and failing. This project recommends the replacement of the existing kitchen countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards For Accessible Design should be incorporated into the design such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1308 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1992 | 2650 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 15000
1672INT4 | INTERIOR FINISHES | 1672 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1308 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1992 | 2650 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 13250
1672SFT2 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 1672 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1308 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1992 | 2650 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 4000
1672ENR1 | HVAC REPLACEMENT | 1672 | The HVAC roof top units and furnaces are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of new HVAC packaged units and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | #1308 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1992 | 2650 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 39750
1672INT5 | VCT FLOORING REPLACEMENT | 1672 | The VCT (vinyl composite tile) flooring in the gymnasium is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. | #1308 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1992 | 2650 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 23850
1672EXT1 | EXTERIOR FINISHES | 1672 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA reports dated 06/17/1998 and 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1308 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1992 | 2650 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 13250
1671SFT2 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 1671 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1309 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1992 | 2650 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 4000
1671ADA3 | ADA SIGNAGE | 1671 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1309 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1992 | 2650 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 1000
1671INT5 | VCT FLOORING REPLACEMENT | 1671 | The VCT (vinyl composite tile) flooring in the gymnasium is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. | #1309 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1992 | 2650 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 23850
1671ENR1 | HVAC REPLACEMENT | 1671 | The HVAC roof top units and furnaces are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of new HVAC packaged units and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | #1309 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1992 | 2650 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 39750
1671ADA2 | ADA RESTROOM REMODEL | 1671 | The building does not have an accessible restroom. The existing restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit of 2 restrooms is necessary. This project would provide funding for construction of 1 unisex accessible restroom in the corridor and 1 unisex accessible restroom for the bedrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1309 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1992 | 2650 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 30000
1959PLM2 | WATER HEATER REPLACEMENT | 1959 | There is a 50 gallon gas-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 5-6 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | #1307 MULTI-PURPOSE | 9993 | HHS | ADSD | DRC | Las Vegas | 1992 | 1450 | 2013-06-04 | Four to Ten Years | Long-Term Needs | 3 | 1500
1671EXT1 | EXTERIOR FINISHES | 1671 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA reports dated 06/17/1998 and 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1309 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1992 | 2650 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 13250
1672ADA2 | ADA RESTROOM REMODEL | 1672 | The building does not have an accessible restroom. The existing restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit of 2 restrooms is necessary. This project would provide funding for construction of 1 unisex accessible restroom in the corridor and 1 unisex accessible restroom for the bedrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1308 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1992 | 2650 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 15000
1959SFT3 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 1959 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1307 MULTI-PURPOSE | 9993 | HHS | ADSD | DRC | Las Vegas | 1992 | 1450 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 4000
1959INT7 | FLOORING REPLACEMENT | 1959 | The VCT (vinyl composite tile) and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the next 2-3 years. | #1307 MULTI-PURPOSE | 9993 | HHS | ADSD | DRC | Las Vegas | 1992 | 1450 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11600
1959INT5 | INTERIOR FINISHES | 1959 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1307 MULTI-PURPOSE | 9993 | HHS | ADSD | DRC | Las Vegas | 1992 | 1450 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7250
1959EXT1 | EXTERIOR FINISHES | 1959 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA reports dated 06/17/1998 and 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1307 MULTI-PURPOSE | 9993 | HHS | ADSD | DRC | Las Vegas | 1992 | 1450 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 7250
1959ENR1 | HVAC REPLACEMENT | 1959 | The HVAC cooling units and furnaces are not energy efficient and have reached the end of their expected and useful life. They are original to the building and are now over 20 years old. This project would provide for installation of new HVAC packaged units and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | #1307 MULTI-PURPOSE | 9993 | HHS | ADSD | DRC | Las Vegas | 1992 | 1450 | 2013-06-04 | Four to Ten Years | Long-Term Needs | 3 | 21750
1959ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 1959 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | #1307 MULTI-PURPOSE | 9993 | HHS | ADSD | DRC | Las Vegas | 1992 | 1450 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 4000
1959INT6 | NONABSORBANT FINISHES | 1959 | 2012 IBC Section 1210 requires the installation of smooth, hard, nonabsorbent surfaces in the following restroom areas: on floors in toilet, bathing and shower rooms that extend upward onto the walls at least 4 inches, within 2 feet of the sides of urinals and water closets to a height of not less than 4 feet above the floor and in shower compartments to a height not less than 70 inches above the drain inlet. Accessories such as grab bars, towel bars, paper dispensers and soap dishes, provided on or within walls, shall be installed and sealed to protect structural elements from moisture. This project recommends the installation of Fiberglass Reinforced Panel (FRP) or an equal material in both restrooms to comply with this code section. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1307 MULTI-PURPOSE | 9993 | HHS | ADSD | DRC | Las Vegas | 1992 | 1450 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
9993EXT3 | EXTERIOR FINISHES, STORAGE SHEDS | 9993 | There are 18 storage sheds located throughout the site ranging from 100 to 216 square feet each for a total of 2,560 square feet. It is important to maintain the finish, weather resistance and appearance of the structures. This project recommends work to protect the buildings, including painting, staining, or other applied finishes, and caulking around flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. This project should be done on a cyclical basis to maintain the integrity of the structures. This project or a portion thereof was previously recommended in the FCA report dated 02/06/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | DESERT REGIONAL CENTER SITE | 9993 | HHS | ADSD | DRC | Las Vegas |  |  | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12800
9993EXT2 | EXTERIOR FINISHES, SHADE RAMADAS | 9993 | There are 10 steel ramadas in different locations throughout the site which measure 18'x22' each for a total of 3,960 square feet. It is important to maintain the finish, weather resistance and appearance of the structures. This project would provide for painting of the structures and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structures. This project or a portion thereof was previously recommended in the FCA report dated 02/06/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | DESERT REGIONAL CENTER SITE | 9993 | HHS | ADSD | DRC | Las Vegas |  |  | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7920
9993ELE1 | INTERCOM SYSTEM REPLACEMENT | 9993 | The buildings on the site are equipped throughout with an intercom system, but the system is older and no longer functioning. This project would provide for a new wireless intercom system including an amplifier, speakers and antennas as required for a complete operating system. The main station would be located in Building #1391 Administration building. 11 residential buildings are recommended for this installation. This project or a portion thereof was previously recommended in the FCA report dated 02/06/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | DESERT REGIONAL CENTER SITE | 9993 | HHS | ADSD | DRC | Las Vegas |  |  | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 65000
9993SIT6 | LANDSCAPE RENOVATIONS | 9993 | The existing landscaping on the site consists of a large amount of lawn interspersed with trees and shrubbery. The maintenance staff noted that the lawn is a maintenance problem due to the cost of water and labor to maintain it in the desert climate of Las Vegas. This project would provide for removal of most of the lawn and replacement with a xeriscape landscape while preserving the more mature trees and shrubbery. This project or a portion thereof was previously recommended in the FCA report dated 02/06/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | DESERT REGIONAL CENTER SITE | 9993 | HHS | ADSD | DRC | Las Vegas |  |  | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 400000
9993SEC2 | SECURITY SYSTEM | 9993 | The facility currently does not have a security system installed. Access on or off of the property is uncontrolled and there have been security problems including the homeless inhabiting areas of the property. This project recommends card-access control, security fencing, security cameras and additional site lighting be installed to remedy this problem. This project or a portion thereof was previously recommended in the FCA report dated 02/06/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | DESERT REGIONAL CENTER SITE | 9993 | HHS | ADSD | DRC | Las Vegas |  |  | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1250000
9993ENV1 | PEST CONTROL | 9993 | There are numerous stray rabbits that have taken up residence throughout the site. The rabbits cause many problems including digging holes that people trip in, damaging the landscaping including eating the plants, leaving droppings all over the campus and possibly spreading diseases. Due to these issues, this project provides for removal of the rabbits and clean up of the droppings by a licensed pest control business. | DESERT REGIONAL CENTER SITE | 9993 | HHS | ADSD | DRC | Las Vegas |  |  | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
9993SIT8 | SEWER SYSTEM REPLACEMENT | 9993 | The sanitary wastewater system is showing signs of deterioration. Because of the deterioration, the system is not working to its full potential. Most of the lines are original to the site and are in fair to poor condition. The passage of time and constant heavy use are contributing factors to problems that arise. Deposits within the pipes will cause them to be restricted, which will slow the flow of water. This project would provide for the complete replacement of the sanitary sewer system on site from the city connection to each occupied building on site. This project would provide for the removal and installation a new sewer / waste water infrastructure in the building including all connections, supports, anchoring. 5,000 lineal feet of cast iron pipe was used to generate this estimate. | DESERT REGIONAL CENTER SITE | 9993 | HHS | ADSD | DRC | Las Vegas |  |  | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500000
9993SIT9 | DRAINAGE REPAIRS | 9993 | There are numerous places where drainage ponding occurs on Transverse Drive. The entire roadway should be removed and replaced, and a sidewalk with curb and gutter should be installed along the north side of Transverse Drive, after grading occurs to achieve proper drainage. This project provides for removal and replacement of the asphalt paving and concrete sidewalks. 40,000 square feet of roadway and sidewalks was used to generate the estimate. | DESERT REGIONAL CENTER SITE | 9993 | HHS | ADSD | DRC | Las Vegas |  |  | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 400000
9993ENR1 | ENERGY MANAGEMENT SYSTEM INSTALLATION | 9993 | This project recommends the installation of an Energy Management System (EMS) for the entire site. This system will monitor and control the heating, ventilation, air conditioning and lighting equipment on the site and in each building through a central computer system. Electronic sensors will be installed on each piece of equipment which will feed information into the computer system. The maintenance staff can then control and monitor the equipment remotely which will significantly lower energy costs. Along with electricity, gas and water meters, this system will provide detailed reports on energy consumption allowing the maintenance staff to analyze and customize the energy used by the facility. A new system has been installed on the Administration building. This estimate is based on installing the system on the rest of the buildings and connecting it to the existing system except for the residential cottages. The system is recommended to coincide with the HVAC project recommendations. This project or a portion thereof was previously recommended in the FCA report dated 02/06/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | DESERT REGIONAL CENTER SITE | 9993 | HHS | ADSD | DRC | Las Vegas |  |  | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500000
9993SIT7 | SLURRY SEAL ASPHALT PAVING | 9993 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site wide including access roads and parking areas. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 130,000 square feet of asphalt area was used to generate this estimate. | DESERT REGIONAL CENTER SITE | 9993 | HHS | ADSD | DRC | Las Vegas |  |  | 2013-06-04 | Four to Ten Years | Long-Term Needs | 3 | 97500
0256INT8 | ADA RESTROOM UPGRADE | 0256 | The Men's and Women's designated ADA restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit of 2 Men's and 2 Women's restrooms is necessary. This project would provide funding for construction of 2 Men's and 2 Women's accessible restrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1391 DRC ADMINISTRATION | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 10656 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 100000
0256ENR1 | WINDOW REPLACEMENT | 0256 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 20 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA reports dated 06/15/1998 and 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1391 DRC ADMINISTRATION | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 10656 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0256ELE2 | ELECTRICAL UPGRADE | 0256 | This building was constructed before the high demand for electrical services were needed for computers and other electrical devices. As time has progressed, the buildings electrical demand and system has changed. It is utilized to its current maximum potential. The electrical panels and receptacles are at their limit. It is recommended the entire system be upgraded to meet the evolving needs of the building. This project or a portion thereof was previously recommended in the FCA report dated 02/06/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1391 DRC ADMINISTRATION | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 10656 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 213120
0256INT5 | JANITORS CLOSET REPAIRS | 0256 | The mop sink in the Janitors Closet is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. This project or a portion thereof was previously recommended in the FCA reports dated 06/15/1998 and 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1391 DRC ADMINISTRATION | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 10656 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
0256ADA5 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0256 | This building contains three water fountains that are not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of four drinking fountains to meet the ADA requirements. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1391 DRC ADMINISTRATION | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 10656 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 8000
0256ADA4 | ADA SIGNAGE | 0256 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1391 DRC ADMINISTRATION | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 10656 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 1500
0256ELE3 | EMERGENCY GENERATOR REPLACEMENT | 0256 | The building does not have an emergency back-up generator. The generator that used to back-up the building has reached the end of its useful life and has been removed. This project would provide for a new diesel powered 300 KVA generator including required connections to utility systems. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1391 DRC ADMINISTRATION | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 10656 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 100000
0256INT9 | INTERIOR FINISHES | 0256 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | #1391 DRC ADMINISTRATION | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 10656 | 2013-06-04 | Four to Ten Years | Long-Term Needs | 3 | 53280
0256INT10 | CARPET REPLACEMENT | 0256 | The carpet in the building is showing signs of extreme wear and should be scheduled for replacement. It is recommended that the carpet be replaced with heavy duty commercial grade carpet in the next 2-3 years. | #1391 DRC ADMINISTRATION | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 10656 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 66500
0256ADA3 | BREAK ROOM REMODEL | 0256 | The kitchenette and associated cabinets in the employee break room are original to the building. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and countertops are delaminating and failing. This project recommends the replacement of the existing kitchen countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards For Accessible Design should be incorporated into the design such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. This project or a portion thereof was previously recommended in the FCA report dated 02/06/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1391 DRC ADMINISTRATION | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 10656 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 15000
0256SFT2 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0256 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 02/06/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1391 DRC ADMINISTRATION | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 10656 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 4000
0256EXT3 | EXTERIOR FINISHES | 0256 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion there of was previously recommended in the FCA reports dated 06/15/1998 and 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1391 DRC ADMINISTRATION | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 10656 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 53280
0627EXT3 | EXTERIOR FINISHES | 0627 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | GAZEBO WEST (STORAGE) | 9993 | HHS | ADSD | DRC | Las Vegas | 1971 | 360 | 2013-06-04 | Four to Ten Years | Long-Term Needs | 3 | 1800
0628EXT3 | EXTERIOR FINISHES | 0628 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | GAZEBO EAST (STORAGE) | 9993 | HHS | ADSD | DRC | Las Vegas | 1971 | 360 | 2013-06-04 | Four to Ten Years | Long-Term Needs | 3 | 1800
0706EXT2 | EXTERIOR DOOR REPLACEMENT | 0706 | The exterior metal doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the doors with new metal doors, frames and hardware. Removal and disposal of the existing doors is included in this estimate. This project or a portion thereof was previously recommended in the FCA reports dated 06/17/1998 and 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1310 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1992 | 2650 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10500
0626EXT3 | EXTERIOR FINISHES | 0626 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | GAZEBO SOUTH (STORAGE) | 9993 | HHS | ADSD | DRC | Las Vegas | 1971 | 360 | 2013-06-04 | Four to Ten Years | Long-Term Needs | 3 | 1800
0369INT8 | INTERIOR FINISHES | 0369 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 5-6 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | #1303 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 5104 | 2013-06-04 | Four to Ten Years | Long-Term Needs | 3 | 25520
0369EXT5 | CONCRETE LANDING REPLACEMENT | 0369 | The client bedrooms have exterior doors which open directly onto concrete landings in eight locations. The landings do not comply with 2012 IBC Section 1008.1.5 which requires the landing to be at the same elevation on each side of the door and to not exceed a two percent slope. This project addresses installing landings designed to current codes and connecting to the existing site flatwork. This report recommends removing shrubbery on the latch edge of the main entry door, and placing concrete level with the front landing to provide an accessible entry. This project or a portion there of was previously recommended in the FCA reports dated 06/17/1998 and 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1303 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 5104 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 40000
0369EXT1 | EXTERIOR DOOR REPLACEMENT | 0369 | The 12 exterior wood man doors appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement of the wood doors with new metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. This estimate does not include the direct exit doors from the bedrooms. This project or a portion there of was previously recommended in the FCA reports dated 06/17/1998 and 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1303 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 5104 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 48000
0369INT7 | INTERIOR DOOR REPLACEMENT | 0369 | There are several existing interior bi-pass closet doors that are damaged from abuse and age. This project would provide for the removal of the existing bi-pass doors and the purchase and installation of new solid core wood hinged doors and hollow metal frames. All hardware, painting and framing materials are included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1303 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 5104 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0369ADA5 | KITCHEN REMODEL | 0369 | The kitchen in the building is in fair to poor condition. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and countertops are delaminating and failing. This project recommends the replacement of the existing kitchen countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards For Accessible Design should be incorporated into the design such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1303 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 5104 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
0369ADA4 | ADA SIGNAGE | 0369 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1303 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 5104 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 1200
0369ADA3 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0369 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1303 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 5104 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 4000
0369ADA2 | ADA RESTROOM REMODEL | 0369 | The building does not have an accessible restroom. The existing restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit of 3 restrooms is necessary. This project would provide funding for construction of 2 unisex accessible restrooms in the corridor and 1 unisex accessible restroom between bedrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1303 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 5104 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 30000
0706ADA3 | ADA SIGNAGE | 0706 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1310 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1992 | 2650 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 1000
0369INT9 | FLOORING REPLACEMENT | 0369 | The VCT (vinyl composite tile) and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base in the next 4-5 years. | #1303 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 5104 | 2013-06-04 | Four to Ten Years | Long-Term Needs | 3 | 40832
0368INT8 | FLOORING REPLACEMENT | 0368 | The VCT (vinyl composite tile) flooring in the building is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. | #1302 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 5104 | 2013-06-04 | Four to Ten Years | Long-Term Needs | 3 | 45936
0369SFT3 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0369 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1303 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 5104 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 4000
0369EXT4 | EXTERIOR FINISHES | 0369 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 02/06/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1303 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 5104 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25520
0369INT5 | NONABSORBENT FINISHES | 0369 | 2012 IBC Section 1210 requires the installation of smooth, hard, nonabsorbent surfaces in the following restroom areas: on floors in toilet, bathing and shower rooms that extend upward onto the walls at least 4 inches, within 2 feet of the sides of urinals and water closets to a height of not less than 4 feet above the floor and in shower compartments to a height not less than 70 inches above the drain inlet. Accessories such as grab bars, towel bars, paper dispensers and soap dishes, provided on or within walls, shall be installed and sealed to protect structural elements from moisture. This project recommends the installation of Fiberglass Reinforced Panel (FRP) or an equal material to comply with this code section. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1303 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 5104 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
0370EXT2 | EXTERIOR DOOR REPLACEMENT | 0370 | The 5 exterior wood man doors appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement of the wood doors with new metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. This estimate does not include the direct exit doors from the bedrooms. This project or a portion there of was previously recommended in the FCA reports dated 06/17/1998 and 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1301 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 2924 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0370ADA5 | KITCHEN REMODEL | 0370 | The kitchen in the building is in fair to poor condition. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and countertops are delaminating and failing. This project recommends the replacement of the existing kitchen countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards For Accessible Design should be incorporated into the design such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1301 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 2924 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0370SFT3 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0370 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1301 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 2924 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 4000
0370ADA4 | ADA RESTROOM REMODEL | 0370 | The building does not have an accessible restroom. The existing restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit of 2 restrooms is necessary. This project would provide funding for construction of 1 unisex accessible restrooms in the corridor and 1 unisex accessible restroom between bedrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1301 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 2924 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 75000
0370INT4 | INTERIOR FINISHES | 0370 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA reports dated 06/17/1998 and 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1301 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 2924 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14620
0369ENR1 | HVAC REPLACEMENT | 0369 | The HVAC roof top units and furnaces are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of new HVAC packaged units and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | #1303 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 5104 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 76560
0367SFT3 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0367 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 02/06/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1304 OFFICE | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 4685 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 4000
0367HVA1 | REPLACE HVAC SYSTEM | 0367 | The heating and cooling to this building is provided by forced air furnaces with cooling coils that are original equipment. Based on the age of the equipment, this report recommends scheduling replacement of these units within the next two to four years. This project or a portion there of was previously recommended in the FCA report dated 06/17/1998. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2008. Project complete. | #1304 OFFICE | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 4685 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18000
0367PLM3 | PLUMBING REPAIRS | 0367 | In the kitchen and laundry areas, there are three faucets that have been damaged and should be replaced. The dishwasher in one kitchen was installed without an air gap fitting; this report recommends one be installed. There is one exterior hose bibb that is not freeze proof; its' replacement is recommended. This project or a portion there of was previously recommended in the FCA reports dated 06/15/1998 and 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1304 OFFICE | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 4685 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0367EXT3 | WINDOW REPLACEMENT | 0367 | The existing windows in this building are of single pane wire mesh construction in metal frames. Some are broken and all are not energy efficient. This project would provide for the removal and replacement of the windows with new dual pane security rated window systems. | #1304 OFFICE | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 4685 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
0367INT5 | FLOORING REPLACEMENT | 0367 | The VCT (vinyl composite tile) and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the next 2-3 years. | #1304 OFFICE | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 4685 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 37480
0367ADA2 | ADA RESTROOM UPGRADE | 0367 | There are several restrooms in the building. The existing restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for remodeling the large Men's and Women's restrooms into ADA compliant restrooms. These items may include a new sink, toilet, shower, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1304 OFFICE | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 4685 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 30000
0367ADA3 | BREAK ROOM REMODELS | 0367 | The kitchenettes and associated cabinets in the two employee break rooms are original to the building. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and countertops are delaminating and failing. This project recommends the replacement of the existing kitchen countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards For Accessible Design should be incorporated into the design such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1304 OFFICE | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 4685 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 30000
0367ADA4 | ADA SIGNAGE | 0367 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1304 OFFICE | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 4685 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 900
0367EXT2 | EXTERIOR FINISHES | 0367 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion there of was previously recommended in the FCA reports dated 06/15/1998 and 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1304 OFFICE | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 4685 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 23425
0368ADA5 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0368 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1302 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 5104 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 4000
0367ADA5 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0367 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1304 OFFICE | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 4685 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 4000
0368ENR1 | HVAC REPLACEMENT | 0368 | The HVAC roof top units and furnaces are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of new HVAC packaged units and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | #1302 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 5104 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 76560
0367INT4 | INTERIOR DOOR REPLACEMENT | 0367 | There are several existing interior bi-pass closet doors that are damaged from abuse and age. This project would provide for the removal of the existing bi-pass doors and the purchase and installation of new solid core wood hinged doors and hollow metal frames. All hardware, painting and framing materials are included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 02/06/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1304 OFFICE | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 4685 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0367ENR1 | HVAC REPLACEMENT | 0367 | The HVAC roof top units and furnaces are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of HVAC packaged units and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | #1304 OFFICE | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 4685 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 70275
0368ENR3 | WINDOW REPLACEMENT | 0368 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 27 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion there of was previously recommended in the FCA reports dated 06/15/1998 and 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1302 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 5104 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 27000
0368EXT5 | EXTERIOR FINISHES | 0368 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 02/06/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1302 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 5104 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25520
0368INT6 | INTERIOR FINISHES | 0368 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA reports dated 06/15/1998 and 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1302 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 5104 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25520
0368SFT4 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0368 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 02/06/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1302 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 5104 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 2552
0368SFT3 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0368 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1302 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 5104 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 4000
0370INT6 | INTERIOR DOOR REPLACEMENT | 0370 | There are several existing interior bi-pass closet doors that are damaged from abuse and age. This project would provide for the removal of the existing bi-pass doors and the purchase and installation of new solid core wood hinged doors and hollow metal frames. All hardware, painting and framing materials are included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1301 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 2924 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0367INT3 | INTERIOR FINISHES | 0367 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA reports dated 06/15/1998 and 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1304 OFFICE | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 4685 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 23425
0372SFT3 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0372 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1300 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1972 | 13500 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 10000
0706EXT1 | EXTERIOR FINISHES | 0706 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA reports dated 06/17/1998 and 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1310 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1992 | 2650 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 13250
0706ADA2 | ADA RESTROOM REMODEL | 0706 | The building does not have an accessible restroom. The existing restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit of 2 restrooms is necessary. This project would provide funding for construction of 1 unisex accessible restroom in the corridor and 1 unisex accessible restroom for the bedrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1310 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1992 | 2650 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 30000
0706SFT2 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0706 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1310 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1992 | 2650 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 4000
0706INT4 | INTERIOR FINISHES | 0706 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1310 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1992 | 2650 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 13250
0706ENR1 | HVAC REPLACEMENT | 0706 | The HVAC roof top units and furnaces are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of new HVAC packaged units and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | #1310 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1992 | 2650 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 39750
0706INT5 | VCT FLOORING REPLACEMENT | 0706 | The VCT (vinyl composite tile) flooring in the building is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. | #1310 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1992 | 2650 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 23850
0706ADA4 | KITCHEN REMODEL | 0706 | The kitchen in the building is in fair to poor condition. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and countertops are delaminating and failing. This project recommends the replacement of the existing kitchen countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards For Accessible Design should be incorporated into the design such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1310 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1992 | 2650 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 15000
0370EXT4 | EXTERIOR FINISHES | 0370 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 02/06/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1301 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 2924 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14620
0372PLM3 | WATER HEATER SEISMIC BRACING | 0372 | The water heater and water storage tank are not seismically anchored to the structure. This project would provide funding for seismic bracing of the water heater and water storage tank to the structure. | #1300 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1972 | 13500 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 1000
0370HVA1 | HVAC REPLACEMENT | 0370 | The HVAC roof top units and furnaces are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of new HVAC packaged units and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1301 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 2924 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 43860
0372INT4 | INTERIOR FINISHES | 0372 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1300 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1972 | 13500 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 67500
0372SFT4 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0372 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1300 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1972 | 13500 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 4000
0372INT5 | FLOORING REPLACEMENT | 0372 | The VCT (vinyl composite tile) and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the next 5-6 years. | #1300 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1972 | 13500 | 2013-06-04 | Four to Ten Years | Long-Term Needs | 3 | 108000
0372SIT3 | SITE DRAINAGE IMPROVEMENTS | 0372 | The building has considerable damage to the stucco finish and foundation from improper drainage around the building. The grade does not slope away from the building in several areas, especially on the east and west sides of the building. This is causing water to pool up next to the building, infiltrate the interior and damage the concrete foundation walls. This project would create positive flow away from the building by regrading and installing French drains as needed. | #1300 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1972 | 13500 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
0370ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0370 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1301 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 2924 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 4000
0372EXT5 | EXTERIOR FINISHES | 0372 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1300 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1972 | 13500 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 67500
0370ADA3 | ADA SIGNAGE | 0370 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1301 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 2924 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 1200
0372ELE2 | ELECTRICAL TRANSFORMER REPLACEMENT | 0372 | There is an electrical transformer located inside the mechanical room. The transformer is over 40 years old and was putting off more heat than it should at the time of the survey. This project recommends replacing the transformer with a new 150 kVA 3-phase power transformer. | #1300 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1972 | 13500 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12500
0371EXT1 | EXTERIOR DOOR REPLACEMENT | 0371 | Most of the exterior doors are hollow core metal doors and severely rusted. This project allows for the replacement of 6 existing metal doors and frames with insulated steel doors. The price includes new hardware and disposal of the existing door assemblies. This project or a portion thereof was previously recommended in the FCA reports dated 06/17/1998 and 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1306 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1981 | 4906 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24000
0371ENR1 | WINDOW REPLACEMENT | 0371 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 20 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA reports dated 06/17/1998 and 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1306 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1981 | 4906 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
0371ELE1 | EMERGENCY GENERATOR REPLACEMENT | 0371 | The building does not have an emergency back-up generator. The generator that used to back-up the building has reached the end of its useful life and has been removed. This project would provide for a new diesel powered 300 KVA generator including required connections to utility systems. | #1306 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1981 | 4906 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 100000
0371INT7 | INTERIOR DOOR REPLACEMENT | 0371 | There are several existing interior bi-pass closet doors that are damaged from abuse and age. This project would provide for the removal of the existing bi-pass doors and the purchase and installation of new solid core wood hinged doors and hollow metal frames. All hardware, painting and framing materials are included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1306 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1981 | 4906 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0371EXT3 | EXTERIOR FINISHES | 0371 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1306 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1981 | 4906 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24530
0371INT8 | INTERIOR FINISHES | 0371 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 5-6 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | #1306 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1981 | 4906 | 2013-06-04 | Four to Ten Years | Long-Term Needs | 3 | 24530
0371ADA2 | KITCHEN REMODEL | 0371 | The kitchen in the building is in fair to poor condition. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and countertops are delaminating and failing. This project recommends the replacement of the existing kitchen countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards For Accessible Design should be incorporated into the design such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1306 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1981 | 4906 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18000
0372EXT1 | EXTERIOR DOOR REPLACEMENT | 0372 | The 13 exterior wood and metal man doors appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement of the wood and metal doors with new metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. This project or a portion thereof was previously recommended in the FCA reports dated 06/17/1998 and 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1300 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1972 | 13500 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 52000
0372EXT2 | WINDOW REPLACEMENT | 0372 | The windows and skylights are original and should be scheduled for replacement. The windows are single pane in a wooden frame. These older windows are drafty, not energy efficient and the wooden frames have deteriorated significantly. The skylights have had numerous leaks and are cracked in several places. This project recommends replacing the windows with dual pane, higher efficiency units and replacing the skylights with new skylight systems.. This estimate is for the replacement of 60 window units including wooden frames and 2 skylights. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA reports dated 06/17/1998 and 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1300 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1972 | 13500 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 100000
0371SFT4 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0371 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1306 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1981 | 4906 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 4000
0370ENR1 | WINDOW REPLACEMENT | 0370 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 12 units. Removal and disposal of the existing windows is included in this estimate. | #1301 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 2924 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
2268EXT2 | EXTERIOR FINISHES | 2268 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the vents, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | GENERATOR BUILDING | 9938 | HHS | DCFS | NYTC | Elko | 1995 | 520 | 2013-09-18 | Four to Ten Years | Long-Term Needs | 3 | 2600
2268EXT3 | ROOF REPLACEMENT | 2268 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. | GENERATOR BUILDING | 9938 | HHS | DCFS | NYTC | Elko | 1995 | 520 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6240
2268INT1 | INTERIOR FINISHES | 2268 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. This project or a portion thereof was previously recommended in the FCA report dated 08/23/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | GENERATOR BUILDING | 9938 | HHS | DCFS | NYTC | Elko | 1995 | 520 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2600
2269EXT1 | EXTERIOR FINISHES | 2269 | It is important to maintain the finish, weather resistance and appearance of the building. The structure is rusting due to moisture infiltration and will fail if not sealed properly. This project would provide funding to protect the structure and exterior of the building. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 08/23/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | WELL HOUSE #3 | 9938 | HHS | DCFS | NYTC | Elko | 1997 | 128 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 640
2280EXT1 | EXTERIOR FINISHES | 2280 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | SUPERINTENDENT'S GARAGE | 9938 | HHS | DCFS | NYTC | Elko |  | 750 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3750
2280SIT1 | SITE DRAINAGE | 2280 | The garage has considerable damage to the siding and foundation from improper drainage. The grade does not slope away from the rear of the building. This is causing water to pool up against the rear wall and damage siding and the concrete foundation. This project would create positive flow away from the building by regrading and installing French drains as needed. | SUPERINTENDENT'S GARAGE | 9938 | HHS | DCFS | NYTC | Elko |  | 750 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
9938SIT8 | EXTERIOR SOLAR SITE LIGHTING UPGRADE | 9938 | There many existing light poles around the site which have caused continuous maintenance problems and some are not working. Problems include failing contactors, unavailable replacement parts, failing conduits and rusted metal poles. Due to insufficient lighting and cracked and heaving concrete sidewalks, there have been tripping hazards and complaints from individuals on the campus. This project would provide for the installation of 35 solar powered LED exterior light fixtures, 20 foot tall poles and 30" diameter raised concrete bases. This installation will eliminate the need for trenching and installing new electrical connections. | NEVADA YOUTH TRAINING CENTER SITE - ELKO | 9938 | HHS | DCFS | NYTC | Elko |  |  | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 227500
9938ENR1 | ENERGY MANAGEMENT SYSTEM INSTALLATION | 9938 | This project recommends the installation of an Energy Management System (EMS) for the site. This system will monitor and control the heating, ventilation, air conditioning and lighting equipment through a central computer system. Electronic sensors will be installed on each piece of equipment which will feed information into the computer system. The maintenance staff can then control and monitor the equipment remotely which will significantly lower energy costs. Along with electricity, natural gas and water meters, this system will provide detailed reports on energy consumption allowing the maintenance staff to analyze and customize the energy used by the facility. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | NEVADA YOUTH TRAINING CENTER SITE - ELKO | 9938 | HHS | DCFS | NYTC | Elko |  |  | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500000
9938SIT4 | SLURRY SEAL ASPHALT PAVING | 9938 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site wide including access roads, parking areas and the maintenance yard. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 200,000 square feet of asphalt area was used to generate this estimate. | NEVADA YOUTH TRAINING CENTER SITE - ELKO | 9938 | HHS | DCFS | NYTC | Elko |  |  | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 150000
9938SIT6 | IRRIGATION UPGRADE | 9938 | The existing landscape irrigation lines throughout the site are reaching the end of their expected life and should be scheduled for replacement. The schedule 20 piping is not durable enough for the application and should be replaced with a stronger pipe. This project would provide for the removal of the existing irrigation lines and the purchase and installation of new lines. 12,000 linear feet was used to generate this estimate. | NEVADA YOUTH TRAINING CENTER SITE - ELKO | 9938 | HHS | DCFS | NYTC | Elko |  |  | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 48000
9938ENV1 | PEST ABATEMENT | 9938 | The site and buildings have been inhabited by swallows. The birds introduce a potential risk of disease, cause maintenance problems with the mechanical systems, and cost labor time for general clean-up. This project provides for removal and disposal of swallow debris, nests, eggs and carcasses from the site and buildings by a licensed pest control business. | NEVADA YOUTH TRAINING CENTER SITE - ELKO | 9938 | HHS | DCFS | NYTC | Elko |  |  | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 7500
9938SIT2 | CONCRETE SIDEWALK REPLACEMENTS | 9938 | The site has several areas of damaged concrete sidewalks that have not been replaced recently. These areas pose tripping hazards from heaving and settling and the cracks will continue to grow from freeze/ thaw impacts. This project would provide for the removal and replacement of the damaged concrete sidewalks. 5,000 SF of 4" thick concrete sidewalk was used for this estimate. | NEVADA YOUTH TRAINING CENTER SITE - ELKO | 9938 | HHS | DCFS | NYTC | Elko |  |  | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
9938ELE1 | SITEWIDE ELECTRICAL UPGRADE | 9938 | The site's electrical distribution system is original and now over 50 years old. The main switchgear, wiring and conduits have reached the end of there useful life and are in need of replacement. In each building, the electrical boxes, panels, outlets and switches are original and due for replacement as well. Maintenance staff also reported that the voltage varies between 400 and 500 volts at any given time. This causes premature wear to the equipment across the site and can damage safety equipment. This project would provide for a complete electrical upgrade including replacement of the main switchgear, transformers, conduit and wiring to all existing buildings on site including trenching and backfill and replacement of electrical equipment in each building. Removal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | NEVADA YOUTH TRAINING CENTER SITE - ELKO | 9938 | HHS | DCFS | NYTC | Elko |  |  | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500000
9938SFT5 | SITE FIRE ALARM UPGRADE | 9938 | This site is equipped with a fire detection and alarm system, but the system is old and inoperative in some buildings. Recurring problems have been noted with the system and related site communications systems since installation. It is recommended that the fire detection and alarm system be completely upgraded, including multiple point off-site notification pull stations or a similar system acceptable to the State Fire Marshal. The site could benefit from a wireless system, which may provide reduced costs and system redundancy in the event of lightning, floods or other problems which could otherwise disable the system. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | NEVADA YOUTH TRAINING CENTER SITE - ELKO | 9938 | HHS | DCFS | NYTC | Elko |  |  | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 250000
9938SIT3 | BACKFLOW PREVENTION | 9938 | The domestic water for the campus is fed from two water tanks which are supplied by a well. The domestic water system does not have a backflow prevention device. State law mandates that backflow prevention devices be installed on all domestic, fire protection and irrigation systems to prevent contamination. This project would provide for three backflow prevention devices to be installed in heated above ground vaults. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | NEVADA YOUTH TRAINING CENTER SITE - ELKO | 9938 | HHS | DCFS | NYTC | Elko |  |  | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 75000
9938ADA2 | ADA PARKING STALL STRIPING | 9938 | The ADA accessible parking area for the Gymnasium does not have striping to identify the parking stall and loading zone. The area should be re-striped to comply with the 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | NEVADA YOUTH TRAINING CENTER SITE - ELKO | 9938 | HHS | DCFS | NYTC | Elko |  |  | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 1500
0228INT2 | INTERIOR FINISHES | 0228 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | PIONEER COTTAGE #5 | 9938 | HHS | DCFS | NYTC | Elko | 1964 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19235
0229ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0229 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | FRONTIER COTTAGE #6 | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 3990 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 4000
0228ENR3 | LIGHTING UPGRADE | 0228 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, utility closets and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | PIONEER COTTAGE #5 | 9938 | HHS | DCFS | NYTC | Elko | 1964 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5771
0228ENR1 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0228 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | PIONEER COTTAGE #5 | 9938 | HHS | DCFS | NYTC | Elko | 1964 | 3847 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 5000
0229HVA2 | EXHAUST FAN REPLACEMENT | 0229 | The exhaust fans in the showers and restroom areas are inadequate for their application contributing to moisture accumulation and possible mold infiltration. This project would provide for the removal of the existing exhaust fan assemblies and the purchase and installation of new exhaust fan assemblies including ducting and connections to utilities. This report recommends the installation of high efficiency exhaust fans with humidity detection and delayed shut-off to exhaust all moisture and prevent future accumulation issues. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | FRONTIER COTTAGE #6 | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 3990 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0228ADA2 | DUAL LEVEL DRINKING FOUNTAIN | 0228 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | PIONEER COTTAGE #5 | 9938 | HHS | DCFS | NYTC | Elko | 1964 | 3847 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 4000
0228ENR2 | EXTERIOR ENERGY RETROFIT | 0228 | The building is constructed of concrete masonry units (CMU) with no insulation. The windows are original to the building, and of single pane construction. Buildings of this type are not energy efficient. This project recommends adding an exterior insulating finish system (EIFS) over the CMU and replacing the windows with new dual-pane, higher efficiency units. This estimate includes removal and disposal of the existing windows. The estimate is based on $10.00 per square foot for the EIFS plus $1000.00 per window for 20 windows. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | PIONEER COTTAGE #5 | 9938 | HHS | DCFS | NYTC | Elko | 1964 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 58470
0228EXT5 | EXTERIOR FINISHES | 0228 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | PIONEER COTTAGE #5 | 9938 | HHS | DCFS | NYTC | Elko | 1964 | 3847 | 2013-09-18 | Four to Ten Years | Long-Term Needs | 3 | 19235
0228SIT1 | REMOVE SPRINKLERED LAWN WITHIN 3' OF BUILDING | 0228 | The building has considerable damage to the painted CMU from lawn sprinklers wetting the exterior walls. This project would create drip irrigated planters within three feet of the building and relocate sprinklers so they do not wet the building. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | PIONEER COTTAGE #5 | 9938 | HHS | DCFS | NYTC | Elko | 1964 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0229EXT2 | EXTERIOR FINISHES | 0229 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | FRONTIER COTTAGE #6 | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 3990 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19950
0229EXT3 | EXTERIOR DOOR REPLACEMENT | 0229 | The exterior metal door at the rear of the building is damaged from age and general wear and tear and has reached the end of its expected life. This project would provide for the replacement of the door assembly with new a metal door, frame and hardware. Removal and disposal of the existing door is included in this estimate. | FRONTIER COTTAGE #6 | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 3990 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0228HVA2 | EXHAUST FAN REPLACEMENT | 0228 | The exhaust fans in the showers and restroom areas are inadequate for their application contributing to moisture accumulation and possible mold infiltration. This project would provide for the removal of the existing exhaust fan assemblies and the purchase and installation of new exhaust fan assemblies including ducting and connections to utilities. This report recommends the installation of high efficiency exhaust fans with humidity detection and delayed shut-off to exhaust all moisture and prevent future accumulation issues. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | PIONEER COTTAGE #5 | 9938 | HHS | DCFS | NYTC | Elko | 1964 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0223SFT3 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0223 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | ADMINISTRATION | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 1924
0228HVA4 | HVAC SYSTEM UPGRADE | 0228 | The existing HVAC system consists of a site-wide closed loop hot water boiler system with hydronic coils. Cooling is provided by roof-mounted evaporative coolers. This system is in fair condition but the pneumatic controls are not working, there are several leaks in the chilled water piping and valves and staff noted that there appears to be leaks in the make-up water lines somewhere which has not been located. This project provides for installing a new HVAC system independent from the site hot water loop including removing the hydronic coils and pneumatic controls and installing new furnaces, air conditioners and ducting throughout the building. The new system shall be designed to significantly reduce electrical and natural gas usage in order to comply with the 2009 IECC and ASHRAE 90.1 and to reduce utility costs. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | PIONEER COTTAGE #5 | 9938 | HHS | DCFS | NYTC | Elko | 1964 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 57705
0228EXT4 | EXTERIOR DOOR REPLACEMENT | 0228 | The exterior metal door at the rear entrance is damaged from age and general wear and tear and has reached the end of its expected life. This project would provide for the replacement of the door assembly with new a metal door, frame and hardware. Removal and disposal of the existing door is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | PIONEER COTTAGE #5 | 9938 | HHS | DCFS | NYTC | Elko | 1964 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0228PLM1 | RESTROOM FIXTURES REPLACEMENT | 0228 | The sink faucets and shower valves were replaced in 1995. The systems installed have not held up well under the high usage typical in a building of this type, and are beginning to fail. This project recommends replacing the faucets and shower mixing control valves with heavy duty rated commercial grade units and includes disposal of the existing fixtures. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | PIONEER COTTAGE #5 | 9938 | HHS | DCFS | NYTC | Elko | 1964 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12500
0228INT1 | KITCHEN REPLACEMENT | 0228 | The kitchen equipment and cabinets were replaced in the building in the mid 1990s. The quality of construction and installation were inadequate for the high usage at these facilities, and the cabinets and counter tops are delaminating and failing. This project recommends the replacement of the existing kitchen counters, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. This estimate includes disposal of the existing materials. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | PIONEER COTTAGE #5 | 9938 | HHS | DCFS | NYTC | Elko | 1964 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0228ADA1 | ADA ENTRANCE DOORS | 0228 | The exterior metal entrance doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the double door assembly with new metal doors, frames and lever-operated hardware. Removal and disposal of the existing doors is included in this estimate. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | PIONEER COTTAGE #5 | 9938 | HHS | DCFS | NYTC | Elko | 1964 | 3847 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 6000
0227HVA4 | HVAC SYSTEM REPLACEMENT | 0227 | The existing HVAC system consists of a site-wide closed loop hot water boiler system with hydronic coils. Cooling is provided by roof-mounted evaporative coolers. This system is in fair condition but the pneumatic controls are not working, there are several leaks in the chilled water piping and valves and staff noted that there appears to be leaks in the make-up water lines somewhere which has not been located. This project provides for installing a new HVAC system independent from the site hot water loop including removing the hydronic coils and pneumatic controls and installing new furnaces, air conditioners and ducting throughout the building. The new system shall be designed to significantly reduce electrical and natural gas usage in order to comply with the 2009 IECC and ASHRAE 90.1 and to reduce utility costs. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | INDIAN COTTAGE #4 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 57705
0227ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0227 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | INDIAN COTTAGE #4 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 4000
0227SEC1 | MAGNETIC DOOR LOCK SYSTEM | 0227 | The existing sleeping room door locks are older and problematic. They are not designed for this application and have become a security and safety concern for the inhabitants. The existing locks require constant maintenance because they do not hold up to the abuse by the residents. This project would provide for a new electric door control system including magnetic locks, control panel and all required electrical connections. | INDIAN COTTAGE #4 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 75000
0227ENR1 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0227 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | INDIAN COTTAGE #4 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 5000
0229ENR2 | EXTERIOR ENERGY RETROFIT | 0229 | The building is constructed of concrete masonry units (CMU) with no insulation. The windows are original to the building, and of single pane construction. Buildings of this type are not energy efficient. This project recommends adding an exterior insulating finish system (EIFS) over the CMU and replacing the windows with new dual-pane, higher efficiency units. This estimate includes removal and disposal of the existing windows. The estimate is based on $10.00 per square foot for the EIFS, $1000.00 per window for 11 windows and $15,000 for the aluminum storefront entrance system. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | FRONTIER COTTAGE #6 | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 3990 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 65900
0223SFT4 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0223 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | ADMINISTRATION | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 4000
0230INT3 | CLOTHES WASHER REPLACEMENT | 0230 | One of the commercial steam powered clothes washers/ extractors is original to the building, the other has been replaced recently. The older one is reaching the end of its useful life and should be scheduled for replacement. This project provides for removal and disposal of the existing washer/ extractor and replacing it with a new unit. | MULTIPURPOSE, DINING & CULINARY | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 15856 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0223ADA6 | ADA ENTRANCE DOOR | 0223 | The existing exterior entrance doors and thresholds to the Administration building is not accessible. This project would provide for new accessible door and threshold assemblies including removal of the existing door assembly and installation of the new accessible door assembly. ADA compliant signage is also included in this project. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | ADMINISTRATION | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 2000
0223ENR2 | EXTERIOR ENERGY RETROFIT | 0223 | The building is constructed of concrete masonry units (CMU) with no insulation. The windows are original to the building, and of single pane construction. Buildings of this type are not energy efficient. This project recommends adding an exterior insulating finish system (EIFS) over the CMU and replacing the windows with new dual-pane, higher efficiency units. This estimate includes removal and disposal of the existing windows. The estimate is based on $10.00 per square foot for the EIFS plus $1000.00 per window for 72 windows. This project or a portion thereof was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | ADMINISTRATION | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 108470
0227ENR3 | LIGHTING UPGRADE | 0227 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, utility closets and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | INDIAN COTTAGE #4 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5771
0227EXT4 | EXTERIOR DOOR REPLACEMENT | 0227 | The exterior metal door at the rear entrance is damaged from age and general wear and tear and has reached the end of its expected life. This project would provide for the replacement of the door assembly with new a metal door, frame and hardware. Removal and disposal of the existing door is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | INDIAN COTTAGE #4 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0231PLM1 | WATER HEATER REPLACEMENT | 0231 | There is a 89 gallon gas-fired water heater in the building that is more than 10 years old. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | CLASSROOMS & INFIRMARY | 9938 | HHS | DCFS | NYTC | Elko | 1972 | 20590 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3500
0231INT5 | CEILING REPAIR | 0231 | The ceilings in the building consist of a 12x12 acoustical tile installed over wood T & G decking. The acoustical tiles are falling off throughout the building due to poor application and it is recommended that they be removed and replaced with gypsum board. This project would provide for removal and disposal of the acoustical tiles and installation of textured and painted gypsum board. Another option would be to remove tiles and paint exposed wood decking. The cost for this option would be $2.50 / SF or $51,475. This project or a portion thereof was previously recommended in the FCA report dated 08/23/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | CLASSROOMS & INFIRMARY | 9938 | HHS | DCFS | NYTC | Elko | 1972 | 20590 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 164720
0231SFT1 | FIRE DAMPER INSPECTION/ REPAIR | 0231 | The fire dampers throughout the building's HVAC plenums are not functioning properly according to staff. These dampers are an integral part of the fire and smoke protection system of the building. This project would provide funds to inspect, test and if necessary, repair the fire dampers. This project or a portion thereof was previously recommended in the FCA report dated 08/23/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | CLASSROOMS & INFIRMARY | 9938 | HHS | DCFS | NYTC | Elko | 1972 | 20590 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 11000
0231SFT4 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0231 | The building is partially a B occupancy per the 2012 IBC and is over 12,000 square feet in area. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 or R-2 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. This project or a portion thereof was previously recommended in the FCA report dated 08/23/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | CLASSROOMS & INFIRMARY | 9938 | HHS | DCFS | NYTC | Elko | 1972 | 20590 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 288260
0231ADA4 | ADA SIGNAGE | 0231 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 08/23/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | CLASSROOMS & INFIRMARY | 9938 | HHS | DCFS | NYTC | Elko | 1972 | 20590 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 7500
0231ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0231 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. This project or a portion thereof was previously recommended in the FCA report dated 08/23/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | CLASSROOMS & INFIRMARY | 9938 | HHS | DCFS | NYTC | Elko | 1972 | 20590 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 4000
0231EXT4 | EXTERIOR DOOR REPLACEMENT | 0231 | The existing exterior metal doors and frames appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement and installation of 15 new hollow metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/23/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | CLASSROOMS & INFIRMARY | 9938 | HHS | DCFS | NYTC | Elko | 1972 | 20590 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 60000
0231EXT3 | WINDOW REPLACEMENT | 0231 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 125 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/23/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | CLASSROOMS & INFIRMARY | 9938 | HHS | DCFS | NYTC | Elko | 1972 | 20590 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 187500
0231EXT2 | EXTERIOR FINISHES | 0231 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 08/23/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | CLASSROOMS & INFIRMARY | 9938 | HHS | DCFS | NYTC | Elko | 1972 | 20590 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 102950
0231INT3 | ADA BREAK ROOM REMODEL | 0231 | The kitchenette and associated cabinets in the employee break room are original to the building. This project recommends the replacement of the existing kitchen countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards For Accessible Design should be incorporated into the design such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/23/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | CLASSROOMS & INFIRMARY | 9938 | HHS | DCFS | NYTC | Elko | 1972 | 20590 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0231SFT2 | COMMUNICATIONS SYSTEM UPGRADE | 0231 | This building is equipped with a communications system that is at least 20 years old. The system provides paging and phone communications to classrooms and is an integral component of the notification and safety procedures for the classrooms. The system is problematic and replacement parts are no longer available. It is recommended that the communication systems be upgraded including installation of a new bell clock system. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/23/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | CLASSROOMS & INFIRMARY | 9938 | HHS | DCFS | NYTC | Elko | 1972 | 20590 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 102950
0231ENV1 | REFRIGERATED MEDICAL CABINET REPLACEMENT | 0231 | The infirmary has a medical grade refrigeration cabinet that is used to store temperature sensitive medications and materials. The cabinet is older and has been problematic, forcing staff to rely on a portable unit and a non-medical grade refrigerator, which are less secure and do not provide adequate storage. This project will provide for a new medical grade refrigerated storage cabinet and associated equipment. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/23/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | CLASSROOMS & INFIRMARY | 9938 | HHS | DCFS | NYTC | Elko | 1972 | 20590 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 15000
0231EXT1 | ROOF REPLACEMENT | 0231 | The standing seam metal roof on this building was in poor condition at the time of the survey and had active leaks. It is recommended that this building be re-roofed in the next 1-2 years with a new single-ply roofing system which will be installed directly over the existing metal roof. This will allow the roof to qualify for the statewide roofing program warranty and preventative maintenance agreement. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/23/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | CLASSROOMS & INFIRMARY | 9938 | HHS | DCFS | NYTC | Elko | 1972 | 20590 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 247080
0230SIT1 | SITE DRAINAGE IMPROVEMENTS | 0230 | The building has a drainage problem on the north side where grade does not properly slope away from the building. This is causing water to pool up next to the building which may infiltrate the interior during inclement weather and cause damage to the concrete foundation walls. This project would create positive flow away from the building by regrading and installing French drains as needed. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | MULTIPURPOSE, DINING & CULINARY | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 15856 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 3500
0231ENR2 | LIGHTING UPGRADE | 0231 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, closets and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/23/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | CLASSROOMS & INFIRMARY | 9938 | HHS | DCFS | NYTC | Elko | 1972 | 20590 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30885
0229INT2 | INTERIOR FINISHES | 0229 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | FRONTIER COTTAGE #6 | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 3990 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19950
0231SFT6 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0231 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. | CLASSROOMS & INFIRMARY | 9938 | HHS | DCFS | NYTC | Elko | 1972 | 20590 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 10295
0226ADA1 | ADA ENTRANCE DOORS | 0226 | The exterior metal entrance doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the double door assembly with new metal doors, frames and lever-operated hardware. Removal and disposal of the existing doors is included in this estimate. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | EXPLORER R & C COTTAGE #3 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 6000
0230PLM3 | WATER VALVE REPLACEMENT | 0230 | The Belimo hot and cold water control valves for the mechanical system have had leaks since installation and should be replaced in the next two to three years. This project would provide for replacing the valves throughout the HVAC plumbing lines. | MULTIPURPOSE, DINING & CULINARY | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 15856 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0227ENR2 | EXTERIOR ENERGY RETROFIT | 0227 | The building is constructed of concrete masonry units (CMU) with no insulation. The windows are original to the building, and of single pane construction. Buildings of this type are not energy efficient. This project recommends adding an exterior insulating finish system (EIFS) over the CMU and replacing the windows with new dual-pane, higher efficiency units. This estimate includes removal and disposal of the existing windows. The estimate is based on $10.00 per square foot for the EIFS plus $1000.00 per window for 20 windows. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | INDIAN COTTAGE #4 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 58470
0230INT2 | INTERIOR FINISHES | 0230 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | MULTIPURPOSE, DINING & CULINARY | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 15856 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 79280
0230EXT3 | EXTERIOR FINISHES | 0230 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | MULTIPURPOSE, DINING & CULINARY | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 15856 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 79280
0230HVA1 | HEATER INSTALLATION | 0230 | The Laundry Room does not currently have any heating equipment and is uncomfortably cold in the winter. It is recommended to install heating equipment in the room to ensure a comfortable work environment. This project would provide for the purchase and installation of a natural gas fired heater including all required connections to existing utilities. | MULTIPURPOSE, DINING & CULINARY | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 15856 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3500
0229HVA3 | HVAC REPLACEMENT | 0229 | There are 6 FAU's located in the mechanical room which provide heat for this unit as well as the Adventurer Cottage. They are currently in good operational condition but due to age and expected life span, these units should be scheduled for replacement within the 6 to 8 years. Also included is one wall-mounted evaporative cooler, the other 3 have been recently replaced. This project address both the Frontier and Adventurer. A figure of $8,000 was used for the heaters and $3,000 for evaporative cooler. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | FRONTIER COTTAGE #6 | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 3990 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 51000
0229SIT1 | REMOVE SPRINKLERED LAWN WITHIN 3' OF BUILDING | 0229 | The building has considerable damage to the painted CMU from lawn sprinklers wetting the exterior walls. This project would create drip irrigated planters within three feet of the building and relocate sprinklers so they do not wet the building. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | FRONTIER COTTAGE #6 | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 3990 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0229ENR3 | LIGHTING UPGRADE | 0229 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, utility closets and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | FRONTIER COTTAGE #6 | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 3990 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5985
0229ENR1 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0229 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | FRONTIER COTTAGE #6 | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 3990 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0229ADA4 | ADA RESTROOM UPGRADE | 0229 | This cottage is designated as the "ADA" cottage according to staff. The existing restroom does not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom. These items may include a new sink, toilet, shower controls, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | FRONTIER COTTAGE #6 | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 3990 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 15000
0229INT1 | KITCHEN REPLACEMENT | 0229 | The kitchen equipment and cabinets were replaced in the building in the mid 1990s. At the time of the survey, the stovetop, oven and refrigerator were not operating. The quality of construction and installation were inadequate for the high usage at these facilities, and the cabinets and counter tops are delaminating and failing. This project recommends the replacement of the existing kitchen counters, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. This estimate includes disposal of the existing materials. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | FRONTIER COTTAGE #6 | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 3990 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0231INT1 | FLOORING REPLACEMENT | 0231 | The VCT (vinyl composite tile), carpet and ceramic tile flooring in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base, heavy duty commercial grade carpet and new ceramic tile in the next 2-3 years. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/23/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | CLASSROOMS & INFIRMARY | 9938 | HHS | DCFS | NYTC | Elko | 1972 | 20590 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 164720
0224ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0224 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | FORESTER COTTAGE #1 | 9938 | HHS | DCFS | NYTC | Elko | 1964 | 3847 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 4000
0225SIT2 | REMOVE SPRINKLERED LAWN WITHIN 3' OF BUILDING | 0225 | The building has considerable damage to the painted CMU from lawn sprinklers wetting the exterior walls. This project would create drip irrigated planters within three feet of the building and relocate sprinklers so they do not wet the building. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | MOUNTAINEER COTTAGE #2 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0225PLM1 | RESTROOM FIXTURES REPLACEMENT | 0225 | The sink faucets and shower valves were replaced in 1995. The systems installed have not held up well under the high usage typical in a building of this type, and are beginning to fail. This project recommends replacing the faucets and shower mixing control valves with heavy duty rated commercial grade units and includes disposal of the existing fixtures. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | MOUNTAINEER COTTAGE #2 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12500
0225ENR1 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0225 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | MOUNTAINEER COTTAGE #2 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 5000
0225HVA2 | EXHAUST FAN REPLACEMENT | 0225 | The exhaust fans in the showers and restroom areas are inadequate for their application contributing to moisture accumulation and possible mold infiltration. This project would provide for the removal of the existing exhaust fan assemblies and the purchase and installation of new exhaust fan assemblies including ducting and connections to utilities. This report recommends the installation of high efficiency exhaust fans with humidity detection and delayed shut-off to exhaust all moisture and prevent future accumulation issues. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | MOUNTAINEER COTTAGE #2 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0225INT3 | INTERIOR FINISHES | 0225 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 5-6 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | MOUNTAINEER COTTAGE #2 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Four to Ten Years | Long-Term Needs | 3 | 19235
0225SEC1 | MAGNETIC DOOR LOCK SYSTEM | 0225 | The existing sleeping room door locks are older and problematic. They are not designed for this application and have become a security and safety concern for the inhabitants. The existing locks require constant maintenance because they do not hold up to the abuse by the residents. This project would provide for a new electric door control system including magnetic locks, control panel and all required electrical connections. | MOUNTAINEER COTTAGE #2 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 75000
0225ADA1 | ADA ENTRANCE DOORS | 0225 | The exterior metal entrance doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the double door assembly with new metal doors, frames and lever-operated hardware. Removal and disposal of the existing doors is included in this estimate. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | MOUNTAINEER COTTAGE #2 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 6000
0224SFT3 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0224 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | FORESTER COTTAGE #1 | 9938 | HHS | DCFS | NYTC | Elko | 1964 | 3847 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 5000
0224SFT4 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0224 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | FORESTER COTTAGE #1 | 9938 | HHS | DCFS | NYTC | Elko | 1964 | 3847 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 4000
0224HVA1 | EXHAUST FAN REPLACEMENT | 0224 | The exhaust fans in the showers and restroom areas are inadequate for their application contributing to moisture accumulation and possible mold infiltration. This project would provide for the removal of the existing exhaust fan assemblies and the purchase and installation of new exhaust fan assemblies including ducting and connections to utilities. This report recommends the installation of high efficiency exhaust fans with humidity detection and delayed shut-off to exhaust all moisture and prevent future accumulation issues. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | FORESTER COTTAGE #1 | 9938 | HHS | DCFS | NYTC | Elko | 1964 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0224ENR2 | EXTERIOR ENERGY RETROFIT | 0224 | The building is constructed of concrete masonry units (CMU) with no insulation. The windows are original to the building, and of single pane construction. Buildings of this type are not energy efficient. This project recommends adding an exterior insulating finish system (EIFS) over the CMU and replacing the windows with new dual-pane, higher efficiency units. This estimate includes removal and disposal of the existing windows. The estimate is based on $10.00 per square foot for the EIFS plus $1000.00 per window for 20 windows. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | FORESTER COTTAGE #1 | 9938 | HHS | DCFS | NYTC | Elko | 1964 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 58470
0224ENR3 | LIGHTING UPGRADE | 0224 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, utility closets and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | FORESTER COTTAGE #1 | 9938 | HHS | DCFS | NYTC | Elko | 1964 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5771
0226HVA3 | HVAC SYSTEM UPGRADE | 0226 | The existing HVAC system consists of a site-wide closed loop hot water boiler system with hydronic coils. Cooling is provided by roof-mounted evaporative coolers. This system is in fair condition but the pneumatic controls are not working, there are several leaks in the chilled water piping and valves and staff noted that there appears to be leaks in the make-up water lines somewhere which has not been located. This project provides for installing a new HVAC system independent from the site hot water loop including removing the hydronic coils and pneumatic controls and installing new furnaces, air conditioners and ducting throughout the building. The new system shall be designed to significantly reduce electrical and natural gas usage in order to comply with the 2009 IECC and ASHRAE 90.1 and to reduce utility costs. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | EXPLORER R & C COTTAGE #3 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 57705
0224EXT4 | EXTERIOR FINISHES | 0224 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | FORESTER COTTAGE #1 | 9938 | HHS | DCFS | NYTC | Elko | 1964 | 3847 | 2013-09-18 | Four to Ten Years | Long-Term Needs | 3 | 19235
0226EXT1 | EXTERIOR FINISHES | 0226 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | EXPLORER R & C COTTAGE #3 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Four to Ten Years | Long-Term Needs | 3 | 19235
0224ADA1 | ADA ENTRANCE DOORS | 0224 | The exterior metal entrance doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the double door assembly with new metal doors, frames and lever-operated hardware. Removal and disposal of the existing doors is included in this estimate. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | FORESTER COTTAGE #1 | 9938 | HHS | DCFS | NYTC | Elko | 1964 | 3847 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 6000
0223ENR4 | HVAC SYSTEM UPGRADE | 0223 | The existing HVAC system consists of a site-wide closed loop hot water boiler system with hydronic coils. Cooling is provided by a chiller located inside the building. This system is in fair condition but the pneumatic controls are not working, there are several leaks in the chilled water piping and valves and staff noted that there appears to be leaks in the make-up water lines somewhere which has not been located. This project provides for installing a new HVAC system independent from the site hot water loop including removing the hydronic coils and pneumatic controls and installing new air conditioning, furnaces and ducting throughout the building. Additional cooling will be included for the server room which currently gets overheated. The new system shall be designed to significantly reduce electrical and natural gas usage in order to comply with the 2009 IECC and ASHRAE 90.1 and to reduce utility costs. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | ADMINISTRATION | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 57705
0225INT1 | KITCHEN REPLACEMENT | 0225 | The kitchen equipment and cabinets were replaced in the building in the mid 1990s. The quality of construction and installation were inadequate for the high usage at these facilities, and the cabinets and counter tops are delaminating and failing. This project recommends the replacement of the existing kitchen counters, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. This estimate includes disposal of the existing materials. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | MOUNTAINEER COTTAGE #2 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0225ENR3 | LIGHTING UPGRADE | 0225 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, utility closets and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | MOUNTAINEER COTTAGE #2 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5771
0225EXT3 | EXTERIOR DOOR REPLACEMENT | 0225 | The exterior metal door at the rear entrance is damaged from age and general wear and tear and has reached the end of its expected life. This project would provide for the replacement of the door assembly with new a metal door, frame and hardware. Removal and disposal of the existing door is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | MOUNTAINEER COTTAGE #2 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0225ENR2 | EXTERIOR ENERGY RETROFIT | 0225 | The building is constructed of concrete masonry units (CMU) with no insulation. The windows are original to the building, and of single pane construction. Buildings of this type are not energy efficient. This project recommends adding an exterior insulating finish system (EIFS) over the CMU and replacing the windows with new dual-pane, higher efficiency units. This estimate includes removal and disposal of the existing windows. The estimate is based on $10.00 per square foot for the EIFS plus $1000.00 per window for 20 windows. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | MOUNTAINEER COTTAGE #2 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 58470
0225EXT5 | EXTERIOR FINISHES | 0225 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MOUNTAINEER COTTAGE #2 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Four to Ten Years | Long-Term Needs | 3 | 19235
0224PLM1 | RESTROOM FIXTURES REPLACEMENT | 0224 | The sink faucets and shower valves were replaced in 1995. The systems installed have not held up well under the high usage typical in a building of this type, and are beginning to fail. This project recommends replacing the faucets and shower mixing control valves with heavy duty rated commercial grade units and includes disposal of the existing fixtures. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | FORESTER COTTAGE #1 | 9938 | HHS | DCFS | NYTC | Elko | 1964 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12500
0224EXT3 | EXTERIOR DOOR REPLACEMENT | 0224 | The exterior metal door at the rear entrance is damaged from age and general wear and tear and has reached the end of its expected life. This project would provide for the replacement of the door assembly with new a metal door, frame and hardware. Removal and disposal of the existing door is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | FORESTER COTTAGE #1 | 9938 | HHS | DCFS | NYTC | Elko | 1964 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0224SIT2 | REMOVE SPRINKLERED LAWN WITHIN 3' OF BUILDING | 0224 | The building has considerable damage to the painted CMU from lawn sprinklers wetting the exterior walls. This project would create drip irrigated planters within three feet of the building and relocate sprinklers so they do not wet the building. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | FORESTER COTTAGE #1 | 9938 | HHS | DCFS | NYTC | Elko | 1964 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0224INT2 | KITCHEN REPLACEMENT | 0224 | The kitchen equipment and cabinets were replaced in the building in the mid 1990s. The quality of construction and installation were inadequate for the high usage at these facilities, and the cabinets and counter tops are delaminating and failing. This project recommends the replacement of the existing kitchen counters, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. This estimate includes disposal of the existing materials. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | FORESTER COTTAGE #1 | 9938 | HHS | DCFS | NYTC | Elko | 1964 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0231INT4 | INTERIOR FINISHES | 0231 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be cleaned and sealed or painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 08/23/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | CLASSROOMS & INFIRMARY | 9938 | HHS | DCFS | NYTC | Elko | 1972 | 20590 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 102950
0224HVA3 | HVAC SYSTEM UPGRADE | 0224 | The existing HVAC system consists of a site-wide closed loop hot water boiler system with hydronic coils. Cooling is provided by evaporative coolers which have been replaced recently. This system is in fair condition but the pneumatic controls are not working, there are several leaks in the chilled water piping and valves and staff noted that there appears to be leaks in the make-up water lines somewhere which has not been located. This project provides for installing a new HVAC system independent from the site hot water loop including removing the hydronic coils and pneumatic controls and installing new furnaces and ducting throughout the building. The new system shall be designed to significantly reduce electrical and natural gas usage in order to comply with the 2009 IECC and ASHRAE 90.1 and to reduce utility costs. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | FORESTER COTTAGE #1 | 9938 | HHS | DCFS | NYTC | Elko | 1964 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 38470
0223EXT3 | EXTERIOR FINISHES | 0223 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | ADMINISTRATION | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Four to Ten Years | Long-Term Needs | 3 | 19235
0227EXT5 | EXTERIOR FINISHES | 0227 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | INDIAN COTTAGE #4 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Four to Ten Years | Long-Term Needs | 3 | 19235
0227SIT1 | REMOVE SPRINKLERED LAWN WITHIN 3' OF BUILDING | 0227 | The building has considerable damage to the painted CMU from lawn sprinklers wetting the exterior walls. This project would create drip irrigated planters within three feet of the building and relocate sprinklers so they do not wet the building. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | INDIAN COTTAGE #4 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0227PLM1 | RESTROOM FIXTURES REPLACEMENT | 0227 | The sink faucets and shower valves were replaced in 1995. The systems installed have not held up well under the high usage typical in a building of this type, and are beginning to fail. This project recommends replacing the faucets and shower mixing control valves with heavy duty rated commercial grade units and includes disposal of the existing fixtures. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | INDIAN COTTAGE #4 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12500
0227HVA2 | EXHAUST FAN REPLACEMENT | 0227 | The exhaust fans in the showers and restroom areas are inadequate for their application contributing to moisture accumulation and possible mold infiltration. This project would provide for the removal of the existing exhaust fan assemblies and the purchase and installation of new exhaust fan assemblies including ducting and connections to utilities. This report recommends the installation of high efficiency exhaust fans with humidity detection and delayed shut-off to exhaust all moisture and prevent future accumulation issues. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | INDIAN COTTAGE #4 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0227INT1 | KITCHEN REPLACEMENT | 0227 | The kitchen equipment and cabinets were replaced in the building in the mid 1990s. The quality of construction and installation were inadequate for the high usage at these facilities, and the cabinets and counter tops are delaminating and failing. This project recommends the replacement of the existing kitchen counters, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. This estimate includes disposal of the existing materials. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | INDIAN COTTAGE #4 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0227ADA1 | ADA ENTRANCE DOORS | 0227 | The exterior metal entrance doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the double door assembly with new metal doors, frames and lever-operated hardware. Removal and disposal of the existing doors is included in this estimate. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | INDIAN COTTAGE #4 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 6000
0226PLM1 | RESTROOM FIXTURES REPLACEMENT | 0226 | The sink faucets and shower valves were replaced in 1995. The systems installed have not held up well under the high usage typical in a building of this type, and are beginning to fail. This project recommends replacing the faucets and shower mixing control valves with heavy duty rated commercial grade units and includes disposal of the existing fixtures. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | EXPLORER R & C COTTAGE #3 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12500
0226EXT5 | EXTERIOR DOOR REPLACEMENT | 0226 | The exterior metal door at the rear entrance is damaged from age and general wear and tear and has reached the end of its expected life. This project would provide for the replacement of the door assembly with new a metal door, frame and hardware. Removal and disposal of the existing door is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | EXPLORER R & C COTTAGE #3 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0226HVA2 | EXHAUST FAN REPLACEMENT | 0226 | The exhaust fans in the showers and restroom areas are inadequate for their application contributing to moisture accumulation and possible mold infiltration. This project would provide for the removal of the existing exhaust fan assemblies and the purchase and installation of new exhaust fan assemblies including ducting and connections to utilities. This report recommends the installation of high efficiency exhaust fans with humidity detection and delayed shut-off to exhaust all moisture and prevent future accumulation issues. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | EXPLORER R & C COTTAGE #3 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0226ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0226 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | EXPLORER R & C COTTAGE #3 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 4000
0232EXT3 | WINDOW REPLACEMENT | 0232 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 2 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | INDUSTRIAL/VOCATIONAL | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 11264 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
0226INT1 | KITCHEN REPLACEMENT | 0226 | The kitchen equipment and cabinets were replaced in the building in the mid 1990s. The quality of construction and installation were inadequate for the high usage at these facilities, and the cabinets and counter tops are delaminating and failing. This project recommends the replacement of the existing kitchen counters, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. This estimate includes disposal of the existing materials. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | EXPLORER R & C COTTAGE #3 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0225ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0225 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | MOUNTAINEER COTTAGE #2 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 4000
0226ENR2 | EXTERIOR ENERGY RETROFIT | 0226 | The building is constructed of concrete masonry units (CMU) with no insulation. The windows are original to the building, and of single pane construction. Buildings of this type are not energy efficient. This project recommends adding an exterior insulating finish system (EIFS) over the CMU and replacing the windows with new dual-pane, higher efficiency units. This estimate includes removal and disposal of the existing windows. The estimate is based on $10.00 per square foot for the EIFS plus $1000.00 per window for 20 windows. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | EXPLORER R & C COTTAGE #3 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 58470
0225HVA4 | HVAC SYSTEM UPGRADE | 0225 | The existing HVAC system consists of a site-wide closed loop hot water boiler system with hydronic coils. Cooling is provided by roof-mounted evaporative coolers. This system is in fair condition but the pneumatic controls are not working, there are several leaks in the chilled water piping and valves and staff noted that there appears to be leaks in the make-up water lines somewhere which has not been located. This project provides for installing a new HVAC system independent from the site hot water loop including removing the hydronic coils and pneumatic controls and installing new furnaces, air conditioners and ducting throughout the building. The new system shall be designed to significantly reduce electrical and natural gas usage in order to comply with the 2009 IECC and ASHRAE 90.1 and to reduce utility costs. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | MOUNTAINEER COTTAGE #2 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 57705
0223EXT4 | EXTERIOR DOOR REPLACEMENT | 0223 | The 3 exterior wood man doors appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement of the wood doors with new metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | ADMINISTRATION | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
0223ADA9 | ADA RAMP REPLACEMENT | 0223 | This facility has an ADA accessible ramp located in front of the building. This ramp is on the accessible path of travel from the accessible parking space to the entrance of the building. The ramp does not have compliant landings, handrails or curbs. This project would provide for replacing the ramp with a fully ADA compliant ramp. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | ADMINISTRATION | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 45000
0223SIT1 | CONCRETE STAIRS REPLACEMENT | 0223 | The two sets of concrete stairs that access the building are deteriorating. Spalling and cracking have occurred. Exposure to the elements is a contributing factor and one set of stairs was closed due to tripping hazards. It appears these stairs are original to the building. An immediate replacement is recommended. | ADMINISTRATION | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 12000
0223INT3 | INTERIOR FINISHES | 0223 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | ADMINISTRATION | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Four to Ten Years | Long-Term Needs | 3 | 19235
0223ENR3 | LIGHTING UPGRADE | 0223 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, conference rooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | ADMINISTRATION | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5771
0223ADA5 | ADA PARKING AND SIGNAGE | 0223 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The existing ADA parking spaces do not entirely meet the requirements of the code. This project provides funding to bring the existing ADA parking spaces up to code including removal of the asphalt and replacement with P.C. concrete, updated signage, re-striping, re-grading and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | ADMINISTRATION | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 17500
0223ADA7 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0223 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. This project or a portion thereof was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | ADMINISTRATION | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 4000
0223ADA8 | ADA SIGNAGE | 0223 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | ADMINISTRATION | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 1200
0224INT1 | INTERIOR FINISHES | 0224 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | FORESTER COTTAGE #1 | 9938 | HHS | DCFS | NYTC | Elko | 1964 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19235
0226ENR1 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0226 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | EXPLORER R & C COTTAGE #3 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 5000
0226SIT1 | REMOVE SPRINKLERED LAWN WITHIN 3' OF BUILDING | 0226 | The building has considerable damage to the painted CMU from lawn sprinklers wetting the exterior walls. This project would create drip irrigated planters within three feet of the building and relocate sprinklers so they do not wet the building. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | EXPLORER R & C COTTAGE #3 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0226INT3 | INTERIOR FINISHES | 0226 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 5-6 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | EXPLORER R & C COTTAGE #3 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Four to Ten Years | Long-Term Needs | 3 | 19235
0227INT3 | INTERIOR FINISHES | 0227 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 5-6 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | INDIAN COTTAGE #4 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Four to Ten Years | Long-Term Needs | 3 | 19235
0226ENR3 | LIGHTING UPGRADE | 0226 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, utility closets and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | EXPLORER R & C COTTAGE #3 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5771
0234PLM1 | WATER HEATER REPLACEMENT | 0234 | There is a 50 gallon natural gas-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | SUPERINTENDENT'S RESIDENCE | 9938 | HHS | DCFS | NYTC | Elko | 1989 | 1456 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1750
0233EXT2 | EXTERIOR FINISHES | 0233 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | GYMNASIUM | 9938 | HHS | DCFS | NYTC | Elko | 1976 | 15316 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 76580
0233INT5 | INTERIOR DOOR REPLACEMENT | 0233 | The interior doors in this building are hollow core metal units and most are damaged from general wear and tear. This project would provide for the installation of new solid core interior doors including frames, lever action door handles, hardware and paint. Removal and disposal of the existing doors is included in this cost estimate. A total of 14 interior doors was used in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | GYMNASIUM | 9938 | HHS | DCFS | NYTC | Elko | 1976 | 15316 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 28000
0233HVA3 | HVAC SYSTEM REPLACEMENT | 0233 | The existing HVAC system consists of a closed loop hot water system with heat exchangers located throughout the ceiling areas. The boiler is original to the building, the water tubes are leaking, the sheet metal panels are rusted and the air handler's pneumatics are non-operational. The Gymnasium also lacks cooling. This project would provide for a new boiler system with heat exchangers to provide heating and cooling of the building including connections to a site wide energy management system (EMS). This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | GYMNASIUM | 9938 | HHS | DCFS | NYTC | Elko | 1976 | 15316 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 229740
0233INT2 | INTERIOR FINISHES | 0233 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | GYMNASIUM | 9938 | HHS | DCFS | NYTC | Elko | 1976 | 15316 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 76580
0233ADA4 | ADA LOCKER ROOM RESTROOM UPGRADE | 0233 | The restroom and shower fixtures in the locker rooms are worn and damaged from many years of use including the water closets, urinals, lavatories, faucets, shower heads and handles. Many fixtures are or have been leaking and have caused extensive scaling and staining to the fixtures themselves. It is recommended that all fixtures be replaced with new ADA compliant units. This project includes removal and disposal of the existing fixtures and installation of new fixtures. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | GYMNASIUM | 9938 | HHS | DCFS | NYTC | Elko | 1976 | 15316 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
0233HVA2 | EXHAUST FAN REPLACEMENT | 0233 | The exhaust fans in the showers, restrooms and locker room areas are inadequate for their application contributing to moisture accumulation and possible mold growth. This project would provide for the removal of the existing exhaust fan assemblies and the purchase and installation of high efficiency exhaust fans with humidity detection and delayed shut-off to exhaust all moisture and prevent future accumulation issues. Removal and disposal of the existing equipment is included in this estimate. This project excludes the restrooms adjacent to the Lobby as they were addressed in CIP project 05-C35. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | GYMNASIUM | 9938 | HHS | DCFS | NYTC | Elko | 1976 | 15316 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0233INT3 | GYMNASIUM FLOOR REPLACEMENT | 0233 | The existing rubber flooring in the gymnasium is reaching the end of its useful life. This project would provide for the removal of the existing flooring and installation of a new wood floor. A 25/32" thick maple on a sleeper system was used for this estimate. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | GYMNASIUM | 9938 | HHS | DCFS | NYTC | Elko | 1976 | 15316 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 124020
0233EXT4 | ROOF DRAIN DOWNSPOUT MODIFICATIONS | 0233 | The roof drain downspouts currently terminate within inches of the building with no continuous drainage away from the foundation. This is causing the water to pool next to the foundation and damage the foundation and walls. This project would provide for the extension of the roof drains from the downspouts to approximately 5'-0" away from the perimeter of the building to prevent pooling and damage to the building. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | GYMNASIUM | 9938 | HHS | DCFS | NYTC | Elko | 1976 | 15316 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0233INT7 | BASKETBALL BACKSTOP REPLACEMENT | 0233 | The existing backstops in the gymnasium are reaching the end of their useful life and should be scheduled for replacement. The cables and mechanisms are worn out and do not function properly. This project would provide for the removal and disposal of the existing backstops and installation of new ones. An electrically operated, ceiling suspended, fold up basketball backstop was used for this estimate. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | GYMNASIUM | 9938 | HHS | DCFS | NYTC | Elko | 1976 | 15316 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16500
0233ADA1 | ADA SIGNAGE | 0233 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | GYMNASIUM | 9938 | HHS | DCFS | NYTC | Elko | 1976 | 15316 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 5000
0233INT4 | BLEACHER REPLACEMENT | 0233 | The existing wood bleachers in the gymnasium are reaching the end of their useful life. This project would provide for the removal and disposal of the existing bleachers and installation of new bleachers. Wood, manually telescoping bleachers to seat 500 people were used for this estimate. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | GYMNASIUM | 9938 | HHS | DCFS | NYTC | Elko | 1976 | 15316 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 112500
0233SFT1 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0233 | The building is partially a B occupancy per the 2012 IBC and is over 12,000 square feet in area. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 or R-2 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | GYMNASIUM | 9938 | HHS | DCFS | NYTC | Elko | 1976 | 15316 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 214424
0234EXT1 | ROOF REPLACEMENT | 0234 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 1-2 years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | SUPERINTENDENT'S RESIDENCE | 9938 | HHS | DCFS | NYTC | Elko | 1989 | 1456 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 17472
0234ENR1 | HVAC REPLACEMENT | 0234 | The existing HVAC system consists of a natural gas fired furnace and a split system air conditioner. The equipment is not energy efficient and has reached the end of its expected and useful life. This project would provide for installation of new HVAC equipment and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | SUPERINTENDENT'S RESIDENCE | 9938 | HHS | DCFS | NYTC | Elko | 1989 | 1456 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 21840
0234INT2 | CARPET REPLACEMENT | 0234 | The carpet in the building is showing signs of extreme wear and should be scheduled for replacement. It is recommended that the carpet be replaced with heavy duty commercial grade carpet in the next 2-3 years. | SUPERINTENDENT'S RESIDENCE | 9938 | HHS | DCFS | NYTC | Elko | 1989 | 1456 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8400
0234SIT1 | SITE DRAINAGE | 0234 | The house has considerable damage to the siding and foundation from improper drainage. The grade does not slope away from the rear of the building. This is causing water to pool up against the rear wall and damage siding and the concrete foundation walls. This project would create positive flow away from the building by regrading and installing French drains as needed. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | SUPERINTENDENT'S RESIDENCE | 9938 | HHS | DCFS | NYTC | Elko | 1989 | 1456 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 3000
0234EXT2 | EXTERIOR FINISHES | 0234 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | SUPERINTENDENT'S RESIDENCE | 9938 | HHS | DCFS | NYTC | Elko | 1989 | 1456 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7280
0234SFT2 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0234 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | SUPERINTENDENT'S RESIDENCE | 9938 | HHS | DCFS | NYTC | Elko | 1989 | 1456 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 4000
0234SFT1 | EXTERIOR STAIR HANDRAIL INSTALLATION | 0234 | The concrete exterior stairs at the entry are lacking a handrail as required in section R311.7.8 of the 2012 International Residential Code. This project would provide for a tubular steel framed handrail to be installed in accordance with the code. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | SUPERINTENDENT'S RESIDENCE | 9938 | HHS | DCFS | NYTC | Elko | 1989 | 1456 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 5000
0234INT1 | INTERIOR FINISHES | 0234 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | SUPERINTENDENT'S RESIDENCE | 9938 | HHS | DCFS | NYTC | Elko | 1989 | 1456 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7280
0310EXT1 | ROOF REPLACEMENT | 0310 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. There are missing shingles and active leaks and the wood roof structure is failing. It is recommended that this building be re-roofed in the next 1-2 years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. | ASSISTANT SUPERINTENDENT HOUSE | 9938 | HHS | DCFS | NYTC | Elko |  | 890 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 10680
0310SEC1 | CONSERVE AND PROTECT VACANT BUILDING | 0310 | This residence is vacant and currently used for incidental storage. The structure is deteriorating including broken windows, doors falling off and roof failing. The broken windows in the building have allowed pigeons, bats and other pests access to the building, with related health hazards and allowed rain to enter the building. In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the Department of Interior Recommended Guidelines in Preservation Brief 31. Windows and doors will be secured and covered, some with louvers to permit ventilation of the structure. A basic security system including a smoke/fire alarm will also be installed. A sump and drain system will keep water from the under floor areas and basement. This project or a portion thereof was previously recommended in the FCA report dated 08/23/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | ASSISTANT SUPERINTENDENT HOUSE | 9938 | HHS | DCFS | NYTC | Elko |  | 890 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 17800
0233INT8 | LOCKER REPLACEMENT | 0233 | The 30 existing lockers in the gymnasium are reaching the end of their useful life and should be scheduled for replacement when sports are reintroduced to the school. This project would provide for the removal and disposal of the existing lockers and installation of new lockers. An 18"x15"x72" steel, baked enamel locker was used for this estimate. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | GYMNASIUM | 9938 | HHS | DCFS | NYTC | Elko | 1976 | 15316 | 2013-09-18 | Four to Ten Years | Long-Term Needs | 3 | 15000
0232SFT3 | PAINT BOOTH REPLACEMENT | 0232 | The building has a paint room which is used by the wood shop, automotive repair shop and various other uses. The equipment is antiquated and obsolete and is not presently used. This project provides funding to remodel the paint booth/ room in order to bring it up to current standards, including necessary electrical, egress and OSHA upgrades. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | INDUSTRIAL/VOCATIONAL | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 11264 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0231HVA3 | HEATING SYSTEM REPLACEMENT | 0231 | The existing steam boiler, burner, air handler, pumps and fan coils throughout the building are original equipment and they have reached the end of their expected life. The air handler pneumatics do not work and replacement parts are no longer available. This project would provide for the removal of this equipment and the purchase and installation of a new steam or hot water boiler heating system. This project or a portion thereof was previously recommended in the FCA report dated 08/23/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | CLASSROOMS & INFIRMARY | 9938 | HHS | DCFS | NYTC | Elko | 1972 | 20590 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 200000
0232SFT8 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0232 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | INDUSTRIAL/VOCATIONAL | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 11264 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 15000
0232INT1 | INTERIOR DOOR REPLACEMENT | 0232 | The interior doors in this building are hollow core wood units and are damaged from general wear and tear. This project would provide for the installation of new solid core metal interior doors including frames, lever action door handles, hardware and paint. Removal and disposal of the existing doors is included in this cost estimate. A total of 10 interior doors was used in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | INDUSTRIAL/VOCATIONAL | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 11264 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
0232SFT2 | FIRE SUPPRESSION SYSTEM REPLACEMENT | 0232 | This building has an outdated fire suppression system. The sprinkler heads appear to be a model that have been recalled, and the system will need to be replaced. Costs are estimated for complete system replacement, as the new design may require replacement of uprights, pipe and controls. This project recommends replacing the existing system and implementing a comprehensive testing and service schedule to prevent problems from occurring in the future. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | INDUSTRIAL/VOCATIONAL | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 11264 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 157696
0232ENR2 | LIGHTING UPGRADE | 0232 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, closets and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | INDUSTRIAL/VOCATIONAL | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 11264 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16896
0233ADA2 | EXTERIOR DOOR REPLACEMENT | 0233 | The entrances to the building are a mix of single leaf and double leaf commercial grade metal door assemblies and a storefront entrance system at the main entrance. None of these are ADA compliant. The doors and frames are old damaged and are in need of replacement. This project would provide for the installation of new metal door assemblies with lever-operated hardware and a new storefront entrance system complete with all required ADA accessible hardware. Painting of the new doors and removal and disposal of the old doors is included in this estimate. 10 doors were used for this estimate. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | GYMNASIUM | 9938 | HHS | DCFS | NYTC | Elko | 1976 | 15316 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 60000
0232PLM3 | WATER HEATER REPLACEMENT | 0232 | There is a 65 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new natural gas-fired water heater be installed for more efficient use of energy. This estimate includes: 100 feet of gas pipe, fittings, couplers, and labor for installation. Removal and disposal of the existing equipment is included in this estimate. | INDUSTRIAL/VOCATIONAL | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 11264 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
0233SFT3 | OCCUPANT LOAD SIGNAGE | 0233 | The 2012 IBC Chapter 1004.3 states that an assembly occupancies shall have the occupant load of the room or space posted in a conspicuous place, near the main exit or exit access doorway from the room or space. The gymnasium meets this criteria. This project provides for creating and installing compliant signage for the gymnasium. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | GYMNASIUM | 9938 | HHS | DCFS | NYTC | Elko | 1976 | 15316 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 1500
0232ENV1 | DUST COLLECTION SYSTEM REPLACEMENT | 0232 | The building has a woodshop which has an inoperative dust collection system. The existing exhaust fan is undersized for the equipment being used. This project recommends the replacement of the dust collection system with a higher capacity system, including the fan, motor and ducting to each piece of equipment. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | INDUSTRIAL/VOCATIONAL | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 11264 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0232SFT7 | VEHICLE EXHAUST EXTRACTION SYSTEM | 0232 | The vehicle maintenance garage has an exhaust extraction system that is no longer functioning. Table 403.7 in the 2012 Uniform Mechanical Code states that "Auto repair rooms where engines are run shall have exhaust systems that directly connect to the engine exhaust and prevent escape of fumes". This project would provide for the purchase and installation of a vehicle exhaust extraction system including, hoses, automatic shut off, electrical connections and roof mounted exhaust fans and equipment as provided by the manufacturer. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | INDUSTRIAL/VOCATIONAL | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 11264 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 100000
0232ADA1 | ADA RESTROOM UPGRADE | 0232 | The four restrooms in the building are original to the building and in overall poor condition. The finishes, fixtures, cabinets, toilets, showers and exhaust fans are showing signs of wear and deterioration and none of them meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit of each restroom is necessary. This project would provide funding for construction of four unisex accessible restrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | INDUSTRIAL/VOCATIONAL | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 11264 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 60000
0232HVA1 | HVAC EQUIPMENT UPGRADE | 0232 | The existing HVAC system consists of a closed loop hot water system served by a boiler and several evaporative coolers. The boiler and water treatment systems are in good condition. Several ceiling mounted heating units are not operational due to missing parts and they have reached the end of their expected life. There are also several evaporative coolers that are not working or are in need of replacement. This project would provide for replacing all of the heating units and evaporative coolers. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | INDUSTRIAL/VOCATIONAL | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 11264 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 67584
0232PLM2 | HOSE BIBB REPLACEMENT | 0232 | The hose bibbs on the exterior of the building have not stood up to the winter climate. They are broken and are no longer in use. This report recommends replacing six exterior hose bibbs with freeze-proof wall hydrants. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | INDUSTRIAL/VOCATIONAL | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 11264 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
0232EXT6 | SKYLIGHT REPLACEMENT | 0232 | There are ten 6’x6’ acrylic sky-lights located on the roof. Several of the units are allowing water to penetrate inside during rain or snow events. This project would provide for the removal, disposal and replacement of ten acrylic skylight units. Minor roof repairs are included in this estimate. | INDUSTRIAL/VOCATIONAL | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 11264 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 40000
0232EXT4 | EXTERIOR DOOR REPLACEMENT | 0232 | The entrances to the shop areas in the building are single leaf, commercial grade metal door assemblies. The 6 doors and frames are old and damaged and are in need of replacement. This project would provide for the installation of new metal doors, frames and lever-operated hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | INDUSTRIAL/VOCATIONAL | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 11264 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24000
0233ENR2 | LIGHTING UPGRADE | 0233 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade T-12 lamps to T-8 lamps with electronic ballasts and upgrade the HID (high intensity discharge) lamps to current standards, resulting in increased efficiency and reduced costs associated with illumination and HVAC load. Occupancy sensors will be installed in restrooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | GYMNASIUM | 9938 | HHS | DCFS | NYTC | Elko | 1976 | 15316 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 22974
0233ADA5 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0233 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | GYMNASIUM | 9938 | HHS | DCFS | NYTC | Elko | 1976 | 15316 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 4000
0233ENR1 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0233 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | GYMNASIUM | 9938 | HHS | DCFS | NYTC | Elko | 1976 | 15316 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 5000
0232EXT2 | EXTERIOR FINISHES | 0232 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | INDUSTRIAL/VOCATIONAL | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 11264 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 56320
0232INT2 | INTERIOR FINISHES | 0232 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | INDUSTRIAL/VOCATIONAL | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 11264 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 56320
0231ADA1 | ADA RESTROOM UPGRADE | 0231 | The Men's and Women's designated ADA restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for remodeling the Men's and Women's restrooms into ADA compliant restrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 08/23/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | CLASSROOMS & INFIRMARY | 9938 | HHS | DCFS | NYTC | Elko | 1972 | 20590 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 100000
0232EXT5 | OVERHEAD DOOR REPLACEMENT | 0232 | There are eight 12'x12' overhead doors which are damaged and do not function properly. Exposure and wind have caused the doors to bend, crack and lose their finish. They are original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead coiling doors and replacement with new manually operated overhead coiling doors. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | INDUSTRIAL/VOCATIONAL | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 11264 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 40000
0232SFT6 | SAFETY CABINETS | 0232 | The building contains many different paints, stains, pesticides, liquid gases and other hazardous products on open shelves and on the floor. This does not meet OSHA standards for hazardous materials containment. This project would provide two hazardous storage containers in the building and install placards on the building exterior in accordance with OSHA 1910.106 (d). This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | INDUSTRIAL/VOCATIONAL | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 11264 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 1000
0615EXT3 | ROOF REPLACEMENT | 0615 | The standing seam metal roof on this building was in poor condition at the time of the survey and had at least one active leak. It is recommended that this building be re-roofed in the next 2-3 years with a new single-ply roofing system which will be installed directly over the existing metal roof. This will allow the roof to qualify for the statewide roofing program warranty and preventative maintenance agreement. | WAREHOUSE | 9938 | HHS | DCFS | NYTC | Elko | 1988 | 7240 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 86880
0615SFT5 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0615 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. | WAREHOUSE | 9938 | HHS | DCFS | NYTC | Elko | 1988 | 7240 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 3620
0615SFT4 | EXTERIOR STAIR HANDRAIL REPLACEMENT | 0615 | The exterior stair handrails on the concrete stairs are older and do not meet code for safety or accessibility. The gripping surfaces are incorrect and they do not have compliant extensions at the top and bottom of the stair. This project recommends the replacement of the handrails on both sides of the stairs. Removal and disposal of the existing railing is included. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 08/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | WAREHOUSE | 9938 | HHS | DCFS | NYTC | Elko | 1988 | 7240 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 5000
0615EXT1 | EXTERIOR FINISHES | 0615 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 08/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | WAREHOUSE | 9938 | HHS | DCFS | NYTC | Elko | 1988 | 7240 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 36200
0615INT2 | INTERIOR FINISHES | 0615 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 08/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | WAREHOUSE | 9938 | HHS | DCFS | NYTC | Elko | 1988 | 7240 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 36200
0615PLM1 | HOSE BIBB REPLACEMENT | 0615 | The hose bibbs on the exterior of the building have not stood up to the winter climate. They are broken and are no longer in use. This report recommends replacing 4 exterior hose bibbs with freeze-proof wall hydrants. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | WAREHOUSE | 9938 | HHS | DCFS | NYTC | Elko | 1988 | 7240 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0615INT1 | NONABSORBANT FINISHES | 0615 | 2012 IBC Section 1210 requires the installation of smooth, hard, nonabsorbent surfaces in the following restroom areas: on floors in toilet, bathing and shower rooms that extend upward onto the walls at least 4 inches, within 2 feet of the sides of urinals and water closets to a height of not less than 4 feet above the floor and in shower compartments to a height not less than 70 inches above the drain inlet. Accessories such as grab bars, towel bars, paper dispensers and soap dishes, provided on or within walls, shall be installed and sealed to protect structural elements from moisture. This project recommends the installation of Fiberglass Reinforced Panel (FRP) or an equal material to comply with this code section. This project or a portion thereof was previously recommended in the FCA report dated 08/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | WAREHOUSE | 9938 | HHS | DCFS | NYTC | Elko | 1988 | 7240 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0615PLM2 | WATER HEATER REPLACEMENT | 0615 | There is a 10 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new on-demand electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | WAREHOUSE | 9938 | HHS | DCFS | NYTC | Elko | 1988 | 7240 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0615HVA2 | HVAC EQUIPMENT REPLACEMENT | 0615 | The existing HVAC system consists of 2 ceiling mounted packaged units located above the walk-in cooler and freezer. These provide heat to the warehouse and cooling to the freezers and refrigerators, but do not provide cooling to the warehouse. There is a need for cooling equipment to provide a comfortable work environment in the summer. This project would provide for removal and replacement of the 2 HVAC packaged units to provide heating and air conditioning to the warehouse. This project or a portion thereof was previously recommended in the FCA report dated 08/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | WAREHOUSE | 9938 | HHS | DCFS | NYTC | Elko | 1988 | 7240 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
0615ENR2 | LIGHTING UPGRADE | 0615 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, closets and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | WAREHOUSE | 9938 | HHS | DCFS | NYTC | Elko | 1988 | 7240 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10860
0615SIT1 | ROOF DRAIN DOWNSPOUT MODIFICATIONS | 0615 | The roof drain downspouts currently terminate within inches of the building with no continuous drainage away from the foundation. This is causing the water to pool next to the foundation and damage the foundation and walls. This project would provide for the extension of the roof drains from the downspouts to approximately 5'-0" away from the perimeter of the building to prevent pooling and damage to the building. | WAREHOUSE | 9938 | HHS | DCFS | NYTC | Elko | 1988 | 7240 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0615ENR3 | ROLLUP DOOR REPLACEMENT | 0615 | The existing 10'x12' rollup door does not function properly due to age and abuse and repair parts are difficult to find. It is also uninsulated and not energy efficient. This project would provide for the removal and disposal of the existing door and the purchase and installation of a new manually operated insulated rollup door. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | WAREHOUSE | 9938 | HHS | DCFS | NYTC | Elko | 1988 | 7240 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0535ENR2 | LIGHTING UPGRADE | 0535 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, utility closets and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | ADVENTURER COTTAGE | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 3990 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5985
0535EXT3 | EXTERIOR DOOR REPLACEMENT | 0535 | The exterior metal door at the rear of the building is damaged from age and general wear and tear and has reached the end of its expected life. This project would provide for the replacement of the door assembly with new a metal door, frame and hardware. Removal and disposal of the existing door is included in this estimate. | ADVENTURER COTTAGE | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 3990 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0535SIT1 | REMOVE SPRINKLERED LAWN WITHIN 3' OF BUILDING | 0535 | The building has considerable damage to the painted CMU from lawn sprinklers wetting the exterior walls. This project would create drip irrigated planters within three feet of the building and relocate sprinklers so they do not wet the building. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | ADVENTURER COTTAGE | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 3990 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0535INT1 | KITCHEN REPLACEMENT | 0535 | The kitchen equipment and cabinets were replaced in the building in the mid 1990s. At the time of the survey, the stovetop, oven and refrigerator were not operating. The quality of construction and installation were inadequate for the high usage at these facilities, and the cabinets and counter tops are delaminating and failing. This project recommends the replacement of the existing kitchen counters, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. This estimate includes disposal of the existing materials. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | ADVENTURER COTTAGE | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 3990 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0535ENR3 | EXTERIOR ENERGY RETROFIT | 0535 | The building is constructed of concrete masonry units (CMU) with no insulation. The windows are original to the building, and of single pane construction. Buildings of this type are not energy efficient. This project recommends adding an exterior insulating finish system (EIFS) over the CMU and replacing the windows with new dual-pane, higher efficiency units. This estimate includes removal and disposal of the existing windows. The estimate is based on $10.00 per square foot for the EIFS, $1000.00 per window for 11 windows and $15,000 for the aluminum storefront entrance system. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | ADVENTURER COTTAGE | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 3990 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 65900
0535PLM1 | RESTROOM FIXTURES REPLACEMENT | 0535 | The sink faucets and shower valves were replaced in 1995. The systems installed have not held up well under the high usage typical in a building of this type, and are beginning to fail. This project recommends replacing the faucets and shower mixing control valves with heavy duty rated commercial grade units and includes disposal of the existing fixtures. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | ADVENTURER COTTAGE | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 3990 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12500
0535ENR1 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0535 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | ADVENTURER COTTAGE | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 3990 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0535EXT2 | EXTERIOR FINISHES | 0535 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | ADVENTURER COTTAGE | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 3990 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19950
0535HVA2 | EXHAUST FAN REPLACEMENT | 0535 | The exhaust fans in the showers and restroom areas are inadequate for their application contributing to moisture accumulation and possible mold infiltration. This project would provide for the removal of the existing exhaust fan assemblies and the purchase and installation of new exhaust fan assemblies including ducting and connections to utilities. This report recommends the installation of high efficiency exhaust fans with humidity detection and delayed shut-off to exhaust all moisture and prevent future accumulation issues. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | ADVENTURER COTTAGE | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 3990 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0535INT2 | INTERIOR FINISHES | 0535 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | ADVENTURER COTTAGE | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 3990 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19950
0535ADA1 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0535 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | ADVENTURER COTTAGE | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 3990 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 4000
2428INT2 | INTERIOR FINISHES | 2428 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 6-7 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | ADMINISTRATION & EDUCATION | 9908 | HHS | DCFS | SVYCC | North Las Vegas | 2000 | 27782 | 2014-01-28 | Four to Ten Years | Long-Term Needs | 3 | 138910
2429SEC3 | DOORS, LOCKS AND MECHANISMS REPLACEMENT | 2429 | Housing Unit #1 was constructed in 2000. The sleeping room doors, controls, locks and mechanisms are original to the building and have been problematic due to wear and tear, abuse and age. This project would provide for installing new sleeping room doors, locks and mechanisms. A total of 48 doors was used for this estimate. Removal and disposal of the existing equipment is included in this estimate. | HOUSING UNIT #1 - SIERRA | 9908 | HHS | DCFS | SVYCC | North Las Vegas | 2000 | 10454 | 2014-01-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 600000
2429EXT3 | ROOF REPLACEMENT | 2429 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2000. It is recommended that this building be re-roofed in the next 4-5 years to be consistent with the roofing program and the end of the warranty period. | HOUSING UNIT #1 - SIERRA | 9908 | HHS | DCFS | SVYCC | North Las Vegas | 2000 | 10454 | 2014-01-28 | Four to Ten Years | Long-Term Needs | 3 | 181200
2428EXT3 | EXTERIOR FINISHES | 2428 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 7-8 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | ADMINISTRATION & EDUCATION | 9908 | HHS | DCFS | SVYCC | North Las Vegas | 2000 | 27782 | 2014-01-28 | Four to Ten Years | Long-Term Needs | 3 | 138910
2428ADA1 | ADA SIGNAGE | 2428 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | ADMINISTRATION & EDUCATION | 9908 | HHS | DCFS | SVYCC | North Las Vegas | 2000 | 27782 | 2014-01-28 | Immediate to Two Years | Currently Critical | 1 | 3750
2428ADA2 | ADA DINING UPGRADE | 2428 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. There are two small dining rooms in the building for the residents. The tables in the dining rooms do not provide an accessible place to sit. This project would provide for installing an accessible dining seat in each of the two dining rooms. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards For Accessible Design should be incorporated into the design. | ADMINISTRATION & EDUCATION | 9908 | HHS | DCFS | SVYCC | North Las Vegas | 2000 | 27782 | 2014-01-28 | Immediate to Two Years | Currently Critical | 1 | 2500
2429PLM1 | WATER HEATER REPLACEMENT | 2429 | There is a 100 gallon gas-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | HOUSING UNIT #1 - SIERRA | 9908 | HHS | DCFS | SVYCC | North Las Vegas | 2000 | 10454 | 2014-01-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
2428EXT4 | ROOF REPLACEMENT | 2428 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2000. It is recommended that this building be re-roofed in the next 4-5 years to be consistent with the roofing program and the end of the warranty period. | ADMINISTRATION & EDUCATION | 9908 | HHS | DCFS | SVYCC | North Las Vegas | 2000 | 27782 | 2014-01-28 | Four to Ten Years | Long-Term Needs | 3 | 333384
2430INT1 | INTERIOR FINISHES | 2430 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 06/08/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/28/2014. | HOUSING UNIT #2 - EVEREST | 9908 | HHS | DCFS | SVYCC | North Las Vegas | 2000 | 10454 | 2014-01-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 75500
2428ELE1 | CLOTHES DRYER REPLACEMENT | 2428 | The two commercial tumbler dryers in the laundry are original to the building and are troublesome and problematic to operate. Considering the age of the machines and the evolving needs of the facility it is recommended to replace them. This project provides for removal and disposal of the existing tumbler dryers and replacement with two new units. | ADMINISTRATION & EDUCATION | 9908 | HHS | DCFS | SVYCC | North Las Vegas | 2000 | 27782 | 2014-01-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
2428ENR1 | HVAC EQUIPMENT REPLACEMENT | 2428 | The HVAC system was installed in 2000 and is original to the building. It consists of 21 rooftop packaged units with natural gas-fired furnaces and air conditioners utilizing R-22 coolant. The system is not energy efficient and has reached the end of its expected and useful life. The R-22 coolant is no longer allowable for cooling. This project would provide for installation of a new HVAC system and cleaning of the existing duct work and grilles. The new system shall be designed to significantly reduce electrical and natural gas usage in order to comply with the 2009 IECC and ASHRAE 90.1 and to reduce utility costs. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | ADMINISTRATION & EDUCATION | 9908 | HHS | DCFS | SVYCC | North Las Vegas | 2000 | 27782 | 2014-01-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 416830
2431INT1 | INTERIOR FINISHES | 2431 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 5-6 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | GYMNASIUM | 9908 | HHS | DCFS | SVYCC | North Las Vegas | 2000 | 7773 | 2014-01-28 | Four to Ten Years | Long-Term Needs | 3 | 39865
2432ENR1 | HVAC REPLACEMENT | 2432 | The existing HVAC system consists of ceiling mounted natural gas fired heaters and wall mounted evaporative coolers. The system is inefficient, does not provide enough heating or cooling and should be scheduled for replacement. This project would provide for replacing the existing system. The new system shall be designed to significantly reduce electrical and natural gas usage in order to comply with the 2009 IECC and ASHRAE 90.1 and to reduce utility costs. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | WAREHOUSE/MAINTENANCE SHOP | 9908 | HHS | DCFS | SVYCC | North Las Vegas | 2000 | 3750 | 2014-01-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 22500
2432SIT1 | DOCK LIFT REPLACEMENT | 2432 | The 10,000 pound capacity scissor dock lift is damaged from age and general wear and tear and has reached the end of its expected life. Staff reported that the lift has not been operable in over 7 years and that additional fees are added to deliveries to compensate for the lack of a dock lift. This project would provide for the replacement of the lift with a new dock lift for deliveries. Removal and disposal of the existing lift is included in this estimate. It may be possible to repair the existing lift or replace parts on the existing lift to save costs. | WAREHOUSE/MAINTENANCE SHOP | 9908 | HHS | DCFS | SVYCC | North Las Vegas | 2000 | 3750 | 2014-01-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
2432EXT3 | OVERHEAD DOOR REPAIRS | 2432 | The (2) 10'x10' overhead doors are showing signs of wear and tear and are due for maintenance. The cables are fraying and the pulleys and other hardware are worn. This project would provide for the inspection and maintenance of the doors including replacing the springs, cables and rollers, greasing the hardware and replacing any other parts as necessary. | WAREHOUSE/MAINTENANCE SHOP | 9908 | HHS | DCFS | SVYCC | North Las Vegas | 2000 | 3750 | 2014-01-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
2432INT2 | INTERIOR FINISHES | 2432 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 06/08/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/28/2014. | WAREHOUSE/MAINTENANCE SHOP | 9908 | HHS | DCFS | SVYCC | North Las Vegas | 2000 | 3750 | 2014-01-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18750
2432EXT2 | EXTERIOR FINISHES | 2432 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 06/08/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/28/2014. | WAREHOUSE/MAINTENANCE SHOP | 9908 | HHS | DCFS | SVYCC | North Las Vegas | 2000 | 3750 | 2014-01-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3750
2430EXT2 | EXTERIOR FINISHES | 2430 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units, painting the metal trim and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 7-8 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT #2 - EVEREST | 9908 | HHS | DCFS | SVYCC | North Las Vegas | 2000 | 10454 | 2014-01-28 | Four to Ten Years | Long-Term Needs | 3 | 75500
2431ENR1 | HVAC REPLACEMENT | 2431 | The existing HVAC system consists of ceiling mounted natural gas fired heaters and wall mounted evaporative coolers. The system is inefficient, does not provide enough heating or cooling and should be scheduled for replacement. This project would provide for replacing the existing system. The new system shall be designed to significantly reduce electrical and natural gas usage in order to comply with the 2009 IECC and ASHRAE 90.1 and to reduce utility costs. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | GYMNASIUM | 9908 | HHS | DCFS | SVYCC | North Las Vegas | 2000 | 7773 | 2014-01-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 47838
2429INT2 | INTERIOR FINISHES | 2429 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 6-7 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HOUSING UNIT #1 - SIERRA | 9908 | HHS | DCFS | SVYCC | North Las Vegas | 2000 | 10454 | 2014-01-28 | Four to Ten Years | Long-Term Needs | 3 | 75500
2430SEC3 | DOORS, LOCKS AND MECHANISMS REPLACEMENT | 2430 | Housing Unit #2 was constructed in 2000. The sleeping room doors, controls, locks and mechanisms are original to the building and have been problematic due to wear and tear, abuse and age. This project would provide for installing new sleeping room doors, locks and mechanisms. A total of 48 doors was used for this estimate. Removal and disposal of the existing equipment is included in this estimate. | HOUSING UNIT #2 - EVEREST | 9908 | HHS | DCFS | SVYCC | North Las Vegas | 2000 | 10454 | 2014-01-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 600000
2430PLM1 | WATER HEATER REPLACEMENT | 2430 | There is a 100 gallon gas-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | HOUSING UNIT #2 - EVEREST | 9908 | HHS | DCFS | SVYCC | North Las Vegas | 2000 | 10454 | 2014-01-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
2430ENR1 | HVAC REPLACEMENT | 2430 | The six HVAC roof top units were installed in 2000. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for purchasing and installing six new HVAC packaged units and cleaning of the existing duct work and grilles. The new system shall be designed to significantly reduce electrical and natural gas usage in order to comply with the 2009 IECC and ASHRAE 90.1 and to reduce utility costs. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | HOUSING UNIT #2 - EVEREST | 9908 | HHS | DCFS | SVYCC | North Las Vegas | 2000 | 10454 | 2014-01-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 226500
2430EXT3 | ROOF REPLACEMENT | 2430 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2000. It is recommended that this building be re-roofed in the next 4-5 years to be consistent with the roofing program and the end of the warranty period. | HOUSING UNIT #2 - EVEREST | 9908 | HHS | DCFS | SVYCC | North Las Vegas | 2000 | 10454 | 2014-01-28 | Four to Ten Years | Long-Term Needs | 3 | 181200
2429ENR1 | HVAC REPLACEMENT | 2429 | The six HVAC roof top units were installed in 2000. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for purchasing and installing six new HVAC packaged units and cleaning of the existing duct work and grilles. The new system shall be designed to significantly reduce electrical and natural gas usage in order to comply with the 2009 IECC and ASHRAE 90.1 and to reduce utility costs. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | HOUSING UNIT #1 - SIERRA | 9908 | HHS | DCFS | SVYCC | North Las Vegas | 2000 | 10454 | 2014-01-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 226500
2429EXT2 | EXTERIOR FINISHES | 2429 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units, painting the metal trim and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 7-8 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT #1 - SIERRA | 9908 | HHS | DCFS | SVYCC | North Las Vegas | 2000 | 10454 | 2014-01-28 | Four to Ten Years | Long-Term Needs | 3 | 75500
2431EXT2 | EXTERIOR FINISHES | 2431 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units, painting the metal trim and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 7-8 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | GYMNASIUM | 9908 | HHS | DCFS | SVYCC | North Las Vegas | 2000 | 7773 | 2014-01-28 | Four to Ten Years | Long-Term Needs | 3 | 39865
2428INT3 | FLOORING REPLACEMENT | 2428 | The VCT (vinyl composite tile) and carpet in the building are in fair condition. It is recommended that the flooring is scheduled for replacement. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the next 7-8 years. | ADMINISTRATION & EDUCATION | 9908 | HHS | DCFS | SVYCC | North Las Vegas | 2000 | 27782 | 2014-01-28 | Four to Ten Years | Long-Term Needs | 3 | 104000
9908SIT3 | SLURRY SEAL ASPHALT PAVING | 9908 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site wide including access roads, parking areas and the maintenance yard. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 65,000 square feet of asphalt area was used to generate this estimate. This project or a portion thereof was previously recommended in the FCA report dated 06/08/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/28/2014. | SUMMIT VIEW YOUTH CORRECTIONAL CENTER | 9908 | HHS | DCFS | SVYCC | North Las Vegas | 2000 |  | 2014-01-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 48750
9908ADA1 | ADA PARKING SIGNS | 9908 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The parking signage does not comply with this criteria and there is no directional signage to the building entrance. This project would provide funding for purchase and installation of ADA signage including new parking signs and directional signage from parking to accessible building entrances. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | SUMMIT VIEW YOUTH CORRECTIONAL CENTER | 9908 | HHS | DCFS | SVYCC | North Las Vegas | 2000 |  | 2014-01-28 | Immediate to Two Years | Currently Critical | 1 | 2500
9908SEC1 | PERIMETER FENCE REPAIRS | 9908 | The chain link perimeter fence currently has an anti-climb mesh attached to it. The anti-climb mesh is not strong enough for this application and is due for replacement. Staff reported that the wind blows it off of the fence and that a heavier material would be more secure. This project would provide for removing the existing anti-climb mesh and replacing it with a heavier material with stronger attachments. | SUMMIT VIEW YOUTH CORRECTIONAL CENTER | 9908 | HHS | DCFS | SVYCC | North Las Vegas | 2000 |  | 2014-01-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
9908SIT1 | DRY WELL INSTALLATION | 9908 | West of the Administration building, storm water runoff does not drain properly and pools up next to the curb and sidewalk. It is recommended to install a dry well to collect and dispose of the water. This project provides for installing a concrete dry well with a silt basin on the west side of the Administration building to mitigate the drainage problem. | SUMMIT VIEW YOUTH CORRECTIONAL CENTER | 9908 | HHS | DCFS | SVYCC | North Las Vegas | 2000 |  | 2014-01-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12500
9908ADA2 | ADA ACCESSIBLE PATH OF TRAVEL | 9908 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. Currently, the path of travel from the entrance gate to the entrance door of the Administration building exceeds 5% in several places and does not have a compliant landing at the door. A compliant path of travel is necessary to comply with ADA accessibility requirements. This will require removing the existing concrete walkway, regrading, placement of P.C. concrete, signage, and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. 700 square feet of concrete was used for this estimate. | SUMMIT VIEW YOUTH CORRECTIONAL CENTER | 9908 | HHS | DCFS | SVYCC | North Las Vegas | 2000 |  | 2014-01-28 | Immediate to Two Years | Currently Critical | 1 | 12500
9908ENR1 | EXTERIOR SOLAR SITE LIGHTING UPGRADE | 9908 | The existing site lighting is over 13 years old and the equipment is beginning to fail. A common problem that would need to be addressed is wires fraying and shorting out due to age and rubbing against the inside of the poles. This project would provide for the installation of 25 solar powered LED exterior light fixtures, 20 foot tall poles and 30" diameter raised concrete bases. This installation will eliminate the need for trenching and electrical connections. Some of the existing poles may be acceptable to re-use. If so, the estimate can be reduced accordingly. | SUMMIT VIEW YOUTH CORRECTIONAL CENTER | 9908 | HHS | DCFS | SVYCC | North Las Vegas | 2000 |  | 2014-01-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 162500
2508EXT1 | EXTERIOR FINISHES | 2508 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units, painting the stucco and metal trim and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | RAWSON-NEAL HOSPITAL BUILDING 1 | 9894 | HHS | DPBH | SNAMHS | Las Vegas | 2006 | 61938 | 2015-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 309690
2508PLM1 | WATER HEATER REPLACEMENT | 2508 | There is a 100 gallon natural gas-fired water heater in the building that was installed in 2006. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | RAWSON-NEAL HOSPITAL BUILDING 1 | 9894 | HHS | DPBH | SNAMHS | Las Vegas | 2006 | 61938 | 2015-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
2508ADA1 | ADA EMPLOYEE LOUNGE UPGRADES | 2508 | The employee lounge does not meet the Americans with Disabilities Act (ADA) requirements. It is recommended to upgrade some of the features of the room for compliance with accessibility standards for employees. This project would provide funding for construction of an accessible sink and faucet, an accessible space at one of the dining tables and an accessible path of travel throughout the room. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | RAWSON-NEAL HOSPITAL BUILDING 1 | 9894 | HHS | DPBH | SNAMHS | Las Vegas | 2006 | 61938 | 2015-03-17 | Immediate to Two Years | Currently Critical | 1 | 2000
2508INT2 | RESTROOM REMODELS | 2508 | The 7 restrooms in the client living areas are original to the building and in overall poor condition. The finishes, fixtures, cabinets, toilets, showers and exhaust fans are showing signs of wear and deterioration. The original ceramic water closets pose a safety hazard and should be replaced with stainless steel fixtures. There is also a need for anti-ligature fixtures including the faucets. This project would provide for a complete remodel of the restrooms. The removal and disposal of the existing fixtures and finishes is included in this estimate. | RAWSON-NEAL HOSPITAL BUILDING 1 | 9894 | HHS | DPBH | SNAMHS | Las Vegas | 2006 | 61938 | 2015-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 105000
2508INT1 | INTERIOR FINISHES | 2508 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | RAWSON-NEAL HOSPITAL BUILDING 1 | 9894 | HHS | DPBH | SNAMHS | Las Vegas | 2006 | 61938 | 2015-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 309690
2510EXT1 | EXTERIOR FINISHES | 2510 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units, painting the stucco and metal trim and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | RAWSON-NEAL HOSPITAL BUILDING 2 | 9894 | HHS | DPBH | SNAMHS | Las Vegas | 2006 | 54146 | 2015-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 270730
2510INT2 | RESTROOM REMODELS | 2510 | The 12 restrooms in the client living areas are original to the building and in overall poor condition. The finishes, fixtures, cabinets, toilets, showers and exhaust fans are showing signs of wear and deterioration. The original ceramic water closets pose a safety hazard and should be replaced with stainless steel fixtures. There is also a need for anti-ligature fixtures including the faucets. This project would provide for a complete remodel of the restrooms. The removal and disposal of the existing fixtures and finishes is included in this estimate. | RAWSON-NEAL HOSPITAL BUILDING 2 | 9894 | HHS | DPBH | SNAMHS | Las Vegas | 2006 | 54146 | 2015-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 180000
2510INT1 | INTERIOR FINISHES | 2510 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | RAWSON-NEAL HOSPITAL BUILDING 2 | 9894 | HHS | DPBH | SNAMHS | Las Vegas | 2006 | 54146 | 2015-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 270730
9894SIT1 | CRACK FILL & SEAL ASPHALT PAVING | 9894 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the paving site wide including access roads and parking areas. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 164,000 square feet of asphalt area was used to generate this estimate. | RAWSON-NEAL PSYCHIATRIC HOSPITAL SITE | 9894 | HHS | DPBH | SNAMHS | Las Vegas | 2006 |  | 2015-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 98400
9894ENR1 | EXTERIOR SOLAR SITE LIGHTING UPGRADE | 9894 | There are approximately 16 existing light poles around the site with sodium halide fixtures. The older fixtures are not energy efficient and are due for an upgrade to a higher efficiency unit with a longer life cycle. This project would provide for the installation of 16 solar powered LED exterior light fixtures on the existing poles. | RAWSON-NEAL PSYCHIATRIC HOSPITAL SITE | 9894 | HHS | DPBH | SNAMHS | Las Vegas | 2006 |  | 2015-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 40000
9894SIT3 | STORAGE BUILDING INSTALLATION | 9894 | There is a major lack of storage on the site to support the various functions conducted by the facility. The Snack Bar is used exclusively as a storage space for the facility maintenance and janitorial personnel. Items stored here include paper goods, light bulbs, cleaning supplies, medical supplies and medical equipment. There is not enough storage space anywhere else in the building for these items. This project would provide for the purchase and installation of a 40' x 60' engineered steel building on a concrete foundation including connection to the existing electrical, water, sewer and propane services. | RAWSON-NEAL PSYCHIATRIC HOSPITAL SITE | 9894 | HHS | DPBH | SNAMHS | Las Vegas | 2006 |  | 2015-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 84000
9894ADA1 | ADA PARKING SIGNAGE | 9894 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The 4 accessible parking areas on the south and east sides of the building are missing proper signage and striping to comply with ADA requirements. This project would provide for striping, signage and any other necessary upgrades to the parking spaces. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | RAWSON-NEAL PSYCHIATRIC HOSPITAL SITE | 9894 | HHS | DPBH | SNAMHS | Las Vegas | 2006 |  | 2015-03-17 | Immediate to Two Years | Currently Critical | 1 | 6000
9894SIT2 | GATE OPERATOR REPLACEMENT | 9894 | The site has a secured access gate for ambulances and other secured deliveries or pick ups. The hydraulic gate operator is 10 years old and has difficulty opening and closing the gates. This project recommends replacing the hydraulic swing gate operator and twin posts with a similar high quality operator as well as servicing the gates and related hardware to ensure prolonged operation. The gate operators will be required to meet UL Standard 325, per NRS 405.270. | RAWSON-NEAL PSYCHIATRIC HOSPITAL SITE | 9894 | HHS | DPBH | SNAMHS | Las Vegas | 2006 |  | 2015-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 45000
2001ADA4 | ADA RESTROOM UPGRADE | 2001 | The building does not have an accessible restroom. The existing restroom does not meet the ADA requirements. A complete retrofit is necessary. This project would provide funding for remodeling the Men's and Women's restrooms per ADA regulations. Items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | CYC SCHOOL - NEW | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 22000 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 40000
2001SFT1 | EXTERIOR LANDING INSTALLATION | 2001 | There are two out-swinging exterior doors on the building. These doors swing out over a step that does not have a landing. This does not comply with 2012 IBC Section 1008.1 which requires a proper landing and for the landing to not be more than 1/2" below the threshold. This project would provide for the installation of compliant landings. | CYC SCHOOL - NEW | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 22000 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
2001ADA3 | BREAK ROOM REMODEL | 2001 | The kitchenette and associated cabinets in the employee break room are original to the building. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and countertops are delaminating and failing. This project recommends the replacement of the existing kitchen countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards for Accessible Design should be incorporated into the design such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. | CYC SCHOOL - NEW | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 22000 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 15000
2001SFT2 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 2001 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CYC SCHOOL - NEW | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 22000 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 9000
2001EXT3 | OVERHEAD DOOR REPLACEMENT | 2001 | There is an 8'x8' overhead coiling door on the building which is damaged and does not function properly. It is original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead coiling door and replacement with a new manually operated overhead coiling door. Removal and disposal of the existing door is included in this estimate. | CYC SCHOOL - NEW | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 22000 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7000
2001SIT1 | SITE DRAINAGE UPGRADES | 2001 | The grade does not slope away effectively from the buildings. Water has pooled against the foundation. In the winter months, as the water freezes against the foundation, over time, this can cause damage to the foundation. It is recommended per IBC 1804.3 Site Grading the ground immediately adjacent to the foundation shall be sloped away from the building at a slope of not less than one vertical in 20 units horizontal (5-percent slope) for a minimum distance of 10 feet (3048 mm) measured perpendicular to the face of the wall. This project would create a 5% slope away from the buildings. Additional drainage swales shall be installed, as needed. It is recommended that the grading be completed within 2-3 years. | CYC SCHOOL - NEW | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 22000 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
2001EXT4 | EXTERIOR DOOR REPLACEMENT | 2001 | The existing exterior metal doors and frames appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement and installation of eight new metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | CYC SCHOOL - NEW | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 22000 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24000
2001HVA4 | EXHAUST FAN REPLACEMENT | 2001 | Many of the exhaust fans in the restrooms areas were inoperative and/or damaged at the time of the survey. Due to building code requirements, this project would provide funding for the purchase and installation of high volume commercial exhaust fans. | CYC SCHOOL - NEW | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 22000 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
2001INT3 | SINK INSTALLATION | 2001 | The classroom that teaches silk screening does not have a sink or an area to clean up after the silk screening activities. This project recommends installing a new sink with plumbing for the use and cleanup of the silk screening functions. | CYC SCHOOL - NEW | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 22000 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
2001PLM1 | WATER HEATER REPLACEMENT | 2001 | There is a 119 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is missing proper seismic bracing and an expansion tank. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | CYC SCHOOL - NEW | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 22000 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
2001SFT4 | EXIT SIGN AND EGRESS LIGHTING INSTALLATION | 2001 | The building does not have emergency lighting and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC 2012 Chapter 10 was referenced for this project. | CYC SCHOOL - NEW | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 22000 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 110000
2001ADA1 | ADA SIGNAGE | 2001 | ADA regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with these criteria. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC SCHOOL - NEW | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 22000 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 2500
2001HVA2 | HVAC EQUIPMENT REPLACEMENT | 2001 | The HVAC roof top units were installed in 1994. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of new HVAC packaged units and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing equipment and all required connections to utilities. | CYC SCHOOL - NEW | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 22000 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 550000
2001ENR1 | LIGHTING UPGRADE | 2001 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC SCHOOL - NEW | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 22000 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 176000
2001INT2 | INTERIOR FINISHES | 2001 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC SCHOOL - NEW | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 22000 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 220000
2001EXT1 | EXTERIOR FINISHES | 2001 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. Repairs to the damaged EIFS on the south side of the building should be completed as soon as possible to prevent further damage to the structure. It is recommended that the building be painted and repaired in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC SCHOOL - NEW | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 22000 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 220000
2001ADA2 | ADA UPGRADES | 2001 | The building does not have a designated accessible office and the door handles are not compliant with the ADA. This project would provide for an accessible office area, path of travel throughout the building and ADA compliant lever action door hardware. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADAAG were used as references for this project. | CYC SCHOOL - NEW | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 22000 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 10000
2001EXT5 | WINDOW REPLACEMENT | 2001 | The windows are original, double pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 8 units. Removal and disposal of the existing windows is included in this estimate. | CYC SCHOOL - NEW | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 22000 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
2001HVA3 | AIR CONDITIONER INSTALLATION | 2001 | The server room is not sufficiently cooled by the existing HVAC system. If the room is too warm, the computer equipment will prematurely age and may fail due to overheating. It is recommended to install an air conditioning system in the room to ensure that the temperature is properly regulated. This project would provide for the purchase and installation of an air conditioner including all required connections to existing utilities. | CYC SCHOOL - NEW | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 22000 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
2001SFT3 | PANIC HARDWARE IN ELECTRICAL ROOMS | 2001 | The electrical room with the uninterruptable power supply contains equipment that meets or exceeds 1,200 amps. It is recommended per the 2012 IBC 1008.1.10 that panic and fire exit hardware be installed. This equipment was not required at the time the building was built in 1994, but is suggested in this report as an increased safety measure. It is recommended that this project be completed within 1-2 years. The estimate is based on one door that requires panic hardware. | CYC SCHOOL - NEW | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 22000 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 3000
2943PLM1 | WATER HEATER REPLACEMENT | 2943 | There is a 20 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | CYC RECREATIONAL CENTER | 9950 | HHS | DCFS | CYC | Caliente | 2008 | 3060 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
2166SFT1 | EXTERIOR LANDING INSTALLATION | 2166 | There are two out-swinging exterior doors on the building. These doors swing out over a step that does not have a landing. This does not comply with 2012 IBC Section 1008.1 which requires a proper landing and for the landing to not be more than 1/2" below the threshold. This project would provide for the installation of compliant landings. | CYC GENERATOR BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 300 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
2168INT2 | JANITORS CLOSET REPAIRS | 2168 | The mop sink in the Janitors Closet is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide FRP to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | CYC MAINTENANCE BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 2000 | 6000 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
2168SFT4 | OSHA COMPLIANT LADDER | 2168 | The ladder in the building was constructed in-house and does not comply with OSHA guidelines. This project recommends an OSHA compliant ladder per OSHA 1926.1053 for the interior of the building. | CYC MAINTENANCE BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 2000 | 6000 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 800
2168ENR3 | LIGHTING UPGRADE | 2168 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | CYC MAINTENANCE BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 2000 | 6000 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 48000
2168EXT1 | EXTERIOR FINISHES | 2168 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC MAINTENANCE BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 2000 | 6000 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 60000
2168SFT1 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 2168 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC MAINTENANCE BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 2000 | 6000 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 6000
2168INT1 | INTERIOR FINISHES | 2168 | The interior finishes are in fair condition. About one quarter of the interior has finished gypsum board walls. It is recommended that the interior finished walls be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC MAINTENANCE BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 2000 | 6000 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 60000
2168ENR1 | WINDOW REPLACEMENT | 2168 | The windows are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 2 units. Removal and disposal of the existing windows is included in this estimate. | CYC MAINTENANCE BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 2000 | 6000 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
2168ENR2 | HVAC EQUIPMENT UPGRADE | 2168 | The existing HVAC system consists of ceiling mounted electric heaters and does not have any cooling equipment. The electricity powered heaters are inefficient and should be replaced with propane fired heaters. There is a need for cooling equipment as well to provide a comfortable work environment in the summer. This project would provide for replacing the existing heaters with exterior ground mounted packaged units that provide propane fired heating as well as air conditioning. Propane gas service will be required and is included in the cost. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC MAINTENANCE BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 2000 | 6000 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35000
2168SFT2 | FIRE ALARM SYSTEM INSTALLATION | 2168 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2009 Section 7 and the 2012 International Fire Code. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC MAINTENANCE BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 2000 | 6000 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 24000
2166ELE2 | ELECTRICAL PANEL UNUSED OPENINGS | 2166 | The wiring in the electrical panel has missing breakers and needs to have blanks installed at the unused openings. Per NEC 408.7 Unused Openings. Unused openings for circuit breakers and switches shall be closed using identified closures, or other approved means that provide protection substantially equivalent to the wall of the enclosure. Unused openings create a safety issue during repairs or upgrades. This project would provide for blanks to be installed where the missing breakers are located. | CYC GENERATOR BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 300 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 250
2943EXT1 | EXTERIOR FINISHES | 2943 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC RECREATIONAL CENTER | 9950 | HHS | DCFS | CYC | Caliente | 2008 | 3060 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30600
2166EXT3 | ROOF REPLACEMENT | 2166 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1994. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. | CYC GENERATOR BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 300 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
2943SFT1 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 2943 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC 2012 Chapter 10 was referenced for this project. | CYC RECREATIONAL CENTER | 9950 | HHS | DCFS | CYC | Caliente | 2008 | 3060 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 6120
2166INT1 | INTERIOR FINISHES | 2166 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC GENERATOR BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 300 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
2943EXT2 | WINDOW REPLACEMENT | 2943 | The windows are original, double pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 20 units. Removal and disposal of the existing windows is included in this estimate. | CYC RECREATIONAL CENTER | 9950 | HHS | DCFS | CYC | Caliente | 2008 | 3060 | 2017-03-01 | Four to Ten Years | Long-Term Needs | 3 | 30000
2943ADA1 | ADA RESTROOM UPGRADE | 2943 | The building does not have an accessible restroom. The existing restroom does not meet the ADA requirements. A complete retrofit is necessary. This project would provide funding for remodeling the Men's and Women's restrooms per ADA regulations. Items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as references for this project. | CYC RECREATIONAL CENTER | 9950 | HHS | DCFS | CYC | Caliente | 2008 | 3060 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 40000
2166EXT1 | EXTERIOR FINISHES | 2166 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the vents, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC GENERATOR BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 300 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
2166EXT2 | EXTERIOR DOOR REPLACEMENT | 2166 | The exterior metal doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the double door assembly with new metal doors, frame and hardware. Removal and disposal of the existing doors is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC GENERATOR BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 300 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
2943ENR2 | LIGHTING UPGRADE | 2943 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | CYC RECREATIONAL CENTER | 9950 | HHS | DCFS | CYC | Caliente | 2008 | 3060 | 2017-03-01 | Four to Ten Years | Long-Term Needs | 3 | 24480
2168ADA1 | ADA RESTROOM UPGRADE | 2168 | The men's and women's designated ADA restrooms do not meet the ADA requirements. A complete retrofit is necessary. This project would provide funding for construction of two unisex accessible restrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | CYC MAINTENANCE BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 2000 | 6000 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 25000
2943HVA1 | HVAC EQUIPMENT REPLACEMENT | 2943 | There are 2 packaged HVAC units that are original to the building and should be scheduled for replacement. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of new HVAC packaged units and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | CYC RECREATIONAL CENTER | 9950 | HHS | DCFS | CYC | Caliente | 2008 | 3060 | 2017-03-01 | Four to Ten Years | Long-Term Needs | 3 | 40000
2943ENR1 | OCCUPANCY SENSOR INSTALLATION | 2943 | There are no occupancy sensors installed in the restrooms to control lighting. It is recommended to install sensors in the Men's and Women's restrooms in order to reduce energy costs. This project provides for purchase and installation of 2 sensors. | CYC RECREATIONAL CENTER | 9950 | HHS | DCFS | CYC | Caliente | 2008 | 3060 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
2943INT1 | INTERIOR FINISHES | 2943 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC RECREATIONAL CENTER | 9950 | HHS | DCFS | CYC | Caliente | 2008 | 3060 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30600
2166ELE1 | GFCI OUTLETS | 2166 | The existing receptacle on the outside of the building is a standard duplex receptacle. The 2011 NEC 210.8 requires these locations to have GFCI protection. This project would provide for removing the standard receptacles and installing GFCI receptacles. | CYC GENERATOR BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 300 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 400
3159ELE1 | ELECTRICAL MAINTENANCE | 3159 | The building has at least one electrical panel which is missing the panel cover. This project would provide for the inspection of all electrical devices to repair and/or replacement of missing or damaged panel and device covers. | CYC GREEN HOUSE | 9950 | HHS | DCFS | CYC | Caliente | 2012 | 1800 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 250
9950SFT2 | COMMUNICATIONS SYSTEM UPGRADE | 9950 | This facility is equipped with a communications system which has reached the end of its expected life. The telephone system has had numerous problems including a repeater that was destroyed in a windstorm in 2004. The emergency phones and intercom system have been inoperative since the early 1990's. The system provides paging and phone communications to classrooms and is an integral component of the notification and safety procedures for the classrooms. It is recommended that the entire communication systems be upgraded site wide. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CALIENTE YOUTH CENTER SITE | 9950 | HHS | DCFS | CYC | Caliente | 1962 |  | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 2143624
3078EXT1 | EXTERIOR FINISHES | 3078 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC CURRIE STORAGE SHED | 9950 | HHS | DCFS | CYC | Caliente | 2010 | 96 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 960
9950SIT1 | CRACK FILL & SEAL ASPHALT PAVING | 9950 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site wide including access roads, parking areas and the maintenance yard. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 125,000 square feet of asphalt area was used to generate this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CALIENTE YOUTH CENTER SITE | 9950 | HHS | DCFS | CYC | Caliente | 1962 |  | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 156250
9950SEC1 | SECURITY SYSTEM INSTALLATION | 9950 | The site does not have a security system. This project recommends motion detection, door switches, access control and related items be installed and interfaced with the fire alarm. | CALIENTE YOUTH CENTER SITE | 9950 | HHS | DCFS | CYC | Caliente | 1962 |  | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 640430
9950ENR1 | EXTERIOR SOLAR SITE LIGHTING INSTALLATION | 9950 | There are two pole lights in the parking lot that have reached the end of their expected life and are not energy efficient. This project would provide for the installation of 4 solar powered LED exterior light fixtures, 20 foot tall poles and 30" diameter raised concrete bases. This installation will eliminate the need for trenching and electrical connections. It may be feasible to use the two existing poles and only change out the heads. The estimate should be adjusted accordingly. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CALIENTE YOUTH CENTER SITE | 9950 | HHS | DCFS | CYC | Caliente | 1962 |  | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 26000
9950PLM1 | REPLACE IRRIGATION WATER MAIN | 9950 | The grounds are irrigated via galvanized piping from the well. The piping is original to the site and is increasingly failing resulting in flooding. The age and type of the pipe makes it difficult to repair or replace. This project recommends replacing the existing water main with a Schedule 40 PVC or similar material, and the installation of a back-flow device to protect the well from cross contamination. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CALIENTE YOUTH CENTER SITE | 9950 | HHS | DCFS | CYC | Caliente | 1962 |  | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 100000
9950ADA1 | ADA PATH OF TRAVEL UPGRADES | 9950 | The ADA provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the office are necessary to comply with ADA accessibility requirements. This project would provide for a concrete van accessible ADA parking and loading space and concrete walkway to the existing sidewalk. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. 750 square feet of concrete was used for this estimate. It is recommended that this project coincide with the paving project. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CALIENTE YOUTH CENTER SITE | 9950 | HHS | DCFS | CYC | Caliente | 1962 |  | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 25000
3079EXT1 | EXTERIOR FINISHES | 3079 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC BEOWAWE STORAGE SHED | 9950 | HHS | DCFS | CYC | Caliente | 2010 | 96 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 960
3077EXT1 | EXTERIOR FINISHES | 3077 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC HAMILTON STORAGE SHED | 9950 | HHS | DCFS | CYC | Caliente | 2010 | 96 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 960
3076EXT1 | EXTERIOR FINISHES | 3076 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC JARBIDGE STORAGE SHED | 9950 | HHS | DCFS | CYC | Caliente | 2010 | 96 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 960
3075EXT2 | ROOF REPLACEMENT | 3075 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition shingle roof and new underlayment. This estimate includes removal and disposal of the old roof. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC INDUSTRIAL ARTS STORAGE | 9950 | HHS | DCFS | CYC | Caliente | 2010 | 416 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6240
3075EXT1 | EXTERIOR FINISHES | 3075 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC INDUSTRIAL ARTS STORAGE | 9950 | HHS | DCFS | CYC | Caliente | 2010 | 416 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4160
3074EXT1 | EXTERIOR FINISHES | 3074 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sealing the concrete masonry units, sanding, priming and painting the wood siding and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC WORK CREW STORAGE | 9950 | HHS | DCFS | CYC | Caliente | 2010 | 256 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2560
3073EXT1 | EXTERIOR FINISHES | 3073 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC GREENHOUSE STORAGE 2 | 9950 | HHS | DCFS | CYC | Caliente | 0 | 80 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 800
3072EXT1 | EXTERIOR FINISHES | 3072 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC GREENHOUSE STORAGE 1 | 9950 | HHS | DCFS | CYC | Caliente | 0 | 96 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 960
3080EXT1 | EXTERIOR FINISHES | 3080 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC AURORA STORAGE SHED | 9950 | HHS | DCFS | CYC | Caliente | 2010 | 96 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 960
0212EXT2 | EXTERIOR FINISHES | 0212 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 4-5 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | CYC BEOWAWE DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Four to Ten Years | Long-Term Needs | 3 | 41850
0213EXT5 | EXTERIOR DOOR REPLACEMENT | 0213 | The exterior wood exit double doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the double door assembly with new metal doors, frames, hardware and paint. Removal and disposal of the existing doors is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC CURRIE DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0213ADA3 | ADA SIGNAGE | 0213 | ADA regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with these criteria. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC CURRIE DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 1500
0213SFT6 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 0213 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CYC CURRIE DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 9000
0213EXT2 | EXTERIOR FINISHES | 0213 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 4-5 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | CYC CURRIE DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Four to Ten Years | Long-Term Needs | 3 | 41850
0213PLM4 | WATER HEATER REPLACEMENT | 0213 | There is a 50 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | CYC CURRIE DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0213ADA4 | KITCHEN REMODEL | 0213 | The kitchen and associated cabinets in the kitchen area are original to the building. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and countertops are delaminating and failing. This project recommends the replacement of the existing kitchen countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards for Accessible Design should be incorporated into the design such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. | CYC CURRIE DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 15000
0213ADA2 | ADA RESTROOM UPGRADE | 0213 | The designated restroom does not meet the ADA requirements. A complete retrofit is necessary. This project would provide funding for construction of a new accessible restroom. Items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC CURRIE DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 25000
0213INT3 | CABINET REPLACEMENT | 0213 | The sleeping rooms have a built-in desk, dresser and wardrobe closet for the students clothing and personal effects. They are constructed of chipboard and are of poor quality. Many are missing pulls and handles, have broken drawer faces and broken drawer slides. This project recommends replacing the existing units with heavy duty, institutional type desks and storage units constructed of metal or plywood with a washable surface. There are 18 built-in units and 2 portable units in the confinement rooms. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC CURRIE DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16000
0212PLM4 | WATER HEATER REPLACEMENT | 0212 | There is a 50 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | CYC BEOWAWE DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0213SFT4 | SPRINKLER PIPE ENCAPSULATION | 0213 | The sprinkler piping is hung from the ceiling of the dormitory and is exposed to the occupants. This creates a safety hazard in two ways. One is that the occupants could damage the piping and cause flooding in the building. The other is that the occupants can tie things around the pipes and cause harm to themselves. This project recommends encapsulating the piping with wallboard and texturing and painting to match the adjacent ceiling finishes. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC CURRIE DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 3000
0214EXT2 | EXTERIOR FINISHES | 0214 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 4-5 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | CYC HAMILTON DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1964 | 4185 | 2017-03-01 | Four to Ten Years | Long-Term Needs | 3 | 41850
0213INT2 | INTERIOR FINISHES | 0213 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC CURRIE DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 41850
0213ENR1 | EXTERIOR ENERGY RETROFIT | 0213 | The building is constructed of CMU with no insulation. The windows are original to the building, and of single pane construction. Buildings of this type are not energy efficient. This project recommends adding an EIFS over the CMU and replacing the windows with new dual-pane, safety glazed windows. This estimate includes removal and disposal of the existing windows. The estimate is based on $10.00 per square foot for the EIFS plus $1500.00 per window for 20 windows. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC CURRIE DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 71850
0214INT2 | INTERIOR FINISHES | 0214 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC HAMILTON DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1964 | 4185 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 41850
0214SFT4 | EXTERIOR LANDING | 0214 | The exterior landing at the secondary exit door is in need of replacement due to the door swinging out over a 7" step. The 2012 IBC Chapter 10 requires a flat landing no more than 1/2 inch below finish floor where the door swings out over the landing. This project would provide for a new concrete landing to be installed. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC HAMILTON DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1964 | 4185 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 5000
0214ENR1 | EXTERIOR ENERGY RETROFIT | 0214 | The building is constructed of CMU with no insulation. The windows are original to the building, and of single pane construction. Buildings of this type are not energy efficient. This project recommends adding an EIFS over the CMU and replacing the windows with new dual-pane, safety glazed windows. This estimate includes removal and disposal of the existing windows. The estimate is based on $10.00 per square foot for the EIFS plus $1500.00 per window for 20 windows. | CYC HAMILTON DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1964 | 4185 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 71850
0214EXT5 | EXTERIOR DOOR REPLACEMENT | 0214 | The exterior wood exit double doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the double door assembly with new metal doors, frames, hardware and paint. Removal and disposal of the existing doors is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC HAMILTON DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1964 | 4185 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0214SFT2 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0214 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC HAMILTON DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1964 | 4185 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 4185
0214ADA2 | ADA RESTROOM UPGRADE | 0214 | The designated restroom does not meet the ADA requirements. A complete retrofit is necessary. This project would provide funding for construction of a new accessible restroom. Items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | CYC HAMILTON DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1964 | 4185 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 25000
0212ADA4 | KITCHEN REMODEL | 0212 | The kitchen and associated cabinets in the kitchen area are original to the building. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and countertops are delaminating and failing. This project recommends the replacement of the existing kitchen countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards for Accessible Design should be incorporated into the design such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. | CYC BEOWAWE DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 15000
0214PLM4 | WATER HEATER REPLACEMENT | 0214 | There is a 50 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | CYC HAMILTON DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1964 | 4185 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0211EXT5 | EXTERIOR DOOR REPLACEMENT | 0211 | The exterior wood exit double doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the double door assembly with new metal doors, frames, hardware and paint. Removal and disposal of the existing doors is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC AURORA DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0214SFT6 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 0214 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CYC HAMILTON DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1964 | 4185 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 9000
0215SFT2 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0215 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC JARBIDGE DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1964 | 4185 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 4185
0215ENR3 | EXTERIOR ENERGY RETROFIT | 0215 | The building is constructed of CMU with no insulation. The windows are original to the building, and are of single pane construction. Buildings of this type are not energy efficient. This project recommends adding an EIFS over the CMU and replacing the windows with new dual-pane, safety glazed windows. This estimate includes removal and disposal of the existing windows. The estimate is based on $10.00 per square foot for the EIFS plus $1500.00 per window for 20 windows. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC JARBIDGE DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1964 | 4185 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 71850
0215INT2 | INTERIOR FINISHES | 0215 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC JARBIDGE DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1964 | 4185 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 41850
0214ADA3 | KITCHEN REMODEL | 0214 | The kitchen and associated cabinets in the kitchen area are original to the building. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and countertops are delaminating and failing. This project recommends the replacement of the existing kitchen countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards for Accessible Design should be incorporated into the design such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. | CYC HAMILTON DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1964 | 4185 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 15000
0211SFT4 | SPRINKLER PIPE ENCAPSULATION | 0211 | The sprinkler piping is hung from the ceiling of the dormitory and is exposed to the occupants. This creates a safety hazard in two ways. One is that the occupants could damage the piping and cause flooding in the building. The other is that the occupants can tie things around the pipes and cause harm to themselves. This project recommends encapsulating the piping with wallboard and texturing and painting to match the adjacent ceiling finishes. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC AURORA DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 3000
0199INT1 | INTERIOR FINISHES | 0199 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC MENTAL HEALTH BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 1800 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18000
0199ADA4 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0199 | This building contains two water fountains that are not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | CYC MENTAL HEALTH BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 1800 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 8000
0199ENR4 | EXTERIOR LIGHTING REPLACEMENT | 0199 | The building has perimeter lighting on the exterior of the building, but the light fixtures are old, failing and not energy efficient. This project would provide for the replacement of the exterior lighting fixtures with new LED light fixtures, using existing wiring. | CYC MENTAL HEALTH BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 1800 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0199EXT2 | EXTERIOR FINISHES | 0199 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC MENTAL HEALTH BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 1800 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18000
0199ENR2 | WINDOW REPLACEMENT | 0199 | The windows are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 5 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC MENTAL HEALTH BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 1800 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
0199ADA1 | ADA RESTROOM UPGRADE | 0199 | The men's and women's designated ADA restrooms do not meet the ADA requirements. A complete retrofit is necessary. This project would provide funding for construction of two unisex accessible restrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC MENTAL HEALTH BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 1800 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 25000
0199ADA3 | ADA SIGNAGE | 0199 | ADA regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with these criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADAAG were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC MENTAL HEALTH BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 1800 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 1500
0199PLM1 | WATER HEATER REPLACEMENT | 0199 | There is a 15 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC MENTAL HEALTH BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 1800 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
0199ADA2 | ADA ENTRY UPGRADES | 0199 | The ADA provides for accessibility to sites and services for people with physical limitations. At the threshold between the entrance door and the landing there is a large gap. The gap is large enough to compromise the compliance of the path of travel and should be altered. This project would provide for installing an extended threshold to cover the gap and bring the path of travel into compliance with the code. The 2012 IBC, ICC/ANSI A117.1 - 2009 and the most current version of the ADAAG were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC MENTAL HEALTH BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 1800 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 500
0211SFT2 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0211 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC AURORA DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 1500
0211INT3 | CABINET REPLACEMENT | 0211 | The sleeping rooms have a built-in desk, dresser and wardrobe closet for the students clothing and personal effects. They are constructed of particle board and are of poor quality. Many are missing pulls and handles, have broken drawer faces and broken drawer slides. This project recommends replacing the existing units with heavy duty, institutional type desks and storage units constructed of metal or plywood with a washable surface. There are 18 built-in units and 2 portable units in the sleeping rooms. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC AURORA DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16000
0211PLM5 | WATER HEATER REPLACEMENT | 0211 | There is a 50 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | CYC AURORA DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0211SFT6 | EXTERIOR LANDING | 0211 | The exterior landing at the secondary exit door is in need of replacement due to the door swinging out over a 7" step. The 2012 IBC Chapter 10 requires a flat landing no more than 1/2 inch below finish floor where the door swings out over the landing. This project would provide for a new concrete landing to be installed. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC AURORA DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 1500
0212EXT5 | EXTERIOR DOOR REPLACEMENT | 0212 | The exterior wood exit double doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the double door assembly with new metal doors, frames, hardware and paint. Removal and disposal of the existing doors is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC BEOWAWE DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0211ADA2 | ADA RESTROOM UPGRADE | 0211 | The designated restroom does not meet the ADA requirements. A complete retrofit is necessary. This project would provide funding for construction of a new accessible restroom. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | CYC AURORA DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 25000
0211SFT7 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 0211 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CYC AURORA DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 9000
0211EXT2 | EXTERIOR FINISHES | 0211 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 4-5 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | CYC AURORA DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Four to Ten Years | Long-Term Needs | 3 | 41850
0211ADA3 | KITCHEN REMODEL | 0211 | The kitchen and associated cabinets in the kitchen area are original to the building. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and countertops are delaminating and failing. This project recommends the replacement of the existing kitchen countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards for Accessible Design should be incorporated into the design such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. | CYC AURORA DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 15000
0211ENR1 | EXTERIOR ENERGY RETROFIT | 0211 | The building is constructed of CMU with no insulation. The windows are original to the building, and of single pane construction. Buildings of this type are not energy efficient. This project recommends adding an EIFS over the CMU and replacing the windows with new dual-pane, safety glazed windows. This estimate includes removal and disposal of the existing windows. The estimate is based on $10.00 per square foot for the EIFS plus $1500.00 per window for 20 windows. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC AURORA DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 71850
0212INT3 | CABINET REPLACEMENT | 0212 | The sleeping rooms have a built-in desk, dresser and wardrobe closet for the students clothing and personal effects. They are constructed of particle board and are of poor quality. Many are missing pulls and handles, have broken drawer faces and broken drawer slides. This project recommends replacing the existing units with heavy duty, institutional type desks and storage units constructed of metal or plywood with a washable surface. There are 18 built-in units and 2 portable units in the confinement rooms. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC BEOWAWE DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16000
0215EXT5 | EXTERIOR DOOR REPLACEMENT | 0215 | The exterior wood exit double doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the double door assembly with new metal doors, frames, hardware and paint. Removal and disposal of the existing doors is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC JARBIDGE DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1964 | 4185 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0212SFT4 | SPRINKLER PIPE ENCAPSULATION | 0212 | The sprinkler piping is hung from the ceiling of the dormitory and is exposed to the occupants. This creates a safety hazard in two ways. One is that the occupants could damage the piping and cause flooding in the building. The other is that the occupants can tie things around the pipes and cause harm to themselves. This project recommends encapsulating the piping with wallboard and texturing and painting to match the adjacent ceiling finishes. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC BEOWAWE DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 3000
0221ADA6 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0221 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | CYC MULTI-PURPOSE BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 1966 | 36630 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 2000
0212ADA2 | ADA RESTROOM UPGRADE | 0212 | ADA regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with these criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC BEOWAWE DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 25000
0212ADA3 | ADA SIGNAGE | 0212 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with these criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC BEOWAWE DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 1500
0212SFT7 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 0212 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CYC BEOWAWE DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 9000
0211INT1 | INTERIOR FINISHES | 0211 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC AURORA DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 41850
0220ADA5 | INSTALL LEVER ACTION DOOR HARDWARE | 0220 | The existing door handles are round knob type and are not ADA compliant. This project would provide for the installation of new lever action door hardware on all doors in the facility. This estimate is for 15 units. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADAAG were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC EVALUATION/ INFIRMARY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 1578 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 5250
0221ADA4 | ADA UPGRADES - STAGE | 0221 | The auditorium is lacking an accessible path to the stage. The stage is required to have an accessible path to it per the ADA regulations. This project would provide for an accessible ramp or powered lift to access the stage. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADAAG were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC MULTI-PURPOSE BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 1966 | 36630 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 7500
0221PLM3 | WATER TREATMENT SYSTEM INSTALLATION | 0221 | The existing water softening/ treatment system in the building only serves the boiler for the Laundry and Culinary. The other boiler and the rest of the HVAC equipment should have a water treatment system as well. Failure to treat the water can cause wear and tear on the domestic water supply lines, plumbing fixtures and HVAC equipment. This project would provide for the purchase and installation of water softeners/ treatment systems to serve all of the mechanical and plumbing equipment. This project would also provide for a chemical treatment program including an updated chemicals control system, service and employee training provided by a qualified water treatment vendor for the HVAC systems. The annual maintenance fee charged by the water treatment vendor would be determined after an investigation of the water system is complete. These annual costs are not included in this project cost. For budgeting purposes, a $12,000 fee is suggested. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC MULTI-PURPOSE BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 1966 | 36630 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0221INT2 | FLOORING REPLACEMENT | 0221 | The VCT and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the next 2-3 years. The gymnasium and concrete floors are excluded from the square footage. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC MULTI-PURPOSE BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 1966 | 36630 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 200000
0221SFT3 | FIRE ALARM SYSTEM UPGRADE | 0221 | This building is equipped with an automatic fire detection and alarm system that no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 "If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure". When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC MULTI-PURPOSE BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 1966 | 36630 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 146520
0221ADA3 | ADA SIGNAGE | 0221 | ADA regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with these criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADAAG were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC MULTI-PURPOSE BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 1966 | 36630 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 8000
0221ADA5 | ADA ACCESSIBILITY IMPROVEMENTS | 0221 | The existing building is in need of an ADA accessibility upgrade. This project would provide for new lever action door hardware throughout, modifications to dining and serving tables and counters in the culinary and dining areas and modifications to the existing Men's and Women's restrooms which are used by the public during special events. The locker rooms in the Gym are also included in this estimate. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADAAG were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC MULTI-PURPOSE BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 1966 | 36630 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 100000
0220ENR4 | LIGHTING UPGRADE | 0220 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | CYC EVALUATION/ INFIRMARY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 1578 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 12624
0220HVA1 | HVAC EQUIPMENT REPAIRS | 0220 | There and two HVAC split systems that were installed in 2015. Both of the systems have ductwork, line sets, A/C condenser and heaters installed improperly. This project would provide for the proper installation of both HVAC split systems. This project includes removal and installation of the existing equipment and all required connections to utilities. | CYC EVALUATION/ INFIRMARY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 1578 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
0220INT3 | JANITORS CLOSET REPAIRS | 0220 | The mop sink in the Janitors Closet is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide FRP to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | CYC EVALUATION/ INFIRMARY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 1578 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
0219ADA5 | ADA ACCESSIBLE COUNTER | 0219 | The ADA provides for accessibility to sites and services for people with physical limitations. The entrance of the building has a service counter for the public to approach which does not meet current requirements. Section 904.4 of the ADA Standards for Accessible Design states that a portion of the counter surface that is 36" long minimum and 36" high maximum above the finish floor shall be provided. This project will provide an accessible counter space in accordance with this requirement. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as a references for this project. | CYC SCHOOL - OLD | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 11760 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 4000
0220SFT2 | FIRE ALARM SYSTEM UPGRADE | 0220 | This building is equipped with an automatic fire detection and alarm system that no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 "If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure". When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC EVALUATION/ INFIRMARY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 1578 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 6312
0221INT1 | INTERIOR FINISHES | 0221 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC MULTI-PURPOSE BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 1966 | 36630 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 366300
0220INT2 | INTERIOR FINISHES | 0220 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC EVALUATION/ INFIRMARY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 1578 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15780
0220ADA4 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0220 | This building contains water fountains on each floor that are not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of four drinking fountains to meet the ADA requirements, two on each floor. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC EVALUATION/ INFIRMARY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 1578 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 4000
0220EXT1 | EXTERIOR FINISHES | 0220 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC EVALUATION/ INFIRMARY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 1578 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15780
0220ADA1 | ADA RESTROOM UPGRADE | 0220 | The building does not have an accessible restroom. The existing restroom does not meet the ADA requirements. A complete retrofit is necessary. This project would provide funding for remodeling the Men's and Women's restrooms per ADA regulations. Items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC EVALUATION/ INFIRMARY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 1578 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 40000
0220ADA3 | ADA SIGNAGE | 0220 | ADA regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/ pictograms; and sign contrast and finish. The signage in this facility does not comply with these criteria. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC EVALUATION/ INFIRMARY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 1578 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 1500
0220ENR3 | WINDOW REPLACEMENT | 0220 | The windows are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 11 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC EVALUATION/ INFIRMARY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 1578 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16500
0219ELE2 | ELECTRICAL UPGRADE | 0219 | This building was constructed before the high demand for electrical services were needed. As time has progressed, the building’s electrical demand and system has changed. It is utilized to its current maximum potential. The electrical panels and receptacles are at their limit and they do not comply with NEC 2011. It is recommended to have the entire system upgraded to meet the current standards. | CYC SCHOOL - OLD | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 11760 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 294000
0219ELE1 | PROVIDE CLEARANCE AT ELECTRICAL PANELS | 0219 | There are electrical panels in the building which do not have proper clear floor space around them. The 2012 IFC Section 605.3 states that, "A working space of not less than 30 inches in width, 36 inches in depth and 78 inches in height shall be provided in front of electrical service equipment. Where the electrical service equipment is wider than 30 inches, the working space shall not be less than the width of the equipment. No storage of any materials shall be located within the designated working space." This project would provide funds to relocate the stored materials blocking the working space. | CYC SCHOOL - OLD | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 11760 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 400
0221ELE1 | WIRING CLEANUP | 0221 | The building has wiring that is disorganized and not in proper electrical boxes, particularly in the near the stage area. This creates a safety issue during repairs or upgrades. This project would provide for organization, proper labeling and for the wiring to be placed in electrical boxes per NEC 2011. | CYC MULTI-PURPOSE BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 1966 | 36630 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
0220PLM1 | WATER HEATER REPLACEMENT | 0220 | There are 3 on-demand propane-fired water heaters on the roof of the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, these units are showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that 3 new on-demand propane-fired water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. | CYC EVALUATION/ INFIRMARY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 1578 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
0292EXT2 | EXTERIOR FINISHES | 0292 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC POOL HOUSE AND POOL | 9950 | HHS | DCFS | CYC | Caliente | 1964 | 2000 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0292SFT1 | FLUE REPLACEMENT | 0292 | There is a flue vent in the building which does not comply with UMC 2012 chapter 8, chimneys and vents. The flue vent was installed with an improper flue and per section 804 direct vent terminations vent terminals direct vented appliances shall be installed in accordance with the manufacturer’s installation instructions. The flue vent is taped and does not allow for the proper air flow. It is recommended that the flue vent be replaced per UMC and the manufacturer’s instructions. This project would provide funding to replace the flue vent. | CYC POOL HOUSE AND POOL | 9950 | HHS | DCFS | CYC | Caliente | 1964 | 2000 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0292EXT4 | EXTERIOR DOOR REPLACEMENT | 0292 | The exterior metal doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the south double door assembly and the north single door assembly with new metal doors, frames and hardware. Removal and disposal of the existing doors is included in this estimate. | CYC POOL HOUSE AND POOL | 9950 | HHS | DCFS | CYC | Caliente | 1964 | 2000 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0292ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0292 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | CYC POOL HOUSE AND POOL | 9950 | HHS | DCFS | CYC | Caliente | 1964 | 2000 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 2000
0292SFT2 | SAFETY CABINETS | 0292 | The building contains pool chemicals and other hazardous products located on open shelves and on the floor. This does not meet OSHA standards or IFC for hazardous materials containment. This project would provide a self-closing hazardous storage container in the building and install placards on the building’s exterior in accordance with OSHA 1910.106 (d) and IFC Chapter 57 Section 5704.3.2.1.3. | CYC POOL HOUSE AND POOL | 9950 | HHS | DCFS | CYC | Caliente | 1964 | 2000 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 5000
0292PLM3 | WATER HEATER REPLACEMENT | 0292 | There is a 75 gallon propane water heater in the building. The average lifespan of a water heater is eight to ten years. It is recommended that a new propane water heater, seismic straps, braided steel hose, expansion tank, ball valves, new flex gas line and pan be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC POOL HOUSE AND POOL | 9950 | HHS | DCFS | CYC | Caliente | 1964 | 2000 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 2500
0292SFT3 | HAZARDOUS MATERIALS STORAGE | 0292 | The building contains hazardous materials (i.e. pool chemicals). Per IFC 2012 Hazardous Materials, and in accordance with NFPA; where hazardous materials are stored, dispensed or used, Section 5003 states the proper use and application is to have mechanical exhaust and ventilation, and hazard identification signs shall be installed. Refer to Section 5004 and 5005 for the proper use and setup. It is important to comply with all applicable codes. This project would provide for all requirements in IFC 2012, to include Section 105 permits and inspections through the State Fire Marshal’s Office and the State Public Works Division. | CYC POOL HOUSE AND POOL | 9950 | HHS | DCFS | CYC | Caliente | 1964 | 2000 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 30000
0292SFT4 | HAZARDOUS COMMUNICATION PROGRAM | 0292 | Due to the storage of hazardous materials, this site shall comply with IFC 2012 Chapter 4 Emergency Planning and Preparedness, and have a written Hazardous Materials Management Plan, including but not limited to, Section 5003 Safety Data Sheets, Section 406 Employee Training and Response Procedures and Section 407 Hazard Communication. Chapter 50 Section 5001 will provide additional assistance in devising and implementing a hazardous communication program. | CYC POOL HOUSE AND POOL | 9950 | HHS | DCFS | CYC | Caliente | 1964 | 2000 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 2000
0292PLM4 | POOL EQUIPMENT REPLACEMENT | 0292 | The existing pool circulation pump, water filter, heater, chemical feeder, clocks and plumbing were in poor condition at the time of the survey. The pool equipment is beyond its useful life expectancy. This project would provide for the purchase and installation of new pool equipment and all required connections to utilities. This project would also provide for a chemical treatment program to include an updated chemical control system, service and employee training to be provided by a qualified water treatment vendor. The annual maintenance fee charged by the water treatment vendor would be determined after an investigation of the water system is complete. These annual costs are not included in this project cost. For budgeting purposes, a $12,000 fee is suggested. | CYC POOL HOUSE AND POOL | 9950 | HHS | DCFS | CYC | Caliente | 1964 | 2000 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14000
0292ENR1 | LIGHTING UPGRADE | 0292 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC POOL HOUSE AND POOL | 9950 | HHS | DCFS | CYC | Caliente | 1964 | 2000 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16000
0221HVA1 | HVAC SYSTEM UPGRADE | 0221 | The HVAC system consists of many roof mounted packaged units, boilers and evaporative coolers. They are not energy efficient and have reached the end of their expected and useful life. The air handlers are troublesome and require constant maintenance to remain in working condition. This project would provide for installation of a new HVAC system and cleaning of the existing duct work and grilles and any new ducting and associated work. The new system should be designed by a mechanical engineer who will determine the most economical and efficient way to upgrade the existing building. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC MULTI-PURPOSE BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 1966 | 36630 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2143624
0292ADA1 | RESTROOM REMODEL | 0292 | The showers and restroom facilities are damaged from wear and tear, not operational and do not meet the ADA requirements. A complete retrofit is necessary. This project would provide funding for remodeling the restrooms and constructing an accessible shower and restroom. These items may include a new shower stall, sink, toilet, hardware, mirrors, fixtures, flooring and paint. NRS 338.180, IBC 2012, ICC/ANSI A117.1 – 2009 and the most current version of the ADAAG were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC POOL HOUSE AND POOL | 9950 | HHS | DCFS | CYC | Caliente | 1964 | 2000 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 40000
0221CUL1 | ICE MACHINE REPLACEMENT | 0221 | There is an ice machine in the dining room. This unit is showing signs of wear including extensive leaks which are ruining the flooring and should be scheduled for replacement in the next 2-3 years. It is recommended that a new ice machine be purchased and installed. Removal and disposal of the existing machine is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC MULTI-PURPOSE BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 1966 | 36630 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
0290EXT1 | EXTERIOR FINISHES | 0290 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC GARAGE/ STORAGE | 9950 | HHS | DCFS | CYC | Caliente | 1977 | 2000 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0290EXT2 | EXTERIOR DOOR REPLACEMENT | 0290 | The exterior metal man door is damaged from age and general wear and tear and has reached the end of its expected life. This project would provide for the replacement of the door assembly with a new metal door, frame and hardware. Removal and disposal of the existing door is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC GARAGE/ STORAGE | 9950 | HHS | DCFS | CYC | Caliente | 1977 | 2000 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0221ENR2 | LIGHTING UPGRADE | 0221 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | CYC MULTI-PURPOSE BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 1966 | 36630 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 293040
0212INT2 | INTERIOR FINISHES | 0212 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC BEOWAWE DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 41850
0221SFT4 | ANCHOR SHELVES | 0221 | OSHA recommends that the bottom of all columns be furnished with column base plates, and be anchored to the floor with anchor bolts capable of resisting the forces caused by the loads on the shelving unit. Per OSHA standard 1926.250(a)(1) All materials stored in tiers shall be stacked, racked, blocked, interlocked, or otherwise secured to prevent sliding, falling or collapse. This project would provide for a licensed contractor to install anchor bolts and properly secure the shelving units to the floor and to the other shelves. This project should be overseen by a license engineer or architect. | CYC MULTI-PURPOSE BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 1966 | 36630 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 10000
0221CUL2 | CULINARY EQUIPMENT REPLACEMENT | 0221 | The kitchen equipment is original to the building and has reached the end of its useful life. It is recommended that the equipment be scheduled for replacement in the next 2-3 years, including the ovens and hoods, grills, sinks and dishwashers. This project provides for the removal and disposal of the existing equipment and replacement with new equipment. | CYC MULTI-PURPOSE BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 1966 | 36630 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 150000
0221INT3 | JANITORS CLOSET REPAIRS | 0221 | The mop sink in the Janitors Closet is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide FRP to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | CYC MULTI-PURPOSE BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 1966 | 36630 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
0221PLM4 | WATER HEATER REPLACEMENT | 0221 | There are two 120 gallon electric water heaters in the building. The average lifespan of a water heater is eight to ten years. It is recommended that 2 new electric water heaters, seismic straps, braided steel hose, expansion tanks, ball valves and pans be installed within a year. Removal and disposal of the existing equipment is included in this estimate. | CYC MULTI-PURPOSE BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 1966 | 36630 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 10000
0221EXT1 | EXTERIOR FINISHES | 0221 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the stucco and concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC MULTI-PURPOSE BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 1966 | 36630 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 366300
0219PLM2 | WATER HEATER REPLACEMENT | 0219 | There is a 300 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next year. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | CYC SCHOOL - OLD | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 11760 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 10000
0292INT1 | INTERIOR FINISHES | 0292 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC POOL HOUSE AND POOL | 9950 | HHS | DCFS | CYC | Caliente | 1964 | 2000 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0216SFT4 | SPRINKLER PIPE ENCAPSULATION | 0216 | The sprinkler piping is hung from the ceiling of the dormitory and is exposed to the occupants. This creates a safety hazard in two ways. One is that the occupants could damage the piping and cause flooding in the building. The other is that the occupants can tie things around the pipes and cause harm to themselves. This project recommends encapsulating the piping with wallboard and texturing and painting to match the adjacent ceiling finishes. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC KIMBERLY DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1977 | 4592 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 3000
0217EXT2 | EXTERIOR FINISHES | 0217 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 4-5 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | CYC LINCOLN DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1977 | 4592 | 2017-03-01 | Four to Ten Years | Long-Term Needs | 3 | 45920
0217PLM4 | WATER HEATER REPLACEMENT | 0217 | There is a 50 gallon electric water heater in the building. The average lifespan of a water heater is eight to ten years. This unit was not installed correctly and was missing an element cover at the time of the survey. It is recommended that a new electric water heater, seismic straps, braided steel hoses, expansion tank, ball valve and a pan be installed. Removal and disposal of the existing equipment is included in this estimate. | CYC LINCOLN DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1977 | 4592 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0217ADA2 | KITCHEN REMODEL | 0217 | The kitchen and associated cabinets in the kitchen area are original to the building. The quality of construction and installation are inadequate for the high usage at this facility, but the cabinets and countertops are delaminating and failing. This project recommends the replacement of the existing kitchen countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards for Accessible Design should be incorporated into the design such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. | CYC LINCOLN DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1977 | 4592 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 15000
0217ADA3 | ADA RESTROOM UPGRADE | 0217 | The designated restroom does not meet the ADA requirements. A complete retrofit is necessary. This project would provide funding for construction of a new accessible restroom. Items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | CYC LINCOLN DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1977 | 4592 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 25000
0217SFT4 | SPRINKLER PIPE ENCAPSULATION | 0217 | The sprinkler piping is hung from the ceiling of the dormitory and is exposed to the occupants. This creates a safety hazard in two ways. One is that the occupants could damage the piping and cause flooding in the building. The other is that the occupants can tie things around the pipes and cause harm to themselves. This project recommends encapsulating the piping with wallboard and texturing and painting to match the adjacent ceiling finishes. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC LINCOLN DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1977 | 4592 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 3000
0217ENR1 | EXTERIOR ENERGY RETROFIT | 0217 | The building is constructed of CMU with no insulation. The windows are original to the building, and are of single pane construction. Buildings of this type are not energy efficient. This project recommends adding an EIFS over the CMU and replacing the windows with new dual-pane, safety glazed windows. This estimate includes removal and disposal of the existing windows. The estimate is based on $10.00 per square foot for the EIFS plus $1500.00 per window for 20 windows. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC LINCOLN DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1977 | 4592 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 75920
0217INT2 | INTERIOR FINISHES | 0217 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC LINCOLN DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1977 | 4592 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 45920
0216PLM4 | WATER HEATER REPLACEMENT | 0216 | There is an on-demand electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new on-demand electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | CYC KIMBERLY DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1977 | 4592 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0216ADA3 | KITCHEN REMODEL | 0216 | The kitchen and associated cabinets in the kitchen area are original to the building. The quality of construction and installation were inadequate for the high usage at this facility. The cabinets and countertops are delaminating and failing. This project recommends the replacement of the existing kitchen countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards for Accessible Design should be incorporated into the design such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. | CYC KIMBERLY DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1977 | 4592 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 15000
0219ELE3 | PANIC HARDWARE IN ELECTRICAL ROOMS | 0219 | The electrical room with the uninterruptable power supply contains equipment that meets or exceeds 1,200 amps. It is recommended per the 2012 IBC 1008.1.10 that panic and fire exit hardware be installed. This equipment was not required when the building was constructed in 1962. When a remodel occurs, it is suggested to comply with current code. It is recommended that this project be completed within 1-2 years. The estimate is based on one door that requires panic hardware. | CYC SCHOOL - OLD | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 11760 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 3000
0216EXT2 | EXTERIOR FINISHES | 0216 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 4-5 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | CYC KIMBERLY DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1977 | 4592 | 2017-03-01 | Four to Ten Years | Long-Term Needs | 3 | 45920
0218ENR4 | HVAC EQUIPMENT REPLACEMENT | 0218 | The heat pump units and chiller piping are original to the building. They are located in the ceiling above the circular corridor. They have been problematic, have been leaking and have outdated R-22, which will be obsolete by January 1, 2020. The HVAC equipment should be scheduled for replacement within 2-3 years. This project would provide for the replacement of the equipment and cleaning of the existing duct work and grills. This project includes the removal and disposal of the existing equipment and all required connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC ADMINISTRATION | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 62775
0216INT2 | INTERIOR FINISHES | 0216 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC KIMBERLY DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1977 | 4592 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 45920
0216ADA2 | ADA RESTROOM UPGRADE | 0216 | The designated restroom does not meet the ADA requirements. A complete retrofit is necessary. This project would provide funding for construction of a new accessible restroom. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | CYC KIMBERLY DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1977 | 4592 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 25000
0216ENR1 | EXTERIOR ENERGY RETROFIT | 0216 | The building is constructed of CMU with no insulation. The windows are original to the building, and of single pane construction. Buildings of this type are not energy efficient. This project recommends adding an EIFS over the CMU and replacing the windows with new dual-pane, safety glazed windows. This estimate includes removal and disposal of the existing windows. This estimate is based on $10.00 per square foot for the EIFS plus $1,500.00 per window for a total of 20 windows. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC KIMBERLY DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1977 | 4592 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 75920
0216EXT5 | EXTERIOR DOOR REPLACEMENT | 0216 | The existing exterior wood door appears to be original to the building. It is damaged from age and general wear and tear. This project would provide for the replacement of the wood door with a new metal door, frame, hardware and paint. Removal and disposal of the existing door and painting of the new door is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC KIMBERLY DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1977 | 4592 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0215ADA3 | ADA RESTROOM UPGRADE | 0215 | The designated restroom does not meet the ADA requirements. A complete retrofit is necessary. This project would provide funding for construction of a new accessible restroom. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | CYC JARBIDGE DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1964 | 4185 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 25000
0215SFT6 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 0215 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CYC JARBIDGE DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1964 | 4185 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 9000
0215PLM4 | WATER HEATER REPLACEMENT | 0215 | There is a 50 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | CYC JARBIDGE DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1964 | 4185 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0215ADA2 | KITCHEN REMODEL | 0215 | The kitchen and associated cabinets in the kitchen area are original to the building. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and countertops are delaminating and failing. This project recommends the replacement of the existing kitchen countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards for Accessible Design should be incorporated into the design such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. | CYC JARBIDGE DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1964 | 4185 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 15000
0215EXT2 | EXTERIOR FINISHES | 0215 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 4-5 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | CYC JARBIDGE DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1964 | 4185 | 2017-03-01 | Four to Ten Years | Long-Term Needs | 3 | 41850
0216SFT6 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 0216 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CYC KIMBERLY DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1977 | 4592 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 9000
0218ENR1 | EXTERIOR ENERGY RETROFIT | 0218 | The building is constructed of CMU with no insulation. The windows are original to the building, and of single pane construction. Buildings of this type are not energy efficient. This project recommends adding an EIFS over the CMU and replacing the windows with new dual-pane, safety glazed windows. This estimate includes removal and disposal of the existing windows. The estimate is based on $10.00 per square foot for the EIFS plus $1500.00 per window for 20 windows. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC ADMINISTRATION | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 41850
0219SFT4 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0219 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC 2012 Chapter 10 was referenced for this project. | CYC SCHOOL - OLD | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 11760 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 11760
0219ADA4 | ADA SIGNAGE | 0219 | ADA regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with these criteria. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC SCHOOL - OLD | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 11760 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 5000
0219SFT3 | FIRE ALARM SYSTEM UPGRADE | 0219 | This building is equipped with an automatic fire detection and alarm system that no longer complies with current requirements. The current system is problematic and the duct detectors were rendered inoperative in a previous remodel. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 "If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure". When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC SCHOOL - OLD | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 11760 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 47040
0219ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0219 | This building contains a water fountain. The 2012 IBC Section 1109.5 states where a water fountain is provided, at least half should be accessible. This project would provide funding for the purchase and installation of a new accessible fixed high/ low ADA drinking fountain. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC SCHOOL - OLD | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 11760 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 4000
0219ADA1 | ADA RESTROOM UPGRADE | 0219 | The building does not have an accessible restroom. The existing restroom does not meet the ADA requirements. A complete retrofit is necessary. This project would provide funding for remodeling the Men's and Women's restrooms per ADA regulations. Items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC SCHOOL - OLD | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 11760 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 40000
0219ENV1 | NONABSORBENT FINISHES | 0219 | 2012 IBC Section 1210 requires the installation of smooth, hard, nonabsorbent surfaces in the following restroom areas: on floors in toilet and bathing rooms that extend upward onto the walls at least 6 inches, within 2 feet of the sides of urinals and water closets to a height of 4 feet above the floor and in shower compartments to a height not less than 70 inches above the drain inlet. This project recommends the installation of FRP or an equal material in all 8 restroom facilities to comply with this code section. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC SCHOOL - OLD | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 11760 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 27000
0219PLM1 | PLUMBING VALVE REPLACEMENTS | 0219 | The majority of the plumbing isolation valves are gate valves that are original to the building. Most of these valves no longer completely stop water when closed. This project would provide for replacing the valves with new ball valves. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC SCHOOL - OLD | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 11760 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0219EXT1 | EXTERIOR FINISHES | 0219 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. Also included is repairing and painting the wood fascia as needed. It is recommended that the building be painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC SCHOOL - OLD | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 11760 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 117600
0219ENR2 | EXTERIOR ENERGY RETROFIT | 0219 | The building is constructed of CMU with no insulation. The windows are original to the building, and of single pane construction. Buildings of this type are not energy efficient. This project recommends adding an EIFS over the CMU and replacing the windows with new dual-pane, safety glazed windows. This estimate includes removal and disposal of the existing windows. The estimate is based on $10.00 per square foot for the EIFS plus $1500.00 per window for 50 windows. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC SCHOOL - OLD | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 11760 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 192600
0217SFT6 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 0217 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CYC LINCOLN DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1977 | 4592 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 9000
0218SIT1 | SITE DRAINAGE UPGRADES | 0218 | The grade does not slope away effectively from the buildings. Water has pooled against the foundation. In the winter months, as the water freezes against the foundation, over time, this can cause damage to the foundation. It is recommended per IBC 1804.3 Site Grading the ground immediately adjacent to the foundation shall be sloped away from the building at a slope of not less than one vertical in 20 units horizontal (5-percent slope) for a minimum distance of 10 feet (3048 mm) measured perpendicular to the face of the wall. This project would create a 5% slope away from the buildings. Additional drainage swales shall be installed, as needed. It is recommended that the grading be completed within 2-3 years. | CYC ADMINISTRATION | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0218INT3 | INTERIOR FINISHES | 0218 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC ADMINISTRATION | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 41850
0218HVA2 | AIR CONDITIONER INSTALLATION | 0218 | The server room is not sufficiently cooled by the existing HVAC system. If the room is too warm, the computer equipment will prematurely age and may fail due to overheating. It is recommended to install an air conditioning system in the room to ensure that the temperature is properly regulated. This project would provide for the purchase and installation of an air conditioner including all required connections to existing utilities. | CYC ADMINISTRATION | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0218ELE1 | ELECTRICAL UPGRADE | 0218 | This building was constructed before the high demand for electrical services were needed for security systems, computers and other electrical devices. As time has progressed, the buildings electrical demand and system has changed. The electrical panels and receptacles are at their limit. There are also problems with rusting conduits particularly underground conduits. As failures have happened, new conduits have been installed on the interior walls and some are not properly connected. It is recommended the entire system be upgraded to meet the evolving needs of the building and provide safe electrical distribution. | CYC ADMINISTRATION | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 104625
0218HVA3 | EXHAUST FAN REPLACEMENT | 0218 | The existing exhaust fans that serve the bathrooms are original equipment and are not providing adequate ventilation. This project would provide for the removal of the existing exhaust fan assemblies and the purchase and installation of two new exhaust fan assemblies including connections to utilities. | CYC ADMINISTRATION | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0218EXT3 | EXTERIOR FINISHES | 0218 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CYC ADMINISTRATION | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Four to Ten Years | Long-Term Needs | 3 | 41850
0218ADA6 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0218 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | CYC ADMINISTRATION | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 2000
0218PLM2 | WATER HEATER REPLACEMENT | 0218 | There is an older booster water heater in the building that appears to be original to the structure. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new propane-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC ADMINISTRATION | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0218ENV1 | NONABSORBENT FINISHES | 0218 | 2012 IBC Section 1210 requires the installation of smooth, hard, nonabsorbent surfaces in the following restroom areas: on floors in toilet and bathing rooms that extend upward onto the walls at least 6 inches, within 2 feet of the sides of urinals and water closets to a height of 4 feet above the floor and in shower compartments to a height not less than 70 inches above the drain inlet. This project recommends the installation of FRP or an equal material to comply with this code section. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC ADMINISTRATION | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
0218ADA3 | ADA SIGNAGE | 0218 | ADA regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with these criteria. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC ADMINISTRATION | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 2500
0218ADA4 | ADA RESTROOM UPGRADE | 0218 | The men's and women's designated ADA restrooms do not meet the ADA requirements. A complete retrofit is necessary. This project would provide funding for construction of two unisex accessible restrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC ADMINISTRATION | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 25000
0215SFT4 | EXTERIOR LANDING | 0215 | The exterior landing at the secondary exit door is in need of replacement due to the door swinging out over a 7" step. The 2012 IBC Chapter 10 requires a flat landing no more than 1/2 inch below finish floor where the door swings out over the landing. This project would provide for a new concrete landing to be installed. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC JARBIDGE DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1964 | 4185 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 5000
0219INT3 | INTERIOR FINISHES | 0219 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC SCHOOL - OLD | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 11760 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 117600
0212ENR1 | EXTERIOR ENERGY RETROFIT | 0212 | The building is constructed of CMU with no insulation. The windows are original to the building, and are of single pane construction. Buildings of this type are not energy efficient. This project recommends adding an EIFS over the CMU and replacing the windows with new dual-pane, safety glazed windows. This estimate includes removal and disposal of the existing windows. The estimate is based on $10.00 per square foot for the EIFS plus $1500.00 per window for 20 windows. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC BEOWAWE DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 71850
0514EXT2 | DEMOLISH STRUCTURE | 0514 | The structure is built of steel posts and beams, a wood framed roof structure and a concrete slab-on-grade foundation. All of these structural elements are showing signs of failing and the structure should be removed. This project provides for the demolition of the structure, including the foundation and disposal of the materials. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC RAMADA | 9950 | HHS | DCFS | CYC | Caliente | 1977 | 968 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 2500
0322EXT2 | WINDOW REPLACEMENT | 0322 | The windows are original, single pane construction in wood frames. These older windows are drafty and not energy efficient. The windows do not comply with IBC 2012 Chapter 24 Glass and Glazing which requires safety glazing where the bottom edge of the glazing is less than 18" above the floor. This project recommends replacing the windows with dual pane, higher efficiency units that are safety glazed following IBC 2012 Section 2406 Safety Glazing. This estimate is for the replacement of 101 windows. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 11/04/1999, 08/24/2006 and 06/21/2012. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/07/2017. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 151500
0322INT6 | FLOORING REPLACEMENT | 0322 | The VCT and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" cove base and heavy duty commercial grade carpet in the next 2-3 years. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 107088
0322ADA4 | ADA DOOR HARDWARE REPLACEMENT | 0322 | The operable parts on the interior doors are round knobs which do not comply with ADA requirements. Section 309.4 of the ADA Standards for Accessible Design states that operable parts shall be operable with one hand and shall not require tight grasping, pinching, or twisting of the wrist. It is recommended that compliant hardware be installed in this building to meet these guidelines. This project or a portion thereof was previously recommended in the FCA report dated 11/04/1999, 08/24/2006 and 06/21/2012. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/07/2017. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Immediate to Two Years | Currently Critical | 1 | 25000
0322ENR2 | EXTERIOR LIGHTING REPLACEMENT | 0322 | There are 25 perimeter light fixtures surrounding the building that are incandescent, fluorescent and not energy efficient. This project would provide for the replacement of the exterior lighting fixtures with new LED light fixtures, including wall packs and can lights and will use the existing wiring. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 37500
0322ADA5 | ADA ACCESSIBLE PATH OF TRAVEL | 0322 | The ADA provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the office are necessary to comply with ADA accessibility requirements. This project would provide for a concrete van accessible ADA parking and loading space and concrete walkway to the existing sidewalk. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. 3500 square feet of concrete was used for this estimate. It is recommended that this project coincide with the Crack Fill & Seal Asphalt Paving project. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Immediate to Two Years | Currently Critical | 1 | 87500
0322ADA6 | ADA SIDEWALK REPLACEMENT | 0322 | Many sidewalk sections serving the building and parking areas are deteriorated and failing. In some areas the concrete is spalling considerably and other areas are heaving and settling due to either expansive soils or tree roots. This project addresses the removal and the replacement of the existing sidewalks as needed. 1,250 SF of 4" thick concrete sidewalk was used for this estimate. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Immediate to Two Years | Currently Critical | 1 | 12675
0322ELE5 | GENERATOR REPLACEMENT | 0322 | There is a diesel generator on site that has reached the end of its useful life. A reliable generator is a high priority due to the function and use of these buildings. It is recommended that a new 12 kW diesel generator be installed. This estimate includes the removal and disposal of the old generator. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Immediate to Two Years | Currently Critical | 1 | 100000
0322ELE2 | ELECTRICAL AND COMMUNICATIONS UPGRADE | 0322 | This building was constructed before the high demand for electrical services were needed for computers, communications systems and other electrical devices. As time has progressed, the buildings electrical demand and communications system needs have changed. The electrical system is utilized to its current maximum potential, all the bedrooms require AFCI breakers and the communications system is outdated. The electrical panels, switches and receptacles are at their limit. It is recommended to upgrade the entire electrical and communications systems to meet the evolving needs of the building. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Immediate to Two Years | Currently Critical | 1 | 334650
0322EXT7 | FENCE REPLACEMENT | 0322 | The Redwood fencing at this building is currently falling over and is unsafe. This project would provide for the removal and the replacement of the Redwood fencing with new 465’ of 6’ Redwood fencing. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16275
0322HVA2 | HVAC EQUIPMENT REPLACEMENT | 0322 | The HVAC split systems are not energy efficient and have reached the end of their expected and useful life. The R-22 refrigerant in the cooling systems are no longer EPA compliant and the production is mandated to be phased out completely by January 1, 2020. This project would provide for the installation of 11 new HVAC split systems and the cleaning of the existing duct work and grilles. This project includes the removal and disposal of the existing equipment and all required connections to utilities. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 165000
0322ADA7 | ADA SIGNAGE | 0322 | The ADA provides for accessibility to sites and services for people with physical limitations. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/ pictograms; and sign contrast and finish. The signage in this facility does not comply with these criteria. This project would provide funding for the purchase and the installation of ADA signage to include updated parking signage and directional signage from the accessible parking spaces to the accessible building entrances. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Immediate to Two Years | Currently Critical | 1 | 5000
0322ENV1 | ASBESTOS ABATEMENT | 0322 | The building was tested in September, 2017 and found to have asbestos in the ceiling, joint compound, texture and the flooring mastic. This project would entail the abatement of all asbestos containing materials throughout the building per OSHA Standards (29 CFR 1910.1001) and (29 CFR 1926.58) and the removal and disposal following all OSHA standards. This project should coincide with the alterations and/or remodels listed in this report. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Immediate to Two Years | Currently Critical | 1 | 348036
0322SIT1 | SITE DRAINAGE IMPROVEMENTS | 0322 | The building has considerable damage to the exterior finishes and foundation from improper drainage around the building. The grade does not slope away from the building in many areas. This is causing water to pool up next to the building, infiltrate the windows and damage the concrete foundation walls. This project would create positive flow away from the building by regrading and installing French drains as needed. This project should coincide with the Landscaping Upgrade. This project or a portion thereof was previously recommended in the FCA report dated 06/21/2012. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/07/2017. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
0322SIT2 | LANDSCAPING UPGRADES | 0322 | The landscaping is overgrown and is causing structural, egress and drainage issues. Water accumulates in several areas adjacent to the building which may infiltrate the interior during inclement weather. This standing water also causes premature deterioration of the paving and other landscape improvements. This project would provide for the removal of all trees and bushes surrounding the building and will grade the terrain at a 5% slope for 10’ away from the building and will provide for new landscaping. This project should coincide with the Site Drainage Improvements project. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
0322EXT5 | REPAIR/ REPLACE FASCIA AND SOFFITS | 0322 | The fascia and the soffits on the building are weather beaten, peeling, and are showing signs of considerable wear. This project would provide funding for the removal and disposal of the existing fascia and soffit and the replacement with new fascia and soffit. Also included in this estimate is the sanding, scraping, priming, painting, and any needed roof repairs. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Four to Ten Years | Long-Term Needs | 3 | 24750
0322EXT6 | EXTERIOR FINISHES | 0322 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Four to Ten Years | Long-Term Needs | 3 | 133860
0322SFT14 | OPEN FLAME GRILL REMOVAL | 0322 | There are two fixed open flame grills located within 10 feet of the building. Per IFC 2012 Section 308.1.4 Open-flame cooking device, charcoal burners and other open-flame cooking devices shall not be operated on combustible balconies or within 10 feet (3048 mm) of combustible construction. This project would provide funding for the removal of two grills to comply with this code. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
0322SFT13 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0322 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC 2012 Chapter 10 was referenced for this project. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Immediate to Two Years | Currently Critical | 1 | 26772
0322ELE4 | ELECTRICAL TRANSFORMER REPLACEMENT | 0322 | There is an electrical transformer that is original to the building. The transformer is beyond its life expectancy and should be scheduled for replacement. This project recommends replacing the transformer with a new 30 kVA or greater power transformer. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
0322ELE3 | GFCI OUTLETS | 0322 | There are several outlets throughout the building which are not GFCI protected. These outlets should be changed to GFCI type outlets per the NEC. There are also several GFCI outlets throughout the building which are damaged and not working properly. This project would provide for the purchase and installation of GFCI duplex outlets. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4400
0322INT5 | INTERIOR FINISHES | 0322 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and adequately prepared to receive the coating. An epoxy-based paint should be utilized in wet areas for durability. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 133860
0322INT7 | CEILING SYSTEM REPLACEMENT | 0322 | There is a small section near one of the kitchens where the ceiling height does not meet current code. IBC 2012 Section 1208.2 Minimum Ceiling Heights Occupiable spaces, habitable spaces and corridors shall have a ceiling height of not less than 7 feet 6 inches (2286 mm). Bathrooms, toilet rooms, kitchens, storage rooms and laundry rooms shall be permitted to have a ceiling height of not less than 7 feet (2134 mm). This project would provide funding for the removal and replacement of the ceiling to meet these requirements to include the framing, drywall, texture and paint. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0322SFT11 | FLUE REPLACEMENT | 0322 | The flue vents in the building do not comply with UMC 2012 Chapter 8, Chimneys and Vents. The flue vents were installed with improper flues and per Section 804 direct vent terminations vent terminals for direct vented appliances shall be installed in accordance with the manufacturer’s installation instructions. The flue vents are too close to combustibles, do not have the proper clearances and have a potential to leak CO. Replacements shall meet the manufacturer’s specifications and UMC 2012. The flue vents should be installed by a licensed contractor. This project would provide funds for replacement of the flue vents in the building. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Immediate to Two Years | Currently Critical | 1 | 22000
0322INT4 | ADA RESTROOM UPGRADE | 0322 | The building does not have accessible restrooms. The existing restrooms do not meet ADA requirements. A complete retrofit is necessary of all 10 restrooms. This project would provide funding for construction of 10 unisex accessible restrooms. Items may include relocating walls, new sinks, toilets, hardware, mirrors, fixtures, flooring, showers and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 06/21/2012. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/07/2017. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 300000
0322SFT12 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 0322 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Immediate to Two Years | Currently Critical | 1 | 9000
0322PLM4 | HOSE BIB REPLACEMENT | 0322 | The building has a hose bib that has reached the end of its expected life, has been damaged by freezing temperatures and should be replaced in the next 2-3 years. This project would provide funding for the removal of the existing hose bib and the replacement with a new frost freeze hose bib. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
0322SFT4 | SECURITY SYSTEM INSTALLATION | 0322 | The building does not have a security system and several burglaries have taken place. For security and safety purposes, this project recommends motion detection, door switches, access control and related items to be installed and interfaced with the fire alarm. This project or a portion thereof was previously recommended in the FCA report dated 06/21/2012. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/07/2017. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Immediate to Two Years | Currently Critical | 1 | 66930
0322PLM2 | WATER HEATER REPLACEMENT | 0322 | There is a 5 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
0322INT3 | KITCHEN REMODEL | 0322 | The kitchens were in poor condition at the time of the survey. The cabinets and equipment are showing signs of wear and tear and are approaching the end of their expected life. The electrical outlets are older and do not appear to be GFCI protected. This project recommends the replacement of the existing kitchen cabinets, counters, fixtures, outlets and equipment with mid-range, high quality components. This project or a portion thereof was previously recommended in the FCA report dated 06/21/2012. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/07/2017. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 75000
0322SFT6 | FIRE SUPPRESSION SYSTEM REPLACEMENT | 0322 | This building has an antiquated automatic fire suppression system. This project recommends replacing the existing system with a double-interlock pre-action fire suppression system and implementing a comprehensive testing and service schedule. Removal and disposal of the existing system is included in the estimate. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Immediate to Two Years | Currently Critical | 1 | 187404
0322PLM1 | WATER HEATER REPLACEMENT | 0322 | There is a 40 gallon gas-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0322ENR1 | LIGHTING UPGRADE | 0322 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 107088
0322EXT4 | EXTERIOR DOOR REPLACEMENT | 0322 | The existing exterior metal doors and frames appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement and installation of 15 new metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 45000
0322PLM3 | PLUMBING REPLACEMENT | 0322 | The plumbing and waste system is older and in poor condition. Most of the system appears to be original to the building and should be scheduled for replacement. The sewer lines are rusted, plugging up and failing especially underground. This project recommends replacing all of the water and sewer lines in the building. This estimate includes removal and disposal of the existing system as required. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Immediate to Two Years | Currently Critical | 1 | 334650
0322SFT7 | SPRINKLER HEAD REPLACEMENT | 0322 | The existing fire suppression sprinkler heads are an older style. They are not functioning properly and are susceptible to damage. This project recommends that all of the existing fire suppression sprinkler heads in the building be removed and replaced with new tamper-resistant fire suppression sprinkler heads. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Immediate to Two Years | Currently Critical | 1 | 5800
0322SFT10 | FIRE ALARM SYSTEM REPLACEMENT | 0322 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and due to this the system no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 " If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure." When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and NAC 477 the State Fire Marshal's requirements. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Immediate to Two Years | Currently Critical | 1 | 107088
0322SFT9 | SMOKE ALARM INSTALLATION | 0322 | IRC 2012 Section R314 and R315.3 explains the requirements for smoke alarms in dwelling units. This includes: installing and maintaining smoke alarms in each sleeping room; having a carbon monoxide and smoke detector on the ceiling or wall outside of each sleeping area and in the immediate vicinity of bedrooms when an alteration, repair or addition requiring a permit occurs. IRC 2012 requires that smoke detectors and carbon monoxide alarms be UL rated. State Fire Marshal NAC 477.915 (3) requires that smoke detectors be connected to the wiring in a building and include a battery for emergency backup power. This project would provide funding for the purchase and installation of smoke alarms and carbon monoxide alarms in accordance with IRC and NAC laws in the event that the building is used as a residential occupancy sometime in the future. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Immediate to Two Years | Currently Critical | 1 | 20000
1958INT1 | INTERIOR FINISHES | 1958 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 11/05/1999 and 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | GROUP HOME - BUILDING #14 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1951 | 1524 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7620
1958SFT1 | SMOKE DETECTOR INSTALLATION | 1958 | The 2006 IBC and 2006 IFC, section 907.2.10.1.2 requires smoke detectors in dwelling units be installed in each sleeping room and on the ceiling or wall outside of each separate sleeping area in the immediate vicinity of bedrooms. State Fire Marshal NAC 477.915 (3) requires that smoke detectors be connected to the building wiring with a battery backup. This project would provide funding for the purchase and installation of smoke detectors. This project or a portion thereof was previously recommended in the FCA report dated 11/05/1999 and 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | GROUP HOME - BUILDING #14 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1951 | 1524 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 1000
1958ENR2 | HVAC EQUIPMENT REPLACEMENT | 1958 | The existing HVAC system consists of wall mounted hydronic heaters and window mounted evaporative coolers. This project would provide for replacing the existing equipment with exterior ground mounted packaged units that provide natural gas-fired heating as well as air conditioning. Ducting and vents will need to be installed in either the attic or the crawlspace as well. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 11/05/1999 and 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | GROUP HOME - BUILDING #14 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1951 | 1524 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
1958ENR1 | WINDOW REPLACEMENT | 1958 | The windows are older dual pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 11 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | GROUP HOME - BUILDING #14 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1951 | 1524 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12100
1958ADA1 | ADA UPGRADES | 1958 | The building does not have an accessible entrance and restroom. The existing restroom does not meet the Americans with Disabilities Act (ADA) requirements and a complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom and an ADA accessible ramp and entrance door / hardware. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | GROUP HOME - BUILDING #14 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1951 | 1524 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 25000
1958STR2 | PATIO STRUCTURE REPLACEMENT | 1958 | There is a wood framed patio structure attached to the east side of the house. The wood structure, especially the roof framing is deteriorating and is showing signs of sagging and dry rot. The 4x4 wood posts are also deteriorating, particularly at the connection to the concrete foundation. This project would provide for the removal and replacement of this patio cover including a new asphalt composition roof to match the main home. This project or a portion thereof was previously recommended in the FCA report dated 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | GROUP HOME - BUILDING #14 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1951 | 1524 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
1958EXT2 | EXTERIOR FINISHES | 1958 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry, sanding, priming and painting the wood soffits and fascia and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | GROUP HOME - BUILDING #14 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1951 | 1524 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7620
2059EXT3 | EXTERIOR FINISHES | 2059 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding for the painting of the exterior of the building as needed. Included in the cost is repairing any cracks and sealing the stone masonry as well as caulking the windows and other penetrations. It is recommended that the building envelope be sealed and painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BUILDING #12 - HISTORICAL (VACANT) | 9985 | HHS | DPBH | NNAMHS | Sparks | 1882 | 4076 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20380
2725ADA1 | ADA RESTROOM UPGRADES | 2725 | The designated Men's and Women's ADA accessible restrooms are not fully compliant with the adopted codes. The toilet seat cover dispensers are not in the correct location, the men's toilet seat handle is on the wrong side and the toilet seats do not have the required open-front and elongated shape. A partial retrofit is necessary. This project would provide funding to bring the restrooms into full ADA compliance. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) was used as a reference for this project. | CENTRAL KITCHEN - BUILDING #26 | 9985 | HHS | DPBH | NNAMHS | Sparks | 2007 | 4626 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 1500
2725INT1 | INTERIOR FINISHES | 2725 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | CENTRAL KITCHEN - BUILDING #26 | 9985 | HHS | DPBH | NNAMHS | Sparks | 2007 | 4626 | 2017-10-18 | Four to Ten Years | Long-Term Needs | 3 | 23130
2725EXT1 | EXTERIOR FINISHES | 2725 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CENTRAL KITCHEN - BUILDING #26 | 9985 | HHS | DPBH | NNAMHS | Sparks | 2007 | 4626 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 23130
2449EXT3 | EXTERIOR FINISHES | 2449 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing the exterior, priming and painting the stucco, sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | DINI-TOWNSEND HOSPITAL- BUILDING #25 | 9985 | HHS | DPBH | NNAMHS | Sparks | 2000 | 59040 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 295200
2678EXT1 | EXTERIOR FINISHES | 2678 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for staining of the wood structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | KIOSK | 9985 | HHS | DPBH | NNAMHS | Sparks | 1961 | 36 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 180
2677EXT1 | EXTERIOR FINISHES | 2677 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | PARKING RAMADA | 9985 | HHS | DPBH | NNAMHS | Sparks | 1980 | 512 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1024
2449EXT2 | ROOF REPLACEMENT | 2449 | The single-ply roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average single-ply roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1999. It is recommended that this buildings single-ply roofing be replaced in the next 6-7 years to be consistent with the roofing program and the end of the warranty period. This project does not apply to the asphalt composition shingle roofing. This project or a portion thereof was previously recommended in the FCA report dated 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | DINI-TOWNSEND HOSPITAL- BUILDING #25 | 9985 | HHS | DPBH | NNAMHS | Sparks | 2000 | 59040 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 200000
2449INT1 | INTERIOR FINISHES | 2449 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | DINI-TOWNSEND HOSPITAL- BUILDING #25 | 9985 | HHS | DPBH | NNAMHS | Sparks | 2000 | 59040 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 295200
9985PLM1 | SITE DOMESTIC WATER LINE REPLACEMENT | 9985 | The existing domestic water supply lines and main feeding the campus are aged and should be scheduled for replacement. there have been numerous leaks and the system has been problematic due to age. This project would provide for the complete replacement of the domestic water supply system including trenching, backfill, grading and required backflow prevention. to each occupied building on site. | NNAMHS SITE | 9985 | HHS | DPBH | NNAMHS | Sparks | 1882 |  | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2100000
9985SIT3 | CONCRETE AND PAVING UPGRADE SITEWIDE | 9985 | The site has a mix of PC concrete and asphalt concrete roads, parking lots and pedestrian paths. Many areas are damaged and have settled which have created incorrect slopes and trip hazards. There are limited ADA parking spaces and accessible routes to the public entrances. Some buildings have been recently demolished and may be ideal locations for new parking lots, circulation roads or accessible paths of travel. Additional parking is also necessary to accommodate growing outpatient caseloads and staff. This project would provide for repairing or replacing existing paving and installing new paving including all necessary accessibility upgrades based on a professionally designed sitewide plan. This project should be implemented concurrently with the LANDSCAPE UPGRADES project. This project or a portion thereof was previously recommended in the FCA report dated 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | NNAMHS SITE | 9985 | HHS | DPBH | NNAMHS | Sparks | 1882 |  | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 850000
9985SFT1 | FIRE ALARM SYSTEM UPGRADE | 9985 | The existing wireless portion of the fire alarm system is over 25 years old and has reached its useful life. Certification of the system is costly, parts are no longer available and the system is routinely failing. A common occurrence is that the Fire Department is notified of an alarm, but the system reports the alarm in the wrong building. This can cause vital time loss to control the fire, protect the building and ensure the life safety of the occupants. The wireless annunciation system consists of a repeater panel in each of the 20 buildings and a master control panel that is currently located near Building #12. This project would provide for replacing the repeater in each building, replacing the master control panel and relocating it to Building #25 and providing miscellaneous work to ensure that each buildings alarm system is functioning properly. This project or a portion thereof was previously recommended in the FCA report dated 06/26/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | NNAMHS SITE | 9985 | HHS | DPBH | NNAMHS | Sparks | 1882 |  | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 400000
9985SIT4 | SANITARY SEWER LINE REPLACEMENT | 9985 | The sanitary wastewater system is showing signs of deterioration. Because of the deterioration, the system is not working to its full potential. Some of the lines are original to the site and are in fair to poor condition. The passage of time and constant heavy use are contributing factors to problems that arise. Deposits within the pipes will cause them to be restricted, which will slow the flow of water. This project would provide for the complete replacement of the sanitary sewer system on site from the city connection to each occupied building on site. This project or a portion there of was previously recommended in the FCA report dated 11/03/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/26/2006. | NNAMHS SITE | 9985 | HHS | DPBH | NNAMHS | Sparks | 1882 |  | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 2500000
9985HVA1 | DIRECT DIGITAL CONTROL SYSTEM FOR HVAC SYSTEMS | 9985 | Presently the site has no direct digital control (DDC) supervisory control or automated energy management control programs. Future HVAC considerations should include installation of appropriate hardware to connect any new buildings to the campus energy management network while maintaining local control logic. The new system should allow starting of equipment, monitoring of status, monitoring of space temperatures, monitoring and control of hot and chilled water temperatures, and similar typical centrally controlled elements. For the sake of retention of the relatively new pneumatic equipment, the application of a DDC/pneumatic hybrid system is strongly recommended. Detailed control of the individual elements of the system buildings can yield tremendous benefits based upon the reported operating hours coupled with varying occupancy loads. The system should include a microprocessor control center which monitors and manages all components of the building HVAC system. The system should also have the capability of controlling other building systems (such as lighting, alarms, etc.) and of communicating with the central management system for the campus. This project or a portion thereof was previously recommended in the FCA report dated 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. Did not use this project. | NNAMHS SITE | 9985 | HHS | DPBH | NNAMHS | Sparks | 1882 |  | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 350000
9985SIT1 | LANDSCAPE UPGRADES | 9985 | The landscaping sitewide is in fair condition, but there are several areas that are due for upgrades. The existing galvanized landscape irrigation lines throughout the site are reaching the end of their expected life and should be scheduled for replacement. This old piping breaks often and very likely has underground leaks that are unknown at this point. There are concrete benches and planters around the site that have deteriorated, some to the point of exposing the metal rebar, which should be repaired or replaced. This project would provide for the removal of the existing irrigation lines and the purchase and installation of new lines and repair or replacement of the damaged concrete benches and planters. 6,000 linear feet of irrigation piping was used to generate this estimate. This project should be implemented concurrently with the CONCRETE AND PAVING UPGRADE SITEWIDE project. | NNAMHS SITE | 9985 | HHS | DPBH | NNAMHS | Sparks | 1882 |  | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 75000
9985SIT5 | FENCE REPAIR | 9985 | There is a fence surrounding the back yard of Building #8C. The fence is constructed of 2"x 6" x 5’ dog eared redwood fence planks and 4"x4" redwood posts. It is due for staining and some boards and posts are broken. This project would provide for the repair and/ or replacement of damaged areas of the fence and staining of the entire fence. This project or a portion thereof was previously recommended in the FCA report dated 06/26/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | NNAMHS SITE | 9985 | HHS | DPBH | NNAMHS | Sparks | 1882 |  | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
9985ELE1 | SITE ELECTRICAL UPGRADE | 9985 | The site's electrical distribution system is a mix of old direct buried 4180 volt cable and newer 4180 volt cable in conduit where remodels or upgrades have occurred over the years. The main switchgear and transformers at the emergency generator have reached the end of there useful life and are in need of replacement. This project would provide for a complete upgrade and replacement of 4180 volt cable in conduit where direct buried cable is present from the main switchgear including new transformers, switchgear, trenching and backfill, new conduit to all existing buildings on site. Removal of the old existing cable and equipment is included in this estimate. Individual building electrical upgrades are not included in this estimate. | NNAMHS SITE | 9985 | HHS | DPBH | NNAMHS | Sparks | 1882 |  | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1850000
0326INT4 | CEILING SYSTEM REPLACEMENT | 0326 | The 2nd floor of this building has a suspended acoustical tile ceiling system. The t-bar framing is bent and damaged in many areas and a number of the ceiling tiles are damaged and stained. This project would provide for the replacement of the suspended acoustical tile ceiling system. Removal and disposal of the existing ceiling system is included in this estimate. | ADMINISTRATION - BUILDING #1 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1920 | 32933 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 104000
0326EXT5 | EXTERIOR DOOR REPLACEMENT | 0326 | The storefront system at the entrance and the exterior metal man doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the storefront system and all of the metal man doors except the new ADA door on the east side of the building with new metal doors, frames and hardware. Removal and disposal of the existing doors is included in this estimate. | ADMINISTRATION - BUILDING #1 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1920 | 32933 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0326ADA4 | LEVER HARDWARE INSTALLATION | 0326 | Section 4.13.9 of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) states that handles, pulls, latches, locks and other operating devices on accessible doors shall have a shape that is easy to grasp with one hand and does not require tight grasping, tight pinching, or twisting of the wrist to operate. It is recommended that compliant hardware be installed on approximately 45 interior doors to meet these guidelines. This project or a portion thereof was previously recommended in the FCA report dated 06/27/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | ADMINISTRATION - BUILDING #1 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1920 | 32933 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 22500
0326INT6 | RESTROOM REMODEL | 0326 | The eight restrooms in the north and south wings of the building are over 30 years old and in overall poor condition. The finishes, fixtures, cabinets, partitions, toilets and exhaust fans are showing signs of wear and deterioration. This project would provide for a complete remodel of the restrooms. The removal and disposal of the existing fixtures and finishes is included in this estimate. | ADMINISTRATION - BUILDING #1 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1920 | 32933 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 120000
0326HVA1 | HVAC EQUIPMENT REPLACEMENT | 0326 | The four HVAC roof top units were installed over 25 years ago. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of four new HVAC packaged units and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 02/06/2004 and 06/27/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | ADMINISTRATION - BUILDING #1 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1920 | 32933 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 410610
0326ADA7 | BREAK ROOM REMODEL | 0326 | The kitchenette and associated cabinets in the four employee break rooms are original to the building. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and counter tops are delaminating and failing. This project recommends the replacement of the existing kitchen counters, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) should be incorporated into the design such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. | ADMINISTRATION - BUILDING #1 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1920 | 32933 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 16000
0326EXT1 | ROOF REPLACEMENT | 0326 | The roof on this building was in fair to poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed over 20 years ago. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 06/27/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | ADMINISTRATION - BUILDING #1 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1920 | 32933 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 168000
0327EXT5 | ROOF REPLACEMENT | 0327 | The roof on this building was in fair to poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed over 20 years ago. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. | CANTEEN - DROP-IN CENTER - BUILDING #2 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1961 | 11828 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 118068
0326ADA2 | INTERIOR STAIR HANDRAIL REPLACEMENT | 0326 | The stair handrails are older and do not meet code for safety or accessibility. The gripping surfaces are incorrect and they are not continuous from the top to bottom landings. This project recommends the installation of handrails on both sides of the stairs, with proper returns and supports at three separate flights of stairs. Removal and disposal of the existing railing is included. NRS 338.180, 2006 IBC Chapter 10, Section 1012, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 06/27/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | ADMINISTRATION - BUILDING #1 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1920 | 32933 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 25000
0326SFT2 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0326 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2006 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA reports dated 02/06/2004 and 06/27/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | ADMINISTRATION - BUILDING #1 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1920 | 32933 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 7000
0331INT1 | INTERIOR FINISHES | 0331 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 10/27/1999 and 06/26/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | LAB/PHARMACY - BUILDING #3 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1925 | 15344 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 76720
0329EXT7 | EXTERIOR DOOR REPLACEMENT | 0329 | There are six exterior metal doors that are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of six metal door assemblies with new metal doors, frames and hardware. Removal and disposal of the existing doors is included in this estimate. The storefront door and window systems are not included in this project. | BUILDING #4 (VACANT) | 9985 | HHS | DPBH | NNAMHS | Sparks | 1961 | 19325 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18000
0329INT4 | CEILING SYSTEM REPLACEMENT | 0329 | The majority of the building has a suspended acoustical tile ceiling system. The t-bar framing is old, bent and rusted in many areas and many ceiling tiles are damaged and stained. This project would provide for the replacement of the suspended acoustical tile ceiling system including the framing, acoustical tile and seismic bracing assemblies. Removal and disposal of the existing ceiling system is included in this estimate. | BUILDING #4 (VACANT) | 9985 | HHS | DPBH | NNAMHS | Sparks | 1961 | 19325 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 144000
0330HVA3 | HVAC EQUIPMENT REPLACEMENT | 0330 | The HVAC system was installed in 1999 and should be scheduled for replacement. It consists of roof mounted packaged units and window mounted evaporative coolers. The system is not energy efficient and has reached the end of its expected and useful life. Also, the air conditioner compressor is not functioning. This project would provide for installation of a new HVAC system and cleaning of the existing duct work and grilles. The new system shall be designed to significantly reduce electrical and natural gas usage in order to comply with the 2009 IECC and ASHRAE 90.1 and to reduce utility costs. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 06/28/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | GROUP HOME - BUILDING #8A | 9985 | HHS | DCFS | NNCAS | Sparks | 1977 | 5237 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 78555
0330INT1 | INTERIOR FINISHES | 0330 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA reports dated 10/29/1999 and 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | GROUP HOME - BUILDING #8A | 9985 | HHS | DCFS | NNCAS | Sparks | 1977 | 5237 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 26185
0330EXT4 | SKYLIGHT REPLACEMENT | 0330 | There are two 8’x8’ acrylic sky-lights located on the roof. Both units have cracks in them that are allowing water to penetrate inside during rain or snow events. This project would provide for the removal, disposal and replacement of two acrylic skylight units. Minor roof repairs are included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 06/28/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | GROUP HOME - BUILDING #8A | 9985 | HHS | DCFS | NNCAS | Sparks | 1977 | 5237 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 8000
0330ADA3 | LEVER HARDWARE INSTALLATION | 0330 | Section 4.13.9 of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) states that handles, pulls, latches, locks and other operating devices on accessible doors shall have a shape that is easy to grasp with one hand and does not require tight grasping, tight pinching, or twisting of the wrist to operate. It is recommended that compliant hardware be installed in this building to meet these guidelines. This project would provide for the purchase and installation of 15 lever action hardware to be placed on all the interior doors. This project or a portion thereof was previously recommended in the FCA report dated 06/28/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | GROUP HOME - BUILDING #8A | 9985 | HHS | DCFS | NNCAS | Sparks | 1977 | 5237 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 7500
0330EXT3 | ROOF HATCH | 0330 | The roof hatch is broken and needs to be replaced. This project would provide for the purchase and installation of a new roof hatch. This estimate includes removal and disposal of the existing damaged hatch and any patching and / or repairs to the roof membrane. | GROUP HOME - BUILDING #8A | 9985 | HHS | DCFS | NNCAS | Sparks | 1977 | 5237 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0330ADA4 | ADA SIGNAGE | 0330 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 06/28/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | GROUP HOME - BUILDING #8A | 9985 | HHS | DCFS | NNCAS | Sparks | 1977 | 5237 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 2500
0330INT2 | KITCHEN REMODEL | 0330 | The two kitchens are in fair to poor condition. The cabinets and equipment are showing signs of general wear and tear and are approaching the end of their expected life. This project recommends the replacement of the existing kitchen cabinets, counters, fixtures and equipment with mid range, high quality components. | GROUP HOME - BUILDING #8A | 9985 | HHS | DCFS | NNCAS | Sparks | 1977 | 5237 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0330ADA1 | ADA RESTROOM REMODEL | 0330 | The building does not have an accessible restroom. The existing restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit of two restrooms is necessary. This project would provide funding for construction of two unisex accessible restrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | GROUP HOME - BUILDING #8A | 9985 | HHS | DCFS | NNCAS | Sparks | 1977 | 5237 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 30000
0330EXT5 | EXTERIOR FINISHES | 0330 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 5-6 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | GROUP HOME - BUILDING #8A | 9985 | HHS | DCFS | NNCAS | Sparks | 1977 | 5237 | 2017-10-18 | Four to Ten Years | Long-Term Needs | 3 | 26185
0330ENR2 | WINDOW REPLACEMENT | 0330 | The windows are original, dual pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of approximately 40 units. Removal and disposal of the existing windows is included in this estimate. | GROUP HOME - BUILDING #8A | 9985 | HHS | DCFS | NNCAS | Sparks | 1977 | 5237 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 40000
0330EXT2 | ROOF CLEANING / REPAIRS | 0330 | The roof on this building was in fair condition at the time of the survey. The roof has a few seams that need to be sealed and miscellaneous debris and dirt though out. This project would provide funding to seal the seams and clean off the dirt and debris from the roof. The removal of debris and cleaning must be in conformance with the roofing manufacture's specifications so as not to void the warranty. This project applies to the single-ply membrane portion of the roof. | GROUP HOME - BUILDING #8A | 9985 | HHS | DCFS | NNCAS | Sparks | 1977 | 5237 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 500
0327EXT3 | EXTERIOR FINISHES | 0327 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CANTEEN - DROP-IN CENTER - BUILDING #2 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1961 | 11828 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 49195
0326ADA6 | ADA RESTROOM UPGRADE | 0326 | The staff restrooms near the Lobby do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for remodeling the Men's and Women's restrooms into ADA compliant restrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | ADMINISTRATION - BUILDING #1 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1920 | 32933 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 30000
0326INT5 | INTERIOR DOOR REPLACEMENT | 0326 | Five of the interior doors in this building are damaged and do not operate properly. This project would provide for the installation of new solid core interior doors including frames, lever action door handles, hardware and paint. Removal and disposal of the existing doors is included in this cost estimate. A total of 5 interior doors was used in this estimate. | ADMINISTRATION - BUILDING #1 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1920 | 32933 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0327INT3 | INTERIOR FINISHES | 0327 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA reports dated 10/27/1999 and 06/26/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | CANTEEN - DROP-IN CENTER - BUILDING #2 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1961 | 11828 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 49195
0327ELE2 | ELECTRICAL UPGRADE | 0327 | This building was constructed before the high demand for electrical services were needed for computers and other electrical devices. As time has progressed, the buildings electrical demand and system has changed. Numerous safety issues, missing duplex covers, and painted receptacles are present. It is recommended the entire system be upgraded to meet the evolving needs of the building including a comprehensive rewiring and replacement of outdated and failing outlets, switches and panels, and adding additional capacity for anticipated needs. This project or a portion thereof was previously recommended in the FCA report dated 06/26/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | CANTEEN - DROP-IN CENTER - BUILDING #2 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1961 | 11828 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 196780
0327SFT1 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0327 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2006 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA reports dated 10/27/1999 and 06/26/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | CANTEEN - DROP-IN CENTER - BUILDING #2 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1961 | 11828 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 5000
0327HVA3 | HVAC REPLACEMENT | 0327 | The roof top air handlers are more than 30 years old. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of two new multi-zone air handling units and two new single-zone air handling units and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. This work is currently recommended for the 2013 Capitol Improvement Program. This project or a portion thereof was previously recommended in the FCA reports dated 10/27/1999 and 06/26/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | CANTEEN - DROP-IN CENTER - BUILDING #2 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1961 | 11828 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 250000
0331ADA2 | ADA RESTROOM UPGRADE | 0331 | The building does not have an accessible restroom. The existing restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for remodeling one Men's and one Women's restrooms into ADA compliant restrooms. The items to be addressed may include sinks, toilets, hardware, mirrors, fixtures, flooring and paint. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | LAB/PHARMACY - BUILDING #3 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1925 | 15344 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 60000
0326EXT2 | WINDOW REPLACEMENT | 0326 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of approximately 250 units. Removal and disposal of the existing windows is included in this estimate. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. This project or a portion thereof was previously recommended in the FCA report dated 02/06/2004 and 06/27/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | ADMINISTRATION - BUILDING #1 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1920 | 32933 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 250000
0331ADA4 | ELEVATOR REPAIRS | 0331 | This building has an elevator, but it has been out of service for some time, and it does not comply with ADA standards. This project would provide funding to repair the elevator to improve maintenance, facilitate control of this building and comply with the ICC/ANSI A117.1998 Section 407. These repairs are to include but not limited to updating the control panel, door reversing light beams, call button, hall station upgrades, and a hands-free telephone. | LAB/PHARMACY - BUILDING #3 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1925 | 15344 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0326EXT4 | EXTERIOR FINISHES | 0326 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry and concrete accents and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | ADMINISTRATION - BUILDING #1 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1920 | 32933 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 136870
0326INT7 | SHOWER ROOM REMODEL | 0326 | The Men's and Women's shower rooms on the 2nd floor are over 30 years old and in overall poor condition. The finishes, fixtures and exhaust fans are showing signs of severe wear and deterioration. This project would provide for a complete remodel of the shower rooms. The removal and disposal of the existing fixtures and finishes is included in this estimate. If it is deemed unnecessary to provide shower facilities in the building, it is recommended to remove the showers and remodel the rooms into storage rooms or offices. | ADMINISTRATION - BUILDING #1 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1920 | 32933 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
0331EXT7 | EXTERIOR DOOR REPLACEMENT | 0331 | There are four exterior metal doors that are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of four metal door assemblies with new metal doors, frames and hardware. Removal and disposal of the existing doors is included in this estimate. The storefront door and window systems are not included in this project. | LAB/PHARMACY - BUILDING #3 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1925 | 15344 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
0331INT2 | FLOORING REPLACEMENT | 0331 | The VCT (vinyl composite tile), sheet vinyl and ceramic tile in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the next 2-3 years. Asbestos testing and abatement is NOT included in this estimate if required. | LAB/PHARMACY - BUILDING #3 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1925 | 15344 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 122752
0331INT3 | CEILING SYSTEM REPLACEMENT | 0331 | The majority of the building has a suspended acoustical tile ceiling system. The t-bar framing is old, bent and rusted in many areas and many ceiling tiles are damaged and stained. This project would provide for the replacement of the suspended acoustical tile ceiling system including the framing, acoustical tile and seismic bracing assemblies. Removal and disposal of the existing ceiling system is included in this estimate. | LAB/PHARMACY - BUILDING #3 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1925 | 15344 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 112000
0326ADA8 | DRINKING FOUNTAIN REPLACEMENT | 0326 | This building contains water fountains on each floor that are not ADA compliant. The 2006 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of four drinking fountains to meet the ADA requirements, two on each floor. | ADMINISTRATION - BUILDING #1 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1920 | 32933 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 8000
0327INT4 | FLOORING REPLACEMENT | 0327 | The sheet vinyl flooring in the gymnasium is damaged and reaching the end of its useful life. The gymnasium is the main indoor recreational facility on the site. It is a multi-purpose room where games can be played or different types of gatherings may occur. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base in the next 2-3 years. This project or a portion thereof was previously recommended in the FCA reports dated 10/27/1999 and 06/26/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | CANTEEN - DROP-IN CENTER - BUILDING #2 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1961 | 11828 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 70000
0328INT2 | INTERIOR FINISHES | 0328 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | LIBRARY/MEETING ROOMS - BUILDING #2A | 9985 | HHS | DPBH | NNAMHS | Sparks | 1977 | 5589 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 27945
0326ADA10 | ELEVATOR INSTALLATION | 0326 | There is no elevator in the building to provide an accessible path of travel to the 2nd floor. This building is required to have an accessible path of travel to the 2nd floor if an employee with disabilities is stationed on the 2nd floor per the Americans with Disabilities Act (ADA) regulations. This project would provide for an accessible elevator to be installed to access the 2nd floor of the building. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | ADMINISTRATION - BUILDING #1 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1920 | 32933 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 250000
0328ADA5 | LEVER HARDWARE INSTALLATION | 0328 | Section 4.13.9 of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) states that handles, pulls, latches, locks and other operating devices on accessible doors shall have a shape that is easy to grasp with one hand and does not require tight grasping, tight pinching, or twisting of the wrist to operate. It is recommended that compliant hardware be installed in this building to meet these guidelines. | LIBRARY/MEETING ROOMS - BUILDING #2A | 9985 | HHS | DPBH | NNAMHS | Sparks | 1977 | 5589 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 7500
0328ENR2 | HVAC EQUIPMENT REPLACEMENT | 0328 | The roof mounted HVAC unit was installed in 1999 and should be scheduled for replacement. The system is not energy efficient and has reached the end of its expected and useful life. This project would provide for installation of a new HVAC unit and cleaning of the existing duct work and grilles. The new system shall be designed to significantly reduce electrical and natural gas usage in order to comply with the 2009 IECC and ASHRAE 90.1 and to reduce utility costs. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | LIBRARY/MEETING ROOMS - BUILDING #2A | 9985 | HHS | DPBH | NNAMHS | Sparks | 1977 | 5589 | 2017-10-18 | Four to Ten Years | Long-Term Needs | 3 | 83835
0328ENR1 | WINDOW REPLACEMENT | 0328 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of approximately 20 units. Removal and disposal of the existing windows is included in this estimate. | LIBRARY/MEETING ROOMS - BUILDING #2A | 9985 | HHS | DPBH | NNAMHS | Sparks | 1977 | 5589 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0328ADA2 | ADA RESTROOM UPGRADE | 0328 | The Men's and Women's designated ADA restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for remodeling the Men's and Women's restrooms into ADA compliant restrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | LIBRARY/MEETING ROOMS - BUILDING #2A | 9985 | HHS | DPBH | NNAMHS | Sparks | 1977 | 5589 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 30000
0329HVA1 | HVAC EQUIPMENT REPLACEMENT | 0329 | The HVAC system was installed over 30 years ago and should be scheduled for replacement. It consists of roof mounted heat pumps which cause consistent maintenance problems. The system is not energy efficient and has reached the end of its expected and useful life. This project would provide for installation of a new HVAC system and cleaning of the existing duct work and grilles. The new system shall be designed to significantly reduce electrical and natural gas usage in order to comply with the 2009 IECC and ASHRAE 90.1 and to reduce utility costs. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 10/27/1999 and 06/26/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | BUILDING #4 (VACANT) | 9985 | HHS | DPBH | NNAMHS | Sparks | 1961 | 19325 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 386500
0328INT3 | CEILING SYSTEM REPLACEMENT | 0328 | The Meeting Room on the north side of the building has a suspended acoustical tile ceiling system that is old and should be scheduled for replacement. The t-bar framing is bent in some areas and many ceiling tiles are damaged and stained. This project would provide for the replacement of the suspended acoustical tile ceiling system including the framing, acoustical tile and seismic bracing assemblies. Removal and disposal of the existing ceiling system is included in this estimate. | LIBRARY/MEETING ROOMS - BUILDING #2A | 9985 | HHS | DPBH | NNAMHS | Sparks | 1977 | 5589 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
0329SFT1 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0329 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2006 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA reports dated 10/27/1999 and 06/26/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | BUILDING #4 (VACANT) | 9985 | HHS | DPBH | NNAMHS | Sparks | 1961 | 19325 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 7500
0328ADA4 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0328 | This building contains a water fountain. The 2006 IBC Section 1109.5 states where a water fountain is provided, at least half should be accessible. This project would provide funding for the purchase and installation of a new accessible fixed high/ low ADA drinking fountain. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | LIBRARY/MEETING ROOMS - BUILDING #2A | 9985 | HHS | DPBH | NNAMHS | Sparks | 1977 | 5589 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 4000
0328SFT1 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0328 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2006 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA reports dated 10/27/1999 and 06/26/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | LIBRARY/MEETING ROOMS - BUILDING #2A | 9985 | HHS | DPBH | NNAMHS | Sparks | 1977 | 5589 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 2000
0328EXT4 | ROOF REPLACEMENT | 0328 | The single ply membrane roof and the wood shingle roof on this building were in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new single ply membrane and a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. This project or a portion thereof was previously recommended in the FCA report dated 06/26/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | LIBRARY/MEETING ROOMS - BUILDING #2A | 9985 | HHS | DPBH | NNAMHS | Sparks | 1977 | 5589 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 67068
0327PLM1 | WATER HEATER REPLACEMENT | 0327 | There is a 50 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 6-7 years. It is recommended that a new gas-fired water heater be installed for more efficient use of energy. This estimate includes: 100 feet of gas pipe, fittings, couplers, and labor for installation. Removal and disposal of the existing equipment is included in this estimate. | CANTEEN - DROP-IN CENTER - BUILDING #2 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1961 | 11828 | 2017-10-18 | Four to Ten Years | Long-Term Needs | 3 | 3750
0327INT2 | JANITORS CLOSET REPAIRS | 0327 | The mop sink in the Janitors Closet is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | CANTEEN - DROP-IN CENTER - BUILDING #2 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1961 | 11828 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
0331EXT6 | EXTERIOR FINISHES | 0331 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry and concrete accents and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | LAB/PHARMACY - BUILDING #3 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1925 | 15344 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 76720
0328EXT5 | EXTERIOR FINISHES | 0328 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | LIBRARY/MEETING ROOMS - BUILDING #2A | 9985 | HHS | DPBH | NNAMHS | Sparks | 1977 | 5589 | 2017-10-18 | Four to Ten Years | Long-Term Needs | 3 | 27945
0329INT2 | FLOORING REPLACEMENT | 0329 | The VCT (vinyl composite tile) and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the next 2-3 years. Additional costs are included for the possibility of asbestos abatement. This project or a portion thereof was previously recommended in the FCA report dated 06/26/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | BUILDING #4 (VACANT) | 9985 | HHS | DPBH | NNAMHS | Sparks | 1961 | 19325 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 193250
0327EXT4 | SOFFIT REPLACEMENT | 0327 | The exterior soffits around the building are weather beaten, broken and are showing signs of considerable wear. It appears that this type of suspended ceiling soffit is not holding up well against the inclement weather in this climate. This project would provide funding to replace the soffits with a more durable system. | CANTEEN - DROP-IN CENTER - BUILDING #2 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1961 | 11828 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0326ELE2 | ELECTRICAL UPGRADE | 0326 | This building was constructed before the high demand for electrical services were needed for computers and other electrical devices. As time has progressed, the buildings electrical demand and system has changed. Numerous safety issues including non-GFCI outlets in restrooms or near sinks, missing duplex covers and painted receptacles are present. It is recommended the entire system be upgraded to meet the evolving needs of the building including a comprehensive rewiring and replacement of outdated and failing outlets, switches and panels, and adding additional capacity for anticipated needs. This project or a portion thereof was previously recommended in the FCA report dated 02/06/2004 and 06/27/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | ADMINISTRATION - BUILDING #1 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1920 | 32933 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 547480
0328ADA3 | ADA SIGNAGE | 0328 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | LIBRARY/MEETING ROOMS - BUILDING #2A | 9985 | HHS | DPBH | NNAMHS | Sparks | 1977 | 5589 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 1500
0329INT1 | INTERIOR FINISHES | 0329 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA reports dated 10/27/1999 and 06/26/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | BUILDING #4 (VACANT) | 9985 | HHS | DPBH | NNAMHS | Sparks | 1961 | 19325 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 96625
0326INT8 | JANITORS CLOSET REPAIRS | 0326 | The mop sink in the Janitors Closet in Room 119 is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | ADMINISTRATION - BUILDING #1 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1920 | 32933 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
0329EXT6 | ROOF CLEANING / REPAIRS | 0329 | The roof on this building was in fair condition at the time of the survey. The roof has a few seams that need to be sealed and miscellaneous debris and dirt though out. This project would provide funding to seal the seams and clean off the dirt and debris from the roof. The removal of debris and cleaning must be in conformance with the roofing manufacture's specifications so as not to void the warranty. | BUILDING #4 (VACANT) | 9985 | HHS | DPBH | NNAMHS | Sparks | 1961 | 19325 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 500
0329INT3 | JANITORS CLOSET REPAIRS | 0329 | The mop sinks in the Janitors Closets are mounted adjacent to gypsum board and are showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. Typical of two Janitors Closets. This project or a portion thereof was previously recommended in the FCA report dated 06/26/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | BUILDING #4 (VACANT) | 9985 | HHS | DPBH | NNAMHS | Sparks | 1961 | 19325 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 2800
0326ADA9 | ADA SIGNAGE | 0326 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | ADMINISTRATION - BUILDING #1 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1920 | 32933 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 3000
0329EXT1 | WINDOW REPLACEMENT | 0329 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. Staff reported that these windows are difficult to open and do not seal properly. Several windows allow water to penetrate to the interior. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of approximately 100 units including costs associated with a two story structure. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA reports dated 10/27/1999 and 06/26/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | BUILDING #4 (VACANT) | 9985 | HHS | DPBH | NNAMHS | Sparks | 1961 | 19325 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 150000
0329ADA3 | ADA UPGRADES | 0329 | Restrooms are present in this building. They do not fully meet the Americans with Disabilities Act (ADA) regulations. One existing restroom is designated as an ADA restroom but it does not comply. The minimum turning radius required cannot be achieved in the current configuration. The staff restroom should be converted to an ADA accessible unisex restroom with all new fixtures. This would be the most economical. The second level Men's and Women's restrooms do not comply and either do the showers. These restrooms should be remodeled for compliance to ADA accessibility requirements. This building contains a water fountain. The 2006 IBC Section 1109.5 states where a water fountain is provided, at least half should be accessible. It is recommended this fountain be replaced. Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with these criteria. It is recommended that applicable signage be replaced and/or relocated to comply with ADA requirements. This project or a portion thereof was previously recommended in the FCA reports dated 10/27/1999 and 06/26/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | BUILDING #4 (VACANT) | 9985 | HHS | DPBH | NNAMHS | Sparks | 1961 | 19325 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 150000
0329EXT8 | EXTERIOR FINISHES | 0329 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry and concrete accents and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BUILDING #4 (VACANT) | 9985 | HHS | DPBH | NNAMHS | Sparks | 1961 | 19325 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 96625
0353ADA4 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0353 | This building contains a water fountain. The 2006 IBC Section 1109.5 states where a water fountain is provided, at least half should be accessible. This project would provide funding for the purchase and installation of a new accessible fixed high/ low ADA drinking fountain. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | MAINTENANCE/HOUSEKEEPING BUILDING #22 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1959 | 8040 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 4000
0331EXT4 | ROOF CLEANING / REPAIRS | 0331 | The roof on this building was in fair condition at the time of the survey. The roof has a few seams that need to be sealed and miscellaneous debris and dirt though out. This project would provide funding to seal the seams and clean off the dirt and debris from the roof. The removal of debris and cleaning must be in conformance with the roofing manufacture's specifications so as not to void the warranty. This project applies to the single-ply membrane portion of the roof. | LAB/PHARMACY - BUILDING #3 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1925 | 15344 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 500
0353ENR2 | COOLING EQUIPMENT REPLACEMENT | 0353 | The building is cooled by a combination of roof mounted and wall mounted evaporative coolers and wall mounted air conditioners. All of these units are older and not energy efficient. This project would provide for replacing all of this equipment with new, more energy efficient roof mounted cooling equipment and installing new ducting to non-conditioned spaces. The estimate includes removal and disposal of the old equipment. This project or a portion thereof was previously recommended in the FCA report dated 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | MAINTENANCE/HOUSEKEEPING BUILDING #22 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1959 | 8040 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
0353EXT3 | GUTTER AND DOWNSPOUT INSTALLATION | 0353 | The building only has gutters over entrances and those gutters are damaged and not functioning properly. Currently, the water sheet drain off of the single ply and metal roofing causing erosion to the asphalt and concrete at grade. There are also areas where the runoff pools up near the building causing premature deterioration to the building and creating slip and fall areas during inclement weather. This project would provide funding for the installation of a seamless gutter and downspout system for the building which ties into the site storm system. | MAINTENANCE/HOUSEKEEPING BUILDING #22 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1959 | 8040 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
0353ADA3 | ADA SIGNAGE | 0353 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | MAINTENANCE/HOUSEKEEPING BUILDING #22 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1959 | 8040 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 2000
0353ENR3 | WATER HEATER REPLACEMENT | 0353 | There is a 50 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new natural gas-fired water heater be installed for more efficient use of energy. This estimate includes: 50 feet of gas pipe, fittings, couplers, and labor for installation. Removal and disposal of the existing equipment is included in this estimate. | MAINTENANCE/HOUSEKEEPING BUILDING #22 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1959 | 8040 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3750
0353ADA2 | ADA RESTROOM UPGRADE | 0353 | The building does not have an accessible restroom. The existing restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for remodeling the Men's and Women's restrooms into ADA compliant restrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | MAINTENANCE/HOUSEKEEPING BUILDING #22 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1959 | 8040 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 20000
0521EXT3 | DEMOLISH STRUCTURE | 0521 | The Gazebo Restroom building is dilapidated and deteriorating and has reached the end of its useful life. It has been locked up and not used for several years and is no longer useful since the Dini-Townsend Hospital was built. This project would provide funding for the demolition of the building. | GAZEBO RESTROOM - BUILDING #27 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1976 | 160 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1600
0976EXT3 | EXTERIOR FINISHES | 0976 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | GAZEBO | 9985 | HHS | DPBH | NNAMHS | Sparks | 1976 | 1194 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2388
0353INT1 | INTERIOR FINISHES | 0353 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA report dated 11/02/1999 and 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/29/2006. | MAINTENANCE/HOUSEKEEPING BUILDING #22 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1959 | 8040 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 36070
0353SFT1 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0353 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2006 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | MAINTENANCE/HOUSEKEEPING BUILDING #22 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1959 | 8040 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 3607
0353SFT2 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0353 | The building is a B and S-2 occupancy per the 2006 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 or R-2 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. | MAINTENANCE/HOUSEKEEPING BUILDING #22 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1959 | 8040 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 100996
0334INT1 | INTERIOR FINISHES | 0334 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA reports dated 10/29/1999 and 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | GROUP HOME - BUILDING #8C | 9985 | HHS | DPBH | NNAMHS | Sparks | 1977 | 5237 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 26185
0343SFT1 | SMOKE DETECTOR INSTALLATION | 0343 | The 2006 IBC and 2006 IFC, section 907.2.10.1.2 requires smoke detectors in dwelling units be installed in each sleeping room and on the ceiling or wall outside of each separate sleeping area in the immediate vicinity of bedrooms. State Fire Marshal NAC 477.915 (3) requires that smoke detectors be connected to the building wiring with a battery backup. This project would provide funding for the purchase and installation of smoke detectors. This project or a portion thereof was previously recommended in the FCA report dated 11/05/1999 and 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | GROUP HOME - BUILDING #15 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1949 | 2117 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 1000
0343ADA2 | ACCESSIBLE BUILDING ENTRANCE | 0343 | The building has steps leading into the main entrance which do not comply with accessibility requirements and are missing handrails. The entry door has a threshold and hardware that do not meet the requirements for accessibility. This building is required to have an accessible entrance per the Americans with Disabilities Act (ADA) regulations. This project would provide for an accessible ramp to access the building, handrails, curbing, and replacement of the door hardware and threshold to meet the ADA Accessibility Guidelines. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | GROUP HOME - BUILDING #15 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1949 | 2117 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 35000
0343ADA1 | ADA INTERIOR UPGRADE | 0343 | The family room in this building is accessed by stepping down two steps. A physically challenged person cannot access the kitchen or living room from the family room. It is recommended that an ADA compliant ramp be installed in place of the steps. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 11/05/1999 and 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | GROUP HOME - BUILDING #15 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1949 | 2117 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 10000
0343INT2 | INTERIOR FINISHES | 0343 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 11/05/1999 and 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | GROUP HOME - BUILDING #15 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1949 | 2117 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10585
0343ENR2 | WINDOW REPLACEMENT | 0343 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. Some of the windows have broken seals and are difficult to operate. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 17 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 11/05/1999 and 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | GROUP HOME - BUILDING #15 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1949 | 2117 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 17000
0343ENR1 | HVAC EQUIPMENT REPLACEMENT | 0343 | The existing HVAC system consists of wall mounted hydronic heaters and window mounted evaporative coolers. This project would provide for replacing the existing equipment with exterior ground mounted packaged units that provide natural gas-fired heating as well as air conditioning. Ducting and vents will need to be installed in either the attic or the crawlspace as well. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 11/05/1999 and 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | GROUP HOME - BUILDING #15 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1949 | 2117 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
0334EXT5 | EXTERIOR FINISHES | 0334 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 5-6 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | GROUP HOME - BUILDING #8C | 9985 | HHS | DPBH | NNAMHS | Sparks | 1977 | 5237 | 2017-10-18 | Four to Ten Years | Long-Term Needs | 3 | 26185
0334ENR2 | WINDOW REPLACEMENT | 0334 | The windows are original, dual pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of approximately 40 units. Removal and disposal of the existing windows is included in this estimate. | GROUP HOME - BUILDING #8C | 9985 | HHS | DPBH | NNAMHS | Sparks | 1977 | 5237 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 40000
0353ELE2 | ELECTRICAL UPGRADE | 0353 | This building was constructed before the high demand for electrical services were needed for computers, shop tools, life safety equipment and other electrical devices. As time has progressed, the buildings electrical demand has changed and numerous alterations and additions have been made to the existing electrical system. There are also numerous outlets and switches which are broken or missing proper covers. It is recommended the entire system be upgraded to meet the evolving needs of the building and to bring all components of the system up to current codes. This project or a portion thereof was previously recommended in the FCA report dated 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | MAINTENANCE/HOUSEKEEPING BUILDING #22 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1959 | 8040 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 144280
0334HVA3 | HVAC EQUIPMENT REPLACEMENT | 0334 | The HVAC system was installed in 1999 and should be scheduled for replacement. It consists of roof mounted packaged units and window mounted evaporative coolers. The system is not energy efficient and has reached the end of its expected and useful life. This project would provide for installation of a new HVAC system and cleaning of the existing duct work and grilles. The new system shall be designed to significantly reduce electrical and natural gas usage in order to comply with the 2009 IECC and ASHRAE 90.1 and to reduce utility costs. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 06/28/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | GROUP HOME - BUILDING #8C | 9985 | HHS | DPBH | NNAMHS | Sparks | 1977 | 5237 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 52370
0348ADA1 | ADA RESTROOM UPGRADE | 0348 | The building does not have an accessible restroom. The existing restroom does not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | WAREHOUSE/PURCHASING - BUILDING #21 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1971 | 9642 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 15000
0334INT2 | KITCHEN REMODEL | 0334 | The two kitchens are in fair to poor condition. The cabinets and equipment are showing signs of general wear and tear and are approaching the end of their expected life. This project recommends the replacement of the existing kitchen cabinets, counters, fixtures and equipment with mid range, high quality components. | GROUP HOME - BUILDING #8C | 9985 | HHS | DPBH | NNAMHS | Sparks | 1977 | 5237 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
0334EXT4 | SKYLIGHT REPLACEMENT | 0334 | There are two 8’x8’ acrylic sky-lights located on the roof. Both units have cracks in them that are allowing water to penetrate inside during rain or snow events. This project would provide for the removal, disposal and replacement of two acrylic skylight units. Minor roof repairs are included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 06/28/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | GROUP HOME - BUILDING #8C | 9985 | HHS | DPBH | NNAMHS | Sparks | 1977 | 5237 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 8000
0352SFT2 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0352 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2006 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA reports dated 10/27/1999 and 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | MEDICATION CLINIC - BUILDING #5 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1967 | 5483 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 3500
0352ENR1 | HVAC EQUIPMENT REPLACEMENT | 0352 | The HVAC system has been converted from the central plant steam system to a temporary boiler and chiller with a cooling tower. Funding has been approved to replace the existing chiller and cooling tower, but had not been done at the time of the most recent survey. The large air handler in the basement is also scheduled to be replaced, but was still there in 2012. This project recommends installing a new HVAC system for the building with more energy efficient equipment controlled by an energy management system. The estimate includes removal and disposal of the existing HVAC units and all required connections to utilities. | MEDICATION CLINIC - BUILDING #5 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1967 | 5483 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 75000
0352PLM1 | WATER HEATER REPLACEMENT | 0352 | There is a 50 gallon electric water heater in the basement. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 5-6 years. It is recommended that a new gas-fired water heater be installed for more efficient use of energy. This estimate includes: 50 feet of gas pipe, fittings, couplers, and labor for installation. Removal and disposal of the existing equipment is included in this estimate. | MEDICATION CLINIC - BUILDING #5 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1967 | 5483 | 2017-10-18 | Four to Ten Years | Long-Term Needs | 3 | 3750
0352INT3 | INTERIOR FINISHES | 0352 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 5-6 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | MEDICATION CLINIC - BUILDING #5 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1967 | 5483 | 2017-10-18 | Four to Ten Years | Long-Term Needs | 3 | 27415
0352EXT2 | EXTERIOR FINISHES | 0352 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry, painting the wood panels, soffits and eaves and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | MEDICATION CLINIC - BUILDING #5 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1967 | 5483 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 27415
0353ENR1 | WINDOW REPLACEMENT | 0353 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 20 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | MAINTENANCE/HOUSEKEEPING BUILDING #22 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1959 | 8040 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0334ADA1 | ADA RESTROOM REMODEL | 0334 | The building does not have an accessible restroom. The existing restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit of two restrooms is necessary. This project would provide funding for construction of two unisex accessible restrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | GROUP HOME - BUILDING #8C | 9985 | HHS | DPBH | NNAMHS | Sparks | 1977 | 5237 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 30000
0340ENR2 | WINDOW REPLACEMENT | 0340 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of approximately 85 units. Removal and disposal of the existing windows is included in this estimate. | BUILDING #8 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1958 | 25839 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 85000
0343SFT2 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0343 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. | GROUP HOME - BUILDING #15 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1949 | 2117 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 4000
0343EXT1 | EXTERIOR FINISHES | 0343 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is cleaning and sealing the unpainted walls, painting the painted walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 11/05/1999 and 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | GROUP HOME - BUILDING #15 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1949 | 2117 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10585
0343INT1 | FLOORING REPLACEMENT | 0343 | The carpet in the building is showing signs of extreme wear and should be scheduled for replacement. It is recommended that the carpet be replaced with heavy duty commercial grade carpet in the next 2-3 years. | GROUP HOME - BUILDING #15 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1949 | 2117 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12702
0343ADA3 | ADA RESTROOM REMODEL | 0343 | The building does not have an accessible restroom. The existing restroom does not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | GROUP HOME - BUILDING #15 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1949 | 2117 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 15000
0347SIT1 | BOLLARD INSTALLATION | 0347 | There is a 2,000 gallon diesel tank above ground with no bollards for protection. This project would provide funding for 4 eight inch diameter bollards filled with concrete to be located on each corner of the tank. This project or a portion thereof was previously recommended in the FCA report dated 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | GENERATOR BUILDING - BUILDING #20 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1980 | 1764 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
0340PLM1 | WATER HEATER REPLACEMENT | 0340 | There are two 80 gallon gas-fired water heaters in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, these units are showing signs of wear and should be scheduled for replacement in the next 3-4 years. It is recommended that two new gas-fired water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. | BUILDING #8 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1958 | 25839 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
0340ADA3 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0340 | The Adolescent Services section of the building contains a water fountain. The 2006 IBC Section 1109.5 states where a water fountain is provided, at least half should be accessible. This project would provide funding for the purchase and installation of a new accessible fixed high/ low ADA drinking fountain. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | BUILDING #8 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1958 | 25839 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 4000
0340ADA2 | ADA RESTROOM UPGRADE | 0340 | The Adolescent Services section of the building does not have an accessible restroom. The existing restroom does not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | BUILDING #8 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1958 | 25839 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 15000
0348EXT3 | EXTERIOR FINISHES | 0348 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 10/29/1999 and 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | WAREHOUSE/PURCHASING - BUILDING #21 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1971 | 9642 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 48210
0340EXT4 | EXTERIOR DOOR REPLACEMENT | 0340 | The exterior metal doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of all of the exterior metal man door assemblies with new metal doors, frames and hardware. Removal and disposal of the existing doors is included in this estimate. | BUILDING #8 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1958 | 25839 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 42000
0348ENR1 | WINDOW REPLACEMENT | 0348 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 4 units. Removal and disposal of the existing windows is included in this estimate. | WAREHOUSE/PURCHASING - BUILDING #21 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1971 | 9642 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0340EXT3 | EXTERIOR FINISHES | 0340 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry, painting the painted finishes and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BUILDING #8 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1958 | 25839 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 129195
0340INT2 | INTERIOR FINISHES | 0340 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next 6-8 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | BUILDING #8 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1958 | 25839 | 2017-10-18 | Four to Ten Years | Long-Term Needs | 3 | 129195
0340ELE1 | LIGHTING UPGRADE | 0340 | Existing building lighting fixtures, T-12s, are older fluorescent types and not energy efficient. This project will upgrade lighting fixtures to T-8s with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. This project or a portion there of was previously recommended in the FCA report dated 10/28/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/27/2006. Project complete. | BUILDING #8 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1958 | 25839 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 65000
0347LGT1 | LONG TERM NEEDS | 0347 | Projects in this category address possible long term needs of the facility. This does not represent a cost for all future maintenance but is a budgetary number for future Capital Improvement Projects related to maintenance and is based on a 10 year planning cycle. The cyclical treatment of the building exterior and interior is very important to help maintain the finish, weather proofing, integrity and appearance of the building. This treatment does not include the roofing material itself but it should include everything that has to do with water proofing the building envelope including painting or staining, sealing, repair, and caulking where applicable; for example, around all windows, flashing, fixtures, sills, etc. This also includes interior applied finishes such as paint, grout, caulking, etc. Special attention should be paid to areas that are exposed to moisture. This project or a portion there of was previously recommended in the FCA report dated 10/29/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/29/2006. Reassigned to more specific projects. | GENERATOR BUILDING - BUILDING #20 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1980 | 1764 | 2017-10-18 | Four to Ten Years | Long-Term Needs | 3 | 18000
0347ELE1 | ELECTRICAL EQUIPMENT REPLACEMENT | 0347 | The main electrical switchgear in the building is over 30 years old and should be scheduled for replacement. Staff noted at the time of the survey that the equipment will cost between $250,000 and $500,000 to replace. The equipment was working at the time of the survey, but it is vital to the needs of the campus and therefore should be scheduled for replacement. This project would replace the main switchgear and associated electrical equipment in the building. | GENERATOR BUILDING - BUILDING #20 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1980 | 1764 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500000
0348SFT2 | EGRESS DOOR HARDWARE UPGRADE | 0348 | The egress door located on north west side of the building was locked shut from the inside with deadbolt hardware. IBC 2006 section 1008.1.8.4 prohibits manually operated flush bolts or surface bolts on egress doors. This project would provide for the purchase and installation of emergency panic hardware to be installed on the door and removing the deadbolt locking hardware. This project or a portion thereof was previously recommended in the FCA report dated 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | WAREHOUSE/PURCHASING - BUILDING #21 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1971 | 9642 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 2000
0348EXT2 | ROOF REPLACEMENT | 0348 | The roof on this building was in poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1995. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | WAREHOUSE/PURCHASING - BUILDING #21 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1971 | 9642 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 115704
0348INT1 | INTERIOR FINISHES | 0348 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 10/29/1999 and 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | WAREHOUSE/PURCHASING - BUILDING #21 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1971 | 9642 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
0347EXT2 | EXTERIOR FINISHES | 0347 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 10/29/1999 and 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | GENERATOR BUILDING - BUILDING #20 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1980 | 1764 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8820
0340INT3 | CARPET REPLACEMENT | 0340 | The carpet in the Adolescent Services section of the building is showing signs of extreme wear and should be scheduled for replacement. It is recommended that the carpet be replaced with heavy duty commercial grade carpet in the next 2-3 years. The estimate is based on replacing approximately 6,000 square feet of carpet. | BUILDING #8 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1958 | 25839 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 36000
0333EXT3 | ROOF HATCH | 0333 | The roof hatch is broken and needs to be replaced. This project would provide for the purchase and installation of a new roof hatch. This estimate includes removal and disposal of the existing damaged hatch and any patching and / or repairs to the roof membrane. | GROUP HOME - BUILDING #8B | 9985 | HHS | DPBH | NNAMHS | Sparks | 1977 | 5237 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0347SFT1 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0347 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2006 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | GENERATOR BUILDING - BUILDING #20 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1980 | 1764 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 1000
0353EXT2 | OVERHEAD DOOR REPLACEMENT | 0353 | The existing overhead coiling doors, (2) 10' X 10', (1) 7' X10 and (1) 8' X 7', are original to the building. They are all damaged and do not function properly. Exposure and wind have caused the doors to bend, crack and lose their finish and some minor collisions have occurred. This project would provide for the removal and disposal of the manually operated overhead coiling doors and replacement with new manually operated overhead coiling doors. This project or a portion thereof was previously recommended in the FCA report dated 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | MAINTENANCE/HOUSEKEEPING BUILDING #22 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1959 | 8040 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20800
0331ELE2 | ELECTRICAL UPGRADE | 0331 | This building was constructed before the high demand for electrical services were needed for computers and other electrical devices. The electrical system within the building has been retrofitted and rewired as the needs of the agency have changed over the years. There are numerous safety issues, missing duplex covers, and painted receptacles that need to be repaired. It is recommended the entire system be upgraded to meet the evolving needs of the building including rewiring, replacing switches and panels and adding additional capacity. This project or a portion thereof was previously recommended in the FCA reports dated 10/2701999 and 06/26/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | LAB/PHARMACY - BUILDING #3 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1925 | 15344 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 383600
0331EXT5 | WINDOW REPLACEMENT | 0331 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. Staff reported that these windows are difficult to open and do not seal properly. Several windows allow water to penetrate to the interior. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of approximately 100 units including costs associated with a two story structure. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 06/26/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | LAB/PHARMACY - BUILDING #3 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1925 | 15344 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 150000
0331SFT2 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0331 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2006 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 10/27/1999 and 06/26/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | LAB/PHARMACY - BUILDING #3 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1925 | 15344 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 4000
0331ADA6 | ADA SIGNAGE | 0331 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | LAB/PHARMACY - BUILDING #3 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1925 | 15344 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 2500
0331ADA5 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0331 | This building contains a water fountain on each floor. The 1st and 2nd floor drinking fountains are not accessible. The 2006 IBC Section 1109.5 states where a water fountain is provided, at least half should be accessible. This project would provide funding for the purchase and installation of two new accessible fixed high/ low ADA drinking fountains for the 1st and 2nd floor. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | LAB/PHARMACY - BUILDING #3 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1925 | 15344 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 8000
0333ADA4 | ADA SIGNAGE | 0333 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 06/28/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | GROUP HOME - BUILDING #8B | 9985 | HHS | DPBH | NNAMHS | Sparks | 1977 | 5237 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 1500
0333EXT5 | SKYLIGHT REPLACEMENT | 0333 | There are two 8’x8’ acrylic sky-lights located on the roof. Both units have cracks in them that are allowing water to penetrate inside during rain or snow events. This project would provide for the removal, disposal and replacement of two acrylic skylight units. Minor roof repairs are included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 06/28/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | GROUP HOME - BUILDING #8B | 9985 | HHS | DPBH | NNAMHS | Sparks | 1977 | 5237 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
0333HVA2 | HVAC EQUIPMENT REPLACEMENT | 0333 | The HVAC system was installed in 1999 and should be scheduled for replacement. It consists of roof mounted packaged units and window mounted evaporative coolers. The system is not energy efficient and has reached the end of its expected and useful life. This project would provide for installation of a new HVAC system and cleaning of the existing duct work and grilles. The new system shall be designed to significantly reduce electrical and natural gas usage in order to comply with the 2009 IECC and ASHRAE 90.1 and to reduce utility costs. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 06/28/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | GROUP HOME - BUILDING #8B | 9985 | HHS | DPBH | NNAMHS | Sparks | 1977 | 5237 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 52237
0333EXT4 | EXTERIOR FINISHES | 0333 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 5-6 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | GROUP HOME - BUILDING #8B | 9985 | HHS | DPBH | NNAMHS | Sparks | 1977 | 5237 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 26185
0334ADA3 | LEVER HARDWARE INSTALLATION | 0334 | Section 4.13.9 of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) states that handles, pulls, latches, locks and other operating devices on accessible doors shall have a shape that is easy to grasp with one hand and does not require tight grasping, tight pinching, or twisting of the wrist to operate. It is recommended that compliant hardware be installed in this building to meet these guidelines. This project would provide for the purchase and installation of 15 lever action hardware to be placed on all the interior doors. This project or a portion thereof was previously recommended in the FCA report dated 06/28/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | GROUP HOME - BUILDING #8C | 9985 | HHS | DPBH | NNAMHS | Sparks | 1977 | 5237 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 7500
0334ADA4 | ADA SIGNAGE | 0334 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 06/28/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | GROUP HOME - BUILDING #8C | 9985 | HHS | DPBH | NNAMHS | Sparks | 1977 | 5237 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 1500
0334EXT3 | ROOF HATCH | 0334 | The roof hatch is broken and needs to be replaced. This project would provide for the purchase and installation of a new roof hatch. This estimate includes removal and disposal of the existing damaged hatch and any patching and / or repairs to the roof membrane. | GROUP HOME - BUILDING #8C | 9985 | HHS | DPBH | NNAMHS | Sparks | 1977 | 5237 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0333ADA3 | LEVER HARDWARE INSTALLATION | 0333 | Section 4.13.9 of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) states that handles, pulls, latches, locks and other operating devices on accessible doors shall have a shape that is easy to grasp with one hand and does not require tight grasping, tight pinching, or twisting of the wrist to operate. It is recommended that compliant hardware be installed in this building to meet these guidelines. This project would provide for the purchase and installation of 15 lever action hardware to be placed on all the interior doors. This project or a portion thereof was previously recommended in the FCA report dated 06/28/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | GROUP HOME - BUILDING #8B | 9985 | HHS | DPBH | NNAMHS | Sparks | 1977 | 5237 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 7500
0333EXT2 | ROOF CLEANING / REPAIRS | 0333 | The roof on this building was in fair condition at the time of the survey. The roof has a few seams that need to be sealed and miscellaneous debris and dirt though out. This project would provide funding to seal the seams and clean off the dirt and debris from the roof. The removal of debris and cleaning must be in conformance with the roofing manufacture's specifications so as not to void the warranty. This project applies to the single-ply membrane portion of the roof. | GROUP HOME - BUILDING #8B | 9985 | HHS | DPBH | NNAMHS | Sparks | 1977 | 5237 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 500
0333ADA5 | ADA RESTROOM REMODEL | 0333 | The building does not have an accessible restroom. The existing restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit of two restrooms is necessary. This project would provide funding for construction of two unisex accessible restrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | GROUP HOME - BUILDING #8B | 9985 | HHS | DPBH | NNAMHS | Sparks | 1977 | 5237 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 30000
0333ENR2 | WINDOW REPLACEMENT | 0333 | The windows are original, dual pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of approximately 40 units. Removal and disposal of the existing windows is included in this estimate. | GROUP HOME - BUILDING #8B | 9985 | HHS | DPBH | NNAMHS | Sparks | 1977 | 5237 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 40000
0333INT1 | INTERIOR FINISHES | 0333 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA reports dated 10/29/1999 and 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | GROUP HOME - BUILDING #8B | 9985 | HHS | DPBH | NNAMHS | Sparks | 1977 | 5237 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 26185
0333INT2 | KITCHEN REMODEL | 0333 | The two kitchens are in fair to poor condition. The cabinets and equipment are showing signs of general wear and tear and are approaching the end of their expected life. This project recommends the replacement of the existing kitchen cabinets, counters, fixtures and equipment with mid range, high quality components. | GROUP HOME - BUILDING #8B | 9985 | HHS | DPBH | NNAMHS | Sparks | 1977 | 5237 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
1956EXT2 | EXTERIOR FINISHES | 1956 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SOUTH STORAGE AT BUILDING 600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 348 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1740
1955HVA1 | EXHAUST FAN REPLACEMENT | 1955 | The existing exhaust fans that serve restroom and shower areas are original equipment and are not providing adequate ventilation. This project would provide for the removal of the existing exhaust fan assemblies and the purchase and installation of new exhaust fan assemblies including connections to utilities. This project or a portion thereof was previously recommended in the FCA reports dated 11/05/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR DUAL DIAGNOSIS, BUILDING #325 | 9981 | HHS | ADSD | SRC | Sparks | 1990 | 2428 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
0994INT1 | INTERIOR FINISHES | 0994 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. | WEST STORAGE AT BLDG 600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 360 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1800
1955INT1 | INTERIOR FINISHES | 1955 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA reports dated 11/05/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR DUAL DIAGNOSIS, BUILDING #325 | 9981 | HHS | ADSD | SRC | Sparks | 1990 | 2428 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12140
1955INT6 | FLOORING REPLACEMENT | 1955 | The painted concrete and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be repaired or replaced. This project would provide for stripping and re-painting the concrete with an elastomeric or other water resistant paint and removal and disposal of the carpet and installation of heavy duty commercial grade carpet in the next 4-5 years. | SRC ICF/MR DUAL DIAGNOSIS, BUILDING #325 | 9981 | HHS | ADSD | SRC | Sparks | 1990 | 2428 | 2017-10-19 | Four to Ten Years | Long-Term Needs | 3 | 19424
1955ENR1 | HVAC UPGRADE | 1955 | The existing HVAC system consists of natural gas fired furnaces and split system air conditioning units. This equipment is original to the building, has required excessive maintenance in recent years and replacement parts are no longer available. This project would provide for replacing the existing equipment with new energy efficient equipment. The current design does not provide return air ducting from the sleeping rooms. This issue should be analyzed by the mechanical engineer to determine whether these returns should be installed. The new system shall be designed to significantly reduce electrical and natural gas usage in order to comply with the 2009 IECC and ASHRAE 90.1 and to reduce utility costs. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | SRC ICF/MR DUAL DIAGNOSIS, BUILDING #325 | 9981 | HHS | ADSD | SRC | Sparks | 1990 | 2428 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 36420
0994EXT2 | EXTERIOR FINISHES | 0994 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | WEST STORAGE AT BLDG 600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 360 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1800
1955ADA4 | ADA RESTROOM REMODEL | 1955 | The building does not have an accessible restroom. The existing restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit of all 5 restrooms is necessary. This project would provide funding for construction of five unisex accessible restrooms. These items may include new sinks, toilets, hardware, mirrors, fixtures, flooring, paint and demolition and construction of walls. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | SRC ICF/MR DUAL DIAGNOSIS, BUILDING #325 | 9981 | HHS | ADSD | SRC | Sparks | 1990 | 2428 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 75000
1955ADA2 | ADA DOOR HARDWARE REPLACEMENT | 1955 | The operable parts on the interior doors are round knobs which do not comply with ADA requirements. Section 309.4 of the ADA Standards for Accessible Design states that operable parts shall be operable with one hand and shall not require tight grasping, pinching, or twisting of the wrist. It is recommended that compliant hardware be installed in this building to meet these guidelines. This project or a portion thereof was previously recommended in the FCA reports dated 11/05/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR DUAL DIAGNOSIS, BUILDING #325 | 9981 | HHS | ADSD | SRC | Sparks | 1990 | 2428 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 14000
1955EXT1 | EXTERIOR FINISHES | 1955 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is repairing damaged areas, power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be repaired and painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA reports dated 11/05/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR DUAL DIAGNOSIS, BUILDING #325 | 9981 | HHS | ADSD | SRC | Sparks | 1990 | 2428 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24280
1955SFT1 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 1955 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA reports dated 11/05/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR DUAL DIAGNOSIS, BUILDING #325 | 9981 | HHS | ADSD | SRC | Sparks | 1990 | 2428 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 8500
1955INT3 | KITCHEN COUNTERTOP REPLACEMENT | 1955 | The countertops in the kitchen are showing signs of wear and tear particularly at the Formica edges and corners. The countertops are delaminating and failing. This project recommends the replacement of the existing damaged countertops with heavy duty, quality finishes. This project would provide funding for the removal and replacement of the countertops. This project or a portion thereof was previously recommended in the FCA reports dated 11/05/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR DUAL DIAGNOSIS, BUILDING #325 | 9981 | HHS | ADSD | SRC | Sparks | 1990 | 2428 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2400
1955INT4 | JANITORS CLOSET REPAIRS | 1955 | The mop sink in the Janitors Closet has reached the end of its expected life and the adjacent gypsum board walls are showing signs of water damage. This project would provide for replacement of the sink and faucet and fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. This project or a portion thereof was previously recommended in the FCA reports dated 11/05/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR DUAL DIAGNOSIS, BUILDING #325 | 9981 | HHS | ADSD | SRC | Sparks | 1990 | 2428 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
1955ADA3 | ADA SIGNAGE | 1955 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA reports dated 11/05/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR DUAL DIAGNOSIS, BUILDING #325 | 9981 | HHS | ADSD | SRC | Sparks | 1990 | 2428 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 1500
2691EXT2 | EXTERIOR DOOR REPLACEMENTS | 2691 | The exterior wood man door and sliding barn door appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement of the wood doors with new metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | SRC MAINTENANCE SHOP | 9981 | HHS | ADSD | SRC | Sparks | 0 | 600 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
2691INT1 | INSTALL BUILDING INSULATION | 2691 | This building has no insulation. The temperature extremes create an uncomfortable work environment and are contributing to accelerated decay of the maintenance equipment and supplies. This project will install batt insulation in the walls and ceiling to help moderate temperature fluctuations. It may be possible to use a foamed-in system to fill the cavities where applicable; costs are similar to the batt insulation provided for in this project. | SRC MAINTENANCE SHOP | 9981 | HHS | ADSD | SRC | Sparks | 0 | 600 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2100
2692EXT1 | EXTERIOR FINISHES | 2692 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SRC STORAGE BUILDING | 9981 | HHS | ADSD | SRC | Sparks | 0 | 80 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 80
2693EXT2 | EXTERIOR FINISHES | 2693 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | WEST STORAGE #2 | 9981 | HHS | ADSD | SRC | Sparks | 2003 | 264 | 2017-10-19 | Four to Ten Years | Long-Term Needs | 3 | 1320
2060EXT2 | EXTERIOR FINISHES | 2060 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | EAST STORAGE AT BUILDING 600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 288 | 2017-10-19 | Four to Ten Years | Long-Term Needs | 3 | 1440
2691EXT1 | EXTERIOR FINISHES | 2691 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC MAINTENANCE SHOP | 9981 | HHS | ADSD | SRC | Sparks | 0 | 600 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
2060INT1 | INTERIOR FINISHES | 2060 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. This project or a portion thereof was previously recommended in the FCA report dated 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | EAST STORAGE AT BUILDING 600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 288 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1440
9980SFT1 | HAZARDOUS COMMUNICATION PROGRAM | 9980 | Due to the storage of hazardous materials, this site shall comply with IFC 2012 Chapter 4 Emergency Planning and Preparedness and have a written Hazardous Materials Management Plan, including but not limited to, Section 5003 Safety Data Sheets, Section 406 Employee Training and Response Procedures and Section 407 Hazard Communication. Chapter 50 Section 5001 will provide additional assistance in devising and implementing a hazardous communication program. | LAKES CROSSING CENTER SITE | 9980 | HHS | DPBH | Lakes | Sparks | 1974 |  | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 2000
9980SIT2 | PARKING LOT STRIPING | 9980 | It is important to maintain the striping on the pavement at the site. This project would provide for the necessary striping and painting of the curbs and parking spaces. An ADA parking and loading space emblem will be painted on the concrete that is designated for ADA parking. This project should be scheduled on a 2 year cyclical basis to maintain the integrity of the striping, painting and ADA designation. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | LAKES CROSSING CENTER SITE | 9980 | HHS | DPBH | Lakes | Sparks | 1974 |  | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
9980SIT1 | SLURRY SEAL ASPHALT PAVING | 9980 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site wide including access roads, parking areas and the perimeter road and some regrading on the north west portion of the parking lot. This area does not drain well and causes water to pool up in the parking area. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 45,000 square feet of asphalt area was used to generate this estimate. | LAKES CROSSING CENTER SITE | 9980 | HHS | DPBH | Lakes | Sparks | 1974 |  | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 33750
9980ENR1 | EXTERIOR SOLAR SITE LIGHTING UPGRADE | 9980 | There are ten existing light poles around the site with either one or two light fixtures each. The existing lighting fixtures are the older metal halide type, and are not energy efficient. With increased traffic and development in the area, insufficient site lighting is a security and safety concern. This project would provide for the installation of 14 solar powered LED exterior light fixtures on 10 light poles with 30" diameter raised concrete bases. This installation will eliminate the need for trenching and electrical connections. Some of the existing poles may be acceptable to re-use. If so, the estimate can be reduced accordingly. | LAKES CROSSING CENTER SITE | 9980 | HHS | DPBH | Lakes | Sparks | 1974 |  | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 65000
9980PLM1 | GATE VALVE REPLACEMENT | 9980 | The 6" main water line coming into the site is equipped with a gate valve to control the irrigation system. It has reached the end of its expected life, leaks and should be replaced in the next one to two years. A contributing factor to the deterioration of the valve is that the vault that contains the valve does not have solid sides and allows dirt to build up and bury the valve. This project would provide for replacing the valve and installing a new vault around the valve with a solid cover and solid walls. | LAKES CROSSING CENTER SITE | 9980 | HHS | DPBH | Lakes | Sparks | 1974 |  | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 7500
9980SEC1 | SITE SECURITY SYSTEM REPLACEMENT | 9980 | The site is equipped with a motion detecting security system to monitor and report activity outside of the building. The system is outdated and should be scheduled for replacement. It is over ten years old and it is increasingly difficult to find replacement parts and experienced repairmen to service the sensors and scan pens that the staff carries. Due to the security level of the facility is imperative that a new system is installed for the safety of the staff, clients and the public. This project addresses replacement of the motion detection system including equipment, wiring and controls site wide. | LAKES CROSSING CENTER SITE | 9980 | HHS | DPBH | Lakes | Sparks | 1974 |  | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 150000
9980ADA3 | ADA SIDEWALK REPLACEMENT | 9980 | The concrete sidewalk around the building is in need of replacement. They have cracks and are spalling. This project would provide for the removal and replacement of the concrete sidewalks. 1500 SF of 4" thick concrete was used for this estimate. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | LAKES CROSSING CENTER SITE | 9980 | HHS | DPBH | Lakes | Sparks | 1974 |  | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 22500
9980ADA4 | ADA SIDEWALK REPLACEMENT | 9980 | The concrete sidewalk around the building is in need of replacement. They have cracks and are spalling. This project would provide for the removal and replacement of the concrete sidewalks. 1500 SF of 4" thick concrete was used for this estimate. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | LAKES CROSSING CENTER SITE | 9980 | HHS | DPBH | Lakes | Sparks | 1974 |  | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 22500
9981PLM2 | PLUMBING UPGRADES | 9981 | The domestic and irrigation water lines do not currently have separate meters to report usage. The City of Sparks calculates their sewer fees based on the amount of water used, but the meter is currently reporting domestic water and irrigation water. The fee should be based on only the domestic water use. This project would provide for installation of water meters on each building which will report domestic use separately from irrigation. The 2013 CIP includes a project to do this work. | SIERRA REGIONAL CENTER SITE | 9981 | HHS | ADSD | SRC | Sparks |  |  | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 85000
9981SIT3 | EXTERIOR SOLAR SITE LIGHTING UPGRADE | 9981 | There are nine existing light poles throughout the site. The poles are rusted and damaged and are reaching the end of their useful life. The system is problematic and replacement parts are no longer available. This project would provide for the removal and the disposal of the existing light fixtures, poles and bases and the installation of 12 new solar powered LED exterior light fixtures, 20’ poles and 30" diameter raised concrete bases. This installation will eliminate the need for trenching and electrical connections. | SIERRA REGIONAL CENTER SITE | 9981 | HHS | ADSD | SRC | Sparks |  |  | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 58500
9981HVA1 | DIRECT DIGITAL CONTROL SYSTEM FOR HVAC SYSTEMS | 9981 | Presently the site has no DDC supervisory control or automated energy management control programs. Future HVAC considerations should include installation of appropriate hardware to connect any new buildings to the campus energy management network while maintaining local control logic. The new system should allow starting of equipment, monitoring of status, monitoring of space temperatures, monitoring and control of hot and chilled water temperatures, and similar typical centrally controlled elements. Detailed control of the individual elements of the buildings systems can yield tremendous benefits based upon the reported operating hours coupled with varying occupancy loads. The system should include a microprocessor control center which monitors and manages all components of the buildings HVAC systems. The DDC should also have the capability of controlling other building systems (such as lighting, alarms, etc.) and communicating with the central management system for the campus. This project or a portion thereof was previously recommended in the FCA report dated 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SIERRA REGIONAL CENTER SITE | 9981 | HHS | ADSD | SRC | Sparks |  |  | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 250000
9981ADA1 | ADA SIGNAGE | 9981 | The ADA provides for accessibility to sites and services for people with physical limitations. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/ pictograms; and sign contrast and finish. The signage in this facility does not comply with these criteria. This project would provide funding for the purchase and the installation of ADA signage to include updated parking signage and directional signage from the accessible parking spaces to the accessible building entrances. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 11/04/1999, 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SIERRA REGIONAL CENTER SITE | 9981 | HHS | ADSD | SRC | Sparks |  |  | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 5000
9981SIT2 | CRACK FILL & SEAL ASPHALT PAVING | 9981 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the paving site-wide including access roads and parking areas. Striping is included in this estimate. This project should be scheduled on a 5-year cyclical basis to maintain the integrity of the paving and prevent premature failure. 150,000 square feet of asphalt area was used to generate this estimate. | SIERRA REGIONAL CENTER SITE | 9981 | HHS | ADSD | SRC | Sparks |  |  | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 90000
9981ENV1 | BACKFLOW PREVENTION | 9981 | State Health Law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of backsiphonage or backpressure. Building #600-601 does not have any type of backflow prevention between the water main and the building. This project provides for the installation of double check valves or reduced pressure principle backflow preventers as appropriate to the hazard and in appropriate locations near the potential source of contamination. Costs include an above ground vault, and allowance for 200 feet of 1" conduit to provide power for freeze protection. | SIERRA REGIONAL CENTER SITE | 9981 | HHS | ADSD | SRC | Sparks |  |  | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 25000
9981ADA2 | ADA SITE UPGRADES | 9981 | Many sidewalk sections serving the buildings and parking areas are deteriorated and failing. In some areas the concrete is spalling considerably and other areas are heaving and settling due to either expansive soils or tree roots. This project addresses the removal and the replacement of the existing sidewalks as needed. 1,250 SF of 4" thick concrete sidewalk was used for this estimate. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | SIERRA REGIONAL CENTER SITE | 9981 | HHS | ADSD | SRC | Sparks |  |  | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 12500
0325ENR2 | AIR CONDITIONER REPLACEMENT | 0325 | One of the two air conditioners is older and has reached the end of its useful and expected life. This project would provide for a new split system air conditioner to be installed including all required connections to utilities. The new unit shall be designed to significantly reduce electrical usage in order to comply with the 2009 IECC and ASHRAE 90.1 and to reduce utility costs. This project includes removal and disposal of the existing HVAC unit and all required connections to utilities. | SRC BLDG #604, ICF/MR 2 6-BED HOME | 9981 | HHS | ADSD | SRC | Sparks | 1981 | 4829 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0325INT3 | KITCHEN REMODEL | 0325 | The kitchen is in fair to poor condition. The cabinets and equipment are showing signs of general wear and tear and are approaching the end of their expected life. This project recommends the replacement of the existing kitchen cabinets, counters, fixtures and equipment with mid range, high quality components. | SRC BLDG #604, ICF/MR 2 6-BED HOME | 9981 | HHS | ADSD | SRC | Sparks | 1981 | 4829 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35000
0325ENR1 | WINDOW REPLACEMENT | 0325 | The windows are original, dual pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 30 units. Removal and disposal of the existing windows is included in this estimate. | SRC BLDG #604, ICF/MR 2 6-BED HOME | 9981 | HHS | ADSD | SRC | Sparks | 1981 | 4829 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 22500
0325ADA4 | ADA RESTROOM REMODEL | 0325 | The building does not have an accessible restroom. The existing restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit of all 5 restrooms is necessary. This project would provide funding for construction of five unisex accessible restrooms. These items may include new sinks, toilets, hardware, mirrors, fixtures, flooring, paint and demolition and construction of walls. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | SRC BLDG #604, ICF/MR 2 6-BED HOME | 9981 | HHS | ADSD | SRC | Sparks | 1981 | 4829 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 75000
0324SFT4 | FIRE RISER REPLACEMENT | 0324 | This building has an automatic fire suppression system with an older fire riser. The fire riser appears to be more than 15 years old and should be scheduled for replacement. This project recommends replacing the fire riser and any other older components of the system. Removal and disposal of the existing riser is included in the estimate. | SRC ICF/MR, BLDG #603, 2 6-BED HOME | 9981 | HHS | ADSD | SRC | Sparks | 1979 | 3444 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0320SFT1 | EXIT SIGNS & EGRESS LIGHTING UPGRADE | 0320 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA reports dated 11/05/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR DUAL DIAGNOSIS BLDG #345 | 9981 | HHS | ADSD | SRC | Sparks | 1990 | 2428 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 8500
0320HVA1 | EXHAUST FAN REPLACEMENT | 0320 | The existing exhaust fans that serve restroom and shower areas are original equipment and are not providing adequate ventilation. This project would provide for the removal of the existing exhaust fan assemblies and the purchase and installation of new exhaust fan assemblies including connections to utilities. This project or a portion thereof was previously recommended in the FCA reports dated 11/05/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR DUAL DIAGNOSIS BLDG #345 | 9981 | HHS | ADSD | SRC | Sparks | 1990 | 2428 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
0323ADA3 | ADA SIGNAGE | 0323 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA reports dated 11/05/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR, BLDG #602, 6-BED HOME | 9981 | HHS | ADSD | SRC | Sparks | 1979 | 6725 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 3000
0323SFT1 | FIRE ALARM SYSTEM UPGRADE | 0323 | This building is equipped with an automatic fire detection and alarm system that is more than 15 years old and should be scheduled for replacement. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 "If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure". When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. This project or a portion thereof was previously recommended in the FCA report dated 11/04/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR, BLDG #602, 6-BED HOME | 9981 | HHS | ADSD | SRC | Sparks | 1979 | 6725 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 15000
0323ADA2 | ADA DOOR HARDWARE REPLACEMENT | 0323 | The operable parts on the interior doors are round knobs which do not comply with ADA requirements. Section 309.4 of the ADA Standards for Accessible Design states that operable parts shall be operable with one hand and shall not require tight grasping, pinching, or twisting of the wrist. It is recommended that compliant hardware be installed in this building to meet these guidelines. This project or a portion thereof was previously recommended in the FCA report dated 11/04/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR, BLDG #602, 6-BED HOME | 9981 | HHS | ADSD | SRC | Sparks | 1979 | 6725 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 11250
0323PLM1 | WATER HEATER REPLACEMENT | 0323 | There is a 100 gallon gas-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR, BLDG #602, 6-BED HOME | 9981 | HHS | ADSD | SRC | Sparks | 1979 | 6725 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0323INT3 | KITCHEN REMODEL | 0323 | The two kitchens are original to the building. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and counter tops are delaminating and failing. This project recommends the replacement of the existing kitchen counters, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards For Accessible Design should be incorporated into the design of one of the kitchens such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. | SRC ICF/MR, BLDG #602, 6-BED HOME | 9981 | HHS | ADSD | SRC | Sparks | 1979 | 6725 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7000
0323ADA4 | ADA RESTROOM REMODEL | 0323 | The building does not have an accessible restroom. The existing restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit of all 3 restrooms is necessary. This project would provide funding for construction of three unisex accessible restrooms. These items may include new sinks, toilets, hardware, mirrors, fixtures, flooring, paint and demolition and construction of walls. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | SRC ICF/MR, BLDG #602, 6-BED HOME | 9981 | HHS | ADSD | SRC | Sparks | 1979 | 6725 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 45000
0323ENR1 | WINDOW REPLACEMENT | 0323 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 15 units. Removal and disposal of the existing windows is included in this estimate. | SRC ICF/MR, BLDG #602, 6-BED HOME | 9981 | HHS | ADSD | SRC | Sparks | 1979 | 6725 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11250
0323SFT2 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0323 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. | SRC ICF/MR, BLDG #602, 6-BED HOME | 9981 | HHS | ADSD | SRC | Sparks | 1979 | 6725 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 1722
0324ADA4 | ADA RESTROOM REMODEL | 0324 | The building does not have an accessible restroom. The existing restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit of all 5 restrooms is necessary. This project would provide funding for construction of five unisex accessible restrooms. These items may include new sinks, toilets, hardware, mirrors, fixtures, flooring, paint and demolition and construction of walls. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | SRC ICF/MR, BLDG #603, 2 6-BED HOME | 9981 | HHS | ADSD | SRC | Sparks | 1979 | 3444 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 75000
0324PLM1 | WATER HEATER REPLACEMENT | 0324 | There is a 100 gallon gas-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR, BLDG #603, 2 6-BED HOME | 9981 | HHS | ADSD | SRC | Sparks | 1979 | 3444 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0320EXT1 | EXTERIOR FINISHES | 0320 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is repairing damaged areas, power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be repaired and painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA reports dated 11/04/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR DUAL DIAGNOSIS BLDG #345 | 9981 | HHS | ADSD | SRC | Sparks | 1990 | 2428 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24280
0324ENR2 | HVAC EQUIPMENT REPLACEMENT | 0324 | The HVAC system was installed in 1988 and is original to the building. It consists of two natural gas-fired furnaces and two outdoor condensers. The system is not energy efficient and has reached the end of its expected and useful life. This project would provide for installation of a new HVAC system and cleaning of the existing duct work and grilles. The new system shall be designed to significantly reduce electrical and natural gas usage in order to comply with the 2009 IECC and ASHRAE 90.1 and to reduce utility costs. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | SRC ICF/MR, BLDG #603, 2 6-BED HOME | 9981 | HHS | ADSD | SRC | Sparks | 1979 | 3444 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35000
0323INT4 | INTERIOR FINISHES | 0323 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SRC ICF/MR, BLDG #602, 6-BED HOME | 9981 | HHS | ADSD | SRC | Sparks | 1979 | 6725 | 2017-10-19 | Four to Ten Years | Long-Term Needs | 3 | 17220
0324INT3 | INTERIOR DOOR REPLACEMENT | 0324 | The existing interior doors and frames are damaged from abuse and age. This project would provide for the removal of the existing doors and frames and the purchase and installation of new solid core wood doors and frames. All hardware and painting is included in this estimate. This estimate is for 25 doors. This project or a portion thereof was previously recommended in the FCA report dated 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR, BLDG #603, 2 6-BED HOME | 9981 | HHS | ADSD | SRC | Sparks | 1979 | 3444 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12500
0324INT5 | KITCHEN REMODEL | 0324 | The kitchen is in fair to poor condition. The cabinets and equipment are showing signs of general wear and tear and are approaching the end of their expected life. This project recommends the replacement of the existing kitchen cabinets, counters, fixtures and equipment with mid range, high quality components. | SRC ICF/MR, BLDG #603, 2 6-BED HOME | 9981 | HHS | ADSD | SRC | Sparks | 1979 | 3444 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35000
0324SFT3 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0324 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. | SRC ICF/MR, BLDG #603, 2 6-BED HOME | 9981 | HHS | ADSD | SRC | Sparks | 1979 | 3444 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 3363
0324EXT3 | EXTERIOR DOOR REPLACEMENT | 0324 | Three of the exterior metal doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the doors for both utility rooms and the fire riser room with new metal doors, frames and hardware. Removal and disposal of the existing doors is included in this estimate. | SRC ICF/MR, BLDG #603, 2 6-BED HOME | 9981 | HHS | ADSD | SRC | Sparks | 1979 | 3444 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
0324ENR1 | WINDOW REPLACEMENT | 0324 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 25 units. Removal and disposal of the existing windows is included in this estimate. | SRC ICF/MR, BLDG #603, 2 6-BED HOME | 9981 | HHS | ADSD | SRC | Sparks | 1979 | 3444 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18750
0324INT4 | INTERIOR FINISHES | 0324 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SRC ICF/MR, BLDG #603, 2 6-BED HOME | 9981 | HHS | ADSD | SRC | Sparks | 1979 | 3444 | 2017-10-19 | Four to Ten Years | Long-Term Needs | 3 | 33625
0324ADA2 | ADA DOOR HARDWARE REPLACEMENT | 0324 | The operable parts on the interior doors are round knobs which do not comply with ADA requirements. Section 309.4 of the ADA Standards for Accessible Design states that operable parts shall be operable with one hand and shall not require tight grasping, pinching, or twisting of the wrist. It is recommended that compliant hardware be installed in this building to meet these guidelines. This project or a portion thereof was previously recommended in the FCA report dated 11/04/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR, BLDG #603, 2 6-BED HOME | 9981 | HHS | ADSD | SRC | Sparks | 1979 | 3444 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 7500
0324ADA3 | ADA SIGNAGE | 0324 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA reports dated 11/05/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR, BLDG #603, 2 6-BED HOME | 9981 | HHS | ADSD | SRC | Sparks | 1979 | 3444 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 3500
0325PLM1 | WATER HEATER REPLACEMENT | 0325 | There is a 100 gallon gas-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC BLDG #604, ICF/MR 2 6-BED HOME | 9981 | HHS | ADSD | SRC | Sparks | 1981 | 4829 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0325EXT1 | EXTERIOR FINISHES | 0325 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is repairing damaged areas, power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be repaired and painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA reports dated 11/05/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC BLDG #604, ICF/MR 2 6-BED HOME | 9981 | HHS | ADSD | SRC | Sparks | 1981 | 4829 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 48290
0325ADA3 | ADA SIGNAGE | 0325 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA reports dated 11/05/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC BLDG #604, ICF/MR 2 6-BED HOME | 9981 | HHS | ADSD | SRC | Sparks | 1981 | 4829 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 3000
0325ADA2 | ADA DOOR HARDWARE REPLACEMENT | 0325 | The operable parts on the interior doors are round knobs which do not comply with ADA requirements. Section 309.4 of the ADA Standards for Accessible Design states that operable parts shall be operable with one hand and shall not require tight grasping, pinching, or twisting of the wrist. It is recommended that compliant hardware be installed in this building to meet these guidelines. This project or a portion thereof was previously recommended in the FCA reports dated 11/05/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC BLDG #604, ICF/MR 2 6-BED HOME | 9981 | HHS | ADSD | SRC | Sparks | 1981 | 4829 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 7500
0324EXT1 | EXTERIOR FINISHES | 0324 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is repairing damaged areas, power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be repaired and painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA reports dated 11/05/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR, BLDG #603, 2 6-BED HOME | 9981 | HHS | ADSD | SRC | Sparks | 1979 | 3444 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 34440
0320ADA3 | ADA SIGNAGE | 0320 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA reports dated 11/05/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR DUAL DIAGNOSIS BLDG #345 | 9981 | HHS | ADSD | SRC | Sparks | 1990 | 2428 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 1500
0320ADA4 | ADA RESTROOM REMODEL | 0320 | The building does not have an accessible restroom. The existing restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit of all 5 restrooms is necessary. This project would provide funding for construction of five unisex accessible restrooms. These items may include new sinks, toilets, hardware, mirrors, fixtures, flooring, paint and demolition and construction of walls. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | SRC ICF/MR DUAL DIAGNOSIS BLDG #345 | 9981 | HHS | ADSD | SRC | Sparks | 1990 | 2428 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 75000
0323EXT3 | EXTERIOR FINISHES | 0323 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is repairing damaged areas, power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be repaired and painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA reports dated 11/05/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR, BLDG #602, 6-BED HOME | 9981 | HHS | ADSD | SRC | Sparks | 1979 | 6725 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 34440
0325INT2 | INTERIOR FINISHES | 0325 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC BLDG #604, ICF/MR 2 6-BED HOME | 9981 | HHS | ADSD | SRC | Sparks | 1981 | 4829 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24145
0320INT7 | FLOORING REPLACEMENT | 0320 | The painted concrete and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be repaired or replaced. This project would provide for stripping and re-painting the concrete with an elastomeric or other water resistant paint and removal and disposal of the carpet and installation of heavy duty commercial grade carpet in the next 4-5 years. | SRC ICF/MR DUAL DIAGNOSIS BLDG #345 | 9981 | HHS | ADSD | SRC | Sparks | 1990 | 2428 | 2017-10-19 | Four to Ten Years | Long-Term Needs | 3 | 19424
0320ADA2 | ADA DOOR HARDWARE REPLACEMENT | 0320 | The operable parts on the interior doors are round knobs which do not comply with ADA requirements. Section 309.4 of the ADA Standards for Accessible Design states that operable parts shall be operable with one hand and shall not require tight grasping, pinching, or twisting of the wrist. It is recommended that compliant hardware be installed in this building to meet these guidelines. This project or a portion thereof was previously recommended in the FCA reports dated 11/04/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR DUAL DIAGNOSIS BLDG #345 | 9981 | HHS | ADSD | SRC | Sparks | 1990 | 2428 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 21000
0320INT4 | JANITORS CLOSET REPAIRS | 0320 | The mop sink in the Janitors Closet has reached the end of its expected life and the adjacent gypsum board walls are showing signs of water damage. This project would provide for replacement of the sink and faucet and fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. This project or a portion thereof was previously recommended in the FCA reports dated 11/05/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR DUAL DIAGNOSIS BLDG #345 | 9981 | HHS | ADSD | SRC | Sparks | 1990 | 2428 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0320ENR1 | HVAC UPGRADE | 0320 | The existing HVAC system consists of natural gas fired furnaces and split system air conditioning units. This equipment is original to the building, has required excessive maintenance in recent years and replacement parts are no longer available. This project would provide for replacing the existing equipment with new energy efficient equipment. The current design does not provide return air ducting from the sleeping rooms. This issue should be analyzed by the mechanical engineer to determine whether these returns should be installed. The new system shall be designed to significantly reduce electrical and natural gas usage in order to comply with the 2009 IECC and ASHRAE 90.1 and to reduce utility costs. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | SRC ICF/MR DUAL DIAGNOSIS BLDG #345 | 9981 | HHS | ADSD | SRC | Sparks | 1990 | 2428 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 36420
0320PLM2 | WATER HEATER REPLACEMENT | 0320 | There is a 75 gallon gas-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR DUAL DIAGNOSIS BLDG #345 | 9981 | HHS | ADSD | SRC | Sparks | 1990 | 2428 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0320INT6 | INTERIOR FINISHES | 0320 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SRC ICF/MR DUAL DIAGNOSIS BLDG #345 | 9981 | HHS | ADSD | SRC | Sparks | 1990 | 2428 | 2017-10-19 | Four to Ten Years | Long-Term Needs | 3 | 12140
0516ADA2 | ADA DOOR HARDWARE REPLACEMENT | 0516 | The operable parts on the interior doors are round knobs which do not comply with ADA requirements. Section 309.4 of the ADA Standards for Accessible Design states that operable parts shall be operable with one hand and shall not require tight grasping, pinching, or twisting of the wrist. It is recommended that compliant hardware be installed in this building to meet these guidelines. This project or a portion thereof was previously recommended in the FCA reports dated 11/04/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR DUAL DIAGNOSIS, BUILDING #335 | 9981 | HHS | ADSD | SRC | Sparks | 1990 | 2428 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 21000
0342ADA5 | ADA EMPLOYEE LOUNGE UPGRADES | 0342 | The employee lounge does not meet the Americans with Disabilities Act (ADA) requirements. It is recommended to upgrade some of the features of the room for compliance with accessibility standards for employees. This project would provide funding for construction of an accessible sink and faucet, an accessible space at one of the dining tables and an accessible path of travel throughout the room. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | LAKES CROSSING CENTER - BUILDING #13 | 9980 | HHS | DPBH | Lakes | Sparks | 1974 | 35804 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 2000
0345EXT4 | WINDOW REPLACEMENT | 0345 | One of the two windows is original, single pane construction in a metal frame. The older window is drafty and not energy efficient. This project recommends replacing the window with a dual pane, higher efficiency unit. Removal and disposal of the existing window is included in this estimate. | MAINTENANCE SHOP 2 | 9981 | HHS | ADSD | SRC | Sparks | 1988 | 720 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 750
0342INT2 | INTERIOR FINISHES | 0342 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | LAKES CROSSING CENTER - BUILDING #13 | 9980 | HHS | DPBH | Lakes | Sparks | 1974 | 35804 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 179020
0517ELE2 | ELECTRICAL AND COMMUNICATIONS UPGRADE | 0517 | This building was constructed before the high demand for electrical services were needed for computers, communications systems and other electrical devices. As time has progressed, the buildings electrical demand and communications system has changed. The electrical system is utilized to its current maximum potential and the communications system is outdated. The electrical panels, switches and receptacles are at their limit. It is recommended to upgrade the entire electrical system and communications system to meet the evolving needs of the building. | SRC ADMINISTRATION, BLDG #605 | 9981 | HHS | ADSD | SRC | Sparks | 1979 | 7117 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 177925
0517ADA2 | ADA DOOR HARDWARE REPLACEMENT | 0517 | The operable parts on the interior doors are round knobs which do not comply with ADA requirements. Section 309.4 of the ADA Standards for Accessible Design states that operable parts shall be operable with one hand and shall not require tight grasping, pinching, or twisting of the wrist. It is recommended that compliant hardware be installed in this building to meet these guidelines. This project or a portion thereof was previously recommended in the FCA reports dated 11/05/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ADMINISTRATION, BLDG #605 | 9981 | HHS | ADSD | SRC | Sparks | 1979 | 7117 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 18750
0516SFT1 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0516 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA reports dated 11/04/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR DUAL DIAGNOSIS, BUILDING #335 | 9981 | HHS | ADSD | SRC | Sparks | 1990 | 2428 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 8500
0516PLM1 | WATER HEATER REPLACEMENT | 0516 | There is a 75 gallon gas-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR DUAL DIAGNOSIS, BUILDING #335 | 9981 | HHS | ADSD | SRC | Sparks | 1990 | 2428 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0345INT1 | INTERIOR FINISHES | 0345 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. | MAINTENANCE SHOP 2 | 9981 | HHS | ADSD | SRC | Sparks | 1988 | 720 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3600
0516EXT1 | EXTERIOR FINISHES | 0516 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is repairing damaged areas, power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be repaired and painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA reports dated 11/04/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR DUAL DIAGNOSIS, BUILDING #335 | 9981 | HHS | ADSD | SRC | Sparks | 1990 | 2428 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 22480
0517EXT1 | EXTERIOR FINISHES | 0517 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is repairing damaged areas, power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be repaired and painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA reports dated 11/05/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ADMINISTRATION, BLDG #605 | 9981 | HHS | ADSD | SRC | Sparks | 1979 | 7117 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35585
0516ADA3 | ADA SIGNAGE | 0516 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA reports dated 11/05/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR DUAL DIAGNOSIS, BUILDING #335 | 9981 | HHS | ADSD | SRC | Sparks | 1990 | 2428 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 1500
0516ENR1 | HVAC UPGRADE | 0516 | The existing HVAC system consists of natural gas fired furnaces and split system air conditioning units. This equipment is original to the building, has required excessive maintenance in recent years and replacement parts are no longer available. This project would provide for replacing the existing equipment with new energy efficient equipment. The current design does not provide return air ducting from the sleeping rooms. This issue should be analyzed by the mechanical engineer to determine whether these returns should be installed. The new system shall be designed to significantly reduce electrical and natural gas usage in order to comply with the 2009 IECC and ASHRAE 90.1 and to reduce utility costs. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | SRC ICF/MR DUAL DIAGNOSIS, BUILDING #335 | 9981 | HHS | ADSD | SRC | Sparks | 1990 | 2428 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 36420
0516INT4 | JANITORS CLOSET REPAIRS | 0516 | The mop sink in the Janitors Closet has reached the end of its expected life and the adjacent gypsum board walls are showing signs of water damage. This project would provide for replacement of the sink and faucet and fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. This project or a portion thereof was previously recommended in the FCA reports dated 11/05/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR DUAL DIAGNOSIS, BUILDING #335 | 9981 | HHS | ADSD | SRC | Sparks | 1990 | 2428 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0516INT7 | FLOORING REPLACEMENT | 0516 | The painted concrete and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be repaired or replaced. This project would provide for stripping and re-painting the concrete with an elastomeric or other water resistant paint and removal and disposal of the carpet and installation of heavy duty commercial grade carpet in the next 4-5 years. | SRC ICF/MR DUAL DIAGNOSIS, BUILDING #335 | 9981 | HHS | ADSD | SRC | Sparks | 1990 | 2428 | 2017-10-19 | Four to Ten Years | Long-Term Needs | 3 | 19424
0516INT6 | INTERIOR FINISHES | 0516 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SRC ICF/MR DUAL DIAGNOSIS, BUILDING #335 | 9981 | HHS | ADSD | SRC | Sparks | 1990 | 2428 | 2017-10-19 | Four to Ten Years | Long-Term Needs | 3 | 12140
0516ADA4 | ADA RESTROOM REMODEL | 0516 | The building does not have an accessible restroom. The existing restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit of all 5 restrooms is necessary. This project would provide funding for construction of five unisex accessible restrooms. These items may include new sinks, toilets, hardware, mirrors, fixtures, flooring, paint and demolition and construction of walls. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | SRC ICF/MR DUAL DIAGNOSIS, BUILDING #335 | 9981 | HHS | ADSD | SRC | Sparks | 1990 | 2428 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 75000
0516HVA1 | EXHAUST FAN REPLACEMENT | 0516 | The existing exhaust fans that serve restroom and shower areas are original equipment and are not providing adequate ventilation. This project would provide for the removal of the existing exhaust fan assemblies and the purchase and installation of new exhaust fan assemblies including connections to utilities. This project or a portion thereof was previously recommended in the FCA reports dated 11/05/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR DUAL DIAGNOSIS, BUILDING #335 | 9981 | HHS | ADSD | SRC | Sparks | 1990 | 2428 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
0345ENR1 | LIGHTING UPGRADE | 0345 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Any electrical wiring upgrades are not included in this estimate. | MAINTENANCE SHOP 2 | 9981 | HHS | ADSD | SRC | Sparks | 1988 | 720 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1080
0342EXT2 | EXTERIOR FINISHES | 0342 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit and cement plaster walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | LAKES CROSSING CENTER - BUILDING #13 | 9980 | HHS | DPBH | Lakes | Sparks | 1974 | 35804 | 2017-10-19 | Four to Ten Years | Long-Term Needs | 3 | 179020
0345EXT2 | EXTERIOR DOOR REPLACEMENT | 0345 | The exterior wood man door appears to be original to the building. It is damaged from age and general wear and tear. This project would provide for the replacement of the wood door with a new metal door, frame and hardware. Removal and disposal of the existing door and painting of the new door is included in this estimate. | MAINTENANCE SHOP 2 | 9981 | HHS | ADSD | SRC | Sparks | 1988 | 720 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0518ADA3 | ADA SIGNAGE | 0518 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA reports dated 11/05/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR 6-BED HOME BUILDING #606 | 9981 | HHS | ADSD | SRC | Sparks | 1981 | 4829 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 1500
0342ADA4 | ADA ACCESSIBLE COUNTER | 0342 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The front office has a service counter for the public to approach which does not meet current codes. Section 7.2 of the Americans with Disabilities Act Accessible Guidelines (ADAAG) states that the counter must have a portion which is at least 36" in length with a maximum height of 36" above the finish floor. This project will provide an accessible counter space in accordance with this requirement. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | LAKES CROSSING CENTER - BUILDING #13 | 9980 | HHS | DPBH | Lakes | Sparks | 1974 | 35804 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 1000
0342ADA3 | ADA RESTROOM UPGRADE | 0342 | The Men's and Women's designated ADA restrooms for the staff offices do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for construction of Men's and Women's accessible restrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | LAKES CROSSING CENTER - BUILDING #13 | 9980 | HHS | DPBH | Lakes | Sparks | 1974 | 35804 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 25000
0342SFT4 | FIRE SUPPRESSION SYSTEM REPLACEMENT | 0342 | This building has an automatic fire suppression system. This system is outdated and is not equipped with current code required items such as seismic anchors. The facility is also in the process of acquiring licensure under the Centers for Medicare and Medicaid (CMS) which has additional fire protection system requirements. This project recommends replacing the existing system with a double-interlock pre-action fire suppression system and implementing a comprehensive testing and service schedule. Removal and disposal of the existing system is included in the estimate. | LAKES CROSSING CENTER - BUILDING #13 | 9980 | HHS | DPBH | Lakes | Sparks | 1974 | 35804 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 429648
0345HVA1 | HVAC INSTALLATION | 0345 | The building does not currently have any heating or cooling equipment. It is uncomfortably hot in the summer and cold in the winter. It is recommended to install heating and cooling equipment in the building to ensure a comfortable work environment. This project would provide for the purchase and installation of a packaged heating and cooling unit including all required connections to existing utilities. | MAINTENANCE SHOP 2 | 9981 | HHS | ADSD | SRC | Sparks | 1988 | 720 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
0342HVA3 | HVAC REPLACEMENT | 0342 | The central HVAC system consists of two hot water boilers, two rooftop outside air HVAC units, several rooftop packaged units and other related equipment throughout the building. This equipment was installed in the late 1990's, are not energy efficient and should be scheduled for replacement. The boilers are of poor quality and require constant maintenance including replacement of major components. This project would provide for installation of new boilers, rooftop units, associated equipment and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | LAKES CROSSING CENTER - BUILDING #13 | 9980 | HHS | DPBH | Lakes | Sparks | 1974 | 35804 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 537060
0342SEC1 | INTERIOR DOOR REPLACEMENT | 0342 | The interior doors are damaged from general abuse and age. There are 115 doors within the secured area and 20 doors outside of the secured area. Some of the doors within the secured area are fire rated doors that do not have magnetic hold opens. These fire doors are often propped open for ease of circulation which compromises the fire rating of the area. There are many doors that are loose in their frames and have worn out locking mechanisms. This project would provide for the removal of the existing doors and the purchase and installation of new doors, frames and hardware. This estimate is for 115 security grade hollow metal doors and 20 solid core wood doors. | LAKES CROSSING CENTER - BUILDING #13 | 9980 | HHS | DPBH | Lakes | Sparks | 1974 | 35804 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 250000
0342HVA2 | VENT INSTALLATION | 0342 | The client sleeping rooms have no natural or mechanical ventilation which is required by code. Per the 2006 International Building Code section 1203.4, "Natural ventilation of an occupied space shall be through windows, doors, louvers or other openings to the outdoors. The operating mechanism for such openings shall be provided with ready access so that the openings are readily controllable by the building occupants." This project would provide for the purchase and installation of a louvered vent in the exterior wall of each of the 51 client sleeping quarters to provide ventilation according to the 2006 IBC. | LAKES CROSSING CENTER - BUILDING #13 | 9980 | HHS | DPBH | Lakes | Sparks | 1974 | 35804 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 76500
0342PLM1 | FLOORING REPAIRS | 0342 | Two of the isolation rooms are fitted with floor drains in the concrete floor. Both of these drains are at a point in the floor other than the lowest point resulting in poor drainage when the floor becomes wet. This project recommends removing the top section of the concrete and pouring a new concrete floor with a positive slope towards the drain in each of the two rooms. | LAKES CROSSING CENTER - BUILDING #13 | 9980 | HHS | DPBH | Lakes | Sparks | 1974 | 35804 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0342INT3 | FLOORING REPLACEMENT | 0342 | The carpet in the building is damaged and reaching the end of its useful life. It is recommended that the carpet in the administration areas be replaced with carpet and the carpet in the client areas be replaced with VCT (vinyl composite tile) or sheet vinyl. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the next 2-3 years. | LAKES CROSSING CENTER - BUILDING #13 | 9980 | HHS | DPBH | Lakes | Sparks | 1974 | 35804 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 120000
0518HVA1 | AIR CONDITIONER REMOVAL | 0518 | The utility room near the front entrance has a small air conditioner in it that is not installed correctly. The air intake has been punched through the exterior wall and does not meet code for proper installation. It is recommended to remove the air conditioner. | SRC ICF/MR 6-BED HOME BUILDING #606 | 9981 | HHS | ADSD | SRC | Sparks | 1981 | 4829 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
0518PLM1 | WATER HEATER REPLACEMENT | 0518 | There is a 75 gallon gas-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR 6-BED HOME BUILDING #606 | 9981 | HHS | ADSD | SRC | Sparks | 1981 | 4829 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0518EXT1 | EXTERIOR FINISHES | 0518 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is repairing damaged areas, power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be repaired and painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA reports dated 11/05/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR 6-BED HOME BUILDING #606 | 9981 | HHS | ADSD | SRC | Sparks | 1981 | 4829 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 48290
0518INT1 | CARPET REPLACEMENT | 0518 | The carpet in the building is showing signs of extreme wear and should be scheduled for replacement. It is recommended that the carpet be replaced with heavy duty commercial grade carpet in the next 2-3 years. This project or a portion thereof was previously recommended in the FCA reports dated 11/05/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR 6-BED HOME BUILDING #606 | 9981 | HHS | ADSD | SRC | Sparks | 1981 | 4829 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 31500
0518ADA2 | ADA DOOR HARDWARE REPLACEMENT | 0518 | The operable parts on the interior doors are round knobs which do not comply with ADA requirements. Section 309.4 of the ADA Standards for Accessible Design states that operable parts shall be operable with one hand and shall not require tight grasping, pinching, or twisting of the wrist. It is recommended that compliant hardware be installed in this building to meet these guidelines. This project or a portion thereof was previously recommended in the FCA reports dated 11/05/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR 6-BED HOME BUILDING #606 | 9981 | HHS | ADSD | SRC | Sparks | 1981 | 4829 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 7500
0518SIT1 | REMOVE SHRUBS AND TREES | 0518 | There are several shrubs and trees that are in need of removal or trimming to prevent damage to the structure and to prevent injuries. The shrubs and trees are scratching the exterior finishes and the roots are damaging the foundation. The shrubs at the front entrance are encroaching on the walkway and can scratch people walking into the building. This project would provide for the trimming and/ or removal of the shrubs and trees near the building and along the entrance walkway. | SRC ICF/MR 6-BED HOME BUILDING #606 | 9981 | HHS | ADSD | SRC | Sparks | 1981 | 4829 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0517INT4 | JANITORS CLOSET REPAIRS | 0517 | The mop sink in the Janitors Closet is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | SRC ADMINISTRATION, BLDG #605 | 9981 | HHS | ADSD | SRC | Sparks | 1979 | 7117 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
0345EXT3 | ROOF REPLACEMENT | 0345 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. | MAINTENANCE SHOP 2 | 9981 | HHS | ADSD | SRC | Sparks | 1988 | 720 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8640
0517INT3 | CARPET REPLACEMENT | 0517 | The carpet in the building is showing signs of extreme wear and should be scheduled for replacement. It is recommended that the carpet be replaced with heavy duty commercial grade carpet in the next 2-3 years. | SRC ADMINISTRATION, BLDG #605 | 9981 | HHS | ADSD | SRC | Sparks | 1979 | 7117 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 45500
0518INT4 | JANITORS CLOSET REPAIRS | 0518 | The mop sink in the Janitors Closet is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | SRC ICF/MR 6-BED HOME BUILDING #606 | 9981 | HHS | ADSD | SRC | Sparks | 1981 | 4829 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
0518INT3 | INTERIOR FINISHES | 0518 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SRC ICF/MR 6-BED HOME BUILDING #606 | 9981 | HHS | ADSD | SRC | Sparks | 1981 | 4829 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24145
0517ADA1 | ADA SIGNAGE | 0517 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA reports dated 11/05/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ADMINISTRATION, BLDG #605 | 9981 | HHS | ADSD | SRC | Sparks | 1979 | 7117 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 3000
0345SEC1 | SECURITY SYSTEM INSTALLATION | 0345 | The building does not have a security system. It has been broken into several times and expensive tools and equipment have been stolen. This project recommends motion detection, door switches, access control and related items be installed and interfaced with the fire alarm in the Administration building. | MAINTENANCE SHOP 2 | 9981 | HHS | ADSD | SRC | Sparks | 1988 | 720 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3600
0517ENR1 | AIR CONDITIONER REPLACEMENT | 0517 | Two of the four air conditioners on the west side of the building are older and have reached the end of their useful and expected life. This project would provide for two new split system air conditioners to be installed including all required connections to utilities. The new units shall be designed to significantly reduce electrical usage in order to comply with the 2009 IECC and ASHRAE 90.1 and to reduce utility costs. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | SRC ADMINISTRATION, BLDG #605 | 9981 | HHS | ADSD | SRC | Sparks | 1979 | 7117 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
0517EXT3 | ROOFING REPLACEMENT | 0517 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. | SRC ADMINISTRATION, BLDG #605 | 9981 | HHS | ADSD | SRC | Sparks | 1979 | 7117 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 85404
0517INT1 | INTERIOR FINISHES | 0517 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ADMINISTRATION, BLDG #605 | 9981 | HHS | ADSD | SRC | Sparks | 1979 | 7117 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35585
0342SEC3 | SECURITY CONTROL SYSTEM REPLACEMENT | 0342 | This building is equipped with a security control system that is outdated and should be scheduled for immediate replacement. Problems exist with the door control panel and door motor systems for the client rooms and access doors. The system is over ten years old and it is increasingly difficult to find replacement parts and experienced repairmen to service the equipment. The wiring and conduit are aging and in some areas were not installed properly resulting in premature wear and a higher probability of failure. It is also recommended to install new communications from the main control room to the Nursing Station. Currently, there is no video surveillance in the Nursing Station to monitor clients in the five isolation rooms. Treatment for the clients in the isolation rooms could be enhanced by providing monitoring equipment to the medical staff. Due to the security level of the facility is imperative that a new system is installed for the safety of the staff, clients and the public. This project addresses replacement of the control panels, matrix system, conduit, wiring and door motor systems and installing new conduit, wiring and video surveillance to connect the Nursing Station to the system. This project should be implemented concurrently with the Video Security System Replacement project. | LAKES CROSSING CENTER - BUILDING #13 | 9980 | HHS | DPBH | Lakes | Sparks | 1974 | 35804 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 250000
0342ADA2 | ADA SIGNAGE | 0342 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required and that existing signage be relocated or replaced as needed. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 03/31/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/12/2012. | LAKES CROSSING CENTER - BUILDING #13 | 9980 | HHS | DPBH | Lakes | Sparks | 1974 | 35804 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 5000
0342SFT2 | FIRE ALARM SYSTEM UPGRADE | 0342 | This building is equipped with an automatic fire detection and alarm system that no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 "If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure". When completed, the new system will provide visual, as well as audible notification, in accordance with the 2006 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. The facility is also in the process of acquiring licensure under the Centers for Medicare and Medicaid (CMS) which has additional fire alarm system requirements. | LAKES CROSSING CENTER - BUILDING #13 | 9980 | HHS | DPBH | Lakes | Sparks | 1974 | 35804 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 143216
0342SEC2 | VIDEO SECURITY SYSTEM REPLACEMENT | 0342 | The video security system for the building and the site is outdated and should be scheduled for immediate replacement. The system is over ten years old and it is increasingly difficult to find replacement parts and experienced repairmen to service the equipment. The wiring and conduit are aging and in some areas were not installed properly resulting in premature wear and a higher probability of failure. Due to the security level of the facility is imperative that a new system is installed for the safety of the staff, clients and the public. This project addresses replacement of the cameras, conduit and wiring throughout the facility with all digital equipment as well as sufficient storage capacity. This project should be implemented concurrently with the Security Control System Replacement project. | LAKES CROSSING CENTER - BUILDING #13 | 9980 | HHS | DPBH | Lakes | Sparks | 1974 | 35804 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 250000
0345EXT1 | EXTERIOR FINISHES | 0345 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | MAINTENANCE SHOP 2 | 9981 | HHS | ADSD | SRC | Sparks | 1988 | 720 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3600
1468INT2 | INTERIOR FINISHES | 1468 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | BEHAVIORAL SERVICES HOUSING UNIT B | 9958 | HHS | DCFS | NNCAS | Reno | 1977 | 4000 | 2017-10-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
1468PLM2 | WATER HEATER REPLACEMENT | 1468 | The average life span of a water heater is eight to ten years. The two existing 80 gallon natural gas water heaters in the building have reached the end of their expected life and are not energy efficient. This project would provide for the removal and disposal of the old water heaters and installation of two new 80 gallon water heaters. | BEHAVIORAL SERVICES HOUSING UNIT B | 9958 | HHS | DCFS | NNCAS | Reno | 1977 | 4000 | 2017-10-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3700
1466SFT4 | INSTALL EMERGENCY EGRESS LIGHTING | 1466 | There are older emergency egress lighting in this building. These units have a finite lifespan, and this project recommends their replacement with new egress lights, and providing additional lights on the main exit routes and in individual rooms as needed. This project or a portion thereof was previously recommended in the FCA report dated 04/23/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2008. | ADMINISTRATION/CLASSROOM BUILDING | 9958 | HHS | DCFS | NNCAS | Reno | 1977 | 17210 | 2017-10-24 | Immediate to Two Years | Currently Critical | 1 | 9000
1466PLM2 | MISCELLANEOUS PLUMBING | 1466 | This building received an addition in 1996, and is served by a four pipe hydronic system. Some of the piping for the addition blocks the pans on the fan coil units in the existing building, which prevents maintenance and repairs. The piping affects several fan coils; two have failed and cannot be reached to be replaced. This project provides funding to re-route the piping system to allow access to the affected units, and to replace the failed fan coils. This project or a portion thereof was previously recommended in the FCA report dated 04/23/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2008. | ADMINISTRATION/CLASSROOM BUILDING | 9958 | HHS | DCFS | NNCAS | Reno | 1977 | 17210 | 2017-10-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
1468ENR2 | EXTERIOR LIGHTING UPGRADE | 1468 | The building has perimeter lighting on the exterior of the building, but the light fixtures are old, give off inadequate lighting and are not energy efficient. This project would provide for the replacement of the exterior lighting fixtures with new high intensity, energy efficient light fixtures, including connections to the existing electrical system. | BEHAVIORAL SERVICES HOUSING UNIT B | 9958 | HHS | DCFS | NNCAS | Reno | 1977 | 4000 | 2017-10-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
1468EXT2 | ROOF REPAIRS | 1468 | During the survey of 4/30/2008, there were areas of the composition shingle roof that were missing and / or damaged from a wind event. This project would provide for the repair of the damaged shingles. | BEHAVIORAL SERVICES HOUSING UNIT B | 9958 | HHS | DCFS | NNCAS | Reno | 1977 | 4000 | 2017-10-24 | Immediate to Two Years | Currently Critical | 1 | 1200
1468HVA1 | HVAC SYSTEM REPLACEMENT | 1468 | The HVAC system consists of two gas fired furnaces and two air cooled condensers. One furnace and one condenser are original to the building and have reached the end of their expected life. This project recommends replacing one furnace and one condenser in the next 2 to 3 years. The estimate includes removal and disposal of the existing equipment. | BEHAVIORAL SERVICES HOUSING UNIT B | 9958 | HHS | DCFS | NNCAS | Reno | 1977 | 4000 | 2017-10-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11000
1468PLM1 | REPLACE EXISTING TOILET FIXTURES | 1468 | The existing restrooms date to the construction date of the building. The toilet is an older tank-flush model. Due to variations in the water pressure and the age of the facility, this project recommends the replacement of the existing fixture with a new, pressure-assisted, low-gallonage model. This project or a portion thereof was previously recommended in the FCA report dated 04/23/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2008. | BEHAVIORAL SERVICES HOUSING UNIT B | 9958 | HHS | DCFS | NNCAS | Reno | 1977 | 4000 | 2017-10-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
1466HVA1 | HVAC CONTROLS UPGRADE | 1466 | The HVAC system controls are older and not efficient. There have been ongoing problems with the zone control valves, and a number have had to be replaced. The second floor is reported as too warm, and the main floor too cold. This project recommends the installation of an Energy Management System (EMS) for the entire site. This system will monitor and control the heating, ventilation, air conditioning and lighting equipment in the building through a central computer system. Electronic sensors will be installed on each piece of equipment which will feed information into the computer system. The maintenance staff can then control and monitor the equipment remotely which will significantly lower energy costs. Along with electricity, gas and water meters, this system will provide detailed reports on energy consumption allowing the maintenance staff to analyze and customize the energy used by the facility. This work should be performed concurrently with the "HVAC Upgrade" project. This project or a portion thereof was previously recommended in the FCA report dated 04/23/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2008. | ADMINISTRATION/CLASSROOM BUILDING | 9958 | HHS | DCFS | NNCAS | Reno | 1977 | 17210 | 2017-10-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 129075
1468EXT1 | EXTERIOR FINISHES | 1468 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 2 to 3 years and is recommended on a cyclical basis based on environmental conditions. Elastomeric paint is recommended for the stucco portion of the building. This project or a portion thereof was previously recommended in the FCA report dated 04/23/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2008. | BEHAVIORAL SERVICES HOUSING UNIT B | 9958 | HHS | DCFS | NNCAS | Reno | 1977 | 4000 | 2017-10-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 40000
1466PLM1 | REPLACE EXISTING TOILET FIXTURES | 1466 | The existing restrooms date to the construction date of the building. The toilet is an older tank-flush model. Due to variations in the water pressure and the age of the facility, this project recommends the replacement of the existing fixture with a new, pressure-assisted, low-gallonage model. This project should coincide with the ADA restroom remodel project. This project or a portion thereof was previously recommended in the FCA report dated 04/23/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2008. | ADMINISTRATION/CLASSROOM BUILDING | 9958 | HHS | DCFS | NNCAS | Reno | 1977 | 17210 | 2017-10-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
1467ENR2 | EXTERIOR LIGHTING UPGRADE | 1467 | The building has perimeter lighting on the exterior of the building, but the light fixtures are old, give off inadequate lighting and are not energy efficient. This project would provide for the replacement of the exterior lighting fixtures with new high intensity, energy efficient light fixtures, including connections to the existing electrical system. | BEHAVIORAL SERVICES HOUSING UNIT A | 9958 | HHS | DCFS | NNCAS | Reno | 1977 | 4000 | 2017-10-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
1467INT2 | INTERIOR FINISHES | 1467 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | BEHAVIORAL SERVICES HOUSING UNIT A | 9958 | HHS | DCFS | NNCAS | Reno | 1977 | 4000 | 2017-10-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
1467EXT2 | ROOF REPAIRS | 1467 | During the survey of 4/30/2008, there were areas of the composition shingle roof that were missing and / or damaged from a wind event. This project would provide for the repair of the damaged shingles. | BEHAVIORAL SERVICES HOUSING UNIT A | 9958 | HHS | DCFS | NNCAS | Reno | 1977 | 4000 | 2017-10-24 | Immediate to Two Years | Currently Critical | 1 | 1200
1468INT3 | KITCHEN CABINET REPLACEMENT | 1468 | The kitchen cabinets are original to the building and have reached the end of their expected life. This project recommends the replacement of the existing kitchen counters, cabinets and associated hardware with mid range, high quality components. ADA compliant casework is recommended for this facility. Appliances are not included in this estimate. | BEHAVIORAL SERVICES HOUSING UNIT B | 9958 | HHS | DCFS | NNCAS | Reno | 1977 | 4000 | 2017-10-24 | Four to Ten Years | Long-Term Needs | 3 | 15000
1467EXT3 | WINDOW REPLACEMENT | 1467 | The windows are original, dual pane construction in a metal frame. These older windows have become fogged up and discolored due to moisture infiltrating the glass. This project recommends replacing the windows with dual pane, high efficiency units. This estimate is for the replacement of 12 units. | BEHAVIORAL SERVICES HOUSING UNIT A | 9958 | HHS | DCFS | NNCAS | Reno | 1977 | 4000 | 2017-10-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
1467INT3 | KITCHEN CABINET REPLACEMENT | 1467 | The kitchen cabinets are original to the building and have reached the end of their expected life. This project recommends the replacement of the existing kitchen counters, cabinets and associated hardware with mid range, high quality components. ADA compliant casework is recommended for this facility. Appliances are not included in this estimate. | BEHAVIORAL SERVICES HOUSING UNIT A | 9958 | HHS | DCFS | NNCAS | Reno | 1977 | 4000 | 2017-10-24 | Four to Ten Years | Long-Term Needs | 3 | 15000
1467PLM2 | WATER HEATER REPLACEMENT | 1467 | The average life span of a water heater is eight to ten years. The two existing 80 gallon natural gas water heaters in the building have reached the end of their expected life and are not energy efficient. This project would provide for the removal and disposal of the old water heaters and installation of two new 80 gallon water heaters. | BEHAVIORAL SERVICES HOUSING UNIT A | 9958 | HHS | DCFS | NNCAS | Reno | 1977 | 4000 | 2017-10-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
1467PLM1 | REPLACE EXISTING TOILET FIXTURES | 1467 | The existing restrooms date to the construction date of the building. The toilet is an older tank-flush model. Due to variations in the water pressure and the age of the facility, this project recommends the replacement of the existing fixture with a new, pressure-assisted, low-gallonage model. This project or a portion thereof was previously recommended in the FCA report dated 04/23/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2008. | BEHAVIORAL SERVICES HOUSING UNIT A | 9958 | HHS | DCFS | NNCAS | Reno | 1977 | 4000 | 2017-10-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
1466ENR2 | EXTERIOR LIGHTING UPGRADE | 1466 | The building has perimeter lighting on the exterior of the building, but the light fixtures are old, give off inadequate lighting and are not energy efficient. This project would provide for the replacement of the exterior lighting fixtures with new high intensity, energy efficient light fixtures, including connections to the existing electrical system. | ADMINISTRATION/CLASSROOM BUILDING | 9958 | HHS | DCFS | NNCAS | Reno | 1977 | 17210 | 2017-10-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
1466EXT1 | EXTERIOR FINISHES | 1466 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 2 to 3 years and is recommended on a cyclical basis based on environmental conditions. Elastomeric paint is recommended for the stucco portion of the building. This project or a portion thereof was previously recommended in the FCA report dated 04/23/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2008. | ADMINISTRATION/CLASSROOM BUILDING | 9958 | HHS | DCFS | NNCAS | Reno | 1977 | 17210 | 2017-10-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 172100
1468EXT3 | WINDOW REPLACEMENT | 1468 | The windows are original, dual pane construction in a metal frame. These older windows have broken seals, become fogged up and discolored due to moisture infiltrating the glass. This project recommends replacing the windows with dual pane, high efficiency units. This estimate is for the replacement of 12 units. | BEHAVIORAL SERVICES HOUSING UNIT B | 9958 | HHS | DCFS | NNCAS | Reno | 1977 | 4000 | 2017-10-24 | Four to Ten Years | Long-Term Needs | 3 | 18000
1466SFT5 | EXIT SIGN UPGRADES | 1466 | The exit signs are older and appear to be original to the building. Additional signs are required to identify the paths of exit. These signs should be self-illuminating, or LED signs with internal battery back-up. This project or a portion thereof was previously recommended in the FCA report dated 04/23/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2008. | ADMINISTRATION/CLASSROOM BUILDING | 9958 | HHS | DCFS | NNCAS | Reno | 1977 | 17210 | 2017-10-24 | Immediate to Two Years | Currently Critical | 1 | 10000
1467HVA1 | HVAC SYSTEM REPLACEMENT | 1467 | The HVAC system consists of two furnaces and two air cooled condensers. This equipment is original to the building and has reached the end of its expected life. This project recommends replacing the equipment in the next 2 to 3 years. The estimate includes removal and disposal of the existing equipment. | BEHAVIORAL SERVICES HOUSING UNIT A | 9958 | HHS | DCFS | NNCAS | Reno | 1977 | 4000 | 2017-10-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 22000
1466ADA2 | SIGNAGE FOR ADA COMPLIANCE | 1466 | Americans with Disabilities Act (ADA) regulations pertaining to building access, route of travel and restrooms has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances, route of travel inside the building and restrooms. Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 1998 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/23/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2008. | ADMINISTRATION/CLASSROOM BUILDING | 9958 | HHS | DCFS | NNCAS | Reno | 1977 | 17210 | 2017-10-24 | Immediate to Two Years | Currently Critical | 1 | 4000
1466HVA2 | HVAC UPGRADE | 1466 | The HVAC system is largely original to the building and is due for a major upgrade. This equipment has reached the end of its serviceable and expected life span, and should be scheduled for replacement within the next two to three years. This project would provide for replacement of the two Weil-McLain boilers, the water treatment system and several other parts of the HVAC system including a broken gate valve and the boiler exhaust system. Cleaning of the existing ductwork, grills and diffusers, and balancing is included in the project. The estimate includes all utility connections as well as removal and disposal of the existing equipment. This work should be performed concurrently with the "HVAC Controls Upgrade" project. | ADMINISTRATION/CLASSROOM BUILDING | 9958 | HHS | DCFS | NNCAS | Reno | 1977 | 17210 | 2017-10-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 200000
1466ADA3 | ADA RESTROOM UPGRADE | 1466 | The Men's and Women's designated ADA restrooms do not meet the Americans with Disabilities Act (ADA) regulations. A retrofit is necessary to comply with 2006 IBC Chapter 11, ICC/ANSI A117.1-1998 Sections 603 - 604 and the Americans with Disabilities Act Accessibility Guidelines (ADAAG). Given the current configuration of the restrooms, the work will include the installation of a new toilet, sink, grab bars, faucets, mirrors, dispensers and hardware. Some minor design work will be required and may impact the final cost estimate. This estimate is for one Men's and one Women's restroom facility. The removal and disposal of the old restroom fixtures is included in this estimate. | ADMINISTRATION/CLASSROOM BUILDING | 9958 | HHS | DCFS | NNCAS | Reno | 1977 | 17210 | 2017-10-24 | Immediate to Two Years | Currently Critical | 1 | 64000
1466PLM4 | WATER HEATER REPLACEMENT | 1466 | The average life span of a water heater is eight to ten years. The existing 93 gallon natural gas water heater in the building was installed in 1993. It has reached the end of its expected life and is not energy efficient. This project would provide for the removal and disposal of the old water heater and installation of a new 100 gallon water heater. | ADMINISTRATION/CLASSROOM BUILDING | 9958 | HHS | DCFS | NNCAS | Reno | 1977 | 17210 | 2017-10-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2200
1466ADA1 | POWER DOOR OPENER AND HARDWARE | 1466 | The main entrances to this building are dual leaf, commercial grade aluminum and glass door assemblies. The hardware and configuration of the doors does not fully meet ADA requirements. This project recommends the installation of a power-assisted door opener for the main entrance and side entrance and includes the installation, related wiring and hardware. This project or a portion thereof was previously recommended in the FCA report dated 04/23/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2008. | ADMINISTRATION/CLASSROOM BUILDING | 9958 | HHS | DCFS | NNCAS | Reno | 1977 | 17210 | 2017-10-24 | Immediate to Two Years | Currently Critical | 1 | 10000
1466INT2 | CARPET REPLACEMENT | 1466 | The carpet in the addition is showing signs of extreme wear and some areas were not installed correctly. It is recommended that the carpet be replaced with heavy duty commercial grade carpet in the next two to three years. | ADMINISTRATION/CLASSROOM BUILDING | 9958 | HHS | DCFS | NNCAS | Reno | 1977 | 17210 | 2017-10-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 34200
1466INT1 | INTERIOR FINISHES | 1466 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | ADMINISTRATION/CLASSROOM BUILDING | 9958 | HHS | DCFS | NNCAS | Reno | 1977 | 17210 | 2017-10-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 86050
1466SFT1 | FIRE SUPPRESSION SYSTEM INSTALLATION | 1466 | The building is a B occupancy per the 2003 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. | ADMINISTRATION/CLASSROOM BUILDING | 9958 | HHS | DCFS | NNCAS | Reno | 1977 | 17210 | 2017-10-24 | Immediate to Two Years | Currently Critical | 1 | 240940
1467EXT1 | EXTERIOR FINISHES | 1467 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 2 to 3 years and is recommended on a cyclical basis based on environmental conditions. Elastomeric paint is recommended for the stucco portion of the building. This project or a portion thereof was previously recommended in the FCA report dated 04/23/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2008. | BEHAVIORAL SERVICES HOUSING UNIT A | 9958 | HHS | DCFS | NNCAS | Reno | 1977 | 4000 | 2017-10-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 40000
9958SIT4 | EROSION CONTROL | 9958 | On the north side of the Administration/ Classroom Building, the dirt bank between the building and McCarran Blvd is eroding considerably. The runoff from McCarran Blvd is exacerbating an already poorly designed drainage area. The dirt bank has slowly crept closer to the building and has left little space for water to drain around the building. This is now causing damage to the building from flooding and has also flooded the play yard next to the building. There have been several minor improvements accomplished to control the situation, but it is apparent that a major improvement must happen in order to protect the building from permanent damage. This project recommends installing a retaining wall between the building and the street in order to provide proper drainage and erosion control. The estimate is based on a 500 foot long, 8'-0" high reinforced concrete masonry unit retaining wall. | CHILDREN'S BEHAVIORAL SERVICES SITE | 9958 | HHS | DCFS | NNCAS | Reno | 1977 |  | 2017-10-24 | Immediate to Two Years | Currently Critical | 1 | 100000
9958ADA1 | ADA PARKING | 9958 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The existing ADA parking stalls throughout the campus do not entirely meet the requirements of the code. This project provides funding to bring the existing ADA parking areas up to code including updated signage, re-striping, regrading and any other necessary upgrades. IBC - 2006, ICC/ANSI A117.1 - 2003 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2003 were referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/23/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2008. | CHILDREN'S BEHAVIORAL SERVICES SITE | 9958 | HHS | DCFS | NNCAS | Reno | 1977 |  | 2017-10-24 | Immediate to Two Years | Currently Critical | 1 | 50000
9958SIT1 | SITE DRAINAGE ISSUES | 9958 | The site has recurring problems with water pooling at the lower grassy area between the housing units. Some of this may be attributable to drainage problems at the site. Other problems may be a result from site irrigation. This project recommends installing a dry or French drain to minimize flooding and to carry off accumulations. This project includes trenching, installation of gravel in the trench, a 4 inch perforated pipe, more gravel, a non-woven fabric to prevent soil intrusion into the gravel and pipe, backfilling the trench, tamping to finish grade and removal of spoils or surplus soil. This project is recommended to coincide with the retaining wall project. This project or a portion thereof was previously recommended in the FCA report dated 04/23/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2008. | CHILDREN'S BEHAVIORAL SERVICES SITE | 9958 | HHS | DCFS | NNCAS | Reno | 1977 |  | 2017-10-24 | Immediate to Two Years | Currently Critical | 1 | 35000
9958SEC4 | INSTALL EXTERIOR SITE LIGHTING | 9958 | The site has minimal site lighting in the parking lots and between the buildings which is a security and safety concern. This project would provide funding for purchase and installation of six 20'-0" high light poles including 30" diameter raised concrete bases, electrical trenching, conduit, wiring and connections to existing utilities. This project or a portion thereof was previously recommended in the FCA report dated 04/23/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2008. | CHILDREN'S BEHAVIORAL SERVICES SITE | 9958 | HHS | DCFS | NNCAS | Reno | 1977 |  | 2017-10-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 55224
9958ADA2 | ADA SIDEWALK UPGRADES | 9958 | The concrete sidewalks throughout the campus are in need of replacement or modification. There are many areas that do not meet ADA guidelines and 2006 IBC Chapter 10, Section 1010 requirements for ramps including exceeding minimum slope requirements or missing rails and curbs at ramps. There are also many sections of concrete that have cracks due to settling or are spalling considerably. This project would provide for the removal and replacement of the concrete sidewalks. 5,000 SF of 4" thick concrete sidewalk was used for this estimate. A professional design should be commissioned for this project in order to determine the most cost effective construction. The design will incorporate current ADA requirements to insure 100% compliance on all accessible routes-of-travel. IBC - 2006, ICC/ANSI A117.1 - 2003 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2003 were referenced for this project. | CHILDREN'S BEHAVIORAL SERVICES SITE | 9958 | HHS | DCFS | NNCAS | Reno | 1977 |  | 2017-10-24 | Immediate to Two Years | Currently Critical | 1 | 75000
9958SIT3 | SLURRY SEAL ASPHALT PAVING | 9958 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site wide. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 70,000 square feet of asphalt area was used to generate this estimate. It is recommended that the site drainage project be completed prior to this project. This project or a portion thereof was previously recommended in the FCA report dated 04/23/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2008. | CHILDREN'S BEHAVIORAL SERVICES SITE | 9958 | HHS | DCFS | NNCAS | Reno | 1977 |  | 2017-10-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 42000
9859SIT1 | SLURRY SEAL ASPHALT PAVING | 9859 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site wide including access roads and parking areas. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 60,000 square feet of asphalt area was used to generate this estimate. | NEVADA EARLY INTERVENTION SERVICES SITE | 9859 | HHS | ADSD | B&G | Reno | 0 |  | 2017-10-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 45000
9859SIT2 | EROSION CONTROL | 9859 | On the north side of the building, the dirt bank between the building and McCarran Blvd is eroding considerably. The runoff from McCarran Blvd is exacerbating an already poorly designed drainage area. The dirt bank has spilled over the curb into the access road. There have been several minor improvements accomplished to control the situation, but it is apparent that a major improvement must happen in order to protect the road, parking and the building from permanent damage. This project recommends installing a retaining wall near the curb in order to provide proper drainage and erosion control. The estimate is based on a 300 foot long, 4'-0" high reinforced concrete masonry unit retaining wall. | NEVADA EARLY INTERVENTION SERVICES SITE | 9859 | HHS | ADSD | B&G | Reno | 0 |  | 2017-10-24 | Immediate to Two Years | Currently Critical | 1 | 30000
0515EXT2 | WATERPROOFING UPGRADES | 0515 | The south facing exterior wall experiences water weeping through it during inclement weather. The water infiltration can be seen on the interior of the brick masonry wall and the most extensive weeping occurs directly below the roof scuppers. This project provides for waterproofing the exterior wall and decks by applying sealant and caulking and extending the roof scuppers and deck scuppers to grade rather than draining down the sides of the walls. | NEVADA EARLY INTERVENTION SERVICES | 9859 | HHS | ADSD | B&G | Reno | 1980 | 19800 | 2017-10-24 | Immediate to Two Years | Currently Critical | 1 | 25000
0515PLM1 | WATER HEATER REPLACEMENT | 0515 | There is a 85 gallon gas-fired water heater in the basement. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 5-6 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | NEVADA EARLY INTERVENTION SERVICES | 9859 | HHS | ADSD | B&G | Reno | 1980 | 19800 | 2017-10-24 | Four to Ten Years | Long-Term Needs | 3 | 3000
0515ADA4 | ADA SIGNAGE | 0515 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | NEVADA EARLY INTERVENTION SERVICES | 9859 | HHS | ADSD | B&G | Reno | 1980 | 19800 | 2017-10-24 | Immediate to Two Years | Currently Critical | 1 | 3600
0515INT2 | TILE FLOORING REPLACEMENT | 0515 | The ceramic tile flooring in the entry vestibule is damaged and reaching the end of its useful life. It is recommended that the tile flooring be replaced. This project would provide for removal and disposal of the existing tile and installation of new ceramic tile flooring. | NEVADA EARLY INTERVENTION SERVICES | 9859 | HHS | ADSD | B&G | Reno | 1980 | 19800 | 2017-10-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
0515INT3 | JANITORS CLOSET REPAIRS | 0515 | The mop sink in the Janitor Closet is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | NEVADA EARLY INTERVENTION SERVICES | 9859 | HHS | ADSD | B&G | Reno | 1980 | 19800 | 2017-10-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
0515EXT1 | EXTERIOR FINISHES | 0515 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing the entire building, priming and painting the stucco and trim and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NEVADA EARLY INTERVENTION SERVICES | 9859 | HHS | ADSD | B&G | Reno | 1980 | 19800 | 2017-10-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 99000
0515INT1 | INTERIOR FINISHES | 0515 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | NEVADA EARLY INTERVENTION SERVICES | 9859 | HHS | ADSD | B&G | Reno | 1980 | 19800 | 2017-10-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 99000
0515ADA3 | ADA KITCHEN REMODEL | 0515 | The kitchen is in fair to poor condition and does not meet the Americans with Disabilities Act (ADA) requirements. The cabinets and equipment are showing signs of general wear and tear and are approaching the end of their expected life. ADA features such as accessible fixtures, clear floor space and compliant counter heights should be integrated into the new design. This project recommends the replacement of the existing kitchen cabinets, counters, fixtures and appliances with mid range, high quality components that comply with ADA requirements. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | NEVADA EARLY INTERVENTION SERVICES | 9859 | HHS | ADSD | B&G | Reno | 1980 | 19800 | 2017-10-24 | Immediate to Two Years | Currently Critical | 1 | 20000
0515ENV1 | NONABSORBENT FINISHES | 0515 | 2006 IBC Section 1210 requires the installation of smooth, hard, nonabsorbent surfaces in the following restroom areas: on floors in toilet and bathing rooms that extend upward onto the walls at least 6 inches, within 2 feet of the sides of urinals and water closets to a height of 4 feet above the floor and in shower compartments to a height not less than 70 inches above the drain inlet. This project recommends the installation of Fiberglass Reinforced Panel (FRP) or an equal material to comply with this code section. This project or a portion thereof was previously recommended in the FCA report dated 04/17/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/19/2011. | NEVADA EARLY INTERVENTION SERVICES | 9859 | HHS | ADSD | B&G | Reno | 1980 | 19800 | 2017-10-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10500
2501LGT1 | EXTERIOR FINISHES | 2501 | Projects in this category address possible long term needs of the facility. This does not represent a cost for all future maintenance but is a budgetary number for future Capital Improvement projects related to maintenance. The cyclical treatment of the building exterior is very important to help maintain the finish, weather proofing, and integrity of the building. This project includes painting of exterior door assembly, weather stripping, and sealant around the roof penetrations. | AMMO BUNKER #2 | 9896 | Military | NNG |  | Carson City | 1973 | 600 | 2005-03-03 | Four to Ten Years | Long-Term Needs | 3 | 3000
2502LGT1 | EXTERIOR FINISHES | 2502 | Projects in this category address possible long term needs of the facility. This does not represent a cost for all future maintenance but is a budgetary number for future Capital Improvement projects related to maintenance. The cyclical treatment of the building exterior is very important to help maintain the finish, weather proofing, and integrity of the building. This project includes painting of exterior door assembly, weather stripping, and sealant around the roof penetrations. | AMMO BUNKER #3 | 9896 | Military | NNG |  | Carson City | 1973 | 600 | 2005-03-03 | Four to Ten Years | Long-Term Needs | 3 | 3000
0668LGT1 | EXTERIOR FINISHES | 0668 | Projects in this category address possible long term needs of the facility. This does not represent a cost for all future maintenance but is a budgetary number for future Capital Improvement projects related to maintenance. The cyclical treatment of the building exterior is very important to help maintain the finish, weather proofing, and integrity of the building. This project includes painting of exterior door assembly, weather stripping, and sealant around the roof penetrations. | AMMO BUNKER #1 | 9896 | Military | NNG |  | Carson City | 1973 | 600 | 2005-03-03 | Four to Ten Years | Long-Term Needs | 3 | 3000
2530LGT1 | LONG-TERM NEEDS | 2530 | Projects in this category address possible long term needs of the facility. This does not represent a cost for all maintenance but is a budgetary estimate for future maintenance. The cyclical treatment of the building exterior is important to help maintain the finish, weather proofing, integrity, and appearance of the building. This project does not include the roofing system, but includes items related to water proofing the building envelope, including painting, sealing, repairing, and caulking where applicable. | HAZARDOUS MATERIALS BUILDING | 9884 | Military | NNG |  | Winnemucca | 0 | 66 | 2005-07-28 | Four to Ten Years | Long-Term Needs | 3 | 2500
9884SIT4 | SITE ACCESSIBILITY | 9884 | The accessible parking, travel route, and public entrance are not clearly defined. Currently, the public parks in the rear of the building and must utilize the side entrance for the accessible route of travel from the parking area to the building. The travel route from the parking area to the accessible door is a concrete walk that is in need of replacement. This project would provide for accessible parking, striping, signage and removal and replacement of about 50 lineal feet of a three foot wide concrete accessible route of travel to the building. | WINNEMUCCA ARMORY SITE | 9884 | Military | NNG |  | Winnemucca | 0 |  | 2005-07-28 | Immediate to Two Years | Currently Critical | 1 | 25000
9884SIT3 | REPAIR RETAINING WALL | 9884 | The site has a retaining wall that runs along the rear of the Armory building parking area that separates the lower and upper part of the facility. The wall is constructed of CMU and precast concrete and has numerous cracks due to water infiltration and age. This may be compromising the structural integrity of the wall. This project would provide for repairs to the wall and the application of a sealer to prevent further damage. | WINNEMUCCA ARMORY SITE | 9884 | Military | NNG |  | Winnemucca | 0 |  | 2005-07-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
9884SIT1 | WEED ABATEMENT | 9884 | The Nevada National Guard - Winnemucca Site is overgrown with weeds. This project would provide for the removal and disposal of the weeds on the site and treatment of the area with an herbicide to prevent future weed growth. | WINNEMUCCA ARMORY SITE | 9884 | Military | NNG |  | Winnemucca | 0 |  | 2005-07-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
9884SIT2 | FENCING | 9884 | The Nevada National Guard - Winnemucca Site is currently fenced off to the general public for security and safety reasons. There is a chain link fence dividing the upper level from the lower level located adjacent to the retaining wall. There are some areas of the fence that are damaged and should be replaced. This project would provide for replacement of the 6 foot tall industrial chain link fence. | WINNEMUCCA ARMORY SITE | 9884 | Military | NNG |  | Winnemucca | 0 |  | 2005-07-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4910
9884SIT5 | REPLACE CONCRETE SIDEWALKS AND PARKING AREA | 9884 | The concrete sidewalks and parking appear to be part of the original construction. Deterioration, spalling, and cracking has occurred mainly from exposure to the weather and possible water accumulation. This project would provide for the removal and replacement of the concrete sidewalks in front of the Armory and the concrete parking area in the rear of the Armory. Disposal of the old concrete is included in this estimate. | WINNEMUCCA ARMORY SITE | 9884 | Military | NNG |  | Winnemucca | 0 |  | 2005-07-28 | Four to Ten Years | Long-Term Needs | 3 | 140000
0688LGT1 | LONG TERM NEEDS | 0688 | Projects in this category address possible long term needs of the facility. This does not represent a cost for all future maintenance but is a budgetary number for future Capital Improvement projects related to maintenance. The cyclical treatment of the building exterior and interior is very important to help maintain the finish, weather proofing, integrity and appearance of the building. This treatment does not include the roofing material itself but it should include everything that has to do with water proofing the building envelope including painting or staining, sealing, repair, and caulking where applicable; for example, around all windows, flashing, fixtures, sills, etc. This also includes interior applied finishes such as paint, grout, caulking, etc. Special attention should be paid to areas that are exposed to moisture. | ARMORY | 9884 | Military | NNG |  | Winnemucca | 1959 | 9877 | 2005-07-28 | Four to Ten Years | Long-Term Needs | 3 | 150000
0688SFT1 | SERVICING FIRE SUPPRESION EQUIPMENT | 0688 | The existing fire extinguishers and fire sprinkler system are in need of servicing. Under the NAC 477.460 and 477.410 these items must be serviced and tagged annually. This project would provide funding to inspect and service all the fire extinguishers and fire sprinkler system. | ARMORY | 9884 | Military | NNG |  | Winnemucca | 1959 | 9877 | 2005-07-28 | Immediate to Two Years | Currently Critical | 1 | 1000
0688HVA1 | AIR HANDLER FILTER UPGRADE | 0688 | The existing HVAC system is equipped with an economizer cycle and enthalpy control for "free cooling" of the building. The air-handlers have large gaps in the duct work located around the economizers. The gaps are allowing insects and gnats access inside the building. This project would provide funding to modify the duct work system to eliminate the gaps. | ARMORY | 9884 | Military | NNG |  | Winnemucca | 1959 | 9877 | 2005-07-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0688SFT2 | INSTALL EMERGENCY EGRESS LIGHTING | 0688 | There is no emergency egress lighting in the hallway. This project recommends the installation of egress lighting along the exit pathway in the building. | ARMORY | 9884 | Military | NNG |  | Winnemucca | 1959 | 9877 | 2005-07-28 | Immediate to Two Years | Currently Critical | 1 | 500
0688INT1 | WALL/FLOOR REPAIRS | 0688 | The gypsum board and vinyl tile are separating in the men's restrooms and some damage has already occurred. The separation may be caused from moisture. This project would provide funding for the investigation, repairs and replacement of the damage gypsum board and vinyl tile. Other projects may be developed from the findings of where the moisture source may be coming from and any suggestions on prevention of the moisture infiltration. | ARMORY | 9884 | Military | NNG |  | Winnemucca | 1959 | 9877 | 2005-07-28 | Immediate to Two Years | Currently Critical | 1 | 7500
0688SFT3 | SEISMIC GAS SHUT OFF VALVE | 0688 | Agreements reached between the Nevada Risk Management Office and the State of Nevada's Insurance Underwriter require Seismic Gas Shutoff Valves (SGSV's) on all gas services to all State owned buildings. This project would install a SGSV to the gas line serving the building. | ARMORY | 9884 | Military | NNG |  | Winnemucca | 1959 | 9877 | 2005-07-28 | Immediate to Two Years | Currently Critical | 1 | 3000
2731EXT1 | EXTERIOR FINISHES | 2731 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope including painting or other applied finishes, and caulking around flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | HAZARDOUS WASTE STORAGE | 9796 | Military | NNG | Fire Sci | Carlin | 2006 | 120 | 2007-11-08 | Four to Ten Years | Long-Term Needs | 3 | 360
2040SIT1 | ASPHALT REPLACEMENT | 2040 | The asphalt around the building is failing, with significant alligatoring, settling and cracks observed. It was not included in the 2007 asphalt replacement for the rest of the site. This project covers the removal and replacement of the existing asphalt for parking and site access. Striping for safety, parking and loading zones is included in this estimate. 16,500 square feet was used to generate this estimate. | FIELD MAINTENANCE SHOP 2 | 9920 | Military | NNG |  | Stead | 1994 | 5800 | 2008-07-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 165000
2040INT1 | INTERIOR FINISHES | 2040 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted and / or sealed at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | FIELD MAINTENANCE SHOP 2 | 9920 | Military | NNG |  | Stead | 1994 | 5800 | 2008-07-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 29000
2041EXT1 | REPLACE ROOF | 2041 | The roof was installed in 1997 and is in fair shape. The statewide roofing program has set the useful life of an average roof at 15 years. The roof warranty expires at the end of the same time frame. It is recommended that this building be re-roofed in 2012 to be consistent with the roofing program and the end of the warranty period and prevent future damage to the interior finishes. This project applies to the single-ply membrane system only. This project or a portion thereof was previously recommended in the FCA report dated 08/27/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/17/2008. | WASHOE COUNTY TRAINING CENTER | 9920 | Military | NNG |  | Stead | 1997 | 63358 | 2008-07-17 | Four to Ten Years | Long-Term Needs | 3 | 675000
2040EXT1 | EXTERIOR FINISHES | 2040 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, sealing or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | FIELD MAINTENANCE SHOP 2 | 9920 | Military | NNG |  | Stead | 1994 | 5800 | 2008-07-17 | Four to Ten Years | Long-Term Needs | 3 | 29000
2040PLM1 | WATER HEATER REPLACEMENT | 2040 | The average life span of a water heater is eight to ten years. The existing 50 gallon natural gas fired water heater in the building is reaching the end of its expected life and should be scheduled for replacement. This project would provide for the removal and disposal of the old water heater and installation of a new natural gas fired water heater. | FIELD MAINTENANCE SHOP 2 | 9920 | Military | NNG |  | Stead | 1994 | 5800 | 2008-07-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
2040ADA1 | ADA SIGNAGE | 2040 | The building is lacking ADA signage. Americans with Disabilities Act (ADA) regulations pertaining to building access, route of travel and restrooms has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances, route of travel inside the building and restrooms. Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 1998 was referenced for this project. | FIELD MAINTENANCE SHOP 2 | 9920 | Military | NNG |  | Stead | 1994 | 5800 | 2008-07-17 | Immediate to Two Years | Currently Critical | 1 | 2000
2408INT2 | JANITORS CLOSET REPAIRS | 2408 | The mop sink in the Janitors Closet is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | OSA FLIGHT DETACHMENT 45 | 9920 | Military | NNG |  | Stead | 2000 | 11131 | 2008-07-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
2045ENV1 | INSTALL CARBON MONOXIDE DETECTORS | 2045 | Portions of the facility are served by direct fired gas furnaces. These devices can put out elevated levels of carbon monoxide. This project would install carbon monoxide detectors in all areas served by the direct fired furnaces with both alarms and furnace interlocks. This project or a portion thereof was previously recommended in the FCA report dated 08/27/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/17/2008. | ARMY AVIATION SUPPORT FACILITY | 9920 | Military | NNG |  | Stead | 1984 | 72292 | 2008-07-17 | Immediate to Two Years | Currently Critical | 1 | 5000
2041PLM1 | WATER HEATER REPLACEMENT | 2041 | The average life span of a water heater is eight to ten years. The existing 80 gallon natural gas fired water heater in the building is reaching the end of its expected life and should be scheduled for replacement. This project would provide for the removal and disposal of the old water heater and installation of a new natural gas fired water heater. | WASHOE COUNTY TRAINING CENTER | 9920 | Military | NNG |  | Stead | 1997 | 63358 | 2008-07-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
2045ADA1 | ACCESSIBLE WATER FOUNTAIN | 2045 | This building has three water fountains. IBC-2006 Section 1109.5 states that where a water fountain is provided, at least half should be accessible. This project would provide funding for the purchase and installation of two ADA compliant high/ low water fountains. The installation of the water fountains must comply with ICC/ANSI A117.1-2003 and the most current edition of the Americans with Disabilities Act Accessibility Guidelines (ADAAG). | ARMY AVIATION SUPPORT FACILITY | 9920 | Military | NNG |  | Stead | 1984 | 72292 | 2008-07-17 | Immediate to Two Years | Currently Critical | 1 | 6000
2408EXT1 | EXTERIOR FINISHES | 2408 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It appears that the building was not properly sealed at the time of construction. There is evidence of water penetration on the inside of the CMU walls. It is recommended that this project be implemented as soon as possible and is recommended on a cyclical basis based on environmental conditions. | OSA FLIGHT DETACHMENT 45 | 9920 | Military | NNG |  | Stead | 2000 | 11131 | 2008-07-17 | Immediate to Two Years | Currently Critical | 1 | 111310
2408ADA1 | ADA SIGNAGE | 2408 | The building is lacking ADA signage. Americans with Disabilities Act (ADA) regulations pertaining to building access, route of travel and restrooms has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances, route of travel inside the building and restrooms. Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 1998 was referenced for this project. | OSA FLIGHT DETACHMENT 45 | 9920 | Military | NNG |  | Stead | 2000 | 11131 | 2008-07-17 | Immediate to Two Years | Currently Critical | 1 | 3500
2910INT1 | INTERIOR FINISHES | 2910 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | GUARD SHACK | 9920 | Military | NNG |  | Stead | 0 | 64 | 2008-07-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 320
2408SFT1 | INSTALL SEISMIC GAS SHUT-OFF VALVE | 2408 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel brace. | OSA FLIGHT DETACHMENT 45 | 9920 | Military | NNG |  | Stead | 2000 | 11131 | 2008-07-17 | Immediate to Two Years | Currently Critical | 1 | 3500
2408PLM1 | WATER HEATER REPLACEMENT | 2408 | The average life span of a water heater is eight to ten years. The existing 100 gallon natural gas fired water heater in the building is reaching the end of its expected life and should be scheduled for replacement. This project would provide for the removal and disposal of the old water heater and installation of a new 100 gallon natural gas fired water heater. | OSA FLIGHT DETACHMENT 45 | 9920 | Military | NNG |  | Stead | 2000 | 11131 | 2008-07-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3500
2408INT1 | INTERIOR FINISHES | 2408 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted and / or sealed at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | OSA FLIGHT DETACHMENT 45 | 9920 | Military | NNG |  | Stead | 2000 | 11131 | 2008-07-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 55655
2909EXT1 | EXTERIOR FINISHES | 2909 | This wood framed shade ramada covers picnic tables and a barbecue. It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting the structure and should be done on a cyclical basis based on environmental conditions. | SHADE RAMADA | 9920 | Military | NNG |  | Stead | 0 | 450 | 2008-07-17 | Four to Ten Years | Long-Term Needs | 3 | 900
2910EXT1 | EXTERIOR FINISHES | 2910 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, sealing or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | GUARD SHACK | 9920 | Military | NNG |  | Stead | 0 | 64 | 2008-07-17 | Four to Ten Years | Long-Term Needs | 3 | 320
2408ADA2 | ADA RESTROOM REMODEL | 2408 | The vanities in the Men's and Women's restroom are not accessible and should be replaced with an ADA accessible countertop, sink, faucet and plumbing jacket. There are also showers present which are not compliant. This project also includes remodeling both showers into ADA compliant showers including fixtures. IBC - 2006, ICC/ANSI A117.1 - 2003 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2003 were referenced for this project. | OSA FLIGHT DETACHMENT 45 | 9920 | Military | NNG |  | Stead | 2000 | 11131 | 2008-07-17 | Immediate to Two Years | Currently Critical | 1 | 16000
2055EXT1 | EXTERIOR FINISHES | 2055 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, sealing metal siding penetrations or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | HAZARDOUS WASTE STORAGE #5 | 9920 | Military | NNG |  | Stead | 1984 | 500 | 2008-07-17 | Four to Ten Years | Long-Term Needs | 3 | 800
2041EXT2 | EXTERIOR FINISHES | 2041 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, sealing or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | WASHOE COUNTY TRAINING CENTER | 9920 | Military | NNG |  | Stead | 1997 | 63358 | 2008-07-17 | Four to Ten Years | Long-Term Needs | 3 | 316790
2045INT1 | INTERIOR FINISHES | 2045 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | ARMY AVIATION SUPPORT FACILITY | 9920 | Military | NNG |  | Stead | 1984 | 72292 | 2008-07-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 361460
2046EXT1 | EXTERIOR FINISHES | 2046 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, sealing metal siding penetrations or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | PHYSICAL TRAINING | 9920 | Military | NNG |  | Stead | 1992 | 1632 | 2008-07-17 | Four to Ten Years | Long-Term Needs | 3 | 3264
2046INT1 | INTERIOR FINISHES | 2046 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | PHYSICAL TRAINING | 9920 | Military | NNG |  | Stead | 1992 | 1632 | 2008-07-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8160
2046INT2 | RESTROOM REMODEL | 2046 | The restroom in the building was out of service at the time of the survey. It is original to the building and is due for a complete remodel. This project would provide for a complete remodel of the restroom fixtures, hardware, floor and wall finishes. | PHYSICAL TRAINING | 9920 | Military | NNG |  | Stead | 1992 | 1632 | 2008-07-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
2054EXT1 | EXTERIOR FINISHES | 2054 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, sealing metal siding penetrations or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | HAZARDOUS WASTE STORAGE #4 | 9920 | Military | NNG |  | Stead | 1991 | 252 | 2008-07-17 | Four to Ten Years | Long-Term Needs | 3 | 504
2041INT2 | REPLACE CARPET FLOORING | 2041 | The carpet is showing signs of extreme wear and has reached the end of its useful life. It is recommended that the carpet be replaced with heavy duty commercial grade carpet in the next two to three years. Approximately half of the flooring in the building is carpet. This project or a portion thereof was previously recommended in the FCA report dated 08/27/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/17/2008. | WASHOE COUNTY TRAINING CENTER | 9920 | Military | NNG |  | Stead | 1997 | 63358 | 2008-07-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 158395
2045HVA1 | BOILER REPLACEMENT | 2045 | The building has four hot water boilers servicing the building. Two boilers service the North Hangar and the other two service the South Hangar. Of the two in each Hangar, one is original to the building. The life expectancy of these units is 20 to 25 years with proper maintenance and water treatment programs. Replacement parts for performing routine and emergency maintenance are hard to find for this old equipment. The controls and mixing valves should be replaced for the same reasons. This project would provide for the removal and disposal of the existing boilers, controls and mixing valve and replacement with new equipment including all required connections to utilities and equipment. The estimate is based on a 1,460 MBH output hot water boiler. The existing chemical water treatment system will need to be tested and adjusted once equipment is operational. $2,000 is included in this estimate for testing of the chemical water treatment system. | ARMY AVIATION SUPPORT FACILITY | 9920 | Military | NNG |  | Stead | 1984 | 72292 | 2008-07-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 84000
2048EXT1 | EXTERIOR FINISHES | 2048 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, sealing metal siding penetrations or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | AVIATION STORAGE #2 | 9920 | Military | NNG |  | Stead | 1987 | 960 | 2008-07-17 | Four to Ten Years | Long-Term Needs | 3 | 1920
2049EXT1 | EXTERIOR FINISHES | 2049 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, sealing metal siding penetrations or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | STORAGE BUILDING #10 | 9920 | Military | NNG |  | Stead | 2006 | 3300 | 2008-07-17 | Four to Ten Years | Long-Term Needs | 3 | 6600
2050EXT1 | EXTERIOR FINISHES | 2050 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, sealing metal siding penetrations or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | AVIATION STORAGE #8 | 9920 | Military | NNG |  | Stead | 1987 | 3300 | 2008-07-17 | Four to Ten Years | Long-Term Needs | 3 | 6600
2051EXT1 | EXTERIOR FINISHES | 2051 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, sealing metal siding penetrations or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | POL BUILDING | 9920 | Military | NNG |  | Stead | 1992 | 630 | 2008-07-17 | Four to Ten Years | Long-Term Needs | 3 | 2200
2052EXT1 | EXTERIOR FINISHES | 2052 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, sealing metal siding penetrations or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | HAZARDOUS WASTE STORAGE #1 | 9920 | Military | NNG |  | Stead | 1994 | 1260 | 2008-07-17 | Four to Ten Years | Long-Term Needs | 3 | 2520
2053EXT1 | EXTERIOR FINISHES | 2053 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, sealing metal siding penetrations or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | PUMPHOUSE | 9920 | Military | NNG |  | Stead | 1984 | 480 | 2008-07-17 | Four to Ten Years | Long-Term Needs | 3 | 960
2047EXT1 | EXTERIOR FINISHES | 2047 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, sealing metal siding penetrations or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | AVIATION STORAGE #1 | 9920 | Military | NNG |  | Stead | 1987 | 960 | 2008-07-17 | Four to Ten Years | Long-Term Needs | 3 | 1920
2045PLM1 | WATER HEATER REPLACEMENT | 2045 | The average life span of a water heater is eight to ten years. The two existing 75 gallon natural gas fired water heaters and the 65 gallon natural gas fired water heater in the building have reached the end of their expected life and should be scheduled for replacement. This project would provide for the removal and disposal of the old water heaters and installation of three new natural gas fired water heaters. | ARMY AVIATION SUPPORT FACILITY | 9920 | Military | NNG |  | Stead | 1984 | 72292 | 2008-07-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
2045EXT1 | EXTERIOR FINISHES | 2045 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, sealing or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | ARMY AVIATION SUPPORT FACILITY | 9920 | Military | NNG |  | Stead | 1984 | 72292 | 2008-07-17 | Four to Ten Years | Long-Term Needs | 3 | 361460
2045SFT1 | EGRESS LIGHTING UPGRADE | 2045 | The existing egress lights in this building are older types or are missing altogether. Egress lighting should be installed and/or replaced to provide illumination along the egress route per 2006 IBC Chapter 10, Section 1006. This project would provide for the installation of egress lighting including connections to existing utilities in the office support area of the facility. | ARMY AVIATION SUPPORT FACILITY | 9920 | Military | NNG |  | Stead | 1984 | 72292 | 2008-07-17 | Immediate to Two Years | Currently Critical | 1 | 7500
2041INT1 | INTERIOR FINISHES | 2041 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted and / or sealed at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 08/27/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/17/2008. | WASHOE COUNTY TRAINING CENTER | 9920 | Military | NNG |  | Stead | 1997 | 63358 | 2008-07-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 316790
9920SFT1 | INSTALL MOTORIZED GATES | 9920 | The site has a perimeter fence that has vehicle access gates off Army Aviation Drive. They are mechanically operated, have been problematic, and are difficult to open and close. This project recommends the gates be upgraded to a motorized track system that can handle heavy equipment traffic. The gates will be required to meet UL Standard 325, per NRS 405.270. This project or a portion thereof was previously recommended in the FCA report dated 08/27/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/17/2008. | SEN. HARRY REID READINESS & TRAINING CTR | 9920 | Military | NNG |  | Stead | 0 |  | 2008-07-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
9920SIT3 | SLURRY SEAL ASPHALT PAVING | 9920 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site wide including access roads, aprons and parking areas. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 1,150,000 square feet of asphalt area was used to generate this estimate. | SEN. HARRY REID READINESS & TRAINING CTR | 9920 | Military | NNG |  | Stead | 0 |  | 2008-07-17 | Four to Ten Years | Long-Term Needs | 3 | 862500
2963INT1 | INTERIOR FINISHES | 2963 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next three to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | BLDG #14-SECURITY KIOSK | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 60 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 300
2955ENR1 | OCCUPANCY SENSOR INSTALLATION | 2955 | There are no occupancy sensors installed in the building to control lighting. It is recommended that sensors be installed in order to reduce energy costs. Occupancy sensors will be installed in restrooms, storage rooms, utility rooms and other low occupancy areas for additional savings. This project provides for purchase and installation of 10 sensors. | BLDG #5-TURNOUT | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 11782 | 2009-11-18 | Immediate to Two Years | Currently Critical | 1 | 4000
2967INT1 | INTERIOR FINISHES | 2967 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next three to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | BLDG #9-CLASSROOM/TOILET #2 | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 1320 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6600
2967EXT2 | EXTERIOR FINISHES | 2967 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the masonry and caulking of the control joints, windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BLDG #9-CLASSROOM/TOILET #2 | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 1320 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6600
2967PLM1 | WATER HEATER REPLACEMENT | 2967 | There is an on-demand propane-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new on-demand propane-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | BLDG #9-CLASSROOM/TOILET #2 | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 1320 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
2964INT1 | INTERIOR FINISHES | 2964 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next three to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | DAF/CHEMICAL BUILDING | 9796 | Military | NNG | Fire Sci | Carlin | 2002 | 3696 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18480
2951INT1 | INTERIOR FINISHES | 2951 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next three to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | BLDG #1-ADMINISTRATION | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 8448 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 42240
2953INT1 | INTERIOR FINISHES | 2953 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next three to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | BLDG #3-CLASSROOM | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 19732 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 98660
2954INT1 | INTERIOR FINISHES | 2954 | The interior finishes are in good condition. Most of the walls are covered with wallpaper and does not need to be addressed at this time. It is recommended that the painted gypsum board walls be painted at least once in the next three to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. 500 square feet of area was used to generate this estimate. | BLDG #4-STAFF RESIDENCE | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 9759 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
2954EXT1 | EXTERIOR FINISHES | 2954 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the masonry and caulking of the control joints, metal panels, windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BLDG #4-STAFF RESIDENCE | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 9759 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 48795
2963EXT1 | EXTERIOR FINISHES | 2963 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the masonry and caulking of the control joints, metal panels, windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BLDG #14-SECURITY KIOSK | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 60 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 300
2953INT2 | FLOORING REPLACEMENT | 2953 | The VCT (vinyl composite tile) and carpet in the building are worn and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the next two to three years. The carpet in the Auditorium has recently been replaced and is not included in the estimate. 15,000 square feet was used to generate the estimate. | BLDG #3-CLASSROOM | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 19732 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 120000
2964EXT1 | EXTERIOR FINISHES | 2964 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | DAF/CHEMICAL BUILDING | 9796 | Military | NNG | Fire Sci | Carlin | 2002 | 3696 | 2009-11-18 | Four to Ten Years | Long-Term Needs | 3 | 11088
2955EXT1 | EXTERIOR FINISHES | 2955 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the masonry and caulking of the control joints, metal panels, windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BLDG #5-TURNOUT | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 11782 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 58910
2953EXT2 | ROOF REPLACEMENT | 2953 | The roof on this building was in fair condition at the time of the survey. There are two roof coverings on the building, standing seam metal and Sarnafil single-ply membrane. The statewide roofing program has set the useful life of an average single-ply membrane roof at 15 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1999. It is recommended that the single-ply membrane portion of the roof be replaced by 2014 to be consistent with the roofing program and the end of the warranty period. 4,624 square feet was used to generate this estimate. | BLDG #3-CLASSROOM | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 19732 | 2009-11-18 | Four to Ten Years | Long-Term Needs | 3 | 69360
2955INT2 | FLOORING REPAIRS / REPLACEMENT | 2955 | The sealed concrete and carpet in the building are worn and reaching the end of their useful life. It is recommended that the concrete be stripped and re-sealed and that the carpet in the offices be replaced. This project would provide for stripping the concrete and applying a new coat of sealant and removal and disposal of the carpet and installation of new heavy duty commercial grade carpet in the next two to three years. | BLDG #5-TURNOUT | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 11782 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 58910
2954ENR1 | OCCUPANCY SENSOR INSTALLATION | 2954 | There are no occupancy sensors installed in the building to control lighting. It is recommended that sensors be installed in order to reduce energy costs. Occupancy sensors will be installed in restrooms, utility rooms and other low occupancy areas for additional savings. This project provides for purchase and installation of 6 sensors. | BLDG #4-STAFF RESIDENCE | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 9759 | 2009-11-18 | Immediate to Two Years | Currently Critical | 1 | 2400
2951EXT1 | EXTERIOR FINISHES | 2951 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the masonry and caulking of the control joints, metal panels, windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BLDG #1-ADMINISTRATION | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 8448 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 42240
2954PLM1 | WATER HEATER REPLACEMENT | 2954 | There is a 432 gallon, 985 MBH input propane-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new propane-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | BLDG #4-STAFF RESIDENCE | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 9759 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
2951ENR1 | OCCUPANCY SENSOR INSTALLATION | 2951 | There are no occupancy sensors installed in the building to control lighting. It is recommended that sensors be installed in order to reduce energy costs. Occupancy sensors will be installed in restrooms, conference rooms, utility rooms, and other low occupancy areas for additional savings. This project provides for purchase and installation of 12 sensors. | BLDG #1-ADMINISTRATION | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 8448 | 2009-11-18 | Immediate to Two Years | Currently Critical | 1 | 4800
2951PLM1 | WATER HEATER REPLACEMENT | 2951 | There is a 50 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | BLDG #1-ADMINISTRATION | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 8448 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
2951INT2 | FLOORING REPLACEMENT | 2951 | The VCT (vinyl composite tile) and carpet in the building is worn and reaching the end of its useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the next two to three years. | BLDG #1-ADMINISTRATION | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 8448 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 67584
2952EXT1 | EXTERIOR FINISHES | 2952 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the masonry and caulking of the control joints, metal panels, windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BLDG #2-FOOD SERVICE | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 8941 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 44705
2952INT1 | INTERIOR FINISHES | 2952 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next three to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | BLDG #2-FOOD SERVICE | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 8941 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 44705
2952INT2 | FLOORING REPLACEMENT | 2952 | The VCT (vinyl composite tile) and carpet in the building are worn and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the next two to three years. | BLDG #2-FOOD SERVICE | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 8941 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 71528
2952ENR1 | INCANDESCENT LIGHTING UPGRADE | 2952 | The existing lighting fixtures are incandescent type, and are not energy efficient. This project will upgrade incandescent fixtures to higher efficiency units with a longer life cycle. CFL (compact fluorescent lamps) are suggested. Occupancy sensors will be installed in restrooms, conference rooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | BLDG #2-FOOD SERVICE | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 8941 | 2009-11-18 | Immediate to Two Years | Currently Critical | 1 | 8941
2952PLM1 | WATER HEATER REPLACEMENT | 2952 | There is a 100 gallon propane-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. Removal and disposal of the existing equipment is included in this estimate. | BLDG #2-FOOD SERVICE | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 8941 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
2953EXT1 | EXTERIOR FINISHES | 2953 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the masonry and caulking of the control joints, metal panels, windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BLDG #3-CLASSROOM | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 19732 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 98660
2953ENR1 | INCANDESCENT LIGHTING UPGRADE | 2953 | The existing lighting fixtures are mostly T-8 fluorescent lights and do not require upgrading at this time. However, there are large areas lit by the older incandescent type lamps, and are not energy efficient. This project will upgrade incandescent fixtures to higher efficiency units with a longer life cycle. CFL (compact fluorescent lamps) are suggested. Occupancy sensors will be installed in restrooms, conference rooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | BLDG #3-CLASSROOM | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 19732 | 2009-11-18 | Immediate to Two Years | Currently Critical | 1 | 5000
2953PLM1 | WATER HEATER REPLACEMENT | 2953 | There is a 30 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | BLDG #3-CLASSROOM | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 19732 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1200
2957HVA1 | CENTRAL PLANT UPGRADES | 2957 | The Central Plant contains a hot water boiler and evaporative cooling tower located on the equipment patio on the west side of the Buildings and Grounds building. The patio does not have a roof on it and the inclement weather makes it difficult to maintain the equipment. It is recommended that a roof over the patio be installed and to relocate the cooling tower outside of the patio. This project includes roof framing, installing a standing seam roofing system to match the existing roof, relocating the cooling tower and installing a thermostatically-controlled intake louver in the wall to provide combustion and cooling air to the boiler. Structural calculations will be required to ensure that loads from the new roof are properly supported. | BLDG #7-BUILDINGS AND GROUNDS | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 3168 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
2962INT1 | INTERIOR FINISHES | 2962 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next three to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | BLDG #13-TOWER | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 644 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3220
2962INT2 | VCT FLOORING REPLACEMENT | 2962 | The VCT (vinyl composite tile) flooring on the observation level is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. | BLDG #13-TOWER | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 644 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5796
2962EXT1 | EXTERIOR FINISHES | 2962 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and painting of the steel posts, beams and columns, sealing and caulking of the metal panels, windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted, sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BLDG #13-TOWER | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 644 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12880
2960EXT1 | EXTERIOR FINISHES | 2960 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the masonry and caulking of the control joints, windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BLDG #10-TOILET ROOMS | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 573 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2865
2960PLM1 | WATER HEATER REPLACEMENT | 2960 | There is an on-demand propane-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new on-demand propane-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | BLDG #10-TOILET ROOMS | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 573 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
2960INT1 | INTERIOR FINISHES | 2960 | The interior finishes are in fair condition. Most of the walls are unpainted CMU which do not need to be addressed at this time. It is recommended that the painted gypsum board walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. 150 square feet of area has been used to generate this estimate. | BLDG #10-TOILET ROOMS | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 573 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 750
2959INT1 | INTERIOR FINISHES | 2959 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next three to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | BLDG #9-CLASSROOM/TOILET #1 | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 1320 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6600
2959EXT1 | EXTERIOR FINISHES | 2959 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the masonry and caulking of the control joints, windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BLDG #9-CLASSROOM/TOILET #1 | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 1320 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6600
2959PLM1 | WATER HEATER REPLACEMENT | 2959 | There is an on-demand propane-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new on-demand propane-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | BLDG #9-CLASSROOM/TOILET #1 | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 1320 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
2954INT2 | CARPET REPLACEMENT | 2954 | The carpet in the building is showing signs of extreme wear. It is recommended that the carpet be replaced with heavy duty commercial grade carpet in the next two to three years. 9,000 square feet was used to generate this estimate. | BLDG #4-STAFF RESIDENCE | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 9759 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 63000
2957EXT1 | EXTERIOR FINISHES | 2957 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the masonry and caulking of the control joints, windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BLDG #7-BUILDINGS AND GROUNDS | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 3168 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15840
2957PLM1 | WATER HEATER REPLACEMENT | 2957 | There is a 50 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | BLDG #7-BUILDINGS AND GROUNDS | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 3168 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
2957INT1 | INTERIOR FINISHES | 2957 | The interior finishes are in fair condition. Most of the walls are unpainted CMU which do not need to be addressed at this time. It is recommended that the painted gypsum board walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. 250 square feet of area has been used to generate this estimate. | BLDG #7-BUILDINGS AND GROUNDS | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 3168 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1750
2956EXT1 | EXTERIOR FINISHES | 2956 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the masonry and caulking of the control joints, metal panels, windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BLDG #6-FIRE STATION | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 9720 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 48600
2956INT1 | INTERIOR FINISHES | 2956 | The interior finishes are in fair condition. Most of the walls are unpainted CMU which do not need to be addressed at this time. It is recommended that the painted gypsum board walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. 1,118 square feet of area has been used to generate this estimate. | BLDG #6-FIRE STATION | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 9720 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5590
2956INT2 | FLOORING REPAIRS | 2956 | The sealed concrete in the building is damaged and reaching the end of its useful life. It is recommended that the concrete be sealed in order to extend its useful life. This project would provide for stripping the concrete and applying a new coat of sealant in the next two to three years. | BLDG #6-FIRE STATION | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 9720 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 48600
2956EXT2 | ROOF REPLACEMENT | 2956 | The roof on this building was in fair condition at the time of the survey. There are two roof coverings on the building, standing seam metal and Sarnafil single-ply membrane. The statewide roofing program has set the useful life of an average single-ply membrane roof at 15 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1999. It is recommended that the single-ply membrane portion of the roof be replaced by 2014 to be consistent with the roofing program and the end of the warranty period. 6,600 square feet was used to generate this estimate. | BLDG #6-FIRE STATION | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 9720 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 56550
2956PLM1 | WATER HEATER REPLACEMENT | 2956 | There are two electric water heaters in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, these units are showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that new 50 gallon and 20 gallon electric water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. | BLDG #6-FIRE STATION | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 9720 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
2955INT1 | INTERIOR FINISHES | 2955 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next three to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | BLDG #5-TURNOUT | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 11782 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 58910
2955PLM1 | WATER HEATER REPLACEMENT | 2955 | There is a 432 gallon, 1255 MBH input propane-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new propane-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | BLDG #5-TURNOUT | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 11782 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
2955EXT2 | ROOF REPLACEMENT | 2955 | The roof on this building was in fair condition at the time of the survey. There are two roof coverings on the building, standing seam metal and Sarnafil single-ply membrane. The statewide roofing program has set the useful life of an average single-ply membrane roof at 15 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1999. It is recommended that the single-ply membrane portion of the roof be replaced by 2014 to be consistent with the roofing program and the end of the warranty period. 6,600 square feet was used to generate this estimate. | BLDG #5-TURNOUT | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 11782 | 2009-11-18 | Four to Ten Years | Long-Term Needs | 3 | 99000
2958EXT1 | EXTERIOR FINISHES | 2958 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the masonry and caulking of the control joints, windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BLDG #8-CABANA/STORAGE | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 2480 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12400
3036EXT1 | EXTERIOR FINISHES | 3036 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the masonry and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | DOMESTIC WATER PUMP HOUSE | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 100 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
3037EXT1 | EXTERIOR FINISHES | 3037 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the masonry and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | WELL PUMP HOUSE | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 200 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
3037INT1 | INTERIOR FINISHES | 3037 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next three to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | WELL PUMP HOUSE | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 200 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
3036INT1 | INTERIOR FINISHES | 3036 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next three to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | DOMESTIC WATER PUMP HOUSE | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 100 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
9796SIT1 | SLURRY SEAL ASPHALT PAVING | 9796 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site wide including access roads and parking areas. Striping is included in this estimate. This project should be scheduled on a 4- 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 175,000 square feet of asphalt area was used to generate this estimate. | FIRE SCIENCE ACADEMY SITE | 9796 | Military | NNG | Fire Sci | Carlin | 1998 |  | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 131250
9796ADA1 | INSTALL ADA SIGNAGE | 9796 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. Directional and building signage from the ADA parking spaces to the entrance of the core facility buildings is missing. It is recommended that applicable signage be installed where required. The 2006 IBC, ICC/ANSI A117.1 - 2003 and the most current version of the Americans With Disabilities Act Accessible Guidelines (ADAAG) was used as a reference for this project. | FIRE SCIENCE ACADEMY SITE | 9796 | Military | NNG | Fire Sci | Carlin | 1998 |  | 2009-11-18 | Immediate to Two Years | Currently Critical | 1 | 2500
9796EXT1 | EXTERIOR FINISHES, SHADE RAMADAS | 9796 | There are 10 steel shade ramadas in different locations throughout the site which are either 600 s.f. or 1,366 s.f. for a total of 6,766 square feet. It is important to maintain the finish, weather resistance and appearance of the structures. This project would provide for painting of the structures and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structures. | FIRE SCIENCE ACADEMY SITE | 9796 | Military | NNG | Fire Sci | Carlin | 1998 |  | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 13532
3033EXT1 | EXTERIOR FINISHES | 3033 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the masonry and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SANITARY SEWER BUILDING | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 100 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
3034EXT1 | EXTERIOR FINISHES | 3034 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the masonry and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CHEMICAL STORAGE BUILDING | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 100 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
3034INT1 | INTERIOR FINISHES | 3034 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next three to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | CHEMICAL STORAGE BUILDING | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 100 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
3035EXT1 | EXTERIOR FINISHES | 3035 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the masonry and caulking of the control joints, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | FIRE WATER PUMP HOUSE | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 1220 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6100
3033INT1 | INTERIOR FINISHES | 3033 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next three to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SANITARY SEWER BUILDING | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 100 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
2043ENR1 | WINDOW REPLACEMENT | 2043 | The windows are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 6 units. Removal and disposal of the existing windows is included in this estimate. | STORAGE BUILDING 2 | 9919 | Military | NNG |  | Reno | 1965 | 2611 | 2010-07-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
2043SFT1 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 2043 | There is no emergency egress lighting in the building and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2006 Chapter 10 was referenced for this project. | STORAGE BUILDING 2 | 9919 | Military | NNG |  | Reno | 1965 | 2611 | 2010-07-08 | Immediate to Two Years | Currently Critical | 1 | 1000
2042ENR1 | REPLACE OVERHEAD COILING DOOR | 2042 | The existing overhead coiling door in the drill hall is damaged and is not insulated resulting in increased energy usage. This project would provide for installation of a new power operated insulated overhead coiling door. Removal of the existing door is included in this estimate. A 14'x12' door was used for this estimate. | PLUMB LANE READINESS CENTER | 9919 | Military | NNG |  | Reno | 1965 | 11457 | 2010-07-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
2044EXT2 | EXTERIOR DOOR REPLACEMENT | 2044 | The exterior metal doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the three double door assemblies with new metal doors, frames, and hardware. Removal and disposal of the existing doors is included in this estimate. | STORAGE BUILDING 1 | 9919 | Military | NNG |  | Reno | 1980 | 405 | 2010-07-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
2043SFT3 | FIRE ALARM SYSTEM INSTALLATION | 2043 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2006 Section 7 and the 2006 International Fire Code. | STORAGE BUILDING 2 | 9919 | Military | NNG |  | Reno | 1965 | 2611 | 2010-07-08 | Immediate to Two Years | Currently Critical | 1 | 10444
2042EXT2 | EXTERIOR FINISHES | 2042 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the masonry, priming and painting the stucco, and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Also included is the repairing of the concrete roof deck overhang at the damaged areas. | PLUMB LANE READINESS CENTER | 9919 | Military | NNG |  | Reno | 1965 | 11457 | 2010-07-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 57285
2042ADA6 | ADA UNISEX RESTROOM UPGRADE | 2042 | The designated unisex ADA accessible restroom is not fully compliant. There is no pipe protection, the toilet paper dispenser is not in the correct location, and it is missing a grab bar. A partial retrofit is necessary. This project would provide funding to bring the restroom into full ADA compliance. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) was used as a reference for this project. | PLUMB LANE READINESS CENTER | 9919 | Military | NNG |  | Reno | 1965 | 11457 | 2010-07-08 | Immediate to Two Years | Currently Critical | 1 | 2000
2042PLM1 | REMODEL RESTROOMS | 2042 | The existing Men's and Women's restrooms are original to building and are in need of upgrades. This project would provide for the remodeling of both restrooms including but not limited to new toilets, shower modifications, sinks, fixtures, hardware, and floor and wall finishes. It is also recommended that these restrooms become ADA accessible but there already is a unisex ADA restroom present in the building which would provide minimum ADA restroom facilities after the proposed project for upgrading that restroom is complete. This cost estimate does not include an ADA upgrade which may increase the construction cost. | PLUMB LANE READINESS CENTER | 9919 | Military | NNG |  | Reno | 1965 | 11457 | 2010-07-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
2042SFT4 | EXTERIOR LANDING MODIFICATION | 2042 | The entrance on the south side of the building does not have a proper exterior landing, stairway, and is missing handrails as required by the 2006 IBC, Chapter 10, Section 1008, 1009 and 1012. Also the exit door from the drill hall area swings out over a step. This project would provide for the reworking of the exterior landing and steps to provide a proper landing and stairs including handrails at the south entrance, and adding a new concrete landing at the drill hall exit door. | PLUMB LANE READINESS CENTER | 9919 | Military | NNG |  | Reno | 1965 | 11457 | 2010-07-08 | Immediate to Two Years | Currently Critical | 1 | 3500
2042SFT3 | FIRE ALARM SYSTEM INSTALLATION | 2042 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2006 Section 7 and the 2006 International Fire Code. | PLUMB LANE READINESS CENTER | 9919 | Military | NNG |  | Reno | 1965 | 11457 | 2010-07-08 | Immediate to Two Years | Currently Critical | 1 | 45828
2042SFT2 | FIRE SUPPRESSION SYSTEM INSTALLATION | 2042 | The building is a B occupancy per the 2006 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. | PLUMB LANE READINESS CENTER | 9919 | Military | NNG |  | Reno | 1965 | 11457 | 2010-07-08 | Immediate to Two Years | Currently Critical | 1 | 80199
2044EXT1 | EXTERIOR FINISHES | 2044 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and painting the concrete masonry and caulking of the flashing, fixtures, and all other penetrations. It is recommended that the building be painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | STORAGE BUILDING 1 | 9919 | Military | NNG |  | Reno | 1980 | 405 | 2010-07-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2025
2042INT2 | INTERIOR FINISHES | 2042 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 08/27/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/08/2010. | PLUMB LANE READINESS CENTER | 9919 | Military | NNG |  | Reno | 1965 | 11457 | 2010-07-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 57285
2042ADA4 | ADA SIGNAGE | 2042 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) was used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 08/27/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/08/2010. | PLUMB LANE READINESS CENTER | 9919 | Military | NNG |  | Reno | 1965 | 11457 | 2010-07-08 | Immediate to Two Years | Currently Critical | 1 | 3000
2042INT1 | REPLACE CARPETING | 2042 | The carpet in the facility is worn from age and normal use and is in need of replacement. This project would provide for the installation of about 2,000 square feet of commercial grade carpet. Removal and disposal of the old carpet is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 08/27/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/08/2010. | PLUMB LANE READINESS CENTER | 9919 | Military | NNG |  | Reno | 1965 | 11457 | 2010-07-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
2043EXT1 | EXTERIOR FINISHES | 2043 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry, painting the stucco eaves, and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | STORAGE BUILDING 2 | 9919 | Military | NNG |  | Reno | 1965 | 2611 | 2010-07-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 13055
2042ADA7 | ADA DOOR UPGRADE | 2042 | The exterior entrance door on the east side of the building is on an accessible path of travel. It has a power door opener installed on it which has been disabled for security reasons. Without the power door opener, the entrance is not accessible. This project would provide for replacement of the doors to provide an accessible entrance including new ADA compliant door hardware, threshold, signage and space requirements. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) was used as a reference for this project. The other option would be to activate the power door opener which must open both door leaves along with signage identifying ADA access which may cost less than door replacement. | PLUMB LANE READINESS CENTER | 9919 | Military | NNG |  | Reno | 1965 | 11457 | 2010-07-08 | Immediate to Two Years | Currently Critical | 1 | 5000
9919ADA2 | ADA RAMP UPGRADE | 9919 | This facility has an ADA accessible ramp on the east side of the Readiness Center. This ramp is on the accessible path of travel from the accessible parking spaces to the Readiness Center. The ramp does not have proper landings, the handrails are not compliant, and it is missing edge protection. This project would provide for an upgrade to the ramp to make it fully ADA compliant. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) was used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 08/27/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/08/2010. | PLUMB LANE READINESS CENTER SITE | 9919 | Military | NNG |  | Reno | 1965 |  | 2010-07-08 | Immediate to Two Years | Currently Critical | 1 | 25000
9919SIT3 | SIDEWALK REPLACEMENT | 9919 | The sidewalks serving the building are deteriorated and failing. In some areas, settling has caused changes in elevation in excess of 1/2" and there are cracks in many locations. This project addresses removal and replacement of existing sidewalks and the concrete patio in the rear of the building. 2,500 SF of 4" thick concrete sidewalk was used for this estimate. | PLUMB LANE READINESS CENTER SITE | 9919 | Military | NNG |  | Reno | 1965 |  | 2010-07-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
9919SIT2 | SLURRY SEAL ASPHALT PAVING | 9919 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site-wide including access roads and parking areas. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 102,500 square feet of asphalt area was used to generate this estimate. | PLUMB LANE READINESS CENTER SITE | 9919 | Military | NNG |  | Reno | 1965 |  | 2010-07-08 | Four to Ten Years | Long-Term Needs | 3 | 76875
3087EXT1 | EXTERIOR FINISHES | 3087 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | STORAGE BUILDING | 9885 | Military | NNG |  | Fallon | 0 | 960 | 2012-01-19 | Four to Ten Years | Long-Term Needs | 3 | 960
9885SEC1 | CHAIN LINK FENCE UPGRADE | 9885 | The existing chain link fencing around the site has reached the end of its expected life and is due for an upgrade. It currently does not have a deterrent device such as barbed wire and the swinging vehicle gates require constant maintenance. This project recommends the installation of a 6 foot high 6 gauge wire perimeter chain link fence around the entire site with barbed wire and two 14' wide sliding gates with hardware. The cost estimate also includes demolition and disposal of the existing fence. This project or a portion thereof was previously recommended in the FCA report dated 07/21/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/19/2012. | FALLON ARMORY SITE | 9885 | Military | NNG |  | Fallon | 1962 |  | 2012-01-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 65500
9885SIT1 | SLURRY SEAL ASPHALT PAVING | 9885 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site wide including access roads, parking areas and the maintenance yard. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 45,000 square feet of asphalt area was used to generate this estimate. | FALLON ARMORY SITE | 9885 | Military | NNG |  | Fallon | 1962 |  | 2012-01-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 33750
0678CUL1 | CULINARY FIXTURES REPLACEMENT | 0678 | The existing plumbing fixtures in the culinary are worn and damaged and should be scheduled for replacement. Corrosion and mineral buildup has caused premature deterioration of the fixtures. This project recommends the replacement of the existing fixtures including the sprayers, faucets, handles, valves, filters, injectors and any other piping or equipment which has deteriorated or has signs of corrosion or mineral buildup. This project should be implemented concurrently with the WATER TREATMENT SYSTEM REPLACEMENT project. | FALLON ARMORY | 9885 | Military | NNG |  | Fallon | 1962 | 10404 | 2012-01-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
0678INT3 | JANITORS CLOSET REPAIRS | 0678 | The mop sink in the Janitors Closet is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | FALLON ARMORY | 9885 | Military | NNG |  | Fallon | 1962 | 10404 | 2012-01-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
0678PLM2 | WATER HEATER REPLACEMENT | 0678 | There are two large gas-fired water heaters in the building. One unit was installed in 1993 and the other in 1999. The average life span of a water heater is eight to ten years. With the passage of time and lack of water treatment, these units are showing signs of wear and should be scheduled for replacement in the next 3-4 years. Due to the inconsistent usage of the facility, it is recommended to replace these units with an on demand water heating system to reduce energy costs. Removal and disposal of the existing equipment is included in this estimate. | FALLON ARMORY | 9885 | Military | NNG |  | Fallon | 1962 | 10404 | 2012-01-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
0678EXT1 | EXTERIOR FINISHES | 0678 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | FALLON ARMORY | 9885 | Military | NNG |  | Fallon | 1962 | 10404 | 2012-01-19 | Four to Ten Years | Long-Term Needs | 3 | 52020
0678ELE2 | EXTERIOR OUTLET REPLACEMENT | 0678 | There is an electrical outlet on the south side exterior of the building that does not meet code. This outlet should be changed to a GFCI type outlet per the 2005 NEC. This project would provide for the purchase and installation of one GFCI duplex outlet with a weatherproof cover. | FALLON ARMORY | 9885 | Military | NNG |  | Fallon | 1962 | 10404 | 2012-01-19 | Immediate to Two Years | Currently Critical | 1 | 300
0678ADA1 | ADA SIGNAGE | 0678 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | FALLON ARMORY | 9885 | Military | NNG |  | Fallon | 1962 | 10404 | 2012-01-19 | Immediate to Two Years | Currently Critical | 1 | 750
0678PLM1 | WATER TREATMENT SYSTEM REPLACEMENT | 0678 | The existing water softening/ treatment systems in the building are currently not operational. They have not been maintained and have reached the end of their lifecycles. Failure of the equipment causes wear and tear on the domestic water supply lines, plumbing fixtures and HVAC equipment. This project would provide for the replacement of the existing water softeners/ treatment systems with new equipment. This project would also provide for a chemical treatment program including an updated chemicals control system, service and employee training provided by a qualified water treatment vendor. The annual maintenance fee charged by the water treatment vendor would be determined after an investigation of the water system is complete. These annual costs are not included in this project cost. For budgeting purposes, a $12,000 fee is suggested. This project should be implemented concurrently with the CULINARY FIXTURES REPLACEMENT project. | FALLON ARMORY | 9885 | Military | NNG |  | Fallon | 1962 | 10404 | 2012-01-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0678INT4 | INTERIOR FINISHES | 0678 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | FALLON ARMORY | 9885 | Military | NNG |  | Fallon | 1962 | 10404 | 2012-01-19 | Four to Ten Years | Long-Term Needs | 3 | 52020
0678SFT1 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0678 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 07/21/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/19/2012. | FALLON ARMORY | 9885 | Military | NNG |  | Fallon | 1962 | 10404 | 2012-01-19 | Immediate to Two Years | Currently Critical | 1 | 4000
0996INT1 | INTERIOR FINISHES | 0996 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings in the office areas be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | OMS #2 | 9886 | Military | NNG |  | Yerington | 1995 | 4400 | 2012-01-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
0996EXT3 | EXTERIOR DOOR REPLACEMENT | 0996 | The exterior metal man door on the north side of the building is damaged from age and general wear and tear and has reached the end of its expected life. The threshold and door sweep have deteriorated and allow water to flow under the door. This project would provide for the replacement of the door assembly with a new metal door, frame, hardware, threshold and door sweep to ensure that water cannot get under the door. Removal and disposal of the existing door is included in this estimate. | OMS #2 | 9886 | Military | NNG |  | Yerington | 1995 | 4400 | 2012-01-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0996INT2 | VCT FLOORING REPLACEMENT | 0996 | The VCT (vinyl composite tile) flooring in the office side of the building is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. | OMS #2 | 9886 | Military | NNG |  | Yerington | 1995 | 4400 | 2012-01-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14000
0996EXT4 | GUTTER INSTALLATION | 0996 | The building does not have gutters or downspouts to control the runoff from the roof. The water currently sheet drains off the roof causing extensive erosion to the dirt grade around the foundation. This will eventually lead to failure of the foundation undermining the integrity of the entire structure. This project would provide funding for the installation of a seamless gutter and downspout system for the standing seam metal roof over the shop. Drywells are included at downspout locations. Another option would be to install a gravel filled infiltration trench at drip edges to help mitigate erosion. Costs may vary depending which system is used. | OMS #2 | 9886 | Military | NNG |  | Yerington | 1995 | 4400 | 2012-01-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3500
0996ADA1 | ADA RESTROOM UPGRADES | 0996 | The ADA restrooms in the building do not entirely meet the Americans with Disabilities Act (ADA) requirements. It is necessary to make some specific upgrades to the restrooms to comply with the requirements. This project would provide funding for moving the water closet handle in the Men's restroom, moving the toilet paper dispensers, replacing the faucet handles and any other necessary upgrades to bring the restrooms into compliance. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | OMS #2 | 9886 | Military | NNG |  | Yerington | 1995 | 4400 | 2012-01-26 | Immediate to Two Years | Currently Critical | 1 | 1500
0996EXT1 | EXTERIOR FINISHES | 0996 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | OMS #2 | 9886 | Military | NNG |  | Yerington | 1995 | 4400 | 2012-01-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 22000
0996SFT2 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0996 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 07/21/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/26/2012. | OMS #2 | 9886 | Military | NNG |  | Yerington | 1995 | 4400 | 2012-01-26 | Immediate to Two Years | Currently Critical | 1 | 4000
0996EXT2 | OVERHEAD DOOR REPLACEMENT | 0996 | There are two 16'x14' motorized overhead coiling doors which are damaged and do not function properly. Staff noted that the doors bind and get stuck when rolling up and down and have been serviced many times. They are original to the building, dating back to 1995 and should be scheduled for replacement. This project would provide for the removal and disposal of the motorized overhead coiling doors and replacement with two new motorized doors. | OMS #2 | 9886 | Military | NNG |  | Yerington | 1995 | 4400 | 2012-01-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16000
0996ADA2 | ADA EMPLOYEE LOUNGE UPGRADES | 0996 | The employee lounge does not meet the Americans with Disabilities Act (ADA) requirements. It is recommended to upgrade some of the features of the room for compliance with accessibility standards for employees. This project would provide funding for construction of an accessible sink and faucet, an accessible space at the dining table and an accessible path of travel throughout the room. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | OMS #2 | 9886 | Military | NNG |  | Yerington | 1995 | 4400 | 2012-01-26 | Immediate to Two Years | Currently Critical | 1 | 2000
0996SFT3 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0996 | Approximately half of the building is a B occupancy per the 2006 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 or R-2 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system throughout the entire building and backflow prevention in the event the building is remodeled or an addition is undertaken. | OMS #2 | 9886 | Military | NNG |  | Yerington | 1995 | 4400 | 2012-01-26 | Immediate to Two Years | Currently Critical | 1 | 61600
0996SFT4 | FIRE ALARM SYSTEM INSTALLATION | 0996 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2006 Section 7 and the 2006 International Fire Code. | OMS #2 | 9886 | Military | NNG |  | Yerington | 1995 | 4400 | 2012-01-26 | Immediate to Two Years | Currently Critical | 1 | 17600
0996SFT5 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0996 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2006 Chapter 10 was referenced for this project. | OMS #2 | 9886 | Military | NNG |  | Yerington | 1995 | 4400 | 2012-01-26 | Immediate to Two Years | Currently Critical | 1 | 2200
2058ENR1 | LIGHTING UPGRADE | 2058 | The existing lighting fixtures are the older T-12 fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested as well as an occupancy sensor. Any electrical wiring upgrades are not included in this estimate. | TIRE REPAIR/STORAGE BUILDING | 9886 | Military | NNG |  | Yerington | 1995 | 480 | 2012-01-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 720
2527EXT1 | EXTERIOR FINISHES | 2527 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MCOFF RAMADA | 9886 | Military | NNG |  | Yerington | 0 | 800 | 2012-01-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1600
2528EXT1 | EXTERIOR FINISHES | 2528 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HAZARDOUS MATERIAL STORAGE BUILDING 2 | 9886 | Military | NNG |  | Yerington | 1959 | 252 | 2012-01-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1260
2057EXT1 | EXTERIOR FINISHES | 2057 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HAZARDOUS WASTE STORAGE BUILDING 1 | 9886 | Military | NNG |  | Yerington | 1990 | 252 | 2012-01-26 | Four to Ten Years | Long-Term Needs | 3 | 252
2058SFT1 | EGRESS LIGHTING INSTALLATION | 2058 | There is no emergency egress lighting in the building. Section 1006 of the 2006 IFC states that illumination is required for the means of egress at all times the building space is occupied. This project would provide for the purchase and installation of emergency egress lighting with battery backup in accordance with requirements stated in the code. This project or a portion thereof was previously recommended in the FCA report dated 07/21/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/26/2012. | TIRE REPAIR/STORAGE BUILDING | 9886 | Military | NNG |  | Yerington | 1995 | 480 | 2012-01-26 | Immediate to Two Years | Currently Critical | 1 | 450
2058EXT1 | EXTERIOR FINISHES | 2058 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | TIRE REPAIR/STORAGE BUILDING | 9886 | Military | NNG |  | Yerington | 1995 | 480 | 2012-01-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 480
9886ELE1 | ELECTRICAL REPAIRS | 9886 | The main site electrical equipment is in disrepair and should be scheduled for replacement. Much of the equipment is original to the site dating back more than 50 years, including the transformers and main switchgear. Insects and rodents have infested some exterior boxes due to missing cover plates and the in-ground electrical boxes are missing proper covers and do not drain water effectively. There are also numerous loose and/or exposed electrical wires and damaged electrical outlets, disconnects, switches and wrong identifying covers for electrical pull boxes. This project would provide for replacement of the main electrical switchgear, transformers, in-ground boxes, trenching and backfill, repairs to the damaged electrical outlets, disconnects, new pull box cover lids with the proper identification indicated, and termination of loose or exposed electrical wires. This project or a portion thereof was previously recommended in the FCA report dated 07/21/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/26/2012. | YERINGTON ARMORY SITE | 9886 | Military | NNG |  | Yerington | 1959 |  | 2012-01-26 | Immediate to Two Years | Currently Critical | 1 | 150000
9886SIT4 | ASPHALT PAVING INSTALLATION | 9886 | The majority of the site is covered with dirt and has poor drainage. Other than the front parking lot there is no asphalt paving for vehicle and equipment circulation throughout the yard. Due to the large and heavy equipment commonly on site, the dirt and mud areas quickly become rutted and uneven. Poor drainage in the dirt areas also leaves large areas of standing water further exacerbating the problem. This project would provide asphalt cement paving to cover the majority of the site that is used for vehicle or equipment, circulation or storage. The estimate includes grading, base, compaction and installation of asphalt cement paving. If asphalt is not provided, it is recommended to regrade the site to ensure proper drainage. | YERINGTON ARMORY SITE | 9886 | Military | NNG |  | Yerington | 1959 |  | 2012-01-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 250000
9886SIT5 | LANDSCAPE UPGRADES | 9886 | The landscaping currently consists of shrubs and trees around the buildings which are difficult to maintain. The planting areas are overgrown and leaves and debris have built up over time. Maintenance personnel is understaffed and it is recommended to install less maintenance intensive landscape features. This project would provide for removing most of the shrubs and trees, altering the irrigation as needed and installing more landscape rock for coverage. | YERINGTON ARMORY SITE | 9886 | Military | NNG |  | Yerington | 1959 |  | 2012-01-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
9886SIT3 | SLURRY SEAL ASPHALT PAVING | 9886 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site wide including access roads and the parking lot. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 55,000 square feet of asphalt area was used to generate this estimate. | YERINGTON ARMORY SITE | 9886 | Military | NNG |  | Yerington | 1959 |  | 2012-01-26 | Four to Ten Years | Long-Term Needs | 3 | 41250
0692EXT2 | EXTERIOR FINISHES | 0692 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | OLD OMS - WEIGHT ROOM | 9886 | Military | NNG |  | Yerington | 1959 | 1640 | 2012-01-26 | Four to Ten Years | Long-Term Needs | 3 | 8200
0691INT1 | INTERIOR FINISHES | 0691 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | YERINGTON ARMORY | 9886 | Military | NNG |  | Yerington | 1959 | 10404 | 2012-01-26 | Four to Ten Years | Long-Term Needs | 3 | 52020
0691EXT1 | EXTERIOR FINISHES | 0691 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | YERINGTON ARMORY | 9886 | Military | NNG |  | Yerington | 1959 | 10404 | 2012-01-26 | Four to Ten Years | Long-Term Needs | 3 | 52020
0692INT1 | INTERIOR FINISHES | 0692 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | OLD OMS - WEIGHT ROOM | 9886 | Military | NNG |  | Yerington | 1959 | 1640 | 2012-01-26 | Four to Ten Years | Long-Term Needs | 3 | 8200
0691ENR1 | WINDOW REPLACEMENT | 0691 | The windows in the Drill Hall are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 20 units. Removal and disposal of the existing windows is included in this estimate. | YERINGTON ARMORY | 9886 | Military | NNG |  | Yerington | 1959 | 10404 | 2012-01-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
0691SFT3 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0691 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 07/21/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/26/2012. | YERINGTON ARMORY | 9886 | Military | NNG |  | Yerington | 1959 | 10404 | 2012-01-26 | Immediate to Two Years | Currently Critical | 1 | 4000
0691ENV1 | VCT FLOORING REPLACEMENT | 0691 | The VCT (vinyl composite tile) flooring in the building is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. There is asbestos containing material (ACM) in the mastic and tiles so additional costs for abatement and disposal have been added to the estimate. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. | YERINGTON ARMORY | 9886 | Military | NNG |  | Yerington | 1959 | 10404 | 2012-01-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 40000
0691INT2 | JANITORS CLOSET REPAIRS | 0691 | The mop sink in the Janitors Closet is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | YERINGTON ARMORY | 9886 | Military | NNG |  | Yerington | 1959 | 10404 | 2012-01-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
0691ENR2 | LIGHTING UPGRADE | 0691 | The existing high bay lighting fixtures in the Drill Hall are the older metal halide type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle such as LED fixtures. Any electrical wiring upgrades are not included in this estimate. | YERINGTON ARMORY | 9886 | Military | NNG |  | Yerington | 1959 | 10404 | 2012-01-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0691ENR3 | HVAC REPLACEMENT | 0691 | Two of the four HVAC roof top units are 15 years old and the other two are 10 years old. They are not energy efficient and have reached or will soon reach the end of their expected and useful life. This project would provide for installation of new HVAC packaged units, cleaning of the existing duct work and grilles and a water treatment system for the supply water. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | YERINGTON ARMORY | 9886 | Military | NNG |  | Yerington | 1959 | 10404 | 2012-01-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 156060
2705INT2 | RESTROOM FIXTURE REPLACEMENT | 2705 | It was observed on the date of inspection May 13, 2015 that the mirror is showing moisture infiltration and signs of deterioration. The sink is losing its enamel. The existing restroom fixtures are original to the building. The mirror and sink are worn and damaged and should be scheduled for replacement within 2-3 years. This project recommends the replacement of the existing mirror and sink. | LAS VEGAS READINESS CENTER | 9842 | Military | NNG |  | Las Vegas | 2007 | 78774 | 2015-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
2705HVA1 | BOILER INSPECTION | 2705 | The building has two boiler systems that have not been inspected. Per NAC 455C.150 Inspection for operating permit; Internal inspection: an inspection for an operating permit must be an internal inspection if required by the Enforcement Section. NAC 455C.156 Frequency and scope of inspections; authority to require preparation for inspection; authorization to change interval between inspections (4): a lined potable water heater must have an external inspection at least once every 2 years. It is recommended to have all boiler systems inspected per NAC 455. | LAS VEGAS READINESS CENTER | 9842 | Military | NNG |  | Las Vegas | 2007 | 78774 | 2015-05-13 | Immediate to Two Years | Currently Critical | 1 | 1000
2705SFT0 | STORAGE REMOVAL | 2705 | Items in this building are stored too close to the ceiling. The 2012 IFC Section 315.3.1 states that, "Storage shall be maintained 2 feet or more below the ceiling in nonsprinklered areas of buildings or a minimum of 18 inches below sprinkler head deflectors in sprinklered areas of buildings." This project would provide for the removal of all items in conflict with code requirements to ensure that the fire suppression system operates correctly. | LAS VEGAS READINESS CENTER | 9842 | Military | NNG |  | Las Vegas | 2007 | 78774 | 2015-05-13 | Immediate to Two Years | Currently Critical | 1 | 1000
2705PLM4 | WATER HEATER REPLACEMENT | 2705 | There is a 100 gallon natural gas-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 1-2 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | LAS VEGAS READINESS CENTER | 9842 | Military | NNG |  | Las Vegas | 2007 | 78774 | 2015-05-13 | Immediate to Two Years | Currently Critical | 1 | 5000
2705INT1 | INTERIOR FINISHES | 2705 | The interior finishes are in good condition. It is recommended to paint the interior walls and ceilings at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | LAS VEGAS READINESS CENTER | 9842 | Military | NNG |  | Las Vegas | 2007 | 78774 | 2015-05-13 | Four to Ten Years | Long-Term Needs | 3 | 787740
2705EXT2 | EXTERIOR FINISHES | 2705 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | LAS VEGAS READINESS CENTER | 9842 | Military | NNG |  | Las Vegas | 2007 | 78774 | 2015-05-13 | Four to Ten Years | Long-Term Needs | 3 | 787740
3218EXT1 | EXTERIOR FINISHES | 3218 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HAZMAT BUILDING | 9842 | Military | NNG |  | Las Vegas | 2013 | 960 | 2015-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9600
3111EXT1 | EXTERIOR FINISHES | 3111 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 8-9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MILITARY STORAGE BUILDING | 9842 | Military | NNG |  | Las Vegas | 2008 | 11200 | 2015-05-13 | Four to Ten Years | Long-Term Needs | 3 | 22400
3217INT1 | FLOORING MAINTENANCE | 3217 | It is important to maintain the interior finish of the concrete floor. It is recommended that the concrete be stripped and re-sealed in order to extend its useful life. This project would provide for stripping the concrete and applying an Epoxy concrete paint in the next 5-6 years. | FIELD MAINTENANCE SHOP (FMS #7) | 9842 | Military | NNG |  | Las Vegas | 2013 | 40213 | 2015-05-13 | Four to Ten Years | Long-Term Needs | 3 | 261384
3217INT2 | INTERIOR FINISHES | 3217 | The interior finishes are in good condition. It is recommended to paint the interior walls and ceilings at least once in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | FIELD MAINTENANCE SHOP (FMS #7) | 9842 | Military | NNG |  | Las Vegas | 2013 | 40213 | 2015-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 402130
3640EXT1 | EXTERIOR FINISHES | 3640 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding for the painting of the steel structure. Included in the cost is painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 6-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MV PARKING STRUCTURE - SOUTH | 9842 | Military | NNG |  | Las Vegas | 2013 | 9075 | 2015-05-13 | Four to Ten Years | Long-Term Needs | 3 | 18150
3219EXT1 | EXTERIOR FINISHES | 3219 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding for the painting of the steel structure. Included in the cost is painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 6-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MV PARKING STRUCTURE - NORTH | 9842 | Military | NNG |  | Las Vegas | 2013 | 8250 | 2015-05-13 | Four to Ten Years | Long-Term Needs | 3 | 18150
9842SIT1 | CRACK FILL & SEAL ASPHALT PAVING | 9842 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the paving site wide including access roads and parking areas. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 245,100 square feet of asphalt area was used to generate this estimate. | ANTHONY COMETA COMPLEX SITE | 9842 | Military | NNG |  | Las Vegas | 2007 |  | 2015-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 245100
3217SFT2 | STORAGE REMOVAL | 3217 | Per IFC 2012 315.3.3 combustible material shall not be stored in boiler rooms, mechanical rooms or electrical equipment rooms. It is recommended that all combustible materials be removed from boiler rooms, mechanical rooms or electrical equipment rooms within 1 year. | FIELD MAINTENANCE SHOP (FMS #7) | 9842 | Military | NNG |  | Las Vegas | 2013 | 40213 | 2015-05-13 | Immediate to Two Years | Currently Critical | 1 | 1000
3217EXT2 | EXTERIOR FINISHES | 3217 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the expansion joints, windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | FIELD MAINTENANCE SHOP (FMS #7) | 9842 | Military | NNG |  | Las Vegas | 2013 | 40213 | 2015-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 402130
1490EXT1 | EXTERIOR FINISHES | 1490 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking, sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 11/08/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/23/2016. | STORAGE BUILDING | 9937 | Military | NNG |  | Elko | 1992 | 2160 | 2016-08-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4320
1490SFT2 | EXTERIOR LANDING INSTALLATION | 1490 | There are two out-swinging exterior doors on the building, which swing out over a step that does not have a landing. This does not comply with 2012 IBC Section 1008.1, which requires a proper landing and for the landing to not be more than 1/2" below the threshold. This project would provide for the installation of compliant landings. | STORAGE BUILDING | 9937 | Military | NNG |  | Elko | 1992 | 2160 | 2016-08-23 | Immediate to Two Years | Currently Critical | 1 | 5000
1490ELE2 | LIGHTING UPGRADE | 1490 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 08/19/2002 and 11/08/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/23/2016. | STORAGE BUILDING | 9937 | Military | NNG |  | Elko | 1992 | 2160 | 2016-08-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 17280
9937ADA1 | ADA ACCESSIBLE PATH OF TRAVEL | 9937 | The ADA provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the office are necessary to comply with ADA accessibility requirements. This project would provide for a concrete van accessible ADA parking and loading space and concrete walkway to the existing sidewalk. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. 750 square feet of concrete was used for this estimate. It is recommended that this project coincide with the paving project. This project or a portion thereof was previously recommended in the FCA report dated 11/08/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/23/2016. | ELKO ARMORY SITE | 9937 | Military | NNG |  | Elko |  |  | 2016-08-23 | Immediate to Two Years | Currently Critical | 1 | 30000
9937SIT2 | SLURRY SEAL ASPHALT PAVING | 9937 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site wide. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 72,716 square feet of asphalt area was used to generate this estimate. This project or a portion thereof was previously recommended in the FCA report dated 11/08/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/23/2016. | ELKO ARMORY SITE | 9937 | Military | NNG |  | Elko |  |  | 2016-08-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 90895
9937SEC1 | EXTERIOR LIGHTING | 9937 | The Elko NNG site has minimal site lighting, which affects the ability to mobilize during hours of darkness and has security implications. This project would provide funding for the purchase and installation of ten LED light fixtures, 30 foot tall light poles including 30" diameter raised concrete bases, electrical trenching, conduit, wiring and connections to existing utilities. This project or a portion thereof was previously recommended in the FCA report dated 08/19/2002 and 11/08/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/23/2016. | ELKO ARMORY SITE | 9937 | Military | NNG |  | Elko |  |  | 2016-08-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 80000
0674ADA1 | ADA SIDEWALK REPLACEMENT | 0674 | The concrete sidewalks around the building are in need of replacement. The sidewalks have cracks and are spalling. This project would provide for the removal and replacement of the concrete sidewalks. 1500 SF of 4" thick concrete was used for this estimate. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | ARMORY | 9937 | Military | NNG |  | Elko | 1961 | 10404 | 2016-08-23 | Immediate to Two Years | Currently Critical | 1 | 22500
0674HVA1 | MECHANICAL ROOM HEATER INSTALLATION | 0674 | The mechanical room does not have any heating or automatic louvers. The extreme weather has caused the pipes to freeze and burst in the past and resulted in portions of the plumbing system to be shut down. This project would provide for the room to be fitted with a natural gas fired unit heater as well as automatic wall mounted louvers to regulate the temperature in the room. This project or a portion thereof was previously recommended in the FCA report dated 11/08/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/23/2016. | ARMORY | 9937 | Military | NNG |  | Elko | 1961 | 10404 | 2016-08-23 | Immediate to Two Years | Currently Critical | 1 | 5000
0677SFT1 | BATTERY STORAGE | 0677 | Section 608 of the 2012 IFC explains the requirements for stationary storage of battery systems. This project will provide funding for the proper way to store, charge and/or use batteries indoors. IFC Section 608 states batteries shall have safety caps, spill control and neutralization, mechanical ventilation and/or cabinet ventilation, supervision over the mechanical ventilation, building or cabinet signage, seismically braced, and a smoke alarm. This project would provide funding for the requirement of Section 608 of the 2012 IFC. | HAZARDOUS WASTE STORAGE #1 | 9937 | Military | NNG |  | Elko | 1990 | 252 | 2016-08-23 | Immediate to Two Years | Currently Critical | 1 | 25000
0674EXT1 | EXTERIOR FINISHES | 0674 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 11/08/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/23/2016. | ARMORY | 9937 | Military | NNG |  | Elko | 1961 | 10404 | 2016-08-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 104040
0674PLM1 | WATER HEATER REPLACEMENT | 0674 | The average life span of a water heater is eight to ten years. The existing 250 gallon gas water heater in the building has reached the end of its expected life and is not energy efficient. This project would provide for the removal and disposal of the old water heater and installation of a new 250 gallon gas water heater. This project or a portion thereof was previously recommended in the FCA report dated 11/08/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/23/2016. | ARMORY | 9937 | Military | NNG |  | Elko | 1961 | 10404 | 2016-08-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
0674SFT2 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0674 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel brace. This project or a portion thereof was previously recommended in the FCA report dated 11/08/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/23/2016. | ARMORY | 9937 | Military | NNG |  | Elko | 1961 | 10404 | 2016-08-23 | Immediate to Two Years | Currently Critical | 1 | 4000
0674EXT3 | WINDOW REPLACEMENT | 0674 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 20 units. Removal and disposal of the existing windows is included in this estimate. | ARMORY | 9937 | Military | NNG |  | Elko | 1961 | 10404 | 2016-08-23 | Four to Ten Years | Long-Term Needs | 3 | 30000
0674INT3 | VCT REPLACEMENT | 0674 | The VCT flooring in the building is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. This project or a portion thereof was previously recommended in the FCA report dated 11/08/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/23/2016. | ARMORY | 9937 | Military | NNG |  | Elko | 1961 | 10404 | 2016-08-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 58500
0674HVA2 | HVAC EQUIPMENT REPLACEMENT | 0674 | The five HVAC roof top units were installed in 2006. They are not energy efficient and will soon reach the end of their expected and useful life. This project would provide for installation of five new HVAC packaged units and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing equipment and all required connections to utilities. | ARMORY | 9937 | Military | NNG |  | Elko | 1961 | 10404 | 2016-08-23 | Four to Ten Years | Long-Term Needs | 3 | 75000
0674EXT2 | ROOF REPLACEMENT | 0674 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1997. It is recommended that this building be re-roofed in the next 1-2 years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 11/08/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/23/2016. | ARMORY | 9937 | Military | NNG |  | Elko | 1961 | 10404 | 2016-08-23 | Immediate to Two Years | Currently Critical | 1 | 124848
0674CUL1 | DISHWASHER REPLACEMENT | 0674 | The commercial dishwasher in the kitchen appears to be original to the building and is troublesome and problematic to operate. Considering the age of the dishwasher and the evolving needs of the facility it is recommended to be replaced. This project provides for removal and disposal of the existing dishwasher and replacement with new unit. | ARMORY | 9937 | Military | NNG |  | Elko | 1961 | 10404 | 2016-08-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
0677EXT1 | EXTERIOR FINISHES | 0677 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking, sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 11/08/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/23/2016. | HAZARDOUS WASTE STORAGE #1 | 9937 | Military | NNG |  | Elko | 1990 | 252 | 2016-08-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 504
0677SFT3 | SAFETY CABINETS | 0677 | The building contains many different paints, stains, gasoline, herbicides, pesticides and other hazardous products located on open shelves and on the floor. This does not meet OSHA standards or IFC for hazardous materials containment. This project would provide a self-closing hazardous storage container in the building and install placards on the building exterior in accordance with OSHA 1910.106 (d) and IFC Chapter 57 Section 5704.3.2.1.3. | HAZARDOUS WASTE STORAGE #1 | 9937 | Military | NNG |  | Elko | 1990 | 252 | 2016-08-23 | Immediate to Two Years | Currently Critical | 1 | 5000
0677SFT2 | HAZARDOUS MATERIALS STORAGE | 0677 | The Hazardous Waste Storage #1 building contains hazardous materials (i.e. gasoline, herbicides and pesticides). Per IFC 2012 Hazardous Materials, and in accordance with NFPA; where hazardous materials are stored, dispensed or used, Section 5003 states the proper use and application is to have mechanical exhaust and ventilation, and hazard identification signs shall be installed. Refer to Section 5004 and 5005 for the proper use and setup. It is important to comply with all applicable codes. This project would provide for all requirements in IFC 2012, to include Section 105 permits and inspections through the State Fire Marshal’s Office and the State Public Works Division. | HAZARDOUS WASTE STORAGE #1 | 9937 | Military | NNG |  | Elko | 1990 | 252 | 2016-08-23 | Immediate to Two Years | Currently Critical | 1 | 30000
0674INT1 | INTERIOR FINISHES | 0674 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 11/08/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/23/2016. | ARMORY | 9937 | Military | NNG |  | Elko | 1961 | 10404 | 2016-08-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 104040
2412EXT1 | EXTERIOR FINISHES | 2412 | It is important to maintain the finish, weather resistance, and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 02/01/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | RANGE TOWER | 9912 | Military | NNG |  | Henderson |  | 12120 | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24240
2412SFT1 | GUARDRAIL INSTALLATION | 2412 | The tower is missing a solid wall or guardrail on one side of the platform. This project recommends the installation of a wall or guardrail to form a protective barrier along the open side. This project or a portion thereof was previously recommended in the FCA report dated 02/01/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | RANGE TOWER | 9912 | Military | NNG |  | Henderson |  | 12120 | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 2000
2412EXT2 | ROOF REPLACEMENT | 2412 | The standing seam metal roof, underlayment and sheathing on this building were in poor condition at the time of the survey and had active leaks. It is recommended that this building be re-roofed with new underlayment and sheathing in the next year with a new single-ply roofing system. This will allow the roof to qualify for the statewide roofing program warranty and preventative maintenance agreement. | RANGE TOWER | 9912 | Military | NNG |  | Henderson |  | 12120 | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 181800
9912ENR1 | EXTERIOR SOLAR SITE LIGHTING UPGRADE | 9912 | There are six or seven existing light poles around the site. With increased traffic and development in the area, insufficient site lighting is a security and safety concern. This project would provide for the installation of 12 solar powered LED exterior light fixtures, 20 foot tall poles and 30" diameter raised concrete bases. This installation will eliminate the need for trenching and electrical connections. Some of the existing poles may be acceptable to re-use. If so, the estimate can be reduced accordingly. This project or a portion thereof was previously recommended in the FCA report dated 02/01/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | HENDERSON ARMORY SITE | 9912 | Military | NNG |  | Henderson | 0 |  | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 96000
9912SIT5 | EROSION CONTROL | 9912 | On the north and south sides of the site, the dirt banks are eroding to the sidewalk and parking area. This is now causing damage to the site parking and public sidewalks. There have been several minor improvements accomplished to control the situation, but it is apparent that a major improvement must happen in order to protect the site from permanent damage. This project recommends installing retaining walls in order to provide proper drainage and erosion control. The estimate is based on a 1000 foot long, 5'-0" high reinforced concrete masonry unit retaining wall. | HENDERSON ARMORY SITE | 9912 | Military | NNG |  | Henderson | 0 |  | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 100000
9912PLM1 | SEPTIC SYSTEM REPLACEMENT | 9912 | The septic system serving the Henderson Armory site is original to the site and is in poor condition. The City of Henderson has developed around the Henderson Armory site and has made city sewer available to the site. This project recommends abandoning and filling in the old septic tank and leach field (per NDEP’s rules and regulations), and installing new sewer lines and a hot tap into the City of Henderson’s sewer system. | HENDERSON ARMORY SITE | 9912 | Military | NNG |  | Henderson | 0 |  | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 200000
9912SIT4 | CRACK FILL & SEAL ASPHALT PAVING | 9912 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the paving site wide including access roads and parking areas. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 100,000 square feet of asphalt area was used to generate this estimate. It is recommended that this project coincide with the ADA Accessible Path of Travel project. | HENDERSON ARMORY SITE | 9912 | Military | NNG |  | Henderson | 0 |  | 2016-12-14 | Four to Ten Years | Long-Term Needs | 3 | 125000
9912ADA2 | ADA ACCESSIBLE PATH OF TRAVEL | 9912 | The ADA provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the Henderson Armory are necessary to comply with ADA accessibility requirements. This project would provide for a concrete van accessible ADA parking and loading space and concrete walkway to the existing sidewalk. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2018 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. 750 square feet of concrete was used for this estimate. It is recommended that this project coincide with the paving project. | HENDERSON ARMORY SITE | 9912 | Military | NNG |  | Henderson | 0 |  | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 30000
9912SFT2 | EMERGENCY GENERATOR INSTALLATION | 9912 | The site is lacking an emergency generator to power the buildings in the event of a loss of power. The Armory is designed as an essential services building which is a high priority for being equipped with emergency power. This project provides for the purchase and installation of a 150 kW diesel-engine-driven generator set. This project or a portion thereof was previously recommended in the FCA report dated 02/01/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | HENDERSON ARMORY SITE | 9912 | Military | NNG |  | Henderson | 0 |  | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 125000
9912SFT1 | EXTERIOR STAIR HANDRAIL INSTALLATION | 9912 | There are two sets of concrete stairs on the west side of the property that are lacking handrails as required in the 2018 IBC Chapter 10, Section 1012. The stairs connect the lower east side of the property to the higher west side. This project would provide for tubular steel framed handrails to be installed in accordance with code. If the vertical rise exceeds 12 feet, the entire stairway will need to be removed and replaced with a stair landing at the midpoint. Field verification will need to be done to estimate the vertical rise from the upper landing to the lower landing. This project or a portion thereof was previously recommended in the FCA report dated 02/01/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | HENDERSON ARMORY SITE | 9912 | Military | NNG |  | Henderson | 0 |  | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 10000
3094EXT1 | EXTERIOR FINISHES | 3094 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is painting the walls and roof, and caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 02/01/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | OIL STORAGE BUILDING | 9912 | Military | NNG |  | Henderson | 2005 | 129 | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1290
3094INT1 | INTERIOR FINISHES | 3094 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | OIL STORAGE BUILDING | 9912 | Military | NNG |  | Henderson | 2005 | 129 | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1290
0684EXT1 | EXTERIOR FINISHES | 0684 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 02/01/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | HAZARDOUS WASTE STORAGE BUILDING | 9912 | Military | NNG |  | Henderson | 1990 | 252 | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 504
0682ENR1 | LIGHTING UPGRADE | 0682 | The existing lighting fixtures are the older fluorescent type and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | BUTLER BUILDING #1 - SOUTH | 9912 | Military | NNG |  | Henderson | 1993 | 1600 | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12800
0682EXT2 | EXTERIOR SIDING REPLACEMENT | 0682 | The corrugated metal panels covering the building are original and some are dented, damaged, and should be scheduled for replacement. This project would provide for the removal and the disposal of the existing damaged panels, and the replacement with new pre-painted metal panels. The estimate is based on 96 square feet of 4' wide panels at $17.00 per square foot. | BUTLER BUILDING #1 - SOUTH | 9912 | Military | NNG |  | Henderson | 1993 | 1600 | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1632
0683EXT1 | EXTERIOR FINISHES | 0683 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 02/01/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | BUTLER BUILDING #2 - NORTH | 9912 | Military | NNG |  | Henderson | 1992 | 1600 | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3200
0683EXT2 | EXTERIOR SIDING REPLACEMENT | 0683 | The corrugated metal panels covering the building are original and some are dented, damaged, and should be scheduled for replacement. This project would provide for the removal and the disposal of the existing damaged panels, and the replacement with new pre-painted metal panels. The estimate is based on 96 square feet of 4' wide panels at $17.00 per square foot. | BUTLER BUILDING #2 - NORTH | 9912 | Military | NNG |  | Henderson | 1992 | 1600 | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1632
0684EXT2 | EXTERIOR SIDING REPLACEMENT | 0684 | The corrugated metal panels covering the building are original and some are dented, damaged, and should be scheduled for replacement. This project would provide for the removal and the disposal of the existing damaged panels, and the replacement with new pre-painted metal panels. The estimate is based on 96 square feet of 4' wide panels at $17.00 per square foot. | HAZARDOUS WASTE STORAGE BUILDING | 9912 | Military | NNG |  | Henderson | 1990 | 252 | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1632
0683ENR1 | LIGHTING UPGRADE | 0683 | The existing lighting fixtures are the older fluorescent type and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 02/01/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | BUTLER BUILDING #2 - NORTH | 9912 | Military | NNG |  | Henderson | 1992 | 1600 | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12800
0682SFT1 | ANCHOR SHELVES | 0682 | OSHA recommends that the bottom of all columns be furnished with column base plates, and be anchored to the floor with anchor bolts capable of resisting the forces caused by the loads on the shelving unit. Per OSHA standard 1926.250(a)(1), All materials stored in tiers shall be stacked, racked, blocked, interlocked, or otherwise secured to prevent sliding, falling or collapse. This project would provide for a licensed contractor to install anchor bolts and properly secure the shelving units to the floor and to the other shelves. This project should be overseen by a licensed engineer or architect. | BUTLER BUILDING #1 - SOUTH | 9912 | Military | NNG |  | Henderson | 1993 | 1600 | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 10000
0680SFT4 | EXTERIOR LANDING INSTALLATION | 0680 | Section 1008.1 of the 2018 IBC describes the requirements for doors including floor elevations and landings. The floor or landing shall be at the same elevation on each side of the door and the exterior landing shall not exceed a 2-percent slope and shall have a length measured in the direction of travel of not less than 44 inches. The landing at the door on the building does not comply with this code and poses a safety hazard. This project would provide for the installation of a compliant landing for the door. | HENDERSON ARMORY | 9912 | Military | NNG |  | Henderson | 1971 | 17690 | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 5000
0680ENR1 | EXTERIOR INSULATION & FINISH SYSTEM | 0680 | The building is constructed of concrete masonry units (CMU) with no insulation. Buildings of this type are not energy efficient. This project recommends adding an exterior insulation & finish system (EIFS) over the CMU. The estimate is based on $10.00 per square foot for the EIFS. This project or a portion thereof was previously recommended in the FCA report dated 02/01/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | HENDERSON ARMORY | 9912 | Military | NNG |  | Henderson | 1971 | 17690 | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 176900
0680ADA6 | ADA SIGNAGE | 0680 | ADA regulations pertaining to building access, route of travel and restrooms has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances, route of travel inside the building and restrooms. It is recommended that applicable signage be installed where required. The 2018 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180, and the most current version of the ADA Standards For Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 02/01/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | HENDERSON ARMORY | 9912 | Military | NNG |  | Henderson | 1971 | 17690 | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 1500
0680EXT1 | EXTERIOR FINISHES | 0680 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 02/01/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | HENDERSON ARMORY | 9912 | Military | NNG |  | Henderson | 1971 | 17690 | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 176900
0680SFT3 | FIRE ALARM SYSTEM UPGRADE | 0680 | This building is equipped with an automatic fire detection and alarm system that no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2018 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. This project or a portion thereof was previously recommended in the FCA report dated 02/01/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | HENDERSON ARMORY | 9912 | Military | NNG |  | Henderson | 1971 | 17690 | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 70760
0680SFT1 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0680 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 02/01/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | HENDERSON ARMORY | 9912 | Military | NNG |  | Henderson | 1971 | 17690 | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 4000
0680SFT2 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0680 | The building is a B occupancy per the 2018 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 or R-2 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. This project or a portion thereof was previously recommended in the FCA report dated 02/01/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | HENDERSON ARMORY | 9912 | Military | NNG |  | Henderson | 1971 | 17690 | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 247660
0680ADA7 | ADA RESTROOM UPGRADES | 0680 | The building does not have an accessible restroom. The existing restroom does not meet the ADA requirements. A complete retrofit is necessary. This project would provide funding for remodeling the Men's and Women's restrooms per ADA regulations. Items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2018 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180, and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 02/01/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | HENDERSON ARMORY | 9912 | Military | NNG |  | Henderson | 1971 | 17690 | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 40000
0680EXT3 | OVERHEAD DOOR REPLACEMENT | 0680 | There is one 16'x14' and three 8'x10' overhead coiling doors on the building. They are not insulated and the weather stripping is damaged or missing causing heat loss in the winter and cooling loss in the summer. It is recommended to replace the doors with insulated doors and install new weather stripping. The door frames and mechanical equipment can be re-used with the new doors. This project would provide for the removal and disposal of the roll-up doors and installation of new doors. This project or a portion thereof was previously recommended in the FCA report dated 02/01/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | HENDERSON ARMORY | 9912 | Military | NNG |  | Henderson | 1971 | 17690 | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 32000
0682EXT1 | EXTERIOR FINISHES | 0682 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 02/01/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | BUTLER BUILDING #1 - SOUTH | 9912 | Military | NNG |  | Henderson | 1993 | 1600 | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3200
0680INT5 | SOUND DAMPENING | 0680 | The staff has installed carpet on some of the walls to help reduce the echoing in the classroom in the Henderson Armory; however, the sound echoes to the point that it makes the room unusable. This project would provide carpet or sound soak on the walls. This should dramatically reduce the echoing in the classroom. This project would provide for 600 square feet of carpet or sound soak to be installed on the walls. | HENDERSON ARMORY | 9912 | Military | NNG |  | Henderson | 1971 | 17690 | 2016-12-14 | Four to Ten Years | Long-Term Needs | 3 | 4800
0680ADA5 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0680 | This building contains water fountains on each floor that are not ADA compliant. The 2018 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of four drinking fountains to meet the ADA requirements, two on each floor. This project or a portion thereof was previously recommended in the FCA report dated 10/16/2003 and 02/01/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | HENDERSON ARMORY | 9912 | Military | NNG |  | Henderson | 1971 | 17690 | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 4000
0680ADA10 | RAMP MODIFICATIONS | 0680 | This facility has an ADA accessible ramp located on the side of the building. This ramp is on the accessible path of travel from the accessible parking space to the Henderson Armory building. The ramp does not have proper landings or handrails. This project would provide for an upgrade to the ramp to make it fully ADA compliant. The 2018 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | HENDERSON ARMORY | 9912 | Military | NNG |  | Henderson | 1971 | 17690 | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 25000
0680INT6 | INTERIOR FINISHES | 0680 | It is recommended to paint the interior walls and ceilings at least once in the next 9-10 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HENDERSON ARMORY | 9912 | Military | NNG |  | Henderson | 1971 | 17690 | 2016-12-14 | Four to Ten Years | Long-Term Needs | 3 | 179600
0680PLM1 | WATER HEATER REPLACEMENT | 0680 | There is a 118 gallon natural gas-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is missing proper seismic bracing and an expansion tank. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | HENDERSON ARMORY | 9912 | Military | NNG |  | Henderson | 1971 | 17690 | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0680SFT5 | STORAGE REMOVAL | 0680 | The storage in the Drill Hall room is blocking the exit. The 2018 IBC Chapter 10 Means of Egress explains that exit routes cannot be blocked, reduced, or altered. This project would provide for the removal of all items to ensure that the egress and exit routs are not impeded. | HENDERSON ARMORY | 9912 | Military | NNG |  | Henderson | 1971 | 17690 | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 500
0680INT4 | JANITORS CLOSET REPAIRS | 0680 | The mop sink in the Janitors Closet is mounted adjacent to CMU walls and is showing signs of water damage. This project would provide FRP to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | HENDERSON ARMORY | 9912 | Military | NNG |  | Henderson | 1971 | 17690 | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
0680ADA8 | ADA SHOWER UPGRADE | 0680 | This project would provide for one ADA compliant stainless steel shower cabinet to be installed to provide shower facilities for the disabled. Included in this estimate are the plumbing fixtures and seats. The 2018 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180, and the most current version of the ADA Standards for Accessible Design were used as references for this project. | HENDERSON ARMORY | 9912 | Military | NNG |  | Henderson | 1971 | 17690 | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 50000
9841ADA1 | ADA PARKING | 9841 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. This project provides for a van accessible space and an adjacent loading zone in the existing rear parking lot. The accessible route of travel and public entrance to the Armory will be from a designated rear door. Project includes parking stops, signage, and striping. This project should be done in conjunction with the slurry sealing and any other projected related to the parking area and accessibility. This project or a portion thereof was previously recommended in the FCA report dated 08/16/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | ELY ARMORY SITE | 9841 | Military | NNG |  | Ely | 0 |  | 2017-11-08 | Immediate to Two Years | Currently Critical | 1 | 1500
9841SIT2 | SEAL & STRIPE PARKING LOT | 9841 | The existing paved area around the building is in good condition. This project would provide for striping some designated parking spaces which should be done within the next year and sealing the new AC paving in the next 5 years The striping should be coordinated with the ADA parking/striping project. This project or a portion thereof was previously recommended in the FCA report dated 08/16/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | ELY ARMORY SITE | 9841 | Military | NNG |  | Ely | 0 |  | 2017-11-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
0676EXT3 | EXTERIOR DOOR REPLACEMENT | 0676 | The existing exterior metal doors and frame for the Vault Storage Room are damaged and do not provide the necessary security. They are damaged from age and general wear and tear. This project would provide for the replacement and installation of the solid metal doors, frame and security hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | ELY ARMORY | 9841 | Military | NNG |  | Ely | 1959 | 9877 | 2017-11-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
0676INT3 | INTERIOR FINISHES | 0676 | The interior finishes are in good condition. It is recommended that the interior walls be painted at least once in the next four-five years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 08/16/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | ELY ARMORY | 9841 | Military | NNG |  | Ely | 1959 | 9877 | 2017-11-08 | Four to Ten Years | Long-Term Needs | 3 | 29631
0676PLM1 | FLOOR COVERING REPLACEMENT | 0676 | The floor coverings in this building are in generally poor condition and have reached the end of their serviceable life. At the present time, most of the floor surfaces are 12"x12" vinyl floor tile with only a minimal area of concrete. The majority of the tiles are separating, cracked and loose. This project would provide for the removal, disposal and installation of new 12"x12" vinyl tile in the office areas, corridor and conference rooms. The vinyl floor tiles have been determined to contain asbestos containing material (ACM) and a figure of $4.25/SF @3,500 SF for abatement is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 08/16/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | ELY ARMORY | 9841 | Military | NNG |  | Ely | 1959 | 9877 | 2017-11-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35875
0676EXT2 | EXTERIOR FINISHES | 0676 | The exterior finish is the building's first defense against weather elements. It is important to maintain the finish, weather resistance, and appearance of the building. Moisture and weather intrusion into a building causes indoor air quality issues and premature failure of the building. This project includes items to protect the exterior building envelope other than the roof. This can include re-pointing of mortar joints in areas where necessary or damaged and sealing the building exterior. This sealing can include scraping the paint, applying primer and painting all of the CMU walls and window frames, or reapplying any other type of a building exterior treatment. This project also includes repairing or replacing any flashing, fixtures, and other penetrations or transitions to maintain the building in a good, weather tight condition. This project should occur on a cyclical basis. This project or a portion thereof was previously recommended in the FCA report dated 08/16/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | ELY ARMORY | 9841 | Military | NNG |  | Ely | 1959 | 9877 | 2017-11-08 | Four to Ten Years | Long-Term Needs | 3 | 49385
0676INT2 | INTERIOR FINISHES | 0676 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | ELY ARMORY | 9841 | Military | NNG |  | Ely | 1959 | 9877 | 2017-11-08 | Four to Ten Years | Long-Term Needs | 3 | 52020
0676ADA1 | ADA SIGNAGE | 0676 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | ELY ARMORY | 9841 | Military | NNG |  | Ely | 1959 | 9877 | 2017-11-08 | Immediate to Two Years | Currently Critical | 1 | 1800
0676ENR3 | WINDOW REPLACEMENT | 0676 | The windows in the Drill Hall are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 12 units. Removal and disposal of the existing windows is included in this estimate. | ELY ARMORY | 9841 | Military | NNG |  | Ely | 1959 | 9877 | 2017-11-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
1960HVA2 | HEATING UPGRADE | 1960 | The maintenance shop area is heated by several small wall mounted natural gas fired radiant heaters. They are insufficient in providing heat to the large interior space. Staff noted that the heaters will run continuously, but the temperature at the floor level remains cold. This project would provide for installing new gas fired heating units, preferably closer to the floor of the shop and includes connections to all utilities. | FETC FMS BUILDING | 9879 | Military | NNG |  | North Las Vegas | 1997 | 15589 | 2018-05-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
2023INT1 | INTERIOR FINISHES | 2023 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 10/12/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | FETC USFPO WAREHOUSE | 9879 | Military | NNG |  | North Las Vegas | 1997 | 5600 | 2018-05-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 28000
2023EXT1 | EXTERIOR FINISHES | 2023 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units, painting the metal trim and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 10/12/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | FETC USFPO WAREHOUSE | 9879 | Military | NNG |  | North Las Vegas | 1997 | 5600 | 2018-05-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 28000
1960HVA3 | VEHICLE EXHAUST EXTRACTION SYSTEM | 1960 | The vehicle maintenance garage has an exhaust extraction system that is not in use. Table 403.7 in the 2012 Uniform Mechanical Code states that "Auto repair rooms where engines are run shall have exhaust systems that directly connect to the engine exhaust and prevent escape of fumes". The existing system is not utilized because it is on the floor and most vehicles serviced in the building have exhaust terminations near the top of the vehicle. Also, the existing floor system fills up with water occasionally and does not function. This project would provide for the purchase and installation of eight individual overhead vehicle exhaust extraction systems including, hoses, automatic shut off, electrical connections and roof mounted exhaust fans and equipment as provided by the manufacturer. This project is in design under CIP 11-M05 and the estimate is based off of that project. | FETC FMS BUILDING | 9879 | Military | NNG |  | North Las Vegas | 1997 | 15589 | 2018-05-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 84000
1960INT2 | INTERIOR FINISHES | 1960 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | FETC FMS BUILDING | 9879 | Military | NNG |  | North Las Vegas | 1997 | 15589 | 2018-05-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 77945
1960SIT1 | CONCRETE APRON / LANDING INSTALLATION | 1960 | One of the exterior overhead coiling garage doors does not have a concrete apron in front of it. Also, a concrete landing is missing on the exit door on north side of the building. A concrete landing and apron in front of the doors would reduce the amount of dirt and debris from entering the building and prevent erosion in front of the door. The 2012 IBC requires landings at exit doors. This project would provide for the installation of a new 8" thick concrete slab-on-grade apron at the vehicle garage door and a concrete landing at the exit door. | FETC FMS BUILDING | 9879 | Military | NNG |  | North Las Vegas | 1997 | 15589 | 2018-05-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
1960HVA1 | EXHAUST FAN INSTALLATION | 1960 | The building has a battery charging room. The battery charging room is equipped for flushing and neutralizing spilled electrolytes and charging batteries for vehicles and equipment. The room lacks adequate ventilation for dispersal of fumes from gassing batteries as required by OSHA 1910.178(g) (2). Currently the method of ventilation is to open the exterior door and turn on a portable fan. This project would provide for an exhaust system to be installed with warning alarms. The estimate includes engineering, ducting, wiring, installation and repairs to the roof as required. This project or a portion thereof was previously recommended in the FCA report dated 10/12/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | FETC FMS BUILDING | 9879 | Military | NNG |  | North Las Vegas | 1997 | 15589 | 2018-05-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
1960INT3 | RESTROOM COUNTERTOP REPLACEMENT | 1960 | The countertops in the restrooms are showing signs of wear and tear particularly at the laminated edges and corners. The countertops are delaminating and failing. This project recommends the replacement of the existing damaged countertops with heavy duty, quality finishes. This project would provide funding for the removal and replacement of the countertops. | FETC FMS BUILDING | 9879 | Military | NNG |  | North Las Vegas | 1997 | 15589 | 2018-05-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
1960SFT2 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 1960 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. | FETC FMS BUILDING | 9879 | Military | NNG |  | North Las Vegas | 1997 | 15589 | 2018-05-22 | Immediate to Two Years | Currently Critical | 1 | 7795
1960EXT1 | EXTERIOR FINISHES | 1960 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units, painting of the metal trim and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | FETC FMS BUILDING | 9879 | Military | NNG |  | North Las Vegas | 1997 | 15589 | 2018-05-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 77945
1961INT3 | INTERIOR FINISHES | 1961 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 10/12/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | FETC CSMS | 9879 | Military | NNG |  | North Las Vegas | 1997 | 12648 | 2018-05-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 63240
1960SFT1 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 1960 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 10/12/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | FETC FMS BUILDING | 9879 | Military | NNG |  | North Las Vegas | 1997 | 15589 | 2018-05-22 | Immediate to Two Years | Currently Critical | 1 | 4000
1961HVA2 | VEHICLE EXHAUST EXTRACTION SYSTEMS | 1961 | The vehicle maintenance garage has an exhaust extraction system that is not in use. Table 403.7 in the 2012 Uniform Mechanical Code states that "Auto repair rooms where engines are run shall have exhaust systems that directly connect to the engine exhaust and prevent escape of fumes". The existing system is not utilized because it is on the floor and most vehicles serviced in the building have exhaust terminations near the top of the vehicle. Also, the existing floor system fills up with water occasionally and does not function. This project would provide for the purchase and installation of four individual overhead vehicle exhaust extraction systems including, hoses, automatic shut off, electrical connections and roof mounted exhaust fans and equipment as provided by the manufacturer. This project is in design under CIP 11-M05 and the estimate is based off of that project. | FETC CSMS | 9879 | Military | NNG |  | North Las Vegas | 1997 | 12648 | 2018-05-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 42000
1961SFT1 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 1961 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 10/12/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | FETC CSMS | 9879 | Military | NNG |  | North Las Vegas | 1997 | 12648 | 2018-05-22 | Immediate to Two Years | Currently Critical | 1 | 4000
1960EXT2 | EXTERIOR DOOR REPLACEMENT | 1960 | The exterior metal door for the battery charging station room is damaged from being hit by a forklift. This project would provide for the replacement of the door assembly with a new metal door, frame and hardware. Removal and disposal of the existing door is included in this estimate. | FETC FMS BUILDING | 9879 | Military | NNG |  | North Las Vegas | 1997 | 15589 | 2018-05-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
1961ADA1 | BREAK ROOM REMODEL | 1961 | The kitchenette and associated cabinets in the employee break room are original to the building. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and counter tops are delaminating and failing. This project recommends the replacement of the existing kitchen counters, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards For Accessible Design should be incorporated into the design such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. | FETC CSMS | 9879 | Military | NNG |  | North Las Vegas | 1997 | 12648 | 2018-05-22 | Immediate to Two Years | Currently Critical | 1 | 8000
1961HVA1 | HEATING UPGRADE | 1961 | The maintenance shop area is heated by several small wall mounted natural gas fired radiant heaters. They are insufficient in providing heat to the large interior space. Staff noted that the heaters will run continuously, but the temperature at the floor level remains cold. This project would provide for installing new gas fired heating units, preferably closer to the floor of the shop and includes connections to all utilities. | FETC CSMS | 9879 | Military | NNG |  | North Las Vegas | 1997 | 12648 | 2018-05-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
1961INT2 | RESTROOM COUNTERTOP REPLACEMENT | 1961 | The countertops in the restrooms are showing signs of wear and tear particularly at the laminated edges and corners. The countertops are delaminating and failing. This project recommends the replacement of the existing damaged countertops with heavy duty, quality finishes. This project would provide funding for the removal and replacement of the countertops. This project or a portion thereof was previously recommended in the FCA report dated 10/12/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | FETC CSMS | 9879 | Military | NNG |  | North Las Vegas | 1997 | 12648 | 2018-05-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
1961EXT1 | EXTERIOR FINISHES | 1961 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units, painting the metal trim and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 10/12/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | FETC CSMS | 9879 | Military | NNG |  | North Las Vegas | 1997 | 12648 | 2018-05-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 63240
1962EXT1 | EXTERIOR FINISHES | 1962 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units, painting the metal trim and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 10/12/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | FETC ARMORY STORAGE BUILDING | 9879 | Military | NNG |  | North Las Vegas | 1997 | 2430 | 2018-05-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12150
1962INT1 | INTERIOR FINISHES | 1962 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. This project or a portion thereof was previously recommended in the FCA report dated 10/12/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | FETC ARMORY STORAGE BUILDING | 9879 | Military | NNG |  | North Las Vegas | 1997 | 2430 | 2018-05-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12150
1963EXT1 | EXTERIOR FINISHES | 1963 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units, painting the metal trim and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 10/12/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | FETC CSMS STORAGE BUILDING | 9879 | Military | NNG |  | North Las Vegas | 1997 | 1950 | 2018-05-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9750
1963INT1 | INTERIOR FINISHES | 1963 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. This project or a portion thereof was previously recommended in the FCA report dated 10/12/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | FETC CSMS STORAGE BUILDING | 9879 | Military | NNG |  | North Las Vegas | 1997 | 1950 | 2018-05-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9750
1964EXT1 | EXTERIOR FINISHES | 1964 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 10/12/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | FETC PAINT BOOTH | 9879 | Military | NNG |  | North Las Vegas | 1997 | 1120 | 2018-05-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1120
1964INT1 | INTERIOR FINISHES | 1964 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 10/12/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | FETC PAINT BOOTH | 9879 | Military | NNG |  | North Las Vegas | 1997 | 1120 | 2018-05-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5600
1964SFT1 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 1964 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 10/12/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | FETC PAINT BOOTH | 9879 | Military | NNG |  | North Las Vegas | 1997 | 1120 | 2018-05-22 | Immediate to Two Years | Currently Critical | 1 | 4000
2546INT1 | INTERIOR FINISHES | 2546 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. This project or a portion thereof was previously recommended in the FCA report dated 10/12/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | FETC GUARD SHACK | 9879 | Military | NNG |  | North Las Vegas | 0 | 64 | 2018-05-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 320
2546EXT1 | EXTERIOR FINISHES | 2546 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 10/12/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | FETC GUARD SHACK | 9879 | Military | NNG |  | North Las Vegas | 0 | 64 | 2018-05-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 320
2546EXT2 | EXTERIOR DOOR REPLACEMENT | 2546 | The exterior metal man door is damaged from age and general wear and tear and has reached the end of its expected life. This project would provide for the replacement of the door assembly with a new metal door, frame and hardware. Removal and disposal of the existing door is included in this estimate. | FETC GUARD SHACK | 9879 | Military | NNG |  | North Las Vegas | 0 | 64 | 2018-05-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
2551PLM1 | WATER TOWER MAINTENANCE | 2551 | The tower was installed almost 20 years ago and is due for cyclical maintenance and parts replacement. It provides drinking water for the staff and soldiers as well as water for fire protection. The interior and exterior coatings are breaking down and the pumps and associated controls are unreliable. This breakdown of the coatings can cause the water to become contaminated and the unreliable pumps and controls are a life safety risk. This project would provide for cleaning and sealing the interior and exterior of the tower and replacing the pumps and controls. This project is in design under CIP 11-M45 and the estimate is based off of that project. This project or a portion thereof was previously recommended in the FCA report dated 10/12/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | FETC WATER TANK | 9879 | Military | NNG |  | North Las Vegas | 1996 |  | 2018-05-22 | Immediate to Two Years | Currently Critical | 1 | 250000
9879ENR1 | DIRECT DIGITAL CONTROL SYSTEM UPGRADE | 9879 | Presently the site has two separate direct digital control (DDC) systems, one is an older Siemens system and one is a new Delta system. The Siemens system controls the FMS and the CSMS buildings and is not operating. The Delta system controls the Armory's chiller and boiler. This project would provide for upgrading the Delta system to include all the HVAC systems across the site as well as the lighting and any type of alarm systems. The estimate was provided by the maintenance staff who have procured a quote for this work. | FLOYD EDSALL TRAINING CENTER SITE | 9879 | Military | NNG |  | North Las Vegas | 0 |  | 2018-05-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 90000
3158EXT1 | EXTERIOR FINISHES | 3158 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | FETC STORAGE BUILDING | 9879 | Military | NNG |  | North Las Vegas | 2009 | 1800 | 2018-05-22 | Four to Ten Years | Long-Term Needs | 3 | 1800
3157EXT1 | EXTERIOR FINISHES | 3157 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | FETC VIRTUAL TRAINING FACILITY | 9879 | Military | NNG |  | North Las Vegas | 2012 | 2180 | 2018-05-22 | Four to Ten Years | Long-Term Needs | 3 | 2180
9879SIT4 | SITE DRAINAGE UPGRADES | 9879 | Recent (October 2012) heavy rains exposed drainage problems around the site. The grade does not slope away from the buildings effectively which allowed water to infiltrate all of the buildings to some extent. The perimeter block wall has drainage outlets that quickly clogged up with dirt and debris and prevented water from flowing off property. This project would create positive flow away from the buildings by regrading, paving, installing additional drainage swales as needed and enlarging the outlets in the block wall. | FLOYD EDSALL TRAINING CENTER SITE | 9879 | Military | NNG |  | North Las Vegas | 0 |  | 2018-05-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 75000
9879SIT2 | CRACK FILL & SEAL ASPHALT PAVING | 9879 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the paving site wide including access roads, parking areas and maintenance yards. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 500,000 square feet of asphalt area was used to generate this estimate. | FLOYD EDSALL TRAINING CENTER SITE | 9879 | Military | NNG |  | North Las Vegas | 0 |  | 2018-05-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 300000
0036SIT1 | ROOF DRAIN DOWNSPOUT MODIFICATIONS | 0036 | The roof drain downspouts currently terminate within inches of the building with no continuous drainage away from the foundation. This is causing the water to pool next to the foundation and damage the foundation and walls. This project would provide for the extension of the roof drains from the downspouts to approximately 5'-0" away from the perimeter of the building to prevent pooling and damage to the building. | FETC CLARK COUNTY ARMORY | 9879 | Military | NNG |  | North Las Vegas | 1997 | 76062 | 2018-05-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0036PLM2 | WATER HEATER REPLACEMENT | 0036 | There are three 69 gallon automatic circulating tank water heaters in the central plant. The average life span of a water heater is eight to ten years. With the passage of time and constant use, these units are showing signs of wear and should be scheduled for replacement in the next 3-4 years. It is recommended that three new gas-fired water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. | FETC CLARK COUNTY ARMORY | 9879 | Military | NNG |  | North Las Vegas | 1997 | 76062 | 2018-05-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
0036EXT3 | EXTERIOR FINISHES | 0036 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units, painting the metal trim and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 10/12/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | FETC CLARK COUNTY ARMORY | 9879 | Military | NNG |  | North Las Vegas | 1997 | 76062 | 2018-05-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 380310
0036EXT1 | EXTERIOR DOOR REPLACEMENT | 0036 | The exterior metal man doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of all of the exterior door assemblies with new metal doors, frames and hardware including paint. Removal and disposal of the existing doors is included in this estimate. | FETC CLARK COUNTY ARMORY | 9879 | Military | NNG |  | North Las Vegas | 1997 | 76062 | 2018-05-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 100000
0036ADA1 | ADA ACCESSIBLE COUNTER | 0036 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The lobby at the entrance of the building has a service counter for the public to approach which does not meet current requirements. Section 904.4 of the ADA Standards For Accessible Design states that a portion of the counter surface that is 36" long minimum and 36" high maximum above the finish floor shall be provided. This project will provide an accessible counter space in accordance with this requirement. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | FETC CLARK COUNTY ARMORY | 9879 | Military | NNG |  | North Las Vegas | 1997 | 76062 | 2018-05-22 | Immediate to Two Years | Currently Critical | 1 | 1000
0036INT4 | INTERIOR FINISHES | 0036 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 10/12/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | FETC CLARK COUNTY ARMORY | 9879 | Military | NNG |  | North Las Vegas | 1997 | 76062 | 2018-05-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 380310
1676ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 1676 | This building contains a water fountain. The 2006 IBC Section 1109.5 states where a water fountain is provided, at least half should be accessible. This project would provide funding for the purchase and installation of a new accessible fixed high/ low ADA drinking fountain. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | CSMS BUILDING | 9891 | Military | NNG |  | Carson City | 1992 | 41619 | 2021-02-18 | Immediate to Two Years | Currently Critical | 1 | 4000
1676ENR1 | HVAC EQUIPMENT REPLACEMENT | 1676 | The HVAC system was installed in 1992 and is original to the building. It consists of heating and air conditioning units with ducting to certain areas as well as ceiling mounted unit heaters in the garages and shops. The system is not energy efficient and has reached the end of its expected and useful life. This project would provide for installation of a new HVAC system and cleaning of the existing duct work and grilles. The new system shall be designed to significantly reduce electrical and natural gas usage in order to comply with the 2009 IECC and ASHRAE 90.1 and to reduce utility costs. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 07/07/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/02/2012. | CSMS BUILDING | 9891 | Military | NNG |  | Carson City | 1992 | 41619 | 2021-02-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 499428
1676PLM4 | GATE VALVE REPLACEMENT | 1676 | The 6" main water line coming into the building is equipped with a gate valve to control flow. It has reached the end of its expected life and should be replaced in the next one to two years. This project would provide for replacing the valve and installing a new precast concrete vault around the valve with a solid cover and solid walls. | CSMS BUILDING | 9891 | Military | NNG |  | Carson City | 1992 | 41619 | 2021-02-18 | Immediate to Two Years | Currently Critical | 1 | 4000
1676PLM3 | WATER HEATER REPLACEMENT | 1676 | There is a 50 gallon gas-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 6-7 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | CSMS BUILDING | 9891 | Military | NNG |  | Carson City | 1992 | 41619 | 2021-02-18 | Four to Ten Years | Long-Term Needs | 3 | 1500
1676ADA3 | ADA SHOWER UPGRADE | 1676 | The men's and women's locker rooms each have two shower stalls. The stalls are showing signs of aging and none of the shower stalls are ADA accessible or compliant. This project would provide for one ADA compliant stainless steel shower cabinet and one standard shower stall to be installed in each locker room. Included in this estimate is removal of the existing shower stalls and installation of new stainless steel shower stalls including two ADA compliant shower units complete with accessible plumbing fixtures, seat, etc. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | CSMS BUILDING | 9891 | Military | NNG |  | Carson City | 1992 | 41619 | 2021-02-18 | Immediate to Two Years | Currently Critical | 1 | 16000
1676EXT1 | EXTERIOR FINISHES | 1676 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CSMS BUILDING | 9891 | Military | NNG |  | Carson City | 1992 | 41619 | 2021-02-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 208095
1676ADA4 | ADA RESTROOM UPGRADE | 1676 | The men's and women's locker rooms/ restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A significant retrofit is necessary. This project would provide funding for construction of accessible restroom facilities in the employee locker rooms/ restrooms. These items may include new sinks, toilets, hardware, mirrors, fixtures, flooring, lockers and paint. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | CSMS BUILDING | 9891 | Military | NNG |  | Carson City | 1992 | 41619 | 2021-02-18 | Immediate to Two Years | Currently Critical | 1 | 25000
1676INT1 | INTERIOR FINISHES | 1676 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | CSMS BUILDING | 9891 | Military | NNG |  | Carson City | 1992 | 41619 | 2021-02-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 208095
1453EXT1 | EXTERIOR FINISHES | 1453 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete walls and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HAZ MATERIAL STORAGE #2 | 9891 | Military | NNG |  | Carson City | 2004 | 240 | 2021-02-18 | Four to Ten Years | Long-Term Needs | 3 | 1200
1452EXT1 | EXTERIOR FINISHES | 1452 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete walls and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HAZ MATERIAL STORAGE #1 | 9891 | Military | NNG |  | Carson City | 2004 | 240 | 2021-02-18 | Four to Ten Years | Long-Term Needs | 3 | 1200
1676ADA1 | ADA EMPLOYEE LOUNGE UPGRADES | 1676 | The employee lounge does not meet the Americans with Disabilities Act (ADA) requirements. It is recommended to upgrade some of the features of the room for compliance with accessibility standards for employees. This project would provide funding for construction of an accessible sink and faucet, an accessible space at one of the dining tables and an accessible path of travel throughout the room. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | CSMS BUILDING | 9891 | Military | NNG |  | Carson City | 1992 | 41619 | 2021-02-18 | Immediate to Two Years | Currently Critical | 1 | 2000
1676HVA1 | FUME HOOD EXHAUST SYSTEM INSTALLATION | 1676 | The building has a battery charging room which is equipped for flushing and neutralizing spilled electrolyte. Oxygen and hydrogen gasses are leaked into the air when the batteries are charging and in the right concentrations, these gasses can be highly explosive. The room does not have adequate ventilation for dispersal of these fumes from gassing batteries which is required by OSHA 1910.178(g) (2). This project would provide for a fume hood exhaust system to be installed with warning alarms. The estimate provides for the purchase and installation of an appropriate fume hood exhaust system including the hood, roof exhaust fan, ducting, wiring and any other necessary repairs. This project or a portion thereof was previously recommended in the FCA report dated 07/07/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/02/2012. | CSMS BUILDING | 9891 | Military | NNG |  | Carson City | 1992 | 41619 | 2021-02-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
2521EXT1 | EXTERIOR FINISHES | 2521 | It is important to maintain the finish, weather resistance, and appearance of the structure. This project would provide for painting of the metal and sealing the concrete and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | VEHICLE RAMADA #1 | 9891 | Military | NNG |  | Carson City | 0 | 1575 | 2021-02-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1575
2987EXT1 | EXTERIOR FINISHES | 2987 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | ENTRANCE GUARD STATION | 9891 | Military | NNG |  | Carson City | 2009 | 518 | 2021-02-18 | Four to Ten Years | Long-Term Needs | 3 | 2590
2987INT1 | INTERIOR FINISHES | 2987 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | ENTRANCE GUARD STATION | 9891 | Military | NNG |  | Carson City | 2009 | 518 | 2021-02-18 | Four to Ten Years | Long-Term Needs | 3 | 2590
2199ADA1 | ADA EMPLOYEE LOUNGE UPGRADES | 2199 | There are two employee lounges in the building that do not meet the Americans with Disabilities Act (ADA) requirements. It is recommended to upgrade some of the features of the rooms for compliance with accessibility standards for employees. This project would provide funding for construction of an accessible sink and faucet, an accessible space at one of the dining tables and an accessible path of travel throughout each room. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | OTAG BLDG./LAWRENCE E. JACOBSEN CENTER | 9891 | Military | NNG |  | Carson City | 2002 | 79738 | 2021-02-18 | Immediate to Two Years | Currently Critical | 1 | 4000
2199SIT1 | SITE BOLLARDS | 2199 | There is a concrete loading/unloading tarmac along a portion of the west elevation of the building. There are seven brick columns that are unprotected and have the potential of being damaged by trucks running into them. This project would provide for 14 - eight inch diameter pipe bollards, filled with concrete at each side of the brick columns. This project or a portion thereof was previously recommended in the FCA report dated 06/03/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/02/2012. | OTAG BLDG./LAWRENCE E. JACOBSEN CENTER | 9891 | Military | NNG |  | Carson City | 2002 | 79738 | 2021-02-18 | Four to Ten Years | Long-Term Needs | 3 | 11500
2199EXT1 | EXTERIOR FINISHES | 2199 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete and brick masonry and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | OTAG BLDG./LAWRENCE E. JACOBSEN CENTER | 9891 | Military | NNG |  | Carson City | 2002 | 79738 | 2021-02-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 398690
2199EXT2 | WINDOW REPAIRS | 2199 | There are several windows around the building that are due for repair or replacement. Two windows have a broken seal and moisture has penetrated between the panes. These will need to be replaced. There may be additional windows throughout the building with the same problem. Also, several windows are showing signs of leaks around the frames and should be repaired to maintain a water proof building envelope. These windows were observed in the fitness room. This project would provide funding to repair or replace windows as needed. | OTAG BLDG./LAWRENCE E. JACOBSEN CENTER | 9891 | Military | NNG |  | Carson City | 2002 | 79738 | 2021-02-18 | Immediate to Two Years | Currently Critical | 1 | 7500
2523EXT1 | EXTERIOR FINISHES | 2523 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | STORAGE BUILDING | 9891 | Military | NNG |  | Carson City | 0 | 2500 | 2021-02-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
2520EXT1 | EXTERIOR FINISHES | 2520 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HAZ MATERIAL STORAGE #4 | 9891 | Military | NNG |  | Carson City | 0 | 500 | 2021-02-18 | Four to Ten Years | Long-Term Needs | 3 | 500
2518EXT1 | EXTERIOR FINISHES | 2518 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete walls and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HAZ MAT STORAGE #3 | 9891 | Military | NNG |  | Carson City | 0 | 100 | 2021-02-18 | Four to Ten Years | Long-Term Needs | 3 | 500
2199ADA2 | ADA CANE DETECTION BARRIER INSTALLATION | 2199 | The stairwell in the east corridor does not have 80" of clear head room under the stairs. This project recommends the installation of a permanent barrier under the stairs to warn blind or visually impaired persons of the low head room. NRS 338.180, IBC - 2006 Section 1012 and ADAAG 4.4.2 were referenced for this project. | OTAG BLDG./LAWRENCE E. JACOBSEN CENTER | 9891 | Military | NNG |  | Carson City | 2002 | 79738 | 2021-02-18 | Immediate to Two Years | Currently Critical | 1 | 1000
2199INT1 | INTERIOR FINISHES | 2199 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted or sealed at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | OTAG BLDG./LAWRENCE E. JACOBSEN CENTER | 9891 | Military | NNG |  | Carson City | 2002 | 79738 | 2021-02-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 398690
9891SIT2 | CRACK FILL & SEAL ASPHALT PAVING | 9891 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the paving site wide including access roads, parking areas and maintenance yards. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 500,000 square feet of asphalt area was used to generate this estimate. | NEVADA NATIONAL GUARD CARSON CITY SITE | 9891 | Military | NNG |  | Carson City |  |  | 2021-02-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 300000
0271EXT2 | EXTERIOR FINISHES | 0271 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete and brick masonry and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | USPFO | 9891 | Military | NNG |  | Carson City | 2003 | 32740 | 2021-02-18 | Four to Ten Years | Long-Term Needs | 3 | 163700
0271INT1 | INTERIOR FINISHES | 0271 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted or sealed at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting and sealing, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. In the entry foyer, there is significant efflorescent damage on the brick masonry. This area should be dry-brushed to remove the minerals. With a thorough sealing on the exterior, this problem should be eliminated. | USPFO | 9891 | Military | NNG |  | Carson City | 2003 | 32740 | 2021-02-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 163700
0271ADA1 | ADA EMPLOYEE LOUNGE UPGRADES | 0271 | The two employee lounges in the building do not meet the Americans with Disabilities Act (ADA) requirements. It is recommended to upgrade some of the features of the rooms for compliance with accessibility standards for employees. This project would provide funding for construction of an accessible sink and faucet, an accessible space at one of the dining tables and an accessible path of travel throughout each room. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | USPFO | 9891 | Military | NNG |  | Carson City | 2003 | 32740 | 2021-02-18 | Immediate to Two Years | Currently Critical | 1 | 4000
0271INT2 | CARPET REPLACEMENT | 0271 | The carpet tile floor covering in the building is showing signs of extreme wear. It is original to the building and should be scheduled for replacement. It is recommended that the carpet be replaced with heavy duty commercial grade carpet tiles in the next 2-3 years. The estimate is based on 10,000 square feet of carpet. | USPFO | 9891 | Military | NNG |  | Carson City | 2003 | 32740 | 2021-02-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 70000
0271ELE1 | ROOFTOP ELECTRICAL DUPLEX OUTLETS | 0271 | The building is equipped with several heating, ventilation and air-conditioning (HVAC) units on the roof. There are no electrical duplex outlets on the roof for servicing the rooftop equipment. The 2005 National Electrical Code Section 210.63 and 210.8 requires that a 125-volt, single-phase, 15 or 20 amps -rated GFCI duplex outlet shall be installed at an accessible location for the servicing of HVAC equipment. The receptacle shall be located on the same level and within 25 feet of the unit or units. This project would provide for the installation of eight 125-volt, 20 amp GFCI outlets within 25 feet of the HVAC equipment by a licensed electrical contractor. This project or a portion thereof was previously recommended in the FCA report dated 06/03/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/02/2012. | USPFO | 9891 | Military | NNG |  | Carson City | 2003 | 32740 | 2021-02-18 | Immediate to Two Years | Currently Critical | 1 | 5000
2169SFT1 | FIRE SUPPRESSION SYSTEM INSTALLATION | 2169 | The building is partially a B occupancy per the 2012 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. This project or a portion thereof was previously recommended in the FCA report dated 04/01/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/06/2017. | DMV RENO INSPECTION STATION | 9858 | MtrVeh | B&G |  | Reno | 1975 | 1200 | 2017-03-06 | Immediate to Two Years | Currently Critical | 1 | 16800
2169EXT6 | WINDOW REPLACEMENT | 2169 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 4 units. Removal and disposal of the existing windows is included in this estimate. | DMV RENO INSPECTION STATION | 9858 | MtrVeh | B&G |  | Reno | 1975 | 1200 | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
2169SFT4 | EXIT SIGN AND EGRESS LIGHTING | 2169 | The building does not have emergency egress lighting and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC 2012 Chapter 10 was referenced for this project. | DMV RENO INSPECTION STATION | 9858 | MtrVeh | B&G |  | Reno | 1975 | 1200 | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
2169ELE2 | WIRING CLEANUP | 2169 | The wiring on the roof from the Reno DMV building is daisy chained to the roof of the Reno DMV Inspection Station without using the proper electrical equipment. This project would disconnect the wires from the Reno DMV Inspection Station and re-run the wires through the proper roofing boots, conduits, eye bolts and weather heads. This project would provide for the wiring to be run per NEC 2011. | DMV RENO INSPECTION STATION | 9858 | MtrVeh | B&G |  | Reno | 1975 | 1200 | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
2169HVA4 | HVAC EQUIPMENT REPLACEMENT | 2169 | The packaged unit, swamp cooler and heat pump systems were installed in 1994. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of one new packaged unit, new ductwork, grills, air balancing, DDC and cleaning of the existing duct work. This project includes removal and disposal of the existing equipment and all required connections to utilities. | DMV RENO INSPECTION STATION | 9858 | MtrVeh | B&G |  | Reno | 1975 | 1200 | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
2169EXT5 | GUTTER REPLACEMENT | 2169 | The existing gutter on the Reno DMV Inspection Station eave has numerous joints that have proven impossible to seal against leaks. The leaking gutters will cause premature deterioration to the building finishes and the site hardscape. This project would replace the existing segmented gutter with seamless gutter. | DMV RENO INSPECTION STATION | 9858 | MtrVeh | B&G |  | Reno | 1975 | 1200 | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
2169ELE1 | ELECTRICAL AND COMMUNICATIONS UPGRADE | 2169 | This building was constructed before the high demand for electrical services were needed for computers, communications systems and other electrical devices. As time has progressed, the buildings electrical demand and communications system has changed. The electrical system is utilized to its current maximum potential and the communications system is outdated. The electrical panels, switches and receptacles are at their limit. It is recommended to upgrade the entire electrical system and communications system to meet the evolving needs of the building. | DMV RENO INSPECTION STATION | 9858 | MtrVeh | B&G |  | Reno | 1975 | 1200 | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
2169PLM1 | WATER HEATER REPLACEMENT | 2169 | There is a 15 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | DMV RENO INSPECTION STATION | 9858 | MtrVeh | B&G |  | Reno | 1975 | 1200 | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
2169EXT4 | EXTERIOR DOOR REPLACEMENT | 2169 | The exterior metal doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the 6 door assemblies with new metal doors, frames and hardware. Removal and disposal of the existing doors is included in this estimate. | DMV RENO INSPECTION STATION | 9858 | MtrVeh | B&G |  | Reno | 1975 | 1200 | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
2169ADA2 | ADA RESTROOM UPGRADE | 2169 | The building does not have an accessible restroom. The existing restroom does not meet the ADA requirements. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom. Items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | DMV RENO INSPECTION STATION | 9858 | MtrVeh | B&G |  | Reno | 1975 | 1200 | 2017-03-06 | Immediate to Two Years | Currently Critical | 1 | 15000
2169ENR1 | EXTERIOR LIGHTING REPLACEMENT | 2169 | The building has perimeter lighting on the exterior of the building, but the light fixtures are old, failing and not energy efficient. This project would provide for the replacement of the exterior lighting fixtures with new LED light fixtures, using existing wiring. | DMV RENO INSPECTION STATION | 9858 | MtrVeh | B&G |  | Reno | 1975 | 1200 | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
2169EXT3 | OVERHEAD DOOR REPLACEMENT | 2169 | There are four 12'x14' overhead sectional garage doors which are damaged and do not function properly. They are original to the building and should be scheduled for replacement. It is recommended to install coiling doors as opposed to sectional doors due to the limited space. This project would provide for the removal and disposal of the overhead sectional overhead doors and replacement with coiling doors with new motors. This project or a portion thereof was previously recommended in the FCA report dated 04/01/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/06/2017. | DMV RENO INSPECTION STATION | 9858 | MtrVeh | B&G |  | Reno | 1975 | 1200 | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 32000
2169EXT2 | SOFFIT REPAIR | 2169 | The exterior gypsum board soffit under the roof eave is damaged from exposure to moisture and should be scheduled for replacement. This project would provide for removal of the gypsum board soffit and replacement with a more substantial material such as exterior grade plywood or metal to match the metal fascia on the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/01/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/06/2017. | DMV RENO INSPECTION STATION | 9858 | MtrVeh | B&G |  | Reno | 1975 | 1200 | 2017-03-06 | Immediate to Two Years | Currently Critical | 1 | 14925
2169HVA2 | VEHICLE EXHAUST EXTRACTION SYSTEM | 2169 | The Reno DMV Inspection Station has an exhaust extraction system that is original and is not providing adequate ventilation. Table 403.7 in the 2012 UMC states that "Auto repair rooms where engines are run shall have exhaust systems that directly connect to the engine exhaust and prevent escape of fumes". This project would provide for the purchase and installation of a vehicle exhaust extraction system including, hoses, automatic shut off, electrical connections and roof mounted exhaust fans and equipment as provided by the manufacturer. This project or a portion thereof was previously recommended in the FCA report dated 04/01/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/06/2017. | DMV RENO INSPECTION STATION | 9858 | MtrVeh | B&G |  | Reno | 1975 | 1200 | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
2169HVA1 | REPLACE EXHAUST FANS | 2169 | The existing exhaust fans that serve the vehicle inspection garage are original equipment and are not providing adequate ventilation. This project would provide for the removal of the existing exhaust fan assemblies and the purchase and installation of new exhaust fan assemblies including connections to utilities. | DMV RENO INSPECTION STATION | 9858 | MtrVeh | B&G |  | Reno | 1975 | 1200 | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
2169ENR0 | LIGHTING UPGRADE | 2169 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | DMV RENO INSPECTION STATION | 9858 | MtrVeh | B&G |  | Reno | 1975 | 1200 | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9600
2169SFT3 | PROVIDE CLEARANCE AT ELECTRICAL PANELS | 2169 | There are electrical panels in the building which do not have proper clear floor space around them. The 2012 IFC section 605.3 states that, "A working space of not less than 30 inches in width, 36 inches in depth and 78 inches in height shall be provided in front of electrical service equipment. Where the electrical service equipment is wider than 30 inches, the working space shall not be less than the width of the equipment. No storage of any materials shall be located within the designated working space." This project would provide funds to relocate the tool boxes and other items currently blocking the working space. This project or a portion thereof was previously recommended in the FCA report dated 04/01/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/06/2017. | DMV RENO INSPECTION STATION | 9858 | MtrVeh | B&G |  | Reno | 1975 | 1200 | 2017-03-06 | Immediate to Two Years | Currently Critical | 1 | 250
2169EXT1 | EXTERIOR FINISHES | 2169 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/01/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/06/2017. | DMV RENO INSPECTION STATION | 9858 | MtrVeh | B&G |  | Reno | 1975 | 1200 | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
2169SEC3 | VIDEO SECURITY SYSTEM UPGRADE | 2169 | The video security system for the building and the site is outdated and should be scheduled for immediate replacement. The system is over ten years old and it is increasingly difficult to find replacement parts and experienced repairmen to service the equipment. Due to the security level of the facility is imperative that a new system is installed for the safety of the staff, clients and the public. This project addresses replacement of the cameras, conduit and wiring throughout the facility with all digital equipment as well as sufficient storage capacity. This project should be implemented concurrently with the Security System Installation project. | DMV RENO INSPECTION STATION | 9858 | MtrVeh | B&G |  | Reno | 1975 | 1200 | 2017-03-06 | Four to Ten Years | Long-Term Needs | 3 | 25000
2169SFT2 | FIRE ALARM SYSTEM INSTALLATION | 2169 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2009 Section 7 and the 2012 IFC. This project or a portion thereof was previously recommended in the FCA report dated 04/01/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/06/2017. | DMV RENO INSPECTION STATION | 9858 | MtrVeh | B&G |  | Reno | 1975 | 1200 | 2017-03-06 | Immediate to Two Years | Currently Critical | 1 | 4800
2169EXT7 | ROOF REPLACEMENT | 2169 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2007. It is recommended that this building be re-roofed in the next 9-10 years to be consistent with the roofing program and the end of the warranty period. | DMV RENO INSPECTION STATION | 9858 | MtrVeh | B&G |  | Reno | 1975 | 1200 | 2017-03-06 | Four to Ten Years | Long-Term Needs | 3 | 18000
2169INT1 | REPLACE FLOORING | 2169 | The VCT flooring in the office areas is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. This project or a portion thereof was previously recommended in the FCA report dated 02/05/2003 and 04/01/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/06/2017. | DMV RENO INSPECTION STATION | 9858 | MtrVeh | B&G |  | Reno | 1975 | 1200 | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3600
2169ADA1 | ADA SIGNAGE | 2169 | ADA regulations pertaining to building access, route of travel and restrooms has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/ pictograms; and sign contrast and finish. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances, route of travel inside the building and restrooms. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 02/05/2003 and 04/01/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/06/2017. | DMV RENO INSPECTION STATION | 9858 | MtrVeh | B&G |  | Reno | 1975 | 1200 | 2017-03-06 | Immediate to Two Years | Currently Critical | 1 | 1500
2169INT2 | INTERIOR FINISHES | 2169 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 04/01/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/06/2017. | DMV RENO INSPECTION STATION | 9858 | MtrVeh | B&G |  | Reno | 1975 | 1200 | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
2169SEC1 | SECURITY SYSTEM INSTALLATION | 2169 | The building does not have a security system. This project recommends motion detection, door switches, access control and related items be installed and interfaced with the fire alarm. This project should be implemented concurrently with the Video Security System Upgrade project. This project or a portion thereof was previously recommended in the FCA report dated 02/05/2003 and 04/01/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/06/2017. | DMV RENO INSPECTION STATION | 9858 | MtrVeh | B&G |  | Reno | 1975 | 1200 | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
9858ENR1 | EXTERIOR LIGHTING REPLACEMENT | 9858 | The 6 perimeter light poles around the site have a total of 12 light fixtures. These fixtures are metal halide and not energy efficient. This project would provide for the replacement of the exterior lighting fixtures with new LED light fixtures, using existing wiring. | DMV RENO SITE | 9858 | MtrVeh | B&G |  | Reno | 0 |  | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18000
9858SIT4 | EXTERIOR SIGNAGE | 9858 | The current site identification and directional signage is in poor condition and does not provide adequate directions for the general public. This project would provide funding for new signage throughout the site including site identification, building identification, directional traffic signage and directional pedestrian signage. Where applicable, signage shall comply with ADA regulations including mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish regulations. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | DMV RENO SITE | 9858 | MtrVeh | B&G |  | Reno | 0 |  | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 150000
9858PLM1 | BACKFLOW PREVENTION | 9858 | NAC 445A.67185 and the UPC Section 603 require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, storage and irrigation systems, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of backsiphonage or backpressure. This project allows for the installation of double check valves or reduced pressure principle backflow preventers as appropriate to the hazard and at appropriate locations near the potential source of contamination. Costs include an above ground vault, and allowance for 200 feet of 1" conduit to provide power for freeze protection. | DMV RENO SITE | 9858 | MtrVeh | B&G |  | Reno | 0 |  | 2017-03-06 | Immediate to Two Years | Currently Critical | 1 | 35000
9858ELE1 | EXTERIOR OUTLET REPLACEMENT | 9858 | There is an electrical outlet on the exterior light pole that is broken and does not meet code. This outlet box, cover and GFCI should be changed to comply with NEC 2011. This project would provide for the purchase and installation of one GFCI duplex outlet with a weatherproof box and cover. | DMV RENO SITE | 9858 | MtrVeh | B&G |  | Reno | 0 |  | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 400
9858SIT3 | SIDEWALK AND CURB REPLACEMENT | 9858 | The sidewalks and curbs serving the buildings on this site are deteriorated and failing. In some areas the concrete has heaved and there is settling in other locations. The concrete is pitted and spalling. This project addresses removal and replacement of existing sidewalks and curbs as needed. 10,000SF of 4" thick concrete sidewalk was used for this estimate. NRS 338.180, IBC 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADAAG were used as references for this project. | DMV RENO SITE | 9858 | MtrVeh | B&G |  | Reno | 0 |  | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 100000
9858SIT2 | FENCE INSTALLATION | 9858 | The east side of the property bordering Galletti Way does not have a fence. There have been numerous issues with the public who are not doing business at the DMV offices trespassing on the site and parking and chaining their bikes to the ADA accessible handrails. This project would provide for the installation of a security fence and an electric entrance gate along Galletti Way to deter this activity. This estimate is for 1,600 linear feet of fence at $35 a linear foot and an electric gate. This project should be coordinated with the Asphalt Paving Replacement project. This project or a portion thereof was previously recommended in the FCA report dated 04/01/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/06/2017. | DMV RENO SITE | 9858 | MtrVeh | B&G |  | Reno | 0 |  | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 96000
9858SIT1 | ASPHALT PAVING REPLACEMENT | 9858 | The existing public and employee asphalt paved parking areas are in poor condition. There are numerous asphalt patches, alligator cracking and it has been overlaid to the extent that paving is level with the curbs in some areas causing problems with the drainage. The existing parking spaces provided are at their maximum capacity. This project would provide for the redesign of the parking area to address drainage and overcrowding, removal of the existing landscaped areas, asphalt paving and base as required and installation of new Type II base and valley gutters, 4" of new asphalt paving, striping, and wheel stops. 202,500 square feet was used to generate this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/01/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/06/2017. | DMV RENO SITE | 9858 | MtrVeh | B&G |  | Reno | 0 |  | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2916000
9858ADA1 | ADA PARKING SPACE UPGRADES | 9858 | The ADA provides for accessibility to sites and services for people with physical limitations. The existing ADA parking spaces are no longer compliant and there are not enough of them. Based on the total number of parking spaces at this facility, 11 concrete parking spaces are necessary to comply with ADA requirements. This project would provide for 11 concrete ADA parking spaces and walkways to the existing sidewalk. This will require regrading, installing P.C. concrete, striping, signage and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | DMV RENO SITE | 9858 | MtrVeh | B&G |  | Reno | 0 |  | 2017-03-06 | Immediate to Two Years | Currently Critical | 1 | 82500
0272PLM2 | PLUMBING REPLACEMENT | 0272 | The sanitary wastewater and galvanized plumbing systems are showing signs of deterioration. Due to this deterioration, the systems are not working to their full potential. The galvanized lines are rusting from the inside and the sanitary wastewater lines are deteriorated. The lines are original to the site and are in poor condition. The hard water is a contributing factor to this deterioration. Deposits within the pipes have caused restriction, and have slowed the water flow. This project would provide for the complete replacement of the sanitary sewer and galvanized piping system. | DMV RENO OFFICE | 9858 | MtrVeh | B&G |  | Reno | 1975 | 28800 | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 720000
0272SFT4 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 0272 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention. An inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | DMV RENO OFFICE | 9858 | MtrVeh | B&G |  | Reno | 1975 | 28800 | 2017-03-06 | Immediate to Two Years | Currently Critical | 1 | 9000
0272ELE2 | ELECTRICAL AND COMMUNICATIONS UPGRADE | 0272 | This building was constructed before the high demand for electrical services were needed for computers, communications systems and other electrical devices. As time has progressed, the buildings electrical demand and communications system has changed. The electrical system is utilized to its current maximum potential and the communications system is outdated. The electrical panels, switches and receptacles are at their limit. It is recommended to upgrade the entire electrical system and communications system to meet the evolving needs of the building. | DMV RENO OFFICE | 9858 | MtrVeh | B&G |  | Reno | 1975 | 28800 | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 720000
0272EXT8 | WINDOW REPLACEMENT | 0272 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 160 units. Removal and disposal of the existing windows is included in this estimate. | DMV RENO OFFICE | 9858 | MtrVeh | B&G |  | Reno | 1975 | 28800 | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 240000
0272SEC1 | VIDEO SECURITY SYSTEM UPGRADE | 0272 | The video security system for the building and the site is outdated and should be scheduled for immediate replacement. The system is over ten years old and it is increasingly difficult to find replacement parts and experienced repairmen to service the equipment. Due to the security level of the facility is imperative that a new system is installed for the safety of the staff, clients and the public. This project addresses replacement of the cameras, conduit and wiring throughout the facility with all digital equipment as well as sufficient storage capacity. This project should be implemented concurrently with the Security System Installation project. | DMV RENO OFFICE | 9858 | MtrVeh | B&G |  | Reno | 1975 | 28800 | 2017-03-06 | Four to Ten Years | Long-Term Needs | 3 | 150000
0272EXT6 | EXTERIOR DOOR REPLACEMENT | 0272 | The exterior metal doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of eleven exterior door assemblies with new metal doors, frames and hardware. Removal and disposal of the existing doors is included in this estimate. | DMV RENO OFFICE | 9858 | MtrVeh | B&G |  | Reno | 1975 | 28800 | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 33000
0272ADA3 | ADA SIGNAGE | 0272 | ADA regulations pertaining to building access, route of travel and restrooms have established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. This project would provide funding for the purchase and installation of ADA signage including directional signage from parking to accessible building entrances, route of travel inside the building and restrooms. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/01/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/06/2017. | DMV RENO OFFICE | 9858 | MtrVeh | B&G |  | Reno | 1975 | 28800 | 2017-03-06 | Immediate to Two Years | Currently Critical | 1 | 3000
0272ELE3 | INTERCOM AND PUBLIC ADDRESS SYSTEM INSTALLATION | 0272 | There is no intercom or public address system for this building. This are a large amount of people in the building at any given time and communications are minimal at best. It is important for the employees to be able to communicate with each other quickly as well as address the customers in order to have a safe working environment. This project would provide for the purchase and installation of an intercom and public address system that would work in concert with the other recommended security system upgrade projects. | DMV RENO OFFICE | 9858 | MtrVeh | B&G |  | Reno | 1975 | 28800 | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 75000
0272EXT4 | OVERHEAD DOOR REPLACEMENT | 0272 | There is a 10'x10' overhead sectional door which is damaged and does not function properly. It is original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead sectional door and replacement with a motorized overhead sectional door. This project or a portion thereof was previously recommended in the FCA report dated 04/01/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/06/2017. | DMV RENO OFFICE | 9858 | MtrVeh | B&G |  | Reno | 1975 | 28800 | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7000
0272ADA4 | DUAL LEVEL DRINKING FOUNTAIN REPLACEMENT | 0272 | The existing accessible drinking fountain was installed in 1994. It is worn and damaged from many years of use and should be scheduled for replacement. This project recommends the replacement of the drinking fountain with a new accessible fixed high/ low ADA compliant drinking fountain. The 2012 IBC Chapter 11, ICC/ANSI A117.1 - 2009 and the most current version of the ADAAG was used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/01/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/06/2017. | DMV RENO OFFICE | 9858 | MtrVeh | B&G |  | Reno | 1975 | 28800 | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0272INT7 | BREAK ROOM REMODEL | 0272 | The kitchenette and associated cabinets in the employee break room were replaced in this building in 1994. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and countertops are delaminating and failing. This project recommends the replacement of the existing countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. NRS 338.180, IBC -2012, ICC/ANSI A117.1 -2009 and the most current version of the ADA Standards for Accessible Design should be incorporated into the design and attention to providing an accessible sink is recommended. This estimate includes removal and disposal of the existing materials. This project or a portion thereof was previously recommended in the FCA report dated 04/01/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/06/2017. | DMV RENO OFFICE | 9858 | MtrVeh | B&G |  | Reno | 1975 | 28800 | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0272SFT5 | SPRINKLER HEAD REPLACEMENT | 0272 | The existing fire suppression sprinkler heads are an older style and are located at the exterior of the building. They are rusted and do not comply with NFPA 25. This project recommends that all of the exterior fire suppression sprinkler heads be removed and replaced with new sprinkler heads. | DMV RENO OFFICE | 9858 | MtrVeh | B&G |  | Reno | 1975 | 28800 | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4800
0272ENR2 | EXTERIOR LIGHTING | 0272 | The building has perimeter lighting on the exterior of the building, but the light fixtures are old, failing and not energy efficient. This project would provide for the replacement of the exterior lighting fixtures with new LED light fixtures, using existing wiring. | DMV RENO OFFICE | 9858 | MtrVeh | B&G |  | Reno | 1975 | 28800 | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 28500
0272ENR1 | LIGHTING UPGRADE | 0272 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. A complete removal of the existing system and replacement with LED fixtures is recommended including a lighting control system and occupancy sensors. | DMV RENO OFFICE | 9858 | MtrVeh | B&G |  | Reno | 1975 | 28800 | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 230400
0272PLM1 | WATER HEATER REPLACEMENT | 0272 | There is a 50 gallon gas-fired water heater in the building that was installed in 1996. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next year. The 50 gallon capacity of the existing water heater is not sufficient for the demands of the building. It is recommended that the water heater be upgraded to a 75 gallon gas-fired water heater. This project or a portion thereof was previously recommended in the FCA report dated 04/01/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/06/2017. | DMV RENO OFFICE | 9858 | MtrVeh | B&G |  | Reno | 1975 | 28800 | 2017-03-06 | Immediate to Two Years | Currently Critical | 1 | 3000
0272INT8 | FLOORING REPLACEMENT | 0272 | The VCT, sheet vinyl and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the next 2-3 years. | DMV RENO OFFICE | 9858 | MtrVeh | B&G |  | Reno | 1975 | 28800 | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 230400
0272INT10 | INTERIOR SIGNAGE | 0272 | The current identification and directional signage in the building is in poor condition and does not provide adequate directions for the general public. This project would provide funding for new signage throughout the site including program identification and customer circulation signage. Where applicable, signage shall comply with ADA regulations including mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish regulations. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | DMV RENO OFFICE | 9858 | MtrVeh | B&G |  | Reno | 1975 | 28800 | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 80000
0272ADA6 | RAMP MODIFICATIONS | 0272 | In order to comply with current ADA requirements, modifications will be necessary for the ADA ramps and stairs on the east and west sides of the building. The standards for a ramp require a 36" clear space. Currently, the handrails encroach on this clearance and reduce the clear space to less than 32". The concrete on the stairs and the ramp is deteriorating and the steel poles are rusting at their bases. Exposure to the elements is a contributing factor. This project recommends replacing the steel handrails to comply with ADA guidelines, repairing the concrete on the ramp, and replacing the concrete stairs. The 2012 IBC, ICC/ANSI A117.1 -2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | DMV RENO OFFICE | 9858 | MtrVeh | B&G |  | Reno | 1975 | 28800 | 2017-03-06 | Immediate to Two Years | Currently Critical | 1 | 120000
0272ENR3 | ASBESTOS ABATEMENT/ ENVIRONMENTAL | 0272 | The building has asbestos and environmental concerns in the floor tile mastic and the linoleum. The floor is reaching the end of its useful life expectancy and will need to be removed and remediated per OSHA Standards (29 CFR 1910.1001) and (29 CFR 1926.58). This project would provide for the abatement and remediation of the floor mastic and the linoleum, removal and disposal of the old flooring and the installation of new flooring. | DMV RENO OFFICE | 9858 | MtrVeh | B&G |  | Reno | 1975 | 28800 | 2017-03-06 | Four to Ten Years | Long-Term Needs | 3 | 30000
0272INT9 | INTERIOR DOOR REPLACEMENT | 0272 | The interior doors in this building are hollow core units and most are damaged. This project would provide for the installation of new solid core interior doors including frames, lever action door handles, hardware and paint. Removal and disposal of the existing doors is included in this cost estimate. A total of 40 interior doors was used in this estimate. | DMV RENO OFFICE | 9858 | MtrVeh | B&G |  | Reno | 1975 | 28800 | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 40000
0272ADA5 | EXTERIOR HANDRAIL REPLACEMENT | 0272 | The handrails around the sidewalks are older, are rusting at their bases and are not safe. The gripping surfaces are incorrect and they are not continuous from the top to the bottom landings. This project recommends the installation of new handrails at the sidewalks and for the proper returns and supports to be installed. Removal and disposal of the existing handrails is included in this estimate. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | DMV RENO OFFICE | 9858 | MtrVeh | B&G |  | Reno | 1975 | 28800 | 2017-03-06 | Immediate to Two Years | Currently Critical | 1 | 80000
0272HVA3 | AIR CONDITIONER INSTALLATION | 0272 | The server rooms are not sufficiently cooled by the existing HVAC system. If the rooms are too warm, the computer equipment will prematurely age and may fail due to overheating. It is recommended to install air conditioning systems in the rooms to ensure that the temperature is properly regulated. This project would provide for the purchase and installation of three air conditioners including all required connections to existing utilities. | DMV RENO OFFICE | 9858 | MtrVeh | B&G |  | Reno | 1975 | 28800 | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0272ELE4 | PANIC HARDWARE IN ELECTRICAL ROOMS | 0272 | The electrical room with the uninterruptable power supply contains equipment that meets or exceeds 1,200 amps. It is recommended per the 2012 IBC 1008.1.10 that panic and fire exit hardware be installed. This equipment was not required at the time of the 2007 remodel, but is suggested in this report as an increased safety measure. It is recommended that this project be completed within 1-2 years. The estimate is based on three doors that require panic hardware. | DMV RENO OFFICE | 9858 | MtrVeh | B&G |  | Reno | 1975 | 28800 | 2017-03-06 | Immediate to Two Years | Currently Critical | 1 | 3000
0272SFT6 | EMERGENCY GENERATOR REPLACEMENT | 0272 | The existing emergency generator was installed in 1994 and is approaching the end of its useful life. This project would provide for a new diesel powered 300 KVA generator including a new transfer switch, wiring, concrete pad, fencing and protective bollards. The estimate includes demolition and disposal of the old equipment and materials. | DMV RENO OFFICE | 9858 | MtrVeh | B&G |  | Reno | 1975 | 28800 | 2017-03-06 | Four to Ten Years | Long-Term Needs | 3 | 350000
0272EXT1 | EXTERIOR FINISHES | 0272 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the masonry, painting where necessary and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 02/05/2003 and 04/01/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/06/2017. | DMV RENO OFFICE | 9858 | MtrVeh | B&G |  | Reno | 1975 | 28800 | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 288000
0272ADA1 | RESTROOM REMODELS | 0272 | The building does not have an accessible restroom. The existing restroom does not meet the ADA requirements. A complete retrofit is necessary. This project would provide funding for remodeling the Men's and Women's restrooms per ADA regulations. Items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/01/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/06/2017. | DMV RENO OFFICE | 9858 | MtrVeh | B&G |  | Reno | 1975 | 28800 | 2017-03-06 | Immediate to Two Years | Currently Critical | 1 | 200000
0272INT5 | INTERIOR FINISHES | 0272 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 04/01/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/06/2017. | DMV RENO OFFICE | 9858 | MtrVeh | B&G |  | Reno | 1975 | 28800 | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 288000
0272INT2 | CUSTOMER STATION REPLACEMENT | 0272 | The existing customer stations are damaged and deteriorating due to heavy use and age. The customer service counter spaces do not have adequate room to meet the customers and staff’s needs. This project recommends removing the existing work area counters and installing a modular, ergonomically friendly system which meets the current needs of staff and is movable for future innovations in customer service. Additional costs are included to remove the casework in the public lobby and waiting areas. This project or a portion thereof was previously recommended in the FCA report dated 02/05/2003 and 04/01/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/06/2017. | DMV RENO OFFICE | 9858 | MtrVeh | B&G |  | Reno | 1975 | 28800 | 2017-03-06 | Four to Ten Years | Long-Term Needs | 3 | 250000
0272HVA4 | HVAC EQUIPMENT REPLACEMENT | 0272 | The eight HVAC roof top units and ceiling mounted warehouse heater were installed in 1994. The units are reaching the end of their expected service life and should be scheduled for replacement. This project would provide for the purchase and installation of eight new HVAC packaged units, one new ceiling mounted heater, balancing, DDC system and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 04/01/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/06/2017. | DMV RENO OFFICE | 9858 | MtrVeh | B&G |  | Reno | 1975 | 28800 | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 720000
0272EXT5 | ROOF REPLACEMENT | 0272 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2007. It is recommended that this building be re-roofed in the next 9-10 years to be consistent with the roofing program and the end of the warranty period. | DMV RENO OFFICE | 9858 | MtrVeh | B&G |  | Reno | 1975 | 28800 | 2017-03-06 | Four to Ten Years | Long-Term Needs | 3 | 432000
0272SEC2 | SECURITY SYSTEM INSTALLATION | 0272 | The building does not have a security system. This project recommends motion detection, door switches, access control and related items be installed and interfaced with the fire alarm. This project should be implemented concurrently with the Video Security System Upgrade project. | DMV RENO OFFICE | 9858 | MtrVeh | B&G |  | Reno | 1975 | 28800 | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 144000
2000ADA2 | ADA EMPLOYEE LOUNGE UPGRADES | 2000 | The employee lounge does not meet the Americans with Disabilities Act (ADA) requirements. It is recommended to upgrade some of the features of the room for compliance with accessibility standards for employees. This project would provide funding for construction of an accessible sink and faucet, an accessible space at one of the dining tables and an accessible path of travel throughout the room. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | HENDERSON DMV OFFICE | 9888 | MtrVeh | B&G | MtrVeh | Henderson | 1997 | 18540 | 2018-05-24 | Immediate to Two Years | Currently Critical | 1 | 2000
2000HVA1 | HVAC SYSTEM REPLACEMENT | 2000 | The two hot water boilers and the roof mounted evaporative cooler were installed in 1997. They are not energy efficient and will soon reach the end of their expected and useful life. This project would provide for installation of new HVAC equipment and cleaning of the existing duct work and grilles in the next 6-7 years. This project includes removal and disposal of the existing equipment and all required connections to utilities. | HENDERSON DMV OFFICE | 9888 | MtrVeh | B&G | MtrVeh | Henderson | 1997 | 18540 | 2018-05-24 | Four to Ten Years | Long-Term Needs | 3 | 278100
2000INT4 | INTERIOR FINISHES | 2000 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HENDERSON DMV OFFICE | 9888 | MtrVeh | B&G | MtrVeh | Henderson | 1997 | 18540 | 2018-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 92700
2000EXT3 | EXTERIOR FINISHES | 2000 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the EIFS, sealing the CMU, repairing grout for the tile and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the exterior finishes are addressed in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HENDERSON DMV OFFICE | 9888 | MtrVeh | B&G | MtrVeh | Henderson | 1997 | 18540 | 2018-05-24 | Four to Ten Years | Long-Term Needs | 3 | 92700
2000ADA1 | ADA SIGNAGE | 2000 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 06/09/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2011. | HENDERSON DMV OFFICE | 9888 | MtrVeh | B&G | MtrVeh | Henderson | 1997 | 18540 | 2018-05-24 | Immediate to Two Years | Currently Critical | 1 | 2000
2000EXT4 | ROOF REPLACEMENT | 2000 | The single-ply membrane portion of the roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1997. It is recommended that the single-ply membrane portion of the roof be re-roofed in the next 5-6 years to be consistent with the roofing program and the end of the warranty period. This project does not include replacing the standing seam metal portion of the roof which has a longer life span. | HENDERSON DMV OFFICE | 9888 | MtrVeh | B&G | MtrVeh | Henderson | 1997 | 18540 | 2018-05-24 | Four to Ten Years | Long-Term Needs | 3 | 150000
2000ELE1 | PROVIDE CLEARANCE AT ELECTRICAL PANELS | 2000 | There are electrical panels in the building which do not have proper clear floor space around them. The 2006 IFC section 605.3 states that, "A working space of not less than 30 inches in width, 36 inches in depth and 78 inches in height shall be provided in front of electrical service equipment. Where the electrical service equipment is wider than 30 inches, the working space shall not be less than the width of the equipment. No storage of any materials shall be located within the designated working space." This project would provide funds to relocate the floor cleaning machine and other items currently blocking the working space. | HENDERSON DMV OFFICE | 9888 | MtrVeh | B&G | MtrVeh | Henderson | 1997 | 18540 | 2018-05-24 | Immediate to Two Years | Currently Critical | 1 | 250
2170EXT3 | EXTERIOR DOOR REPLACEMENT | 2170 | The exterior metal man door is damaged from age and general wear and tear and has reached the end of its expected life. This project would provide for the replacement of the metal man door assembly with a new metal door, frame and hardware. Removal and disposal of the existing door is included in this estimate. | DMV INSPECTION STATION | 9888 | MtrVeh | B&G | MtrVeh | Henderson | 1997 | 765 | 2018-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
2170SFT1 | SECURITY LADDER GUARD | 2170 | The roof access ladder is a standard fixed steel ladder with the bottom rung 6 feet above the exterior concrete slab-on-grade sidewalk that is attached to the exterior of the building. The ladder currently does not have a ladder guard to prevent the public from using it and gaining access to the roof. This project would provide for a lockable ladder guard to be installed on the existing ladder to prevent unauthorized use by the public. This project or a portion thereof was previously recommended in the FCA report dated 06/09/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2011. | DMV INSPECTION STATION | 9888 | MtrVeh | B&G | MtrVeh | Henderson | 1997 | 765 | 2018-05-24 | Immediate to Two Years | Currently Critical | 1 | 3000
2516EXT1 | EXTERIOR FINISHES | 2516 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SHADE RAMADA | 9888 | MtrVeh | B&G | MtrVeh | Henderson | 1997 | 400 | 2018-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
2170ELE1 | PROVIDE CLEARANCE AT ELECTRICAL PANELS | 2170 | There are electrical panels in the building which do not have proper clear floor space around them. The 2006 IFC section 605.3 states that, "A working space of not less than 30 inches in width, 36 inches in depth and 78 inches in height shall be provided in front of electrical service equipment. Where the electrical service equipment is wider than 30 inches, the working space shall not be less than the width of the equipment. No storage of any materials shall be located within the designated working space." This project would provide funds to relocate the desk, refrigerator and other items currently blocking the working space. | DMV INSPECTION STATION | 9888 | MtrVeh | B&G | MtrVeh | Henderson | 1997 | 765 | 2018-05-24 | Immediate to Two Years | Currently Critical | 1 | 250
2516ADA1 | ADA PICNIC TABLE INSTALLATION | 2516 | The Shade Ramada provides an employee break area outside including picnic tables. While access to this area appears to be ADA compliant, there are no accessible spaces provided at any of the picnic tables. This project would provide for the purchase and installation of a new accessible picnic table for the Shade Ramada. The table should be placed on an accessible path of travel from the building exit to the accessible space at the picnic table. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | SHADE RAMADA | 9888 | MtrVeh | B&G | MtrVeh | Henderson | 1997 | 400 | 2018-05-24 | Immediate to Two Years | Currently Critical | 1 | 1000
2170EXT2 | EXTERIOR FINISHES | 2170 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the EIFS and stucco, sealing the CMU, repairing grout for the tile and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the exterior finishes are addressed in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | DMV INSPECTION STATION | 9888 | MtrVeh | B&G | MtrVeh | Henderson | 1997 | 765 | 2018-05-24 | Four to Ten Years | Long-Term Needs | 3 | 8775
2170INT2 | INTERIOR FINISHES | 2170 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | DMV INSPECTION STATION | 9888 | MtrVeh | B&G | MtrVeh | Henderson | 1997 | 765 | 2018-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3825
2170INT3 | CARPET REPLACEMENT | 2170 | The carpet in the staff office is showing signs of extreme wear. It is recommended that the carpet be replaced with heavy duty commercial grade carpet in the next 2-3 years. | DMV INSPECTION STATION | 9888 | MtrVeh | B&G | MtrVeh | Henderson | 1997 | 765 | 2018-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1085
2170HVA1 | HVAC EQUIPMENT REPLACEMENT | 2170 | The four HVAC roof top units were installed in 1997. They are not energy efficient and will soon reach the end of their expected and useful life. This project would provide for installation of one new HVAC package unit, three new evaporative coolers and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | DMV INSPECTION STATION | 9888 | MtrVeh | B&G | MtrVeh | Henderson | 1997 | 765 | 2018-05-24 | Four to Ten Years | Long-Term Needs | 3 | 11475
9888SIT3 | SEAL ASPHALT PAVING | 9888 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the paving site wide including access roads, parking areas and testing courses. Striping is included in this estimate. This project should be scheduled on a 4 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 200,000 square feet of asphalt area was used to generate this estimate. | HENDERSON DMV SITE | 9888 | MtrVeh | B&G | MtrVeh | Henderson | 0 |  | 2018-05-24 | Four to Ten Years | Long-Term Needs | 3 | 120000
9901ADA4 | ACCESSIBLE ENTRANCE RAMP | 9901 | This facility has an ADA accessible ramp located on the east side of the building. This ramp is on the accessible path of travel from the accessible parking space to the rear entrance of the building. The ramp itself does not have compliant slopes and landings due to sub-grades shifting, settling and heaving. This project would provide for an upgrade to the ramp to make it fully ADA compliant. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 4/25/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 5/24/2018. | DMV FLAMINGO ROAD SITE | 9901 | MtrVeh | B&G |  | Las Vegas | 0 |  | 2018-05-24 | Immediate to Two Years | Currently Critical | 1 | 35000
9901SIT3 | SIDEWALK REPLACEMENT | 9901 | The sidewalks serving the buildings on this site are deteriorated and failing. 400 SF of 4" thick concrete sidewalk was used for this estimate. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | DMV FLAMINGO ROAD SITE | 9901 | MtrVeh | B&G |  | Las Vegas | 0 |  | 2018-05-24 | Immediate to Two Years | Currently Critical | 1 | 4000
9901SIT2 | CRACK FILL & SEAL ASPHALT PAVING | 9901 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the paving site wide including access roads, parking areas and driving test areas. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 228,382 square feet of asphalt area was used to generate this estimate. the curb stops are cracked and rebar is exposed causing a safety hazard. this project would provide for the replacement of 100 curb stops. | DMV FLAMINGO ROAD SITE | 9901 | MtrVeh | B&G |  | Las Vegas | 0 |  | 2018-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 329735
0366PLM1 | WATER TREATMENT SYSTEM REPLACEMENT | 0366 | The existing water softening/ treatment systems in the building are currently not operational. They are original to the building and approaching the end of their lifecycles. Failure of the equipment causes wear and tear on the domestic water supply lines, plumbing fixtures and HVAC equipment. This project would provide for the replacement of the existing water softeners/ treatment systems with new equipment. This project would also provide for a chemical treatment program including an updated chemicals control system, service and employee training provided by a qualified water treatment vendor. The annual maintenance fee charged by the water treatment vendor would be determined after an investigation of the water system is complete. These annual costs are not included in this project cost. | DMV FLAMINGO INSPECTION STATION | 9901 | MtrVeh | B&G |  | Las Vegas | 1995 | 900 | 2018-05-24 | Immediate to Two Years | Currently Critical | 1 | 22400
0520ADA1 | ADA RAMP UPGRADES | 0520 | This facility has an ADA accessible ramp located on the south side of the building. This ramp is on the accessible path of travel from the accessible parking space to the entrance of the building. The ramp does not have proper handrails, signage or edge protection. This project would provide for an upgrade to the ramp to make it fully ADA compliant. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 4/25/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 5/24/2018. | DMV FLAMINGO WAREHOUSE | 9901 | MtrVeh | B&G |  | Las Vegas | 1995 | 9723 | 2018-05-24 | Immediate to Two Years | Currently Critical | 1 | 35000
0520HVA4 | EVAPORATIVE COOLER REPLACEMENT | 0520 | There are currently six evaporative coolers mounted on the roof of the warehouse. They are severely scaled and have reached the end of their serviceable life. This project would provide for six new evaporative coolers to be installed, and includes removal and disposal of the old evaporative coolers and utility connections to the new units. | DMV FLAMINGO WAREHOUSE | 9901 | MtrVeh | B&G |  | Las Vegas | 1995 | 9723 | 2018-05-24 | Immediate to Two Years | Currently Critical | 1 | 26880
0338INT5 | JANITORS CLOSET REPAIR | 0338 | The mop sink in the Janitors Closet is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | DMV FLAMINGO OFFICE | 9901 | MtrVeh | B&G |  | Las Vegas | 1995 | 31800 | 2018-05-24 | Immediate to Two Years | Currently Critical | 1 | 1400
0520ADA2 | ADA SIGNAGE | 0520 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 4/25/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 5/24/2018. | DMV FLAMINGO WAREHOUSE | 9901 | MtrVeh | B&G |  | Las Vegas | 1995 | 9723 | 2018-05-24 | Immediate to Two Years | Currently Critical | 1 | 2500
0338PLM1 | GAS METER ENCLOSURE REPAIRS | 0338 | The gas meter has a steel fence enclosure that has been damaged by a fork lift truck. This project would repair and repaint the enclosure. This project or a portion thereof was previously recommended in the FCA report dated 11/02/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/24/2018. | DMV FLAMINGO OFFICE | 9901 | MtrVeh | B&G |  | Las Vegas | 1995 | 31800 | 2018-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0520INT1 | INTERIOR FINISHES | 0520 | The interior finishes are in fair condition. It is recommended that the interior gypsum board walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. There are also damaged areas from forklifts that need repairs. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 4/25/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 5/24/2018 | DMV FLAMINGO WAREHOUSE | 9901 | MtrVeh | B&G |  | Las Vegas | 1995 | 9723 | 2018-05-24 | Immediate to Two Years | Currently Critical | 1 | 108898
0366SFT1 | ROOF HATCH REPLACEMENT | 0366 | The roof hatch is original to the building and has reached the end of its useful life. The compression spring operators do not function properly, the latches and handles are worn and the seals and flashing have deteriorated. A faulty roof hatch is a safety hazard to anyone accessing the roof. This project would provide for removal and disposal of the existing roof hatch and purchase and installation of a new roof hatch. | DMV FLAMINGO INSPECTION STATION | 9901 | MtrVeh | B&G |  | Las Vegas | 1995 | 900 | 2018-05-24 | Immediate to Two Years | Currently Critical | 1 | 5600
0366ENR2 | EXTERIOR LIGHTING UPGRADE | 0366 | The existing exterior lighting fixtures are original to the building and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. Light emitting diode (LED) fixtures are suggested. The estimate is for the replacement of six fixtures which are located under the canopy structure and two porch lights, one by each exterior door. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 4/25/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 5/24/2018. | DMV FLAMINGO INSPECTION STATION | 9901 | MtrVeh | B&G |  | Las Vegas | 1995 | 900 | 2018-05-24 | Immediate to Two Years | Currently Critical | 1 | 3528
0366EXT1 | EXTERIOR FINISHES | 0366 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA reports dated 11/02/2004 and 04/25/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/24/2018 | DMV FLAMINGO INSPECTION STATION | 9901 | MtrVeh | B&G |  | Las Vegas | 1995 | 900 | 2018-05-24 | Immediate to Two Years | Currently Critical | 1 | 10080
0338INT3 | RESTROOM REMODEL | 0338 | The restroom is original to the building and in overall poor condition. The finishes, fixtures, toilet and exhaust fan are showing signs of wear and deterioration. This project would provide for a complete remodel of the restroom and tile floor replacement. The removal and disposal of the existing fixtures and finishes is included in this estimate. | DMV FLAMINGO OFFICE | 9901 | MtrVeh | B&G |  | Las Vegas | 1995 | 31800 | 2018-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 150000
0338HVA2 | EVAPORATIVE COOLER REPLACEMENT | 0338 | An evaporative cooler is installed in the mechanical room that is no longer operational. This project would provide for a new evaporative cooler to be installed including all required connections to utilities. The estimate includes removal and disposal of the old cooler. This project or a portion thereof was previously recommended in the FCA report dated 4/25/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 5/24/2018. | DMV FLAMINGO OFFICE | 9901 | MtrVeh | B&G |  | Las Vegas | 1995 | 31800 | 2018-05-24 | Immediate to Two Years | Currently Critical | 1 | 3360
0338PLM2 | WATER HEATER REPLACEMENT | 0338 | There is a 40 gallon gas-fired water heater serving the customer restrooms. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 1-2 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | DMV FLAMINGO OFFICE | 9901 | MtrVeh | B&G |  | Las Vegas | 1995 | 31800 | 2018-05-24 | Immediate to Two Years | Currently Critical | 1 | 1680
0338INT4 | LIGHTING UPGRADE | 0338 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | DMV FLAMINGO OFFICE | 9901 | MtrVeh | B&G |  | Las Vegas | 1995 | 31800 | 2018-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 111300
0338PLM3 | WATER HEATER REPLACEMENT | 0338 | There is a 40 gallon gas-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 5-6 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | DMV FLAMINGO OFFICE | 9901 | MtrVeh | B&G |  | Las Vegas | 1995 | 31800 | 2018-05-24 | Four to Ten Years | Long-Term Needs | 3 | 1500
0338ADA3 | ADA SIGNAGE | 0338 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 4/25/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 5/24/2018. | DMV FLAMINGO OFFICE | 9901 | MtrVeh | B&G |  | Las Vegas | 1995 | 31800 | 2018-05-24 | Immediate to Two Years | Currently Critical | 1 | 5600
0338EXT1 | EXTERIOR FINISHES | 0338 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is cleaning and sealing the concrete masonry units, repairing and painting the stucco and caulking of the metal panels, windows, flashing, fixtures and all other penetrations. Attention should be paid to the stucco which has extensive cracking and may need to be scheduled for repair. It is recommended that the building be sealed, painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA reports dated 11/02/2004 and 04/25/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/24/2018. | DMV FLAMINGO OFFICE | 9901 | MtrVeh | B&G |  | Las Vegas | 1995 | 31800 | 2018-05-24 | Immediate to Two Years | Currently Critical | 1 | 356160
0520EXT1 | EXTERIOR FINISHES | 0520 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA reports dated 11/02/2004 and 4/25/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 5/24/2018. | DMV FLAMINGO WAREHOUSE | 9901 | MtrVeh | B&G |  | Las Vegas | 1995 | 9723 | 2018-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 108898
0366INT1 | INTERIOR FINISHES | 0366 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 4/25/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 5/24/2018. | DMV FLAMINGO INSPECTION STATION | 9901 | MtrVeh | B&G |  | Las Vegas | 1995 | 900 | 2018-05-24 | Immediate to Two Years | Currently Critical | 1 | 10080
0520HVA3 | HVAC REPLACEMENT - OFFICES | 0520 | There are 2 wall-mounted packaged heating and cooling units installed in the offices. They are original to the building and have reached the end of their useful and expected life. This project would provide for 2 new packaged units to be installed including all required connections to utilities. The estimate includes removal and disposal of the old units. This project or a portion thereof was previously recommended in the FCA report dated 4/25/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 5/24/2018. | DMV FLAMINGO WAREHOUSE | 9901 | MtrVeh | B&G |  | Las Vegas | 1995 | 9723 | 2018-05-24 | Immediate to Two Years | Currently Critical | 1 | 16800
2454EXT1 | EXTERIOR FINISHES | 2454 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building finishes are addressed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | DMV INSPECTION STATION | 9869 | MtrVeh | B&G | MtrVeh | Las Vegas | 2006 | 744 | 2018-12-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3720
2454ADA1 | ADA RESTROOM UPGRADES | 2454 | The designated ADA restroom does not fully comply with the Americans with Disabilities Act (ADA) requirements. The seat cover dispenser is not in an accessible location and the condensation drain attached to the sink drain interferes with the required clear space under the sink. This project would provide funding for relocating the seat cover dispenser to a compliant location and relocating the condensation drain from under the sink. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | DMV INSPECTION STATION | 9869 | MtrVeh | B&G | MtrVeh | Las Vegas | 2006 | 744 | 2018-12-10 | Immediate to Two Years | Currently Critical | 1 | 750
2454INT1 | INTERIOR FINISHES | 2454 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | DMV INSPECTION STATION | 9869 | MtrVeh | B&G | MtrVeh | Las Vegas | 2006 | 744 | 2018-12-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3710
2453ADA2 | ADA SIGNAGE | 2453 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | NORTH DECATUR DMV SERVICES CENTER | 9869 | MtrVeh | B&G | MtrVeh | Las Vegas | 2006 | 23568 | 2018-12-10 | Immediate to Two Years | Currently Critical | 1 | 1500
2453INT1 | INTERIOR FINISHES | 2453 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | NORTH DECATUR DMV SERVICES CENTER | 9869 | MtrVeh | B&G | MtrVeh | Las Vegas | 2006 | 23568 | 2018-12-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 118085
2453HVA1 | COOLING TOWER REPAIRS | 2453 | The cooling tower has extensive scaling on the film fill media and the plastic film fill is brittle and broken in many areas. This will cause underperformance of the cooling tower and premature failure. It is recommended to remove the and replace the film fill media to bring the cooling tower back into prime operating condition. | NORTH DECATUR DMV SERVICES CENTER | 9869 | MtrVeh | B&G | MtrVeh | Las Vegas | 2006 | 23568 | 2018-12-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
2453ADA1 | ADA EMPLOYEE LOUNGE UPGRADES | 2453 | The employee lounge does not meet the Americans with Disabilities Act (ADA) requirements. It is recommended to upgrade some of the features of the room for compliance with accessibility standards for employees. This project would provide funding for construction of an accessible sink and faucet, an accessible space at one of the dining tables and an accessible path of travel throughout the room. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | NORTH DECATUR DMV SERVICES CENTER | 9869 | MtrVeh | B&G | MtrVeh | Las Vegas | 2006 | 23568 | 2018-12-10 | Immediate to Two Years | Currently Critical | 1 | 2000
2453EXT1 | EXTERIOR FINISHES | 2453 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting the stucco and EIFS, cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building finishes are addressed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NORTH DECATUR DMV SERVICES CENTER | 9869 | MtrVeh | B&G | MtrVeh | Las Vegas | 2006 | 23568 | 2018-12-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 118085
2453INT3 | LOBBY TILE FLOORING REPLACEMENT | 2453 | The terrazzo tile flooring in the main Lobby is severely damaged throughout and should be scheduled for replacement. The tiles are breaking at the corners, the grout is failing and there are significant cracks across large sections of tiles. This is a heavily used area and could pose a safety issue with potential tripping hazards to the public and employees. This project would provide for removal and disposal of the existing tile and installation of new tile with a 6" cove base. | NORTH DECATUR DMV SERVICES CENTER | 9869 | MtrVeh | B&G | MtrVeh | Las Vegas | 2006 | 23568 | 2018-12-10 | Immediate to Two Years | Currently Critical | 1 | 135000
2453INT2 | CARPET REPLACEMENT | 2453 | The carpet in the building is showing signs of extreme wear. It is recommended that the carpet be replaced with heavy duty commercial grade carpet in the next 2-3 years. | NORTH DECATUR DMV SERVICES CENTER | 9869 | MtrVeh | B&G | MtrVeh | Las Vegas | 2006 | 23568 | 2018-12-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 45500
9832ADA1 | ADA SIGNAGE | 9832 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria including the current parking signs that do not indicate the minimum fine as $250. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | DMV EXPRESS OFFICE SITE | 9832 | MtrVeh | B&G |  | Las Vegas | 1995 |  | 2018-12-10 | Immediate to Two Years | Currently Critical | 1 | 2500
9869ADA1 | ADA UPGRADES | 9869 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The concrete parking area and passenger loading area are missing proper signage and striping to comply with ADA requirements. For example, the 15 existing parking signs indicate a $100 fine which has been raised to a $250 minimum fine. This project would provide for striping, signage and any other necessary upgrades to the parking space. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | NORTH DECATUR DMV SITE | 9869 | MtrVeh | B&G | MtrVeh | Las Vegas | 2006 |  | 2018-12-10 | Immediate to Two Years | Currently Critical | 1 | 2500
9869SIT1 | SEAL ASPHALT PAVING | 9869 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the paving site wide including access roads, parking areas and the maintenance yard. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 300,000 square feet of asphalt area was used to generate this estimate. | NORTH DECATUR DMV SITE | 9869 | MtrVeh | B&G | MtrVeh | Las Vegas | 2006 |  | 2018-12-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 180000
3106EXT1 | EXTERIOR FINISHES | 3106 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide funding for repairing, sealing and caulking of the exterior of the structure. Included in the cost is repairing the damaged concrete masonry units (CMU) and sealing and caulking the CMU, flashing, fixtures and all other penetrations. It is recommended that the building be repaired in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | INSPECTION STATION CANOPY | 9832 | MtrVeh | B&G |  | Las Vegas | 1995 | 3074 | 2018-12-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
9832SIT1 | SEAL ASPHALT PAVING | 9832 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the paving site wide including access roads, parking areas and the test driving area. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 275,000 square feet of asphalt area was used to generate this estimate. This project should be implemented concurrently with the Concrete Curb Replacement project. | DMV EXPRESS OFFICE SITE | 9832 | MtrVeh | B&G |  | Las Vegas | 1995 |  | 2018-12-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 206250
9832SIT3 | FENCE REPAIRS | 9832 | The chain link fence has been damaged and should be repaired immediately. Vagrants have cut a large hole in the fence on the south side of the property and have been entering and exiting through it. This project would provide for removing the damaged section and splicing in a new section of chain link. Further plans to install barbed wire or a similar deterrent can be made by the agency to prevent this from happening in the future. | DMV EXPRESS OFFICE SITE | 9832 | MtrVeh | B&G |  | Las Vegas | 1995 |  | 2018-12-10 | Immediate to Two Years | Currently Critical | 1 | 1500
9832SIT2 | CONCRETE CURB REPLACEMENT | 9832 | The concrete curbing in the parking lot has been damaged and is failing in many areas. There is extensive cracking, crumbling and failure due to vehicles colliding with the curbs. Some replacements have been done recently, but these areas are already failing as well. Due to the high traffic volume and higher percentage of large commercial vehicles in this parking lot, it is recommended to replace the curbs with a more appropriate system. This project would provide for the installation of concrete curbing with a deeper footing throughout and a high strength concrete mix to ensure a longer life cycle of the new curbing. Removal and disposal of the existing curbing is included in this estimate. This project should be implemented concurrently with the Seal Asphalt Paving project. | DMV EXPRESS OFFICE SITE | 9832 | MtrVeh | B&G |  | Las Vegas | 1995 |  | 2018-12-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0265ADA2 | ADA RESTROOM UPGRADES | 0265 | The Men's and Women's designated ADA restrooms do not entirely meet the Americans with Disabilities Act (ADA) requirements. Examples of non-compliant items are the faucet handles and lack of under lavatory protection. Also, the ceramic sink in the Men's restroom is cracked. This project would provide funding for replacing the lavatory and countertop system in each restroom to ensure full compliance with accessibility regulations. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | DMV EXPRESS OFFICE | 9832 | MtrVeh | B&G |  | Las Vegas | 1995 | 5468 | 2018-12-10 | Immediate to Two Years | Currently Critical | 1 | 5000
0265HVA2 | HVAC REPLACEMENT | 0265 | The existing HVAC system consists of 6 exterior mounted heat pumps combined with 6 interior air handlers. They are not energy efficient and are reaching the end of their expected and useful life. This project would provide for installation of new HVAC equipment and cleaning of the existing duct work and grilles. The estimate includes removal and disposal of the existing HVAC units and all required connections to utilities. | DMV EXPRESS OFFICE | 9832 | MtrVeh | B&G |  | Las Vegas | 1995 | 5468 | 2018-12-10 | Four to Ten Years | Long-Term Needs | 3 | 36000
0265INT1 | INTERIOR FINISHES | 0265 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | DMV EXPRESS OFFICE | 9832 | MtrVeh | B&G |  | Las Vegas | 1995 | 5468 | 2018-12-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 27340
0265ADA3 | ADA SIGNAGE | 0265 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | DMV EXPRESS OFFICE | 9832 | MtrVeh | B&G |  | Las Vegas | 1995 | 5468 | 2018-12-10 | Immediate to Two Years | Currently Critical | 1 | 1500
0265ADA4 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0265 | The water fountain in the employee break room does not meet current accessibility requirements. For example, the flow of water from the spout is not parallel to the front of the unit or within the distances provided in the code and at the time of the survey, the knee clearance under the fountain was blocked by a trash can. This project would provide funding for the purchase and installation of a new accessible fixed high/ low ADA drinking fountain. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | DMV EXPRESS OFFICE | 9832 | MtrVeh | B&G |  | Las Vegas | 1995 | 5468 | 2018-12-10 | Immediate to Two Years | Currently Critical | 1 | 4000
0265EXT3 | EXTERIOR FINISHES | 0265 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the stucco and sealing and caulking the CMU, windows, flashing, fixtures and all other penetrations. This includes repairing the broken masonry caps on the employee parking sign and the condenser enclosure. It is recommended that the building be repaired in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | DMV EXPRESS OFFICE | 9832 | MtrVeh | B&G |  | Las Vegas | 1995 | 5468 | 2018-12-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 27340
2037HVA1 | HVAC EQUIPMENT REPLACEMENT | 2037 | The rooftop HVAC units, including the Liebert computer room units are reaching the end of their service life and should be scheduled for replacement. They are not energy efficient and have reached the end of their expected and useful life. The R-22 refrigerant in the cooling system is no longer EPA compliant and its production is mandated to be phased out completely by January 1, 2020. This project would provide for installation of a new HVAC system and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC equipment and all required connections to utilities. | DMV COMPUTER FACILITY | 9906 | MtrVeh | B&G |  | Carson City | 1998 | 10255 | 2020-05-18 | Four to Ten Years | Long-Term Needs | 3 | 205100
2037STR1 | RAISED FLOOR MODIFICATIONS | 2037 | The raised floor in the server room does not appear to have sufficient structural support for the equipment it is carrying. Global Risk Consultants, the State's insurance underwriter also has indicated that the floor does not have adequate seismic and structural support for the equipment. This project would provide for the attachment of the floor to the concrete slab-on-grade and evaluation by a qualified individual for seismic loading. Replacement of the floor with a new code compliant raised flooring system may be an option, but is not included in this cost estimate. This project or a portion thereof was previously recommended in the FCA report dated 01/14/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/18/2020. | DMV COMPUTER FACILITY | 9906 | MtrVeh | B&G |  | Carson City | 1998 | 10255 | 2020-05-18 | Immediate to Two Years | Currently Critical | 1 | 10000
2037INT2 | REPLACE CARPET | 2037 | The carpet is showing signs of wear. It is recommended that the carpet be replaced with heavy duty commercial grade carpet in the next two to three years. Removal and disposal of the existing carpet is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 01/14/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/18/2020. | DMV COMPUTER FACILITY | 9906 | MtrVeh | B&G |  | Carson City | 1998 | 10255 | 2020-05-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 71400
2037EXT2 | EXTERIOR FINISHES | 2037 | The exterior painted surfaces are in poor condition, including the perimeter caulking on the windows. It is important to maintain the finish, weather resistance, and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including sealing and tuck pointing the masonry, and caulking around windows, flashing, fixtures and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 2 - 3 years and is recommended on a cyclical basis to maintain the integrity of the structure. | DMV COMPUTER FACILITY | 9906 | MtrVeh | B&G |  | Carson City | 1998 | 10255 | 2020-05-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30800
2037ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 2037 | This building contains a water fountain in the north entry corridor that is not ADA compliant. The 2018 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | DMV COMPUTER FACILITY | 9906 | MtrVeh | B&G |  | Carson City | 1998 | 10255 | 2020-05-18 | Immediate to Two Years | Currently Critical | 1 | 10000
2037INT1 | INTERIOR FINISHES | 2037 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4 to 5 years and every 8 to 9 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. . | DMV COMPUTER FACILITY | 9906 | MtrVeh | B&G |  | Carson City | 1998 | 10255 | 2020-05-18 | Four to Ten Years | Long-Term Needs | 3 | 82000
1990ENR2 | EXTERIOR LIGHTING REPLACEMENT | 1990 | The building has perimeter lighting on the exterior of the building. The light fixtures are an old incandescent type and not energy efficient. This project would provide for the replacement of the exterior lighting fixtures with new LED light fixtures using existing wiring. | DMV WAREHOUSE | 9906 | MtrVeh | B&G |  | Carson City | 1991 | 16750 | 2020-05-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7000
1990HVA1 | HVAC EQUIPMENT REPLACEMENT | 1990 | The rooftop HVAC units are reaching the end of their service life and should be scheduled for replacement. They are not energy efficient and have reached the end of their expected and useful life. The R-22 refrigerant in the cooling system is no longer EPA compliant and its production is mandated to be phased out completely by January 1, 2020. This project would provide for installation of a new HVAC system and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC equipment and all required connections to utilities. | DMV WAREHOUSE | 9906 | MtrVeh | B&G |  | Carson City | 1991 | 16750 | 2020-05-18 | Four to Ten Years | Long-Term Needs | 3 | 37500
1990EXT3 | EXTERIOR FINISHES | 1990 | The exterior finishes are in poor condition. Caulking has failed between the vertical joints of the exterior tilt-up wall panels allowing free flow of outside air infiltration. It is important to maintain the finish, weather resistance, and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including sealing and tuck pointing the masonry, painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 2 to 3 years and is recommended on a cyclical basis to maintain the integrity of the structure. | DMV WAREHOUSE | 9906 | MtrVeh | B&G |  | Carson City | 1991 | 16750 | 2020-05-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 134000
1990ADA1 | ADA RESTROOM MODIFICATIONS | 1990 | The ADA designated Men's and Women's restrooms on the lower level are not compliant. This project would provide for a new toilet and sink, horizontal and vertical grab bars, and lever action door hardware. The partition located in front of the doors will need to be removed to provide for proper forward approach and is included in this estimate. The signage will need to be relocated. The 2018 IBC Chapter 11, ICC/ANSI A117.1 and the Americans with Disabilities Act Accessibility Guidelines (ADAAG) was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 01/14/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/18/2020. | DMV WAREHOUSE | 9906 | MtrVeh | B&G |  | Carson City | 1991 | 16750 | 2020-05-18 | Immediate to Two Years | Currently Critical | 1 | 15000
1990EXT1 | LOADING DOCK UPGRADES | 1990 | There are two 8'x10' power-operated overhead coiling doors for the loading dock which are damaged and do not function properly. The loading dock lift is also not functioning properly and has reached the end of its useful life. The doors and the lift are original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the doors and the lift and replacement with new power-operated overhead coiling doors and a new hydraulic lift. This project or a portion thereof was previously recommended in the FCA report dated 01/14/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/18/2020. | DMV WAREHOUSE | 9906 | MtrVeh | B&G |  | Carson City | 1991 | 16750 | 2020-05-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
1990INT1 | INTERIOR FINISHES | 1990 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings in the offices and Mail Room be painted at least once in the next 4 to 5 years and every 4 to 5 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. 2,500 square feet was used to generate this estimate. | DMV WAREHOUSE | 9906 | MtrVeh | B&G |  | Carson City | 1991 | 16750 | 2020-05-18 | Four to Ten Years | Long-Term Needs | 3 | 12500
2459EXT2 | EXTERIOR FINISHES | 2459 | The exterior finishes are in good condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, sealing, tuck pointing the brick masonry and caulking around windows, flashing, fixtures and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 8 to 9 years and is recommended on a cyclical basis to maintain the integrity of the structure. | LARGE VEHICLE SCALE BUILDING | 9906 | MtrVeh | B&G |  | Carson City | 1981 | 160 | 2020-05-18 | Four to Ten Years | Long-Term Needs | 3 | 2000
2965EXT1 | EXTERIOR FINISHES | 2965 | The exterior painted surfaces are in fair condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide for painting of the structural steel members, repairing broken welds, tuck pointing and sealing the brick masonry as needed. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis to maintain the integrity of the structure. | GENERATOR BUILDING | 9906 | MtrVeh | B&G |  | Carson City | 0 | 560 | 2020-05-18 | Four to Ten Years | Long-Term Needs | 3 | 1680
2459ENR1 | EXTERIOR LIGHTING REPLACEMENT | 2459 | The building has perimeter lighting on the exterior of the building. The light fixtures are an old incandescent type and not energy efficient. This project would provide for the replacement of the exterior lighting fixtures with new LED light fixtures using existing wiring. | LARGE VEHICLE SCALE BUILDING | 9906 | MtrVeh | B&G |  | Carson City | 1981 | 160 | 2020-05-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
2459INT1 | INTERIOR FINISHES | 2459 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4 to 5 years and every 8 to 9 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. | LARGE VEHICLE SCALE BUILDING | 9906 | MtrVeh | B&G |  | Carson City | 1981 | 160 | 2020-05-18 | Four to Ten Years | Long-Term Needs | 3 | 2000
9906ENR1 | HIGH MAST SITE LIGHTING UPGRADE | 9906 | There are 4 high mast light poles around the site with incandescent fixtures. These fixtures are HPS (high pressure sodium) and not energy efficient. This project would provide for the replacement of the exterior lighting fixtures with new LED light fixtures using existing wiring. | DMV/PUBLIC SAFETY SITE | 9906 | MtrVeh | B&G |  | Carson City | 0 |  | 2020-05-18 | Four to Ten Years | Long-Term Needs | 3 | 4000
9906SIT6 | REPLACE VEHICLE SCALE | 9906 | The vehicle scale is damaged and does not always function properly. The scale platform is showing signs of wear including cracked concrete, broken welds, and general instability. The steel framework for the scale is severely corroded due to flooding / moisture infiltration and clogged drains. The scale is original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the existing vehicle scale and replacement with a new scale. This project or a portion thereof was previously recommended in the FCA report dated 01/14/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/18/2020. | DMV/PUBLIC SAFETY SITE | 9906 | MtrVeh | B&G |  | Carson City | 0 |  | 2020-05-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
9906SIT7 | CRACK FILL & SLURRY SEAL ASPHALT PAVING | 9906 | The site parking lots are in good condition. It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site wide including access roads, parking areas, and the CDL course. Striping is included in this estimate. This project should be scheduled on a 4-5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 120,880 square feet of asphalt area and 1,500 lineal feet of crack fill was used to generate this estimate. | DMV/PUBLIC SAFETY SITE | 9906 | MtrVeh | B&G |  | Carson City | 0 |  | 2020-05-18 | Four to Ten Years | Long-Term Needs | 3 | 96700
0210ENV1 | PEST CONTROL | 0210 | There are substantial bird droppings at the electrical service on the west side of the building. Due to the potential risk of disease, this project provides for treatment and clean up of the pigeon and rodent droppings by a licensed pest control business. | DMV OFFICE BUILDING ADDITION (EAST WING) | 9906 | MtrVeh | B&G |  | Carson City | 1980 | 56688 | 2020-05-18 | Immediate to Two Years | Currently Critical | 1 | 1000
0210ENR1 | EXTERIOR LIGHTING REPLACEMENT | 0210 | The building has perimeter lighting on the exterior of the building. The light fixtures are an old incandescent type and not energy efficient. This project would provide for the replacement of the exterior lighting fixtures with new LED light fixtures using existing wiring. | DMV OFFICE BUILDING ADDITION (EAST WING) | 9906 | MtrVeh | B&G |  | Carson City | 1980 | 56688 | 2020-05-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
0209INT1 | INTERIOR FINISHES | 0209 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next 4 to 5 years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | DMV OFFICE BUILDING (WEST WING) | 9906 | MtrVeh | B&G |  | Carson City | 1965 | 31500 | 2020-05-18 | Four to Ten Years | Long-Term Needs | 3 | 157500
0209EXT1 | EXTERIOR FINISHES | 0209 | The exterior finishes are in poor condition with stucco cracking locations of stucco failure which will be addressed in a separate project. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is painting, staining, or other applied finishes, sealing and tuck pointing the masonry, minor concrete patching, and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2 - 3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project should be implemented after the REPAIR CONCRETE & STUCCO FASCIA project. | DMV OFFICE BUILDING (WEST WING) | 9906 | MtrVeh | B&G |  | Carson City | 1965 | 31500 | 2020-05-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 315000
0209SFT3 | ELECTRICAL SWITCHGEAR / TRANSFORMER MAINTENANCE | 0209 | The electrical switchgear and transformers appear to be more than 40 years old. This project would provide for an infrared thermography inspection and Arc Flash Study to be done on all of the electrical equipment including switchgear, transformers, and subpanels. This would determine the condition of the building's electrical system and its condition. This project is for an inspection only and does not include equipment upgrades or replacement. This project or a portion thereof was previously recommended in the FCA report dated 03/12/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/18/2020. | DMV OFFICE BUILDING (WEST WING) | 9906 | MtrVeh | B&G |  | Carson City | 1965 | 31500 | 2020-05-18 | Immediate to Two Years | Currently Critical | 1 | 15000
0209ADA2 | SPANDREL GLASS REPLACEMENT | 0209 | Multiple panels of Spandrel Glass are cracked on the south side of the bridge between the East and West Wings of the building. These glass panels should be replaced to ensure the exterior envelope integrity. This project would provide for the replacement of the glazing panels including caulking and / or sealing as needed. | DMV OFFICE BUILDING (WEST WING) | 9906 | MtrVeh | B&G |  | Carson City | 1965 | 31500 | 2020-05-18 | Immediate to Two Years | Currently Critical | 1 | 1500
0209HVA1 | HVAC EQUIPMENT REPLACEMENT | 0209 | The penthouse HVAC plant is reaching the end of its service life and should be scheduled for replacement. It is not energy efficient and has reached the end of its expected and useful life. The R-22 refrigerant in the cooling system is no longer EPA compliant and its production is mandated to be phased out completely by January 1, 2020. This project would provide for installation of a new HVAC central plant and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC system and all required connections to utilities. | DMV OFFICE BUILDING (WEST WING) | 9906 | MtrVeh | B&G |  | Carson City | 1965 | 31500 | 2020-05-18 | Four to Ten Years | Long-Term Needs | 3 | 1418000
0209ADA1 | ADA CANE DETECTION BARRIER INSTALLATION | 0209 | The stairwell in the atrium has an overhead hazard at the cane detection area under the stairs. This project recommends the installation of a permanent barrier under the stairs. IBC - 2018 Section 1012 and ADAAG 4.4.2 were referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 03/12/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/18/2020. | DMV OFFICE BUILDING (WEST WING) | 9906 | MtrVeh | B&G |  | Carson City | 1965 | 31500 | 2020-05-18 | Immediate to Two Years | Currently Critical | 1 | 1200
0209ENR3 | EXTERIOR LIGHTING REPLACEMENT | 0209 | The building has perimeter lighting on the exterior of the building. The light fixtures are an old incandescent type and not energy efficient. This project would provide for the replacement of the exterior lighting fixtures with new LED light fixtures using existing wiring. | DMV OFFICE BUILDING (WEST WING) | 9906 | MtrVeh | B&G |  | Carson City | 1965 | 31500 | 2020-05-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
0209EXT4 | ATRIUM STUCCO REPAIR | 0209 | The atrium exterior stucco finish has numerous areas that appear to be cracking. There is evidence of water infiltration on the south side of the building in the interior. This project would provide for the repair of the stucco finish including elastomeric painting of the repair areas. This project should be coordinated with the window replacement project. This project or a portion thereof was previously recommended in the FCA report dated 03/12/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/18/2020. | DMV OFFICE BUILDING (WEST WING) | 9906 | MtrVeh | B&G |  | Carson City | 1965 | 31500 | 2020-05-18 | Immediate to Two Years | Currently Critical | 1 | 5000
0209SFT4 | WATER HEATER SEISMIC BRACING | 0209 | The water heater is not properly seismically anchored to the structure. The 2018 IRC P2801.8 "...water heaters shall be anchored or strapped in the upper one-third and in the lower one-third of the appliance...". This project would provide funding for the installation of compliant seismic bracing. | DMV OFFICE BUILDING (WEST WING) | 9906 | MtrVeh | B&G |  | Carson City | 1965 | 31500 | 2020-05-18 | Immediate to Two Years | Currently Critical | 1 | 600
0210INT1 | INTERIOR FINISHES | 0210 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the 7 to 8 years and every 8 to 9 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | DMV OFFICE BUILDING ADDITION (EAST WING) | 9906 | MtrVeh | B&G |  | Carson City | 1980 | 56688 | 2020-05-18 | Four to Ten Years | Long-Term Needs | 3 | 255000
0210EXT1 | EXTERIOR FINISHES | 0210 | The stucco portion of the exterior finishes are in poor condition and need to be repaired. It is important to maintain the finish, weather resistance, and appearance of the building. This project includes items to protect the exterior building envelope, other than the roof, including sealing and tuck pointing the masonry, painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 2 to 3 years and is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | DMV OFFICE BUILDING ADDITION (EAST WING) | 9906 | MtrVeh | B&G |  | Carson City | 1980 | 56688 | 2020-05-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 51000
0209EXT3 | REPAIR CONCRETE & STUCCO FASCIA | 0209 | There is a concrete fascia along all sides of the building which are damaged. Reinforcing steel is exposed. This project would provide for the repair of the concrete fascia including stucco finish and / or sealing as needed. This project should be implemented prior to the EXTERIOR FINISHES project. This project or a portion thereof was previously recommended in the FCA report dated 03/12/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/18/2020. | DMV OFFICE BUILDING (WEST WING) | 9906 | MtrVeh | B&G |  | Carson City | 1965 | 31500 | 2020-05-18 | Immediate to Two Years | Currently Critical | 1 | 15000
4038INT1 | FLOORING REPLACEMENT | 4038 | The VCT (vinyl composite tile) and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the next 3-4 years. | SOUTH BUILDING (Leased) | 9777 | NA |  |  | Las Vegas | 1988 | 6599 | 2020-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 66253.96
4037ADA4 | CASEWORK REPLACEMENT | 4037 | The cabinets and countertops in the four classrooms are original to the building and have reached the end of their expected life. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and countertops are delaminating and failing. This project recommends the replacement of the existing countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2018, ICC/ANSI A117.1 and the most current version of the ADA Standards for Accessible Design should be incorporated into the design such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. | NORTH MAIN BUILDING (Leased) | 9777 | NA |  |  | Las Vegas | 1992 | 10990 | 2020-02-10 | Immediate to Two Years | Currently Critical | 1 | 40000
4038ADA3 | BREAK ROOM REMODEL | 4038 | The kitchenette and associated cabinets in the employee break room are original to the building and have reached the end of their expected life. The quality of construction and installation were inadequate for the high usage at this facility. This project recommends the replacement of the existing kitchen countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. Design of the kitchenette should be ADA compliant according to NRS 338.180, IBC - 2018, ICC/ANSI A117.1 and the most current version of the ADA Standards for Accessible Design should be incorporated into the design such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. | SOUTH BUILDING (Leased) | 9777 | NA |  |  | Las Vegas | 1988 | 6599 | 2020-02-10 | Immediate to Two Years | Currently Critical | 1 | 18600
4037INT4 | JANITORS CLOSET REPAIRS | 4037 | The mop sink in the Janitors Closet is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide FRP to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. Additionally, consideration should be taken to separate the wet location from the low voltage communication board and other misc. electrical items. | NORTH MAIN BUILDING (Leased) | 9777 | NA |  |  | Las Vegas | 1992 | 10990 | 2020-02-10 | Immediate to Two Years | Currently Critical | 1 | 5000
4037HVA2 | HVAC SERVER EQUIPMENT UPGRADE | 4037 | The HVAC unit cooling the Server Room has failed and a portable cooling unit has been installed. It is not energy efficient and has reached the end of its expected and useful life. This project would provide for the installation of a new HVAC split system. This project includes removal and disposal of the existing equipment, demolition, patching walls and all required connections to utilities. | NORTH MAIN BUILDING (Leased) | 9777 | NA |  |  | Las Vegas | 1992 | 10990 | 2020-02-10 | Immediate to Two Years | Currently Critical | 1 | 8500
4037HVA1 | HVAC EQUIPMENT REPLACEMENT | 4037 | There are 6 rooftop packaged HVAC units that are original (1992) to the building and are not energy efficient. The packaged HVAC units have been a continuing maintenance item requiring compressor and motor replacements. The packaged HVAC units have reached the end of their expected and useful life. This project would provide for the installation of four new 5 ton and two new 4 ton packaged HVAC units. Also included in this estimate is new curb adapters, roofing modifications, 100 feet of new condensate line, crane and rigging removal and installation and all required connections to utilities. Additional features to include economizer and DDC controls. This project should be implemented concurrently with the Roof Replacement project since the rooftop units need to be removed in order to replace the roof. | NORTH MAIN BUILDING (Leased) | 9777 | NA |  |  | Las Vegas | 1992 | 10990 | 2020-02-10 | Immediate to Two Years | Currently Critical | 1 | 66000
4037ADA3 | ADA RESTROOM UPGRADE | 4037 | The staff men's and women's designated ADA restrooms on the east side of the building are approaching the end of their expected life and should be scheduled for remodel. A complete retrofit is necessary. This project would provide funding for construction of two ADA accessible restrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2018 IBC, ICC/ANSI A117.1, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as a reference for this project. | NORTH MAIN BUILDING (Leased) | 9777 | NA |  |  | Las Vegas | 1992 | 10990 | 2020-02-10 | Immediate to Two Years | Currently Critical | 1 | 46650
4037INT3 | FLOORING REPLACEMENT | 4037 | The VCT (vinyl composite tile) and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the next 3-4 years. | NORTH MAIN BUILDING (Leased) | 9777 | NA |  |  | Las Vegas | 1992 | 10990 | 2020-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 110340
4037ADA2 | BREAK ROOM REMODEL | 4037 | The kitchenette and associated cabinets in the employee break room are original to the building and have reached the end of their expected life. The quality of construction and installation were inadequate for the high usage at this facility. This project recommends the replacement of the existing kitchen countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. Design of the kitchenette should be ADA compliant according to NRS 338.180, IBC - 2018, ICC/ANSI A117.1 and the most current version of the ADA Standards for Accessible Design should be incorporated into the design such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. | NORTH MAIN BUILDING (Leased) | 9777 | NA |  |  | Las Vegas | 1992 | 10990 | 2020-02-10 | Immediate to Two Years | Currently Critical | 1 | 25000
4037EXT2 | ROOF REPLACEMENT | 4037 | The rolled asphalt roof on the building is in poor condition and had active leaks at the time of the survey. It is recommended that this building be re-roofed in the next 1-2 years with a new single-ply roofing system. This will allow for the roof to qualify for the statewide roofing warranty and preventative maintenance agreement programs. This project should be implemented concurrently with the HVAC Equipment Replacement since the rooftop units need to be removed in order to replace the roof. | NORTH MAIN BUILDING (Leased) | 9777 | NA |  |  | Las Vegas | 1992 | 10990 | 2020-02-10 | Immediate to Two Years | Currently Critical | 1 | 206830
4037ADA1 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 4037 | This building contains water fountains that are not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | NORTH MAIN BUILDING (Leased) | 9777 | NA |  |  | Las Vegas | 1992 | 10990 | 2020-02-10 | Immediate to Two Years | Currently Critical | 1 | 4970
4037INT2 | GYPSUM BOARD REPAIR | 4037 | Roof leaks and moisture have damaged the gypsum board in the Janitor Closet / Laundry area. If the gypsum board is not removed and replaced, the moisture potentially could cause mold and dry-rot. This project recommends removing the gypsum board and replacing it. | NORTH MAIN BUILDING (Leased) | 9777 | NA |  |  | Las Vegas | 1992 | 10990 | 2020-02-10 | Immediate to Two Years | Currently Critical | 1 | 6220
4037EXT1 | EXTERIOR FINISHES | 4037 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NORTH MAIN BUILDING (Leased) | 9777 | NA |  |  | Las Vegas | 1992 | 10990 | 2020-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 137814.6
4038EXT3 | REPAIR/REPLACE FASCIA AND SOFFITS | 4038 | The fascia and the soffits around the building are showing rot, peeling, and are showing signs of considerable wear. This project would provide funding to repair the fascia and replace the soffits. Repairs include replacing if necessary, sanding, scraping, priming, painting, and roof repairs. | SOUTH BUILDING (Leased) | 9777 | NA |  |  | Las Vegas | 1988 | 6599 | 2020-02-10 | Immediate to Two Years | Currently Critical | 1 | 12536
9777SIT5 | HARDSCAPE PAVER REPLACEMENT | 9777 | Ponding water and staining on the concrete pavers indicates settlement and failure of the base supporting the pavers. This project addresses removal, regrading and compaction of the base and replacement of the pavers. 500 square feet was used for this estimate. | CAPABILITY HEALTH SITE (Leased) | 9777 | NA |  |  | Las Vegas | 0 |  | 2020-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
4037SFT1 | FIRE ALARM SYSTEM UPGRADE | 4037 | This building is equipped with an automatic fire detection and alarm system that no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 "If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure." When completed, the new system will provide visual, as well as audible notification, in accordance with the 2018 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | NORTH MAIN BUILDING (Leased) | 9777 | NA |  |  | Las Vegas | 1992 | 10990 | 2020-02-10 | Immediate to Two Years | Currently Critical | 1 | 55170
4037INT1 | INTERIOR FINISHES | 4037 | It is recommended to paint the interior walls and ceilings at least once in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | NORTH MAIN BUILDING (Leased) | 9777 | NA |  |  | Las Vegas | 1992 | 10990 | 2020-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 137814
4038SFT2 | FIRE SUPPRESSION SYSTEM INSTALLATION | 4038 | This building does not have an automatic fire suppression system. It should be retrofitted with fire sprinklers during the next remodel or addition. This project would provide funding for the installation of fire sprinklers including backflow prevention devices. | SOUTH BUILDING (Leased) | 9777 | NA |  |  | Las Vegas | 1988 | 6599 | 2020-02-10 | Immediate to Two Years | Currently Critical | 1 | 115878.44
4038HVA1 | HVAC EQUIPMENT REPLACEMENT | 4038 | There are 5 rooftop packaged HVAC units that are original (1988) to the building and are not energy efficient. The packaged HVAC units have been a continuing maintenance item requiring compressor and motor replacements and have reached the end of their expected and useful life. This project would provide for the installation of five new HVAC units. Also included in this estimate is new curb adapters, roofing modifications, 100 feet of new condensate line, crane and rigging removal and installation and all required connections to utilities. Additional features to include, economizer and DDC controls. This project should be implemented concurrently with the Roof Replacement project since the rooftop units need to be removed in order to replace the roof. | SOUTH BUILDING (Leased) | 9777 | NA |  |  | Las Vegas | 1988 | 6599 | 2020-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 40000
9777SIT4 | CRACK FILL & SEAL ASPHALT PAVING | 9777 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the paving in the West parking area. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 8,900 square feet of asphalt area was used to generate this estimate. | CAPABILITY HEALTH SITE (Leased) | 9777 | NA |  |  | Las Vegas | 0 |  | 2020-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 13973
9777ADA1 | ADA PARKING SPACE UPGRADES | 9777 | The ADA provides for accessibility to sites and services for people with physical limitations. The existing ADA parking spaces do not entirely meet the requirements of the code. This project provides funding to bring the 10 ADA parking spaces up to code including removal of the asphalt and replacement with concrete, updated signage, re-striping, re-grading and any other necessary upgrades. The 2018 IBC, ICC/ANSI A117.., NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as a reference for this project. | CAPABILITY HEALTH SITE (Leased) | 9777 | NA |  |  | Las Vegas | 0 |  | 2020-02-10 | Immediate to Two Years | Currently Critical | 1 | 87000
9777ADA2 | ADA SIDEWALK REPLACEMENT | 9777 | The concrete sidewalks near the buildings are failing in some areas, partially due to vehicular traffic. This project would provide for the removal and replacement of the concrete sidewalks. 500 SF of 4" thick concrete was used for this estimate. The 2018 IBC, ICC/ANSI A117.1, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as a reference for this project. | CAPABILITY HEALTH SITE (Leased) | 9777 | NA |  |  | Las Vegas | 0 |  | 2020-02-10 | Immediate to Two Years | Currently Critical | 1 | 9410
9777SIT2 | ASPHALT REPLACEMENT | 9777 | The main (East) parking area asphalt for the site is failing, with significant alligatoring, settling and cracks observed. This project covers the removal and replacement of the existing asphalt for parking and site access. Striping for safety, parking and loading zones is included in this estimate. 23,000 square feet was used to generate this estimate. | CAPABILITY HEALTH SITE (Leased) | 9777 | NA |  |  | Las Vegas | 0 |  | 2020-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 212060
9777SIT1 | TRIM OR REMOVE TREES ADJOINING BUILDINGS | 9777 | There are trees that are in need of trimming and / or removal to prevent damage to the canopy roof structure. This project would provide for the trimming and / or removal of the trees along the Canopy Building Connector. | CAPABILITY HEALTH SITE (Leased) | 9777 | NA |  |  | Las Vegas | 0 |  | 2020-02-10 | Immediate to Two Years | Currently Critical | 1 | 3500
9777SIT3 | EXTERIOR LIGHTING REPLACEMENT | 9777 | The eight light poles around the site have a total of nine light fixtures. These are non-LED fixtures (possibly HPS) retrofitted with failing LED lamps. In addition, the change to LED lamps may have adversely affected the light output (photometrics) and may not provide adequate night lighting. This project would provide for the replacement of the exterior lighting fixtures with new LED light fixtures and lamps, using existing wiring and poles. | CAPABILITY HEALTH SITE (Leased) | 9777 | NA |  |  | Las Vegas | 0 |  | 2020-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16740
4039EXT1 | EXTERIOR FINISHES | 4039 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is repairing damaged areas of stucco, power washing, priming and painting. It is recommended that the building be repaired and painted in the next 3 - 4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CANOPY BUILDING CONNECTOR (Leased) | 9777 | NA |  |  | Las Vegas | 1992 | 1141 | 2020-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14308
4038INT3 | GYPSUM BOARD REPAIR | 4038 | Water leaks above the ceiling have damaged the gypsum board in multiple locations. If the gypsum board is not removed and replaced, the moisture potentially could cause mold and dry rot. This project recommends removing the gypsum board, inspecting and fixing the source of the leaks, replacing the drywall, patching and painting. | SOUTH BUILDING (Leased) | 9777 | NA |  |  | Las Vegas | 1988 | 6599 | 2020-02-10 | Immediate to Two Years | Currently Critical | 1 | 12000
4038SFT1 | FIRE ALARM SYSTEM INSTALLATION | 4038 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2009 Section 7 and the 2012 International Fire Code. | SOUTH BUILDING (Leased) | 9777 | NA |  |  | Las Vegas | 1988 | 6599 | 2020-02-10 | Immediate to Two Years | Currently Critical | 1 | 33126
4038EXT2 | ROOF REPLACEMENT | 4038 | The asphalt composition shingle and rolled asphalt roof systems on this building were in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 3-4 years. The project scope includes removal and disposal, new underlayment as required, 50 year asphalt composition shingles, and PVC single ply membrane for low slope areas. This project should be implemented concurrently with the HVAC Equipment Replacement since the rooftop units need to be removed from the roof in order to replace the roof. | SOUTH BUILDING (Leased) | 9777 | NA |  |  | Las Vegas | 1988 | 6599 | 2020-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 124193
4038ADA1 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 4038 | This building contains water fountains that are not ADA compliant. The 2018 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | SOUTH BUILDING (Leased) | 9777 | NA |  |  | Las Vegas | 1988 | 6599 | 2020-02-10 | Immediate to Two Years | Currently Critical | 1 | 4970
4038INT4 | JANITORS CLOSET REPAIRS | 4038 | The mop sink in the Janitors Closet is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide FRP to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. Additionally, consideration should be taken to separate the wet location from the low voltage communication board and other misc. electrical items. | SOUTH BUILDING (Leased) | 9777 | NA |  |  | Las Vegas | 1988 | 6599 | 2020-02-10 | Immediate to Two Years | Currently Critical | 1 | 5000
4038INT2 | INTERIOR FINISHES | 4038 | It is recommended to paint the interior walls and ceilings at least once in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SOUTH BUILDING (Leased) | 9777 | NA |  |  | Las Vegas | 1988 | 6599 | 2020-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 82751
4038ADA2 | ADA RESTROOM UPGRADE | 4038 | The staff men's and women's designated ADA restrooms on the south side of the building do not meet ADA requirements and they are approaching the end of their expected life and should be scheduled for remodel. A complete retrofit is necessary. This project would provide funding for construction of two accessible restrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2018 IBC, ICC/ANSI A117.1, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as a reference for this project. | SOUTH BUILDING (Leased) | 9777 | NA |  |  | Las Vegas | 1988 | 6599 | 2020-02-10 | Immediate to Two Years | Currently Critical | 1 | 31100
4038ELE1 | ELECTRICAL UPGRADE | 4038 | The main electrical meter and breaker panel at this facility are recognized as a safety hazard and should be replaced. Zinsco panels were part of a safety recall; however, Zinsco is no longer in business. This project would provide funding for the installation of a replacement meter/ breaker panel including removal and disposal. | SOUTH BUILDING (Leased) | 9777 | NA |  |  | Las Vegas | 1988 | 6599 | 2020-02-10 | Immediate to Two Years | Currently Critical | 1 | 7500
4039EXT2 | ROOF REPAIRS | 4039 | Clay tile roofs are especially susceptible to damage from walking on tiles, from fallen tree limbs or other objects. This project would provide funding for the removal and replacement of broken tile. | CANOPY BUILDING CONNECTOR (Leased) | 9777 | NA |  |  | Las Vegas | 1992 | 1141 | 2020-02-10 | Immediate to Two Years | Currently Critical | 1 | 870
4038EXT1 | EXTERIOR SIDING REPLACEMENT | 4038 | The building has painted masonite siding that is due for replacement. The existing siding is in poor condition and it appears that the siding was not installed with the proper clearance to grade. This same issue occurs on the roof where there are vertical changes in roof elevation. This project recommends removing the siding and replacing it according to the manufacturer's specifications. Project funding amount has been adjusted upward to account for unforeseen work scope not obvious during a visual inspection. Specifically, the north unpainted extension of the structure does not appear Code compliant. This project also includes all necessary weather caulking, primer and paint. | SOUTH BUILDING (Leased) | 9777 | NA |  |  | Las Vegas | 1988 | 6599 | 2020-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 165568
1478ADA1 | ADA ACCESSIBLE COUNTER | 1478 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. There are two offices that have a service counter for the public to approach which do not meet current codes. Section 7.2 of the Americans with Disabilities Act Accessible Guidelines (ADAAG) states that the counter must have a portion which is at least 36" in length with a maximum height of 36" above the finish floor. This project will provide an accessible counter space for each of these offices in accordance with this requirement. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 08/14/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/14/2011. | SUPREME COURT | 9865 | NevJud | B&G |  | Carson City | 1991 | 118900 | 2021-01-26 | Immediate to Two Years | Currently Critical | 1 | 2000
1478INT3 | INSTALL FRP IN JANITOR'S CLOSET | 1478 | The mop sink in the Janitor's Closet is mounted adjacent to gypsum board that may cause water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | SUPREME COURT | 9865 | NevJud | B&G |  | Carson City | 1991 | 118900 | 2021-01-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
1478ENR2 | HVAC UPGRADE | 1478 | The central HVAC system in the building was installed in 1991. The equipment is not energy efficient and will be reaching the end of its expected and useful life within the next 10 years. This project would provide for installation of a new HVAC system including boilers, chillers, air handlers, fan coil units, water treatment, all associated equipment and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 08/14/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/14/2011. | SUPREME COURT | 9865 | NevJud | B&G |  | Carson City | 1991 | 118900 | 2021-01-26 | Four to Ten Years | Long-Term Needs | 3 | 2972500
1478SFT1 | ROOF SNOWMELT & SNOW RETAINMENT SYSTEM | 1478 | This building has a sloped metal roof with a snow melt and gutter system to capture rain water and retain snow from sliding off the roof. The existing snow guards have been sheared off in most locations causing snow to fall from the roof onto pedestrian walkways. This project would provide for the replacement of the snow melt system and installation of snow guards on the metal roofing system. This project or a portion thereof was previously recommended in the FCA report dated 08/14/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/14/2011. | SUPREME COURT | 9865 | NevJud | B&G |  | Carson City | 1991 | 118900 | 2021-01-26 | Immediate to Two Years | Currently Critical | 1 | 95000
1478ADA2 | ADA SIGNAGE | 1478 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 08/14/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/14/2011. | SUPREME COURT | 9865 | NevJud | B&G |  | Carson City | 1991 | 118900 | 2021-01-26 | Immediate to Two Years | Currently Critical | 1 | 6000
1478EXT1 | EXTERIOR FINISHES | 1478 | It is important to maintain the finish, weather resistance, and appearance of the building. This project recommends work to protect the exterior building envelope other than the roof, including sealing the concrete precast panels, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SUPREME COURT | 9865 | NevJud | B&G |  | Carson City | 1991 | 118900 | 2021-01-26 | Four to Ten Years | Long-Term Needs | 3 | 594500
1478INT2 | REPLACE RESTROOM FLOORING | 1478 | One of the ADA accessible restrooms on the second floor is damaged. This project would provide for the removal of the existing vinyl composition tile (VCT) and replacement with a new VCT floor in one restroom. | SUPREME COURT | 9865 | NevJud | B&G |  | Carson City | 1991 | 118900 | 2021-01-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 800
1478EXT2 | REPLACE MEMBRANE ROOF | 1478 | The existing single-ply roofing system is original to the construction of the building and should be scheduled for replacement in the next two years. The State wide roofing program's warranty is 15 years and has expired. This project would provide for the removal of the existing single-ply membrane and replacement with a new single-ply roofing system. 10,000 square feet of area was used to generate this estimate. | SUPREME COURT | 9865 | NevJud | B&G |  | Carson City | 1991 | 118900 | 2021-01-26 | Immediate to Two Years | Currently Critical | 1 | 120000
1478PLM1 | REPLACE TOILET FIXTURES | 1478 | The justices' restrooms date to the original construction of the building. The toilets are first-generation, water saving tank-flush models. Due to variations in the water pressure and other concerns, several of the toilets have had to be replaced. This project recommends the replacement of the remaining fixtures with new, pressure-assisted, low-gallonage models. This project or a portion thereof was previously recommended in the FCA report dated 08/14/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/14/2011. | SUPREME COURT | 9865 | NevJud | B&G |  | Carson City | 1991 | 118900 | 2021-01-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
1478ENR1 | WATER HEATER REPLACEMENT | 1478 | The two 80 gallon gas fired water heaters are older units and should be scheduled for replacement. The average life span is 8-10 years. This project would provide for the installation of 2 new natural gas fired water heaters including seismic strapping and connections to utilities. Removal and disposal of the old units is included in this estimate. | SUPREME COURT | 9865 | NevJud | B&G |  | Carson City | 1991 | 118900 | 2021-01-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
1478INT1 | INTERIOR FINISHES | 1478 | The interior finishes are in good condition. This project would provide for the cyclical maintenance of the interior finishes including painting, staining, and any required cleaning and preparation of surfaces prior to the application of the finishes to maintain the integrity of the interior walls and ceilings including wood surfaces. | SUPREME COURT | 9865 | NevJud | B&G |  | Carson City | 1991 | 118900 | 2021-01-26 | Four to Ten Years | Long-Term Needs | 3 | 594500
9865SFT1 | SIDEWALK REPLACEMENT | 9865 | Some of the sidewalks serving the site and building entrances are deteriorated and beginning to fail in several areas. Most of the work needs to be done on the west side of the site where there is extensive spalling and some settling. A few sections have deteriorated enough to expose the reinforcing metal and the settling has created a tripping hazard. This project addresses removal and replacement of existing sidewalks as needed. 5,000 SF of 4" thick concrete sidewalk was used for this estimate. | SUPREME COURT SITE | 9865 | NevJud | B&G |  | Carson City | 0 |  | 2021-01-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
9865ADA1 | ADA SIGNAGE | 9865 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The site signage is not fully ADA compliant. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | SUPREME COURT SITE | 9865 | NevJud | B&G |  | Carson City | 0 |  | 2021-01-26 | Immediate to Two Years | Currently Critical | 1 | 2500
9865SIT1 | PLANTER REPAIRS | 9865 | There are many built-in planters around the building. Several of them leak due to failed waterproof membranes and cracks in the concrete. There are also broken irrigation lines and areas with no vegetation. This project would provide for a general refurbishment of the planters including removing the existing dirt, fixing the cracks and irrigation lines, installing new waterproof membranes, filling the dirt back in and installing new plantings if desired. | SUPREME COURT SITE | 9865 | NevJud | B&G |  | Carson City | 0 |  | 2021-01-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
9865SIT2 | TERRACE REPAIRS | 9865 | The terrace on the southwest side of the site has a damaged waterproof membrane. Water is penetrating the membrane and leaking into the basement of the building below. Evidence of leaking can be seen in the mechanical room which may damage the walls, floor, and equipment. This project would provide for a general refurbishment of the terrace waterproof membrane including removing the existing stone tiles, repairing the substrate, caulking all penetrations, and reinstalling the tile. | SUPREME COURT SITE | 9865 | NevJud | B&G |  | Carson City | 0 |  | 2021-01-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
2566ADA0 | ACCESSIBLE BUILDING ENTRANCE | 2566 | The building has steps leading into the main entrance. The entrance does not meet the requirements for ADA Accessibility ICC/ANSI A117.1-1998 404.2.4.1. The entry door has a threshold and hardware that does not meet the requirements for ADA accessibility, ICC/ANSI A117.1-1998 404.2.5. This project would provide funding for an accessible ramp, including upper and lower landing areas, handrails, curbing, and replacement of the door hardware and threshold to meet the ADA Accessibility Guidelines. The ramp construction used in this estimate is metal and would be considered a portable type ramp. | MOAPA/MESQUITE NHP OFFICE | 9873 | PubSafe | NHP |  | Moapa | 2000 | 720 | 2006-03-21 | Immediate to Two Years | Currently Critical | 1 | 15000
2463SFT1 | HANDRAIL INSTALLATION | 2463 | The 2003 International Building Code 1009.11 requires handrails on each side of stairways. The building has a set of stairs to access the residence on the north side and south side which do not have handrails. This project would provide for the purchase and installation of handrails on each side of the stairways. | MOAPA/MESQUITE NHP RESIDENCE | 9873 | PubSafe | NHP |  | Moapa | 0 | 1440 | 2006-03-21 | Immediate to Two Years | Currently Critical | 1 | 4000
2566EXT1 | SKIRTING | 2566 | The skirting around the module building protects the pipes and fixtures from the elements, reduces updrafts, helps controls moisture and reduces energy costs. The building does not have skirting around the perimeter. This project would provide for the purchase and installation of skirting around the modular office trailer. This project includes painting to match existing conditions. | MOAPA/MESQUITE NHP OFFICE | 9873 | PubSafe | NHP |  | Moapa | 2000 | 720 | 2006-03-21 | Four to Ten Years | Long-Term Needs | 3 | 14400
9873ADA1 | ADA PARKING AND SIGNAGE | 9873 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. A parking area, an adjacent passenger loading area and signage are necessary to comply with ADA requirements. This project would provide for one ADA accessible parking space, including an adjacent passenger loading zone in the existing paved parking area. The project includes signage, striping and marking an accessible route of travel to the building. | MOAPA/MESQUITE NHP SUBSTATION SITE | 9873 | PubSafe | NHP |  | Moapa | 0 |  | 2006-03-21 | Immediate to Two Years | Currently Critical | 1 | 3000
9851SIT3 | REPLACE DAMAGED CONCRETE WALKWAYS | 9851 | The concrete walkways from the parking lot to the main entrance and the concrete walk along the east side of the building are damaged from freeze / thaw cycles and ice melting chemicals. This project would provide for the removal and replacement of the concrete walkway including disposal of the existing concrete. 400 square feet of concrete was used to generate this estimate. | DPS TRAINING FACILITY SITE | 9851 | PubSafe | NHP |  | Carson City | 0 |  | 2011-12-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
9851SIT2 | TREE REMOVAL | 9851 | There is a large tree on the south side of the building which has shallow roots that may cause damage to the foundation of the building as it continues to grow. This project would provide for the removal of the tree to prevent damage to the building's foundation. | DPS TRAINING FACILITY SITE | 9851 | PubSafe | NHP |  | Carson City | 0 |  | 2011-12-01 | Four to Ten Years | Long-Term Needs | 3 | 2500
9851SIT1 | SLURRY SEAL PAVING | 9851 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site wide including access roads and parking areas. Striping is included in this estimate. This project should be scheduled on a 4- 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 40,000 square feet of asphalt area was used to generate this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/20/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/01/2011. | DPS TRAINING FACILITY SITE | 9851 | PubSafe | NHP |  | Carson City | 0 |  | 2011-12-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24000
9851SIT4 | PAINT LIGHT POLES | 9851 | There are two light poles in the parking area that are in need of painting. This project would provide for painting of the two light poles including sanding and prep as required. | DPS TRAINING FACILITY SITE | 9851 | PubSafe | NHP |  | Carson City | 0 |  | 2011-12-01 | Four to Ten Years | Long-Term Needs | 3 | 200
9851EXT1 | RELOCATE IRRIGATION SYSTEM | 9851 | The irrigation system is currently wetting the north and south sides of the building and is causing damage to the concrete masonry units (CMU). This may lead to water infiltration into the building. This project would relocate the sprinklers and lawn away from the building and install 36' wide mow strip next to the building along the north and south sides of the building where the lawn abuts the CMU. This project or a portion thereof was previously recommended in the FCA report dated 09/20/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/01/2011. | DPS TRAINING FACILITY SITE | 9851 | PubSafe | NHP |  | Carson City | 0 |  | 2011-12-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0898EXT4 | REPAIR ROOF SCUPPER DOWN SPOUTS | 0898 | The existing down spouts at the roof scupper locations terminate right at grade and / or were missing the last section. The current configuration encourages water to pool up beside the building foundation and CMU walls. This project would provide for repair of the existing down spouts and extend all of them to a drywell away from the building. | DPS TRAINING FACILITY | 9851 | PubSafe | NHP |  | Carson City | 1985 | 11000 | 2011-12-01 | Immediate to Two Years | Currently Critical | 1 | 2500
0898ENR1 | REPLACE WINDOWS | 0898 | The existing dual pane fixed windows are original to the building and are showing signs of failure. Some of the seals have failed and is allowing moisture in between the glazing panels. These old units are no longer energy efficient and should be scheduled for replacement. This project would provide for 34 new energy efficient dual pane window units including frames. Removal and disposal of the old units are included in this estimate. | DPS TRAINING FACILITY | 9851 | PubSafe | NHP |  | Carson City | 1985 | 11000 | 2011-12-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 57800
0898SFT1 | INSTALL GFCI OUTLETS | 0898 | There is one GFCI duplex outlet in a restroom that is broken and two more duplex outlets that need to be GFCI per the 2005 NEC. This project would provide for the installation of three GFCI duplex outlets in the restrooms. | DPS TRAINING FACILITY | 9851 | PubSafe | NHP |  | Carson City | 1985 | 11000 | 2011-12-01 | Immediate to Two Years | Currently Critical | 1 | 150
0898EXT3 | REPLACE ROOF | 0898 | The single-ply roof on this building was in good condition at the time of the survey. This existing roof was installed in about 2000. The statewide roofing program estimates the useful life of an average roof at 20 years. The 15 year roof warranty expires at the end of the this time frame. This building should be schedules for replacement in the next nine years to be consistent with the statewide roofing program guidelines and the warranty period. | DPS TRAINING FACILITY | 9851 | PubSafe | NHP |  | Carson City | 1985 | 11000 | 2011-12-01 | Four to Ten Years | Long-Term Needs | 3 | 110000
0898EXT2 | EXTERIOR FINISHES | 0898 | It is important to maintain the finish, weather resistance and appearance of the building. This project includes items to protect the exterior building envelope other than the roof, including painting, staining, or other applied finishes to the CMU, and sealant and gaskets in and around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. This project or a portion thereof was previously recommended in the FCA report dated 09/20/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/01/2011. | DPS TRAINING FACILITY | 9851 | PubSafe | NHP |  | Carson City | 1985 | 11000 | 2011-12-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 55000
0898EXT1 | REPLACE EXTERIOR DOORS | 0898 | The east and west exterior metal doors are damaged from heavy use and the hardware and weather stripping are showing signs of wear. This project would provide for two new metal door assemblies including hardware. Painting and removal / disposal of existing door assemblies is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/20/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/01/2011. | DPS TRAINING FACILITY | 9851 | PubSafe | NHP |  | Carson City | 1985 | 11000 | 2011-12-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5400
0898INT4 | PAINT INTERIOR FINISHES | 0898 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next four to five years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/20/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/01/2011. | DPS TRAINING FACILITY | 9851 | PubSafe | NHP |  | Carson City | 1985 | 11000 | 2011-12-01 | Four to Ten Years | Long-Term Needs | 3 | 55000
0898ADA1 | INSTALL ADA SIGNAGE | 0898 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) were referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/20/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/01/2011. | DPS TRAINING FACILITY | 9851 | PubSafe | NHP |  | Carson City | 1985 | 11000 | 2011-12-01 | Immediate to Two Years | Currently Critical | 1 | 1500
2462ADA3 | ADA PARKING AND SIGNAGE | 2462 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. A parking area, an adjacent passenger loading area and signage are necessary to comply with ADA requirements. This project would provide for one parking space, including an adjacent accessible loading zone in the existing gravel parking area. The project includes required soil preparation, an asphalt parking area for one vehicle, signage, striping and marking an accessible route of travel to the building. | INDIAN SPRINGS NHP SUBSTATION | 9829 | PubSafe | NHP |  | Indian Springs | 2002 | 720 | 2013-06-05 | Immediate to Two Years | Currently Critical | 1 | 12000
2462ADA1 | ACCESSIBLE BUILDING ENTRANCE | 2462 | The building has steps leading into the main entrance. The entrance does not meet the requirements for ADA Accessibility ICC/ANSI A117.1-1998 404.2.4.1. The entry door has a threshold and hardware that does not meet the requirements for ADA accessibility, ICC/ANSI A117.1-1998 404.2.5. This project would provide funding for an accessible ramp, including upper and lower landing areas, handrails, curbing, and replacement of the door hardware and threshold to meet the ADA Accessibility Guidelines. | INDIAN SPRINGS NHP SUBSTATION | 9829 | PubSafe | NHP |  | Indian Springs | 2002 | 720 | 2013-06-05 | Immediate to Two Years | Currently Critical | 1 | 30000
2462ELE1 | MISCELLANEOUS ELECTRICAL REPAIRS | 2462 | The exterior receptacles are standard duplex receptacles and there are missing safety plugs in the main electrical panel, which is mounted to a telephone pole adjacent to the building. This project would provide funding to install GFIC duplex outlets on the exterior and install safety plugs in the main electrical service including a lock to prevent the public from tampering with the electrical service. | INDIAN SPRINGS NHP SUBSTATION | 9829 | PubSafe | NHP |  | Indian Springs | 2002 | 720 | 2013-06-05 | Immediate to Two Years | Currently Critical | 1 | 1000
2462ADA2 | ADA RESTROOM REMODEL | 2462 | A restroom is present in this building. It does not meet the Americans with Disabilities Act (ADA) regulations. A retrofit is necessary to comply with CABO/ANSI A117.1-1998 Chapter 6 and 2003 IBC Chapter 11. This project would provide funding for construction of a unisex accessible restroom. This project may require a new toilet, grab bars, sink, faucet and hardware. | INDIAN SPRINGS NHP SUBSTATION | 9829 | PubSafe | NHP |  | Indian Springs | 2002 | 720 | 2013-06-05 | Immediate to Two Years | Currently Critical | 1 | 10000
0989ADA5 | ADA ACCESSIBLE COUNTER | 0989 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The entrance to the Traffic Safety Office and the Investigations Office have service counters for the public to approach which do not meet current requirements. Section 904.4 of the ADA Standards For Accessible Design states that a portion of the counter surface that is 36" long minimum and 36" high maximum above the finish floor shall be provided. This project will provide an accessible counter space in accordance with this requirement for each office. The 2018 IBC, ICC/ANSI A117.1, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #107 STATE FIRE MARSHAL | 9971 | PubSafe | FireMars |  | Stewart | 1963 | 32832 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 2400
0989SFT5 | WATER HEATER SEISMIC BRACING | 0989 | The water heater is not seismically anchored to the structure. This project would provide funding for seismic bracing of the water heater to the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #107 STATE FIRE MARSHAL | 9971 | PubSafe | FireMars |  | Stewart | 1963 | 32832 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 200
0989ADA3 | ADA RESTROOM UPGRADE | 0989 | The designated Men's and Women's ADA accessible restrooms are not fully compliant. The flush handle is on the wrong side, the toilet paper dispenser is not in the correct location, and it is missing a grab bar. A partial retrofit is necessary. This project would provide funding to bring the restroom into full ADA compliance. The 2018 IBC, ICC/ANSI A117.1, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #107 STATE FIRE MARSHAL | 9971 | PubSafe | FireMars |  | Stewart | 1963 | 32832 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 4800
0989ENR2 | WINDOW REPLACEMENT | 0989 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 67 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #107 STATE FIRE MARSHAL | 9971 | PubSafe | FireMars |  | Stewart | 1963 | 32832 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50300
0989SFT4 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0989 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2018 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #107 STATE FIRE MARSHAL | 9971 | PubSafe | FireMars |  | Stewart | 1963 | 32832 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 20000
0989INT1 | INTERIOR FINISHES | 0989 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 5 - 6 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | #107 STATE FIRE MARSHAL | 9971 | PubSafe | FireMars |  | Stewart | 1963 | 32832 | 2020-02-07 | Four to Ten Years | Long-Term Needs | 3 | 98500
0989SIT1 | DRAINAGE UPGRADES | 0989 | The building has a drainage problem near the Traffic Safety Office's entrance where grade does not properly slope away from the building. Rain water accumulates in several areas adjacent to the building, creating a water problem which may infiltrate the interior during inclement weather. This project would create positive flow away from the building by regrading, paving and installing additional drainage swales as needed. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #107 STATE FIRE MARSHAL | 9971 | PubSafe | FireMars |  | Stewart | 1963 | 32832 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0989EXT3 | GUTTER INSTALLATION | 0989 | The building does not have continuous gutters to control the runoff from the roof. The existing gutters and downspouts are only installed at exits. The water currently sheet drains off the roof causing extensive erosion to the built-up dirt slope around the foundation. This will eventually lead to failure of the foundation undermining the integrity of the entire structure. This project would provide funding for the installation of a seamless gutter and downspout system for the building. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #107 STATE FIRE MARSHAL | 9971 | PubSafe | FireMars |  | Stewart | 1963 | 32832 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 42000
0989INT2 | JANITORS CLOSET REPAIRS | 0989 | The mop sinks in the Janitors Closets are mounted adjacent to gypsum board and are showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. This is recommended for two Janitors Closets. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #107 STATE FIRE MARSHAL | 9971 | PubSafe | FireMars |  | Stewart | 1963 | 32832 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2800
0989ADA1 | ADA SIGNAGE | 0989 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2018 IBC, ICC/ANSI A117.1, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #107 STATE FIRE MARSHAL | 9971 | PubSafe | FireMars |  | Stewart | 1963 | 32832 | 2020-02-07 | Immediate to Two Years | Currently Critical | 1 | 6000
0989HVA2 | EXHAUST FAN REPLACEMENT | 0989 | The existing exhaust fans that serve the restrooms are original equipment and are not providing adequate ventilation. Some of them were inoperable at the time of the survey. This project would provide for the removal of the existing exhaust fan assemblies and the purchase and installation of new exhaust fan assemblies including connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2020. | #107 STATE FIRE MARSHAL | 9971 | PubSafe | FireMars |  | Stewart | 1963 | 32832 | 2020-02-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
0989EXT1 | EXTERIOR FINISHES | 0989 | The exterior finishes are in good condition. It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting the stucco and wood, sealing the brick masonry and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 8 -9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | #107 STATE FIRE MARSHAL | 9971 | PubSafe | FireMars |  | Stewart | 1963 | 32832 | 2020-02-07 | Four to Ten Years | Long-Term Needs | 3 | 164200
1682EXT2 | EXTERIOR FINISHES | 1682 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete and brick masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | REGIONAL HQ GARAGE/SHOP | 9923 | PubSafe | NHP | B&G | Reno | 1994 | 4900 | 2021-01-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24500
1682PLM1 | WATER HEATER REPLACEMENT | 1682 | There is a 15 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | REGIONAL HQ GARAGE/SHOP | 9923 | PubSafe | NHP | B&G | Reno | 1994 | 4900 | 2021-01-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
1682INT1 | INTERIOR FINISHES | 1682 | The interior finishes are in fair condition. The walls and ceilings are mostly unfinished concrete and brick masonry, but some rooms are finished with painted gypsum board. It is recommended that the finished interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | REGIONAL HQ GARAGE/SHOP | 9923 | PubSafe | NHP | B&G | Reno | 1994 | 4900 | 2021-01-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4900
1682ADA2 | ADA RESTROOM REMODEL | 1682 | The existing accessible restroom does not fully meet the Americans with Disabilities Act (ADA) requirements. This project would provide for minor modifications to the existing restroom including flush handle relocation, sink and fixture modifications and accessory mounted location modifications. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | REGIONAL HQ GARAGE/SHOP | 9923 | PubSafe | NHP | B&G | Reno | 1994 | 4900 | 2021-01-12 | Immediate to Two Years | Currently Critical | 1 | 5000
1682ADA1 | ADA SIGNAGE | 1682 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | REGIONAL HQ GARAGE/SHOP | 9923 | PubSafe | NHP | B&G | Reno | 1994 | 4900 | 2021-01-12 | Immediate to Two Years | Currently Critical | 1 | 750
1682HVA1 | VEHICLE EXHAUST EXTRACTION SYSTEM | 1682 | The vehicle maintenance garages have no exhaust extraction system to remove toxic exhaust fumes. In enclosed areas where motor vehicles operate, mechanical ventilation shall be provided per the 2006 IBC 406.6.3 and UMC 502.14. This project would provide for the purchase and installation of a vehicle exhaust extraction system in two garage bays including, hoses, automatic shut off, electrical connections and roof mounted exhaust fans and equipment as provided and / or required by the manufacturer. | REGIONAL HQ GARAGE/SHOP | 9923 | PubSafe | NHP | B&G | Reno | 1994 | 4900 | 2021-01-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
9923SIT2 | SLURRY SEAL ASPHALT PAVING | 9923 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site wide including access roads, parking areas and the maintenance yard. Striping is included in this estimate. The rear parking lot is extremely tight which has caused numerous minor vehicle accidents. It may be beneficial to redesign the flow of the parking lot and striping pattern. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 60,000 square feet of asphalt area was used to generate this estimate. This project or a portion thereof was previously recommended in the FCA report dated 07/15/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/19/2011. | RENO NHP HQ SITE | 9923 | PubSafe | NHP | B&G | Reno | 1994 |  | 2021-01-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 45000
9923ADA1 | ADA ACCESSIBLE PATH OF TRAVEL | 9923 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. A path of travel from the public street to the accessible public entrance of the building is necessary to comply with ADA accessibility requirements. This project would provide for a concrete walkway from the existing sidewalk to the building. This will require regrading, placement of P.C. concrete, installing a ramp with compliant handrails, signage, striping and any other necessary upgrades. The 2006 IBC, ICC/ANSI A117.1 - 2003 and the most current version of the Americans With Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | RENO NHP HQ SITE | 9923 | PubSafe | NHP | B&G | Reno | 1994 |  | 2021-01-12 | Immediate to Two Years | Currently Critical | 1 | 50000
9923SIT3 | GATE OPERATOR REPLACEMENT | 9923 | The site has a perimeter fence with two automatic vehicle access gates off of Hammill Lane and Kietzke Lane. The gate operators are malfunctioning, have been problematic, and have difficulty opening and closing the gates. This project recommends replacing the two gate operators with high quality operators that can handle heavy traffic as well as servicing the gates and related hardware to ensure prolonged operation. The gate operators will be required to meet UL Standard 325, per NRS 405.270. | RENO NHP HQ SITE | 9923 | PubSafe | NHP | B&G | Reno | 1994 |  | 2021-01-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
9923SIT4 | FENCE REPAIRS | 9923 | The painted wrought iron perimeter fence is in need of repairs. The entire fence is due for painting and there are some areas where the iron tubing has split open. Allowing moisture inside the tubing will cause premature deterioration from rusting and corrosion. This project would provide for painting of the fence and repair or replacement of damaged sections of fencing. 300 lineal feet of fencing was used for this estimate. | RENO NHP HQ SITE | 9923 | PubSafe | NHP | B&G | Reno | 1994 |  | 2021-01-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
0056INT1 | FLOORING REPLACEMENT | 0056 | The carpet throughout the building is showing signs of extreme wear. It is recommended that the carpet be replaced with heavy duty commercial grade carpet in the next 2-3 years. This project or a portion thereof was previously recommended in the FCA report dated 07/15/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/19/2011. | NHP REGIONAL HEADQUARTERS | 9923 | PubSafe | NHP | B&G | Reno | 1994 | 14763 | 2021-01-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 84000
0056ADA4 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0056 | This building contains a water fountain. The 2006 IBC Section 1109.5 states where a water fountain is provided, at least half should be accessible. This project would provide funding for the purchase and installation of a new accessible fixed high/ low ADA drinking fountain. | NHP REGIONAL HEADQUARTERS | 9923 | PubSafe | NHP | B&G | Reno | 1994 | 14763 | 2021-01-12 | Immediate to Two Years | Currently Critical | 1 | 4000
0056PLM1 | WATER HEATER REPLACEMENT | 0056 | There is a 100 gallon gas-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 5-6 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | NHP REGIONAL HEADQUARTERS | 9923 | PubSafe | NHP | B&G | Reno | 1994 | 14763 | 2021-01-12 | Four to Ten Years | Long-Term Needs | 3 | 3000
0056ADA5 | ADA SHOWER UPGRADE | 0056 | The Men's and Women's restrooms each contain at least one shower. The existing showers are not ADA accessible. This project would provide for an ADA compliant shower for each restroom including access, compliant plumbing fixtures and shower seats. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | NHP REGIONAL HEADQUARTERS | 9923 | PubSafe | NHP | B&G | Reno | 1994 | 14763 | 2021-01-12 | Immediate to Two Years | Currently Critical | 1 | 5000
0056HVA1 | AIR CONDITIONER INSTALLATION | 0056 | The server room is not sufficiently cooled by the existing HVAC system. The communications system has already failed due to overheating and when the room is too warm, the computer and communications equipment age prematurely. It is recommended to install an independent air conditioning system in the room to ensure that the temperature is properly regulated. This project would provide for the purchase and installation of an air conditioner including all required connections to existing utilities. | NHP REGIONAL HEADQUARTERS | 9923 | PubSafe | NHP | B&G | Reno | 1994 | 14763 | 2021-01-12 | Immediate to Two Years | Currently Critical | 1 | 2500
0056INT5 | OFFICE REMODEL | 0056 | The Command Secretary desk and office space are in need of a remodel. The configuration of the space is not functional. The built-in desk does not have enough space for computer equipment, is missing a keyboard tray, and does not allow enough space for moving around in an office chair. This project would provide for removing the existing desk and replacing it with a new desk which fits the needs of the employee. | NHP REGIONAL HEADQUARTERS | 9923 | PubSafe | NHP | B&G | Reno | 1994 | 14763 | 2021-01-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0056ADA3 | ADA SIGNAGE | 0056 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 07/15/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/19/2011. | NHP REGIONAL HEADQUARTERS | 9923 | PubSafe | NHP | B&G | Reno | 1994 | 14763 | 2021-01-12 | Immediate to Two Years | Currently Critical | 1 | 3000
0056EXT2 | EXTERIOR FINISHES | 0056 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete and brick masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NHP REGIONAL HEADQUARTERS | 9923 | PubSafe | NHP | B&G | Reno | 1994 | 14763 | 2021-01-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 73815
0056INT3 | INTERIOR FINISHES | 0056 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | NHP REGIONAL HEADQUARTERS | 9923 | PubSafe | NHP | B&G | Reno | 1994 | 14763 | 2021-01-12 | Four to Ten Years | Long-Term Needs | 3 | 73815
0056INT4 | COUNTERTOP REPLACEMENT | 0056 | The countertops in the restrooms and breakroom are showing signs of wear and tear particularly at the Formica edges and corners. The countertops are delaminating and failing. This project recommends the replacement of the existing damaged countertops with heavy duty, quality finishes. This project would provide funding for the removal and replacement of the countertops. | NHP REGIONAL HEADQUARTERS | 9923 | PubSafe | NHP | B&G | Reno | 1994 | 14763 | 2021-01-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
2028SFT1 | SEISMIC RETROFIT | 2028 | This building is a historic wood framed structure on an old concrete foundation consisting of a perimeter stem wall and interior post and piers. The concrete in the stem wall and piers is crumbling and cracked and the wood framing is not properly anchored into the concrete foundation. Additional bracing is also required for the roof and wall framing to stabilize the structure in the event of an earthquake. It is recommended to design and construct a seismic retrofit on the structure to meet current life safety codes. The estimate is for the construction costs only. | MUSEUM ADMINISTRATIVE OFFICE (VACANT) | 9850 | TCA | M&H | Museums | Carson City | 1942 | 1656 | 2011-12-15 | Immediate to Two Years | Currently Critical | 1 | 45000
2028SFT7 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 2028 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. | MUSEUM ADMINISTRATIVE OFFICE (VACANT) | 9850 | TCA | M&H | Museums | Carson City | 1942 | 1656 | 2011-12-15 | Immediate to Two Years | Currently Critical | 1 | 4000
2028PLM1 | WATER HEATER INSTALLATION | 2028 | There is a 19 gallon propane-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 3-4 years. It is recommended that a new natural gas water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | MUSEUM ADMINISTRATIVE OFFICE (VACANT) | 9850 | TCA | M&H | Museums | Carson City | 1942 | 1656 | 2011-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
2028SFT5 | ELECTRICAL OUTLET COVERS | 2028 | The existing floor mounted electrical outlets present a safety hazard. Steam cleaning or shampooing the carpet can introduce moisture into the outlet. Also, being face up, dirt, lint or other items can accumulate in the outlets causing a short or possible fire hazard. This project would provide for replacing the faceplates of the floor mounted outlets with new floor outlet box cover plates. | MUSEUM ADMINISTRATIVE OFFICE (VACANT) | 9850 | TCA | M&H | Museums | Carson City | 1942 | 1656 | 2011-12-15 | Immediate to Two Years | Currently Critical | 1 | 500
2028SFT4 | EXIT SIGN AND EGRESS LIGHTING INSTALLATION | 2028 | The building does not have any emergency lighting or exit signs. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2006 Chapter 10 was referenced for this project. | MUSEUM ADMINISTRATIVE OFFICE (VACANT) | 9850 | TCA | M&H | Museums | Carson City | 1942 | 1656 | 2011-12-15 | Immediate to Two Years | Currently Critical | 1 | 1500
2028SFT2 | FIRE SUPPRESSION SYSTEM INSTALLATION | 2028 | The building is a B occupancy per the 2006 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 or R-2 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. | MUSEUM ADMINISTRATIVE OFFICE (VACANT) | 9850 | TCA | M&H | Museums | Carson City | 1942 | 1656 | 2011-12-15 | Immediate to Two Years | Currently Critical | 1 | 10500
2028ENR3 | ATTIC INSULATION REPLACEMENT | 2028 | The insulation in the attic is a cellulose blown-in type that is old and most likely does not provide an adequate insulation value. This project would provide for installing a new layer of insulation on top of the existing insulation to ensure at least an R-38 insulation value. | MUSEUM ADMINISTRATIVE OFFICE (VACANT) | 9850 | TCA | M&H | Museums | Carson City | 1942 | 1656 | 2011-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
2028SFT6 | FIRE EXTINGUISHER INSTALLATION | 2028 | NAC 477.283.1(L) states that "Portable fire extinguishers must be installed in all group A, B, E, F, H, I, M, R-1, R-2, R-4 and S occupancies. No exceptions will apply.". There are no fire extinguishers in the building. This project would provide for the purchase and installation of two fire extinguishers according to NAC 477.405 and any other requirements of the Fire Marshall. | MUSEUM ADMINISTRATIVE OFFICE (VACANT) | 9850 | TCA | M&H | Museums | Carson City | 1942 | 1656 | 2011-12-15 | Immediate to Two Years | Currently Critical | 1 | 500
2028SFT3 | FIRE ALARM SYSTEM INSTALLATION | 2028 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2006 Section 7 and the 2006 International Fire Code. | MUSEUM ADMINISTRATIVE OFFICE (VACANT) | 9850 | TCA | M&H | Museums | Carson City | 1942 | 1656 | 2011-12-15 | Immediate to Two Years | Currently Critical | 1 | 6000
2028ADA1 | ADA SIGNAGE | 2028 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 02/12/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2011. | MUSEUM ADMINISTRATIVE OFFICE (VACANT) | 9850 | TCA | M&H | Museums | Carson City | 1942 | 1656 | 2011-12-15 | Immediate to Two Years | Currently Critical | 1 | 1000
2028EXT2 | EXTERIOR FINISHES | 2028 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is cleaning the metal siding and caulking of the siding, windows, flashing, fixtures and all other penetrations. It is recommended that the building be cleaned and caulked in the next 3-4 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | MUSEUM ADMINISTRATIVE OFFICE (VACANT) | 9850 | TCA | M&H | Museums | Carson City | 1942 | 1656 | 2011-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
2028INT1 | INTERIOR FINISHES | 2028 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | MUSEUM ADMINISTRATIVE OFFICE (VACANT) | 9850 | TCA | M&H | Museums | Carson City | 1942 | 1656 | 2011-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
9850SIT1 | PIPE BOLLARD INSTALLATION | 9850 | To the north of the building, there is a parking lot for the office building next door. There have been several incidents of vehicles colliding with the building and damaging the siding and possibly the structure. This area is in need of pipe bollards to protect the building. This project would provide funding for 4 eight inch diameter pipe bollards to be located near the north elevation of the building. | MUSEUM ADMINISTRATIVE SITE | 9850 | TCA | M&H | Museums | Carson City | 1910 |  | 2011-12-15 | Immediate to Two Years | Currently Critical | 1 | 2000
9850SIT2 | SLURRY SEAL ASPHALT PAVING | 9850 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving in the parking lot. Striping and signage including updated ADA parking requirements are included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 15,000 square feet of asphalt area was used to generate this estimate. The pavement maintenance is currently Carson City's responsibility even though the State owns the property. This project is for information only. | MUSEUM ADMINISTRATIVE SITE | 9850 | TCA | M&H | Museums | Carson City | 1910 |  | 2011-12-15 | Four to Ten Years | Long-Term Needs | 3 | 15000
3032EXT1 | EXTERIOR FINISHES | 3032 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 11/04/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | MUSEUM CARPORT | 9964 | TCA | M&H | Museums | Overton | 0 | 1000 | 2014-01-20 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
9964SEC1 | EXTERIOR SOLAR SITE LIGHTING INSTALLATION | 9964 | The site has minimal site lighting in the parking lots and between the buildings which is a security and safety concern. This project would provide for the installation of 16 solar powered LED exterior light fixtures, 20 foot tall poles and 30" diameter raised concrete bases. This installation will eliminate the need for trenching and electrical connections. This project or a portion thereof was previously recommended in the FCA report dated 03/21/2002 and 11/04/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | LOST CITY MUSEUM SITE | 9964 | TCA | M&H | Museums | Overton | 1935 |  | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 104000
9964ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 9964 | The Picnic Area contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. This project or a portion thereof was previously recommended in the FCA report dated 11/04/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | LOST CITY MUSEUM SITE | 9964 | TCA | M&H | Museums | Overton | 1935 |  | 2014-01-29 | Immediate to Two Years | Currently Critical | 1 | 4000
9964SIT3 | RETAINING WALL INSTALLATION | 9964 | On the south side of the site along the main entrance driveway, the dirt bank is eroding considerably. The runoff from the parking lot is exacerbating the problem. This project recommends installing a retaining wall along the driveway in order to prevent further erosion. The estimate is based on a 100 foot long reinforced concrete retaining wall. | LOST CITY MUSEUM SITE | 9964 | TCA | M&H | Museums | Overton | 1935 |  | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 40000
9964SIT4 | SIGNAGE REPLACEMENT | 9964 | The Museum has three large signs indentifying the site and providing basic parking directions. The signs are older, difficult to read and in poor locations for visibility. It is recommended to commission and install new signs for the site. This project provides for the replacement of three identification and directional signs for the site. | LOST CITY MUSEUM SITE | 9964 | TCA | M&H | Museums | Overton | 1935 |  | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2250
9964SIT1 | SLURRY SEAL ASPHALT PAVING | 9964 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site wide including access roads and parking areas. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 41,156 square feet of asphalt area was used to generate this estimate. This project was completed in 2014 but should scheduled every 5 or so years as stated above. This project or a portion thereof was previously recommended in the FCA report dated 03/21/2002 and 11/04/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | LOST CITY MUSEUM SITE | 9964 | TCA | M&H | Museums | Overton | 1935 |  | 2014-01-29 | Four to Ten Years | Long-Term Needs | 3 | 30867
0267INT1 | INTERIOR FINISHES | 0267 | The interior finishes are in fair to poor condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. Additional costs are included due to the historic nature of the building and for treating complicated areas such as the wood framing members on the ceiling. An epoxy-based paint should be utilized in wet areas for durability. Due to the historical nature of the facility, this project is subject to review and approval from the State Historical Preservation Office. This project or a portion thereof was previously recommended in the FCA reports dated 03/21/2002 and 11/04/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | LOST CITY MUSEUM | 9964 | TCA | M&H | Museums | Overton | 1935 | 22434 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 168255
0267EXT6 | EXTERIOR DOOR REPAIRS | 0267 | Two of the exterior metal man doors are difficult to operate and due for repairs. The door hardware including the panic bars, hinges and closers are worn from general wear and tear and do not operate smoothly. This project would provide for the purchase and installation of new emergency panic hardware, hinges and closers to be installed on the doors and removing the existing hardware. | LOST CITY MUSEUM | 9964 | TCA | M&H | Museums | Overton | 1935 | 22434 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0267PLM1 | SINK REPAIRS - WORKROOM | 0267 | The sink in the workroom does not drain properly and has been taken out of service. It is believed that the drain line was capped during the last addition on the east side of the building and was not re-attached after construction. This project would provide for a licensed plumber to repair the drain line by saw-cutting the concrete floor to determine the failure and installing a new drain line to bring the sink back into service. This project or a portion thereof was previously recommended in the FCA report dated 11/04/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | LOST CITY MUSEUM | 9964 | TCA | M&H | Museums | Overton | 1935 | 22434 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0267ADA2 | ASSISTED LISTENING SYSTEM INSTALLATION | 0267 | The Lost City Museum is designed to be a self-guided experience. Many of the exhibits and displays would benefit from a further explanation or clarification, but staffing and budget limitations impact those efforts. This project recommends the installation of a public address type system with a listening system that would activate when the visitor approaches the display or activates a switch. This would greatly enhance the experience and provide compliance with ADA requirements for assistive listening devices for the hearing and visually impaired. Prices quoted are for an infrared system. A radio frequency system may prove more appropriate for this application, and both should be evaluated. This project does include costs for developing the material and recording media for the exhibits. These efforts could serve as a test program for similar programs at other museums and sites of interest state-wide. This project or a portion thereof was previously recommended in the FCA reports dated 03/21/2002 and 11/04/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | LOST CITY MUSEUM | 9964 | TCA | M&H | Museums | Overton | 1935 | 22434 | 2014-01-29 | Immediate to Two Years | Currently Critical | 1 | 48000
0267ELE3 | EXHIBIT LIGHTING UPGRADE | 0267 | The existing lighting fixtures in the artifact cabinets are older and costly to maintain. Replacement bulbs are as much as $75.00 each and the Museum's budget cannot support this costly system. This project will upgrade fixtures to a fiber optic system with lower cost replacement bulbs. Any electrical wiring upgrades are not included in this estimate. | LOST CITY MUSEUM | 9964 | TCA | M&H | Museums | Overton | 1935 | 22434 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0267SFT3 | FIRE SUPPRESSION SYSTEM SUPPRESSION | 0267 | The building is a B occupancy per the 2012 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 or R-2 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire suppression system and backflow prevention in the event the building is remodeled or an addition is undertaken. | LOST CITY MUSEUM | 9964 | TCA | M&H | Museums | Overton | 1935 | 22434 | 2014-01-29 | Immediate to Two Years | Currently Critical | 1 | 314076
0267ENR3 | WINDOW REPLACEMENT | 0267 | The windows are original, single pane construction in a wooden frame. These older windows are drafty, not energy efficient and the wooden frames have deteriorated significantly. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replication of 17 units including wooden frames to maintain the historic character of the building. Removal and disposal of the existing windows is included in this estimate. Due to the historical nature of the facility, this project is subject to review and approval from the State Historical Preservation Office. This project or a portion thereof was previously recommended in the FCA report dated 11/04/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | LOST CITY MUSEUM | 9964 | TCA | M&H | Museums | Overton | 1935 | 22434 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25500
0267EXT5 | EXTERIOR FINISHES | 0267 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing and painting the stucco, patching the adobe and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building finishes be treated in the next 5-7 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Due to the historical nature of the facility, this project is subject to review and approval from the State Historical Preservation Office. | LOST CITY MUSEUM | 9964 | TCA | M&H | Museums | Overton | 1935 | 22434 | 2014-01-29 | Four to Ten Years | Long-Term Needs | 3 | 112170
0267PLM2 | WATER HEATER REPLACEMENT | 0267 | There are two electric water heaters in the building. A 19 gallon water heater for the public restrooms and a 40 gallon water heater for the staff restrooms. The average life span of a water heater is eight to ten years. With the passage of time and constant use, these units are showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that two new electric water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. | LOST CITY MUSEUM | 9964 | TCA | M&H | Museums | Overton | 1935 | 22434 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0268EXT2 | EXTERIOR FINISHES | 0268 | This unique structure consists of wood poles and beams covered with reeds and finally packed with soil. It is largely underground and accessed from a hole in the ground with a ladder going down into the Pit House. This type of structure deteriorates over time and requires refurbishment every couple of years. This project provides for removing the soil and reeds, replacing any poles or beams as needed and rebuilding the roof structure. It is recommended that the Pit House be refurbished in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Due to the historical nature of the facility, this project is subject to review and approval from the State Historical Preservation Office. | LOST CITY MUSEUM PIT HOUSE | 9964 | TCA | M&H | Museums | Overton |  | 400 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0267INT3 | OFFICE RESTROOM REMODEL | 0267 | A portion of the original adobe building is used as offices for the staff. There are two restrooms in this area, both are in poor condition and due for a remodel. There have been ongoing problems with the plumbing, and one of the showers is inoperative. This project recommends replacing the finishes, fixtures, cabinets, toilets, tubs/ showers and exhaust fans in both restrooms. The removal and disposal of the existing fixtures and finishes is included in this estimate. Due to the historical nature of the facility, this project is subject to review and approval from the State Historical Preservation Office. This project or a portion thereof was previously recommended in the FCA reports dated 03/21/2002 and 11/04/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | LOST CITY MUSEUM | 9964 | TCA | M&H | Museums | Overton | 1935 | 22434 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
0267INT2 | FLOORING REPLACEMENT | 0267 | The flooring in the museum includes (VCT) vinyl composite tile, carpet, painted concrete, and local sandstone. The floor finishes are damaged and reaching the end of their useful life. This project would provide for removal and disposal of the existing VCT and Carpet flooring and installation of new 12x12 VCT with a 6" base, heavy duty commercial grade carpet and refinishing the painted concrete in the next two to three years. Most of this work is in the old residence and museum display area of the building. The sandstone should remain as is. This project or a portion thereof was previously recommended in the FCA reports dated 03/21/2002 and 11/04/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | LOST CITY MUSEUM | 9964 | TCA | M&H | Museums | Overton | 1935 | 22434 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 136000
0267ADA1 | ADA SIGNAGE | 0267 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required and that the restroom signs are moved off of the doors. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA reports dated 03/21/2002 and 11/04/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | LOST CITY MUSEUM | 9964 | TCA | M&H | Museums | Overton | 1935 | 22434 | 2014-01-29 | Immediate to Two Years | Currently Critical | 1 | 5000
0856ADA1 | ADA ACCESSIBLE PATH OF TRAVEL | 0856 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. A concrete route of travel to the Outdoor Exhibit is necessary to comply with ADA accessibility requirements. This project would provide for installing a concrete walkway to the exhibit. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. 350 square feet of 4" thick concrete was used for this estimate. Due to the historical nature of the facility, this project is subject to review and approval from the State Historical Preservation Office. This project or a portion thereof was previously recommended in the FCA report dated 11/04/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | LOST CITY OUTDOOR EXHIBIT | 9964 | TCA | M&H | Museums | Overton | 1935 | 740 | 2014-01-29 | Immediate to Two Years | Currently Critical | 1 | 8750
0973EXT1 | EXTERIOR FINISHES | 0973 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA reports dated 03/21/2002 and 11/04/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | LOST CITY MUSEUM WORKSHOP | 9964 | TCA | M&H | Museums | Overton | 1989 | 580 | 2014-01-29 | Four to Ten Years | Long-Term Needs | 3 | 2900
0974INT2 | CEILING INSTALLATION | 0974 | The ceiling in the building was intended to be finished with gypsum board. The gypsum board was purchased but never installed and the interior space has remained as an open framed ceiling. At the time of the survey, the roof insulation was falling down through the rafters and in other places the rafters were being used for storing materials. This project would provide for the purchase and installation of gypsum board on the ceiling and insulation attachments to secure the insulation to the roof decking. | LOST CITY STORAGE BUILDING | 9964 | TCA | M&H | Museums | Overton | 1991 | 580 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5800
0974INT1 | INTERIOR FINISHES | 0974 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. This project or a portion thereof was previously recommended in the FCA report dated 11/04/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | LOST CITY STORAGE BUILDING | 9964 | TCA | M&H | Museums | Overton | 1991 | 580 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2900
0974EXT1 | EXTERIOR FINISHES | 0974 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA reports dated 03/21/2002 and 11/04/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | LOST CITY STORAGE BUILDING | 9964 | TCA | M&H | Museums | Overton | 1991 | 580 | 2014-01-29 | Immediate to Two Years | Currently Critical | 1 | 2900
0973ENR2 | HVAC REPLACEMENT | 0973 | The existing HVAC system consists of a wall mounted heat pump and a small wall mounted air conditioner. These units were not operating at the time of the survey. This project would provide for replacing the existing equipment with an exterior ground mounted packaged unit. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | LOST CITY MUSEUM WORKSHOP | 9964 | TCA | M&H | Museums | Overton | 1989 | 580 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0973EXT4 | EXTERIOR DOOR REPLACEMENT | 0973 | The 2 exterior wood man doors appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement of the wood doors with new metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | LOST CITY MUSEUM WORKSHOP | 9964 | TCA | M&H | Museums | Overton | 1989 | 580 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
0973EXT3 | EXTERIOR SIDING REPLACEMENT | 0973 | The shop has a painted masonite siding that is due for replacement. The existing siding is in poor condition and will no longer hold paint. This project recommends removing the masonite siding and replacing it with T1-11 panels finished with an oil-based stain. This project or a portion thereof was previously recommended in the FCA report dated 11/04/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | LOST CITY MUSEUM WORKSHOP | 9964 | TCA | M&H | Museums | Overton | 1989 | 580 | 2014-01-29 | Immediate to Two Years | Currently Critical | 1 | 5800
0973EXT5 | WINDOW REPLACEMENT | 0973 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 3 units. Removal and disposal of the existing windows is included in this estimate. | LOST CITY MUSEUM WORKSHOP | 9964 | TCA | M&H | Museums | Overton | 1989 | 580 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2250
0857EXT3 | EXTERIOR FINISHES | 0857 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is repairing the cracks and applying a new layer of adobe coating over the masonry. It is recommended that the building be repaired in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Due to the historical nature of the facility, this project is subject to review and approval from the State Historical Preservation Office. | LOST CITY PUMP HOUSE | 9964 | TCA | M&H | Museums | Overton | 1935 | 64 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 640
0974EXT3 | EXTERIOR SIDING REPLACEMENT | 0974 | The building has a painted masonite siding that is due for replacement. The existing siding is in poor condition and will no longer hold paint. This project recommends removing the masonite siding and replacing it with T1-11 panels finished with an oil-based stain. This project or a portion thereof was previously recommended in the FCA report dated 11/04/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | LOST CITY STORAGE BUILDING | 9964 | TCA | M&H | Museums | Overton | 1991 | 580 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5800
0858EXT2 | EXTERIOR FINISHES | 0858 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for repairing the adobe coating, sealing and staining the wood beams and refurbishing the ocatillo roofing. It is recommended that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Due to the historical nature of the facility, this project is subject to review and approval from the State Historical Preservation Office. | LOST CITY MUSEUM RAMADA | 9964 | TCA | M&H | Museums | Overton | 1935 | 130 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 650
0973SFT1 | FIRE PROTECTION EQUIPMENT INSTALLATION | 0973 | The building does not have smoke detectors or a portable fire extinguisher available. International Fire Code Section 906 requires that portable fire extinguishers shall be installed in Group F occupancies. They shall be provided for employee use and selected and distributed based on the classes of anticipated workplace fires and on the size and degree of hazard which would affect their use. State Fire Marshal NAC 477.915 (3) requires that smoke detectors be connected to the wiring of the building with a battery backup. This project would provide funding for the purchase and installation of 2 fire extinguishers, cabinets, and the hardware necessary to install them and for the purchase and installation of smoke detectors in accordance with these codes. | LOST CITY MUSEUM WORKSHOP | 9964 | TCA | M&H | Museums | Overton | 1989 | 580 | 2014-01-29 | Immediate to Two Years | Currently Critical | 1 | 1500
0856EXT3 | EXTERIOR FINISHES | 0856 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the structures. Included in the cost is basic adobe maintenance by the staff as well as funds for adobe specialists to come out once a year. These costs should be sufficient to allow the specialists to spend five days per year at the museum over the next four years. This project should be scheduled on a cyclical basis to maintain the integrity of the outdoor exhibit. Due to the historical nature of the facility, this project is subject to review and approval from the State Historical Preservation Office. | LOST CITY OUTDOOR EXHIBIT | 9964 | TCA | M&H | Museums | Overton | 1935 | 740 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 40000
0973INT1 | INTERIOR FINISHES | 0973 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. This project or a portion thereof was previously recommended in the FCA report dated 11/04/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | LOST CITY MUSEUM WORKSHOP | 9964 | TCA | M&H | Museums | Overton | 1989 | 580 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2900
2811EXT4 | ROOF REPAIRS | 2811 | The cooling towers are leaking water onto the single-ply membrane roofing system. The single-ply membrane roofing system is starting to lose the top layer and is showing some of the second layer (scrims). This project would provide funding to repair the cooling tower’s leaks, and have the single-ply membrane patched where needed. | NEVADA STATE MUSEUM, LAS VEGAS | 9817 | TCA | M&H | Museums | Las Vegas | 2008 | 78145 | 2016-05-12 | Immediate to Two Years | Currently Critical | 1 | 2000
2811EXT3 | ROOF DRAIN DOWNSPOUT MODIFICATIONS | 2811 | The roof drainage downspout runs next to the loading dock. Delivery vehicles have run into the down spout and crushed it. Due to this, the water no longer flows away from the building, foundation and loading dock. This project would provide for a new 30’ down spout. The new down spout shall be located away from the loading dock to prevent future vehicle damage and to allow for runoff to flow away from the building. | NEVADA STATE MUSEUM, LAS VEGAS | 9817 | TCA | M&H | Museums | Las Vegas | 2008 | 78145 | 2016-05-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
2811ELE1 | PROVIDE CLEARANCE AT ELECTRICAL PANELS | 2811 | There are electrical panels in the building which do not have proper clear floor space around them. The 2012 IFC Section 605.3 states, a working space of not less than 30 inches in width, 36 inches in depth and 78 inches in height shall be provided in front of electrical service equipment. Where the electrical service equipment is wider than 30 inches, the working space shall not be less than the width of the equipment. No storage of any materials shall be located within the designated working space. This project would provide funding to relocate the items blocking the electrical panels. | NEVADA STATE MUSEUM, LAS VEGAS | 9817 | TCA | M&H | Museums | Las Vegas | 2008 | 78145 | 2016-05-12 | Immediate to Two Years | Currently Critical | 1 | 250
2811PLM2 | ISOLATION VALVE INSTALLATION | 2811 | There are no isolation valves for the building's water lines. The main water line that serves the 78,145 sf building on the site is in need of 25 isolation valves. This will allow the maintenance staff to conduct repairs and maintenance to the plumbing without shutting down the entire building. More importantly, a leak in the building can be shut down quickly minimizing damage in an emergency. This estimate provides for 2-1/2" ball valves to be installed in individual rooms throughout the building. | NEVADA STATE MUSEUM, LAS VEGAS | 9817 | TCA | M&H | Museums | Las Vegas | 2008 | 78145 | 2016-05-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12500
2811EXT1 | EXTERIOR FINISHES | 2811 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NEVADA STATE MUSEUM, LAS VEGAS | 9817 | TCA | M&H | Museums | Las Vegas | 2008 | 78145 | 2016-05-12 | Four to Ten Years | Long-Term Needs | 3 | 781450
2811EXT2 | LOADING DOCK UPGRADES | 2811 | The existing loading dock does not have safety rails on the dock platform nor along the approach ramp, which has a sharp drop on one side of several feet down. There have been several near-miss accidents, where dock users have nearly fallen off the platform due to lack of rails. In addition, the approach ramp to the dock platform has a very sharp angle and is very narrow, which makes it difficult and dangerous to move loading vehicles or equipment from the approach ramp to the platform. This project would provide for the removal of the ramp and the installation of a wider, better angle ramp and for the installation of safety rails per IBC 2012. | NEVADA STATE MUSEUM, LAS VEGAS | 9817 | TCA | M&H | Museums | Las Vegas | 2008 | 78145 | 2016-05-12 | Immediate to Two Years | Currently Critical | 1 | 213012
2811SFT2 | FIRE SUPPRESSION/ MECHANICAL UPGRADE | 2811 | Staff at the Nevada State Museum indicated, during the time of the survey, when the spray booth is in use paint overspray is landing on the fire suppression sprinkler head. They have been written up by the State Fire Marshal’s Office for having paint on a fire suppression sprinkler head. Per NFPA 33 Chapter 7 Section 7.2 states, Each spray area shall be provided with mechanical ventilation that is capable of confining and removing vapors and mists to a safe location and is capable of confining and controlling combustible residues, dusts, and deposits. Section 7.2.3 Mechanical ventilation shall be kept in operation at all times while spray operations are being conducted and for a sufficient time thereafter to allow the vapors from drying coated objects or material and residues to be exhausted. It is recommended to have a Mechanical Engineer determine the proper Cubic Feet per Minute (CFM) needed to remove all paint vapors and install exhaust venting to meet the requirements. Per NFPA 33 Chapter 9 Section 9.4.1 The automatic sprinkler system shall be a wet pipe system, a dry pipe system, a pre action system, or an open-head deluge system, whichever is most appropriate for the portion of the spray operation being protected. This project would provide for removing the plastic from the fire suppression sprinkler head and installing the exhaust venting in order to remove the paint overspray from the booth. | NEVADA STATE MUSEUM, LAS VEGAS | 9817 | TCA | M&H | Museums | Las Vegas | 2008 | 78145 | 2016-05-12 | Immediate to Two Years | Currently Critical | 1 | 15000
2811ELE2 | ELECTRICAL PANEL UNUSED OPENINGS | 2811 | The wiring in the electrical panel has missing breakers and it is recommended to have blanks installed at the unused openings. Per NEC 408.7 states, unused openings for circuit breakers and switches shall be closed using identified closures, or other approved means that provide protection substantially equivalent to the wall of the enclosure. Unused openings create a safety issue during repairs or upgrades. This project would provide for blanks to be installed where the missing breakers are located. | NEVADA STATE MUSEUM, LAS VEGAS | 9817 | TCA | M&H | Museums | Las Vegas | 2008 | 78145 | 2016-05-12 | Immediate to Two Years | Currently Critical | 1 | 250
2811SEC1 | SECURITY SYSTEM UPGRADE | 2811 | At the time of the survey, the lighting and video surveillance systems were failing, inadequate, and non-programmable. The current lighting system runs on a 3" floppy disc and both the lighting and video surveillance systems software are too old to accept software updates. It is recommended that both systems be replaced with new systems and adding a building intrusion infrared alarm system to the 78,145 sf building. This project recommends replacing the panels, software, hardware, and adding additional wiring where needed. | NEVADA STATE MUSEUM, LAS VEGAS | 9817 | TCA | M&H | Museums | Las Vegas | 2008 | 78145 | 2016-05-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 630000
2811PLM1 | WATER HEATER REPLACEMENT | 2811 | There are three, 30 gallon, electric water heaters in the building. The average life span of a water heater is 8-10 years. With the passage of time and constant use, these units are showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that new electric water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. | NEVADA STATE MUSEUM, LAS VEGAS | 9817 | TCA | M&H | Museums | Las Vegas | 2008 | 78145 | 2016-05-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
2811INT1 | INTERIOR FINISHES | 2811 | It is recommended to paint the interior walls and ceilings at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | NEVADA STATE MUSEUM, LAS VEGAS | 9817 | TCA | M&H | Museums | Las Vegas | 2008 | 78145 | 2016-05-12 | Four to Ten Years | Long-Term Needs | 3 | 781450
2811SFT1 | HIGH DENSITY STORAGE REPAIRS | 2811 | The high density storage system in the building is malfunctioning. The photo eyes and security switches are not operating properly, which is a safety concern. It is recommended that a licensed contractor repair the malfunctioning safety devices. | NEVADA STATE MUSEUM, LAS VEGAS | 9817 | TCA | M&H | Museums | Las Vegas | 2008 | 78145 | 2016-05-12 | Immediate to Two Years | Currently Critical | 1 | 4000
2201PLM1 | WATER HEATER REPLACEMENT | 2201 | There is a 15 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new on-demand electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | BOULDER CITY MUSEUM COMFORT STATION | 9951 | TCA | M&H | Museums | Boulder City | 2001 | 144 | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
2202SFT1 | EGRESS STORAGE REMOVAL | 2202 | The exit is currently blocked by items that are being stored in this area. The 2012 IBC Chapter 10 Means of Egress explains that exit routes cannot be blocked, reduced or altered. This project would provide for the removal of all items in conflict with this code requirement to ensure that egress and exit routes are not impeded. | BOULDER CITY MUSEUM GIFT SHOP | 9951 | TCA | M&H | Museums | Boulder City | 2001 | 144 | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 500
2202EXT1 | EXTERIOR FINISHES | 2202 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | BOULDER CITY MUSEUM GIFT SHOP | 9951 | TCA | M&H | Museums | Boulder City | 2001 | 144 | 2016-12-14 | Four to Ten Years | Long-Term Needs | 3 | 1440
2202INT1 | INTERIOR FINISHES | 2202 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | BOULDER CITY MUSEUM GIFT SHOP | 9951 | TCA | M&H | Museums | Boulder City | 2001 | 144 | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1440
2202HVA1 | HVAC EQUIPMENT REPLACEMENT | 2202 | The building is heated and cooled by a wall-mounted combination unit. The average life span of this type of unit is fifteen years. This unit is original to the building and should be scheduled for replacement in the next 5-6 years. This project includes removal and disposal of the existing HVAC unit and all required connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | BOULDER CITY MUSEUM GIFT SHOP | 9951 | TCA | M&H | Museums | Boulder City | 2001 | 144 | 2016-12-14 | Four to Ten Years | Long-Term Needs | 3 | 2000
2202ADA1 | ADA ACCESSIBLE COUNTER | 2202 | The ADA provides for accessibility to sites and services for people with physical limitations. The building is used to sell souvenirs to the general public visiting the museum. The service counter in the building does not meet the current ADA requirements. Section 904.4 of the ADA Standards for Accessible Design states that a portion of the counter surface that is 36" long minimum and 36" high maximum above the finish floor shall be provided. This project will provide an accessible counter space in accordance with this requirement. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | BOULDER CITY MUSEUM GIFT SHOP | 9951 | TCA | M&H | Museums | Boulder City | 2001 | 144 | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 4000
2201HVA1 | HVAC EQUIPMENT REPLACEMENT | 2201 | The building is heated and cooled by two wall-mounted combination units. The average life span of this type of unit is fifteen years. These units are original to the building and should be scheduled for replacement in the next 2-3 years. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | BOULDER CITY MUSEUM COMFORT STATION | 9951 | TCA | M&H | Museums | Boulder City | 2001 | 144 | 2016-12-14 | Four to Ten Years | Long-Term Needs | 3 | 4000
2201EXT1 | EXTERIOR FINISHES | 2201 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-6 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | BOULDER CITY MUSEUM COMFORT STATION | 9951 | TCA | M&H | Museums | Boulder City | 2001 | 144 | 2016-12-14 | Four to Ten Years | Long-Term Needs | 3 | 1440
2203EXT1 | EXTERIOR FINISHES | 2203 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | BOULDER CITY MUSEUM TICKET STATION | 9951 | TCA | M&H | Museums | Boulder City | 2001 | 144 | 2016-12-14 | Four to Ten Years | Long-Term Needs | 3 | 1440
2201INT1 | INTERIOR FINISHES | 2201 | The interior finishes are in fair condition. It is recommended that the interior walls and ceiling be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | BOULDER CITY MUSEUM COMFORT STATION | 9951 | TCA | M&H | Museums | Boulder City | 2001 | 144 | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1440
2204SFT1 | STORAGE REMOVAL | 2204 | Items in this building are stored too close to the ceiling. The 2012 IFC Section 315.3.1 states that, Storage shall be maintained 2 feet or more below the ceiling in non sprinklered areas of buildings or a minimum of 18 inches below sprinkler head deflectors in sprinklered areas of buildings. This project would provide for the removal of all items in conflict with code requirements to ensure that the fire suppression system operates correctly. | BOULDER CITY MUSEUM CREW QUARTERS | 9951 | TCA | M&H | Museums | Boulder City | 2001 | 144 | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 500
2208ADA1 | ADA ACCESS PROGRAM ACCESSIBILITY | 2208 | The Boulder City Museum Shade Structure #4 is open to the public and does not have designated ADA access to the Shade Structure. This project would provide for ADA access inside of the public area of this building and additionally for an audio/ visual presentation at the Shade Structure areas, which may not be ADA accessible. This project includes funds for an audio/ visual consultant to outline and document the Boulder City Railroad Museum operations and to purchase and install required audio/ visual equipment, needed signage, TDD equipment and any minor remodeling of the public area of the building, as required, to accommodate this program. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | BOULDER CITY MUSEUM SHADE STRUCTURE #4 | 9951 | TCA | M&H | Museums | Boulder City | 2001 | 880 | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 20000
2208EXT1 | EXTERIOR FINISHES | 2208 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | BOULDER CITY MUSEUM SHADE STRUCTURE #4 | 9951 | TCA | M&H | Museums | Boulder City | 2001 | 880 | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3520
2207EXT1 | EXTERIOR FINISHES | 2207 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | BOULDER CITY MUSEUM SHADE STRUCTURE #3 | 9951 | TCA | M&H | Museums | Boulder City | 2001 | 1280 | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5120
2207ADA1 | ADA ACCESS PROGRAM ACCESSIBILITY | 2207 | The Boulder City Museum is open to the public and does not have designated ADA access to the Shade Structure. This project would provide for ADA access inside of the public area of this building and additionally for an audio/ visual presentation at the Shade Structure areas, which may not be ADA accessible. This project includes funds for an audio/ visual consultant to outline and document the Boulder City Railroad Museum operations and to purchase and install required audio/ visual equipment, needed signage, TDD equipment and any minor remodeling of the public area of the building, as required, to accommodate this program. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | BOULDER CITY MUSEUM SHADE STRUCTURE #3 | 9951 | TCA | M&H | Museums | Boulder City | 2001 | 1280 | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 20000
2206ADA1 | ADA ACCESS PROGRAM ACCESSIBILITY | 2206 | The Boulder City Museum is open to the public and does not have designated ADA access to the Shade Structure. This project would provide for ADA access inside of the public area of this building and additionally for an audio/ visual presentation at the Shade Structure areas, which may not be ADA accessible. This project includes funds for an audio/ visual consultant to outline and document the Boulder City Railroad Museum operations and to purchase and install required audio/ visual equipment, needed signage, TDD equipment and any minor remodeling of the public area of the building, as required, to accommodate this program. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | BOULDER CITY MUSEUM SHADE STRUCTURE #2 | 9951 | TCA | M&H | Museums | Boulder City | 2001 | 1280 | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 20000
2206EXT1 | EXTERIOR FINISHES | 2206 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | BOULDER CITY MUSEUM SHADE STRUCTURE #2 | 9951 | TCA | M&H | Museums | Boulder City | 2001 | 1280 | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5120
2205EXT1 | EXTERIOR FINISHES | 2205 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | BOULDER CITY MUSEUM SHADE STRUCTURE #1 | 9951 | TCA | M&H | Museums | Boulder City | 2001 | 880 | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3520
2203INT1 | INTERIOR FINISHES | 2203 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | BOULDER CITY MUSEUM TICKET STATION | 9951 | TCA | M&H | Museums | Boulder City | 2001 | 144 | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1440
2204EXT1 | EXTERIOR FINISHES | 2204 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | BOULDER CITY MUSEUM CREW QUARTERS | 9951 | TCA | M&H | Museums | Boulder City | 2001 | 144 | 2016-12-14 | Four to Ten Years | Long-Term Needs | 3 | 1440
2203ADA1 | ADA ACCESSIBLE COUNTER | 2203 | The ADA provides for accessibility to sites and services for people with physical limitations. The building is used to sell tickets to the general public visiting the museum. The service counter on the front of the building does not meet the current ADA requirements. Section 904.4 of the ADA Standards for Accessible Design states that a portion of the counter surface that is 36" long minimum and 36" high maximum above the finish floor shall be provided. This project will provide accessible counter space in accordance with this requirement. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | BOULDER CITY MUSEUM TICKET STATION | 9951 | TCA | M&H | Museums | Boulder City | 2001 | 144 | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 4000
2204HVA1 | HVAC EQUIPMENT REPLACEMENT | 2204 | The building is heated and cooled by a wall-mounted combination unit. The average life span of this type of unit is fifteen years. This unit is original to the building and should be scheduled for replacement in the next 2-4 years. This project includes removal and disposal of the existing HVAC unit and all required connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | BOULDER CITY MUSEUM CREW QUARTERS | 9951 | TCA | M&H | Museums | Boulder City | 2001 | 144 | 2016-12-14 | Four to Ten Years | Long-Term Needs | 3 | 2000
2204ELE1 | PROVIDE CLEARANCE AT ELECTRICAL PANELS | 2204 | There is an electrical panel in the building which does not have the proper clear floor space surrounding it. The 2012 IFC Section 605.3 states that, A working space of not less than 30 inches in width, 36 inches in depth and 78 inches in height shall be provided in front of electrical service equipment. Where the electrical service equipment is wider than 30 inches, the working space shall not be less than the width of the equipment. No storage of any materials shall be located within the designated working space. This project would provide funds to relocate the tables, microwaves and other items currently blocking the working space. | BOULDER CITY MUSEUM CREW QUARTERS | 9951 | TCA | M&H | Museums | Boulder City | 2001 | 144 | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 250
2204SFT2 | EGRESS STORAGE REMOVAL | 2204 | The exit is currently blocked by items that are being stored in this area. The 2012 IBC Chapter 10 Means of Egress explains that exit routes cannot be blocked, reduced or altered. This project would provide for the removal of all items in conflict with this code requirement to ensure that egress and exit routes are not impeded. | BOULDER CITY MUSEUM CREW QUARTERS | 9951 | TCA | M&H | Museums | Boulder City | 2001 | 144 | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 500
2204INT1 | INTERIOR FINISHES | 2204 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | BOULDER CITY MUSEUM CREW QUARTERS | 9951 | TCA | M&H | Museums | Boulder City | 2001 | 144 | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1440
2203ELE1 | PROVIDE CLEARANCE AT ELECTRICAL PANELS | 2203 | There is an electrical panel in the building which does not have the proper clear floor space surrounding it. The 2012 IFC Section 605.3 states that, A working space of not less than 30 inches in width, 36 inches in depth and 78 inches in height shall be provided in front of electrical service equipment. Where the electrical service equipment is wider than 30 inches, the working space shall not be less than the width of the equipment. No storage of any materials shall be located within the designated working space. This project would provide funds to relocate the tables, microwaves and other items currently blocking the working space. | BOULDER CITY MUSEUM TICKET STATION | 9951 | TCA | M&H | Museums | Boulder City | 2001 | 144 | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 250
2205ADA1 | ADA ACCESS PROGRAM ACCESSIBILITY | 2205 | The Boulder City Museum is open to the public and does not have designated ADA access to the Shade Structure. This project would provide for ADA access inside of the public area of this building and additionally for an audio/ visual presentation at the Shade Structure areas, which may not be ADA accessible. This project includes funds for an audio/ visual consultant to outline and document the Boulder City Railroad Museum operations and to purchase and install required audio/ visual equipment, needed signage, TDD equipment and any minor remodeling of the public area of the building, as required, to accommodate this program. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | BOULDER CITY MUSEUM SHADE STRUCTURE #1 | 9951 | TCA | M&H | Museums | Boulder City | 2001 | 880 | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 20000
9951SIT1 | SLURRY SEAL ASPHALT PAVING | 9951 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site wide including access roads, parking areas and the maintenance yard. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 32,000 square feet of asphalt area was used to generate this estimate. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | BOULDER CITY RAILROAD MUSEUM SITE | 9951 | TCA | M&H | Museums | Boulder City | 1996 |  | 2016-12-14 | Four to Ten Years | Long-Term Needs | 3 | 40000
3039EXT1 | EXTERIOR FINISHES | 3039 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | BOULDER CITY MUSEUM TRAIN PAVILION | 9951 | TCA | M&H | Museums | Boulder City | 2007 | 11102 | 2016-12-14 | Four to Ten Years | Long-Term Needs | 3 | 44408
3039ADA1 | ADA ACCESS PROGRAM ACCESSIBILITY | 3039 | The Boulder City Museum is open to the public and does not have designated ADA access to the Train Pavilion. This project would provide for ADA access inside of the public area of this building and additionally for an audio/ visual presentation at the Train Pavilion areas, which may not be ADA accessible. This project includes funds for an audio/ visual consultant to outline and document the Boulder City Railroad Museum operations and to purchase and install required audio/ visual equipment, needed signage, TDD equipment and any minor remodeling of the public area of the building, as required, to accommodate this program. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | BOULDER CITY MUSEUM TRAIN PAVILION | 9951 | TCA | M&H | Museums | Boulder City | 2007 | 11102 | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 20000
9951SIT6 | RAILROAD TRACK REPLACEMENT RAILROAD TRACK REPLACEMENT | 9951 | The site has 5 miles of railroad tracks that were in poor condition and were not in compliance with Federal standards at the time of the survey. This project would remove and replace the existing railroad tracks and replace them with new tracks that meet or exceed the Federal Railroad design standards. | BOULDER CITY RAILROAD MUSEUM SITE | 9951 | TCA | M&H | Museums | Boulder City | 1996 |  | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 80000
9951SFT1 | EXTERIOR SITE LIGHTING INSTALLATION | 9951 | The site has minimal site lighting in the public parking area and between the buildings which is a security and safety concern. This project will provide funding for the purchase and installation of 12 additional LED fixtures; 30’ light poles and 30" diameter raised concrete bases, electrical trenching, conduit, wiring, and required connections to the existing utilities. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | BOULDER CITY RAILROAD MUSEUM SITE | 9951 | TCA | M&H | Museums | Boulder City | 1996 |  | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 112000
9951SIT5 | CONCRETE PAVILION REPAIRS | 9951 | The exterior concrete sidewalks and platforms in the train pavilion are due for repairs. This project would provide for removing and replacing the expansion joints in the concrete and replacing the broken concrete curbing at the entrance to the parking lot. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | BOULDER CITY RAILROAD MUSEUM SITE | 9951 | TCA | M&H | Museums | Boulder City | 1996 |  | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0841SFT6 | SAFETY CABINETS | 0841 | The building contains many different paints, stains, and other hazardous products located on open shelves. This does not meet OSHA standards or IFC for hazardous materials containment. This project would provide a self-closing hazardous storage container in the building and install placards on the building exterior in accordance with OSHA 1910.106 (d) and IFC Chapter 57 Section 5704.3.2.1.3. | BOULDER CITY MUSEUM MAINTENANCE | 9951 | TCA | M&H | Museums | Boulder City | 1996 | 9200 | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 5000
0841INT1 | INTERIOR FINISHES | 0841 | The interior of the building is unfinished except for the office, the restrooms and portions of the metal shop area which together account for about 1,000 square feet of area. The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next 2-4 years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | BOULDER CITY MUSEUM MAINTENANCE | 9951 | TCA | M&H | Museums | Boulder City | 1996 | 9200 | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
0841SFT2 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0841 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | BOULDER CITY MUSEUM MAINTENANCE | 9951 | TCA | M&H | Museums | Boulder City | 1996 | 9200 | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 9200
0841HVA1 | RADIANT HEATER REPAIRS | 0841 | The building is heated by eight wall-mounted natural gas fired radiant heaters. Three of the heaters were not operating at the time of the survey and all eight should be scheduled for replacement. This project provides for the disposal of the existing radiant heaters and replacement with eight new gas fired radiant heaters including connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | BOULDER CITY MUSEUM MAINTENANCE | 9951 | TCA | M&H | Museums | Boulder City | 1996 | 9200 | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0841ENR2 | LIGHTING UPGRADE | 0841 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | BOULDER CITY MUSEUM MAINTENANCE | 9951 | TCA | M&H | Museums | Boulder City | 1996 | 9200 | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 73600
0841SFT4 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0841 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. | BOULDER CITY MUSEUM MAINTENANCE | 9951 | TCA | M&H | Museums | Boulder City | 1996 | 9200 | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 4000
0841EXT3 | EXTERIOR FINISHES | 0841 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations. Special attention should be given to the flashing and seams on the south side of the building where large gaps are visible from inside the building. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Replacing all of the weather striping on the overhead coiling doors is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | BOULDER CITY MUSEUM MAINTENANCE | 9951 | TCA | M&H | Museums | Boulder City | 1996 | 9200 | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 36800
0841SFT3 | FIRE SUPPRESSION SYSTEM MAINTENANCE | 0841 | The fire suppression system is a wet system and the corrosive water is causing damage. With each annual test, the corrosion is accelerated and has recently caused failures in some of the valves and pipes. The system is about 21 years old. It is recommended to perform a five year flush on the system with an inspection of the sprinkler heads at the cost of about $3,500. Should the inspection deem it necessary, a full flush and replacement of the heads would follow at the cost of about $6,500. The five year flush should be scheduled every five years thereafter to maximize the lifecycle of the system. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | BOULDER CITY MUSEUM MAINTENANCE | 9951 | TCA | M&H | Museums | Boulder City | 1996 | 9200 | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
0841ENR1 | REPLACE INSULATION | 0841 | The walls and ceiling in the building have a layer of batt insulation installed that is not enclosed by a finish system. The insulation batts are deteriorating and large sections have fallen out of the walls and ceiling. The existing insulation is R-24 in the ceiling and R-15 in the walls. This project recommends replacing all of the insulation with a foil-backed R-30 batt insulation which will increase the energy efficiency of the building. It may be possible to use a foamed-in system to fill the cavities where applicable; costs are similar to the batt insulation provided for in this project. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | BOULDER CITY MUSEUM MAINTENANCE | 9951 | TCA | M&H | Museums | Boulder City | 1996 | 9200 | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
0841SFT7 | BACKFLOW PREVENTER REPLACEMENT | 0841 | There is a backflow preventer for the fire suppression system in the building. It is leaking and should be scheduled for replacement. This project would provide for replacing the backflow preventer by a licensed fire suppression contractor. | BOULDER CITY MUSEUM MAINTENANCE | 9951 | TCA | M&H | Museums | Boulder City | 1996 | 9200 | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 5000
0841ENR3 | EXTERIOR LIGHTING REPLACEMENT | 0841 | The building has perimeter lighting on the exterior of the building, but the light fixtures are old, failing and not energy efficient. This project would provide for the replacement of the exterior lighting fixtures with new LED light fixtures, using existing wiring. | BOULDER CITY MUSEUM MAINTENANCE | 9951 | TCA | M&H | Museums | Boulder City | 1996 | 9200 | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
0841ELE2 | PROVIDE CLEARANCE AT ELECTRICAL PANELS | 0841 | There is an electrical panel in the building which does not have the proper clear floor space surrounding it. The 2012 IFC Section 605.3 states that, a working space of not less than 30 inches in width, 36 inches in depth and 78 inches in height shall be provided in front of electrical service equipment. Where the electrical service equipment is wider than 30 inches, the working space shall not be less than the width of the equipment. No storage of any materials shall be located within the designated working space. This project would provide funds to relocate the miscellaneous items blocking the working space. | BOULDER CITY MUSEUM MAINTENANCE | 9951 | TCA | M&H | Museums | Boulder City | 1996 | 9200 | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 250
0841SFT8 | EXTERIOR LANDING INSTALLATION | 0841 | Section 1008.1 of the 2012 IBC describes the requirements for doors including floor elevations and landings. The floor or landing shall be at the same elevation on each side of the doors, the exterior landing shall not exceed a 2-percent slope and shall have a length measured in the direction of travel of not less than 44 inches. The landing at the doors on the building does not comply with this code and poses a safety hazard. This project would provide for the installation of compliant landings for both doors. | BOULDER CITY MUSEUM MAINTENANCE | 9951 | TCA | M&H | Museums | Boulder City | 1996 | 9200 | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
0841ELE3 | RATED ELECTRICAL ROOM | 0841 | NFPA 13 requires a fire sprinkler in electrical rooms or if the electrical room complies within NFPA Section 5-13.11, which allows an exception to installing fire sprinklers in an electrical room, the electrical room shall meet all of the following requirements: the electrical room is dedicated to electrical equipment only; only dry-type electrical equipment is used; equipment is installed in a 2-hour fire rated enclosure including the floor and deck above and includes protection for penetrations; no combustible storage is permitted to be stored in the electrical room; any openings (doors) in the room must be properly fire rated at 90-minutes and must be self-closing and positive latching; any ventilation ductwork which penetrates the 2-hour barrier must be equipped with the appropriate fire dampers, and all penetrations must be properly fire stopped. This project would provide a 2 hour separation or a fire sprinkler to be installed in the electrical room per NFPA. | BOULDER CITY MUSEUM MAINTENANCE | 9951 | TCA | M&H | Museums | Boulder City | 1996 | 9200 | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 5000
0841SFT5 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 0841 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BOULDER CITY MUSEUM MAINTENANCE | 9951 | TCA | M&H | Museums | Boulder City | 1996 | 9200 | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 9000
0841HVA2 | EVAPORATIVE COOLER REPLACEMENT | 0841 | There are two evaporative coolers that at the time of the survey were not working. They are severely scaled and have reached the end of their serviceable life. This project would provide for two new evaporative coolers to be installed, and includes removal and disposal of the old evaporative coolers and utility connections to the new units. | BOULDER CITY MUSEUM MAINTENANCE | 9951 | TCA | M&H | Museums | Boulder City | 1996 | 9200 | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 8000
0841EXT4 | OVERHEAD DOOR REPLACEMENT | 0841 | There are four overhead coiling doors which are damaged and do not function properly. Exposure and wind have caused the doors to bend, crack and lose their finish. They are original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead coiling doors and replacement with new manually operated overhead coiling doors. | BOULDER CITY MUSEUM MAINTENANCE | 9951 | TCA | M&H | Museums | Boulder City | 1996 | 9200 | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 80000
0841HVA3 | HVAC EQUIPMENT REPLACEMENT | 0841 | The HVAC split system was installed in 1999. It is not energy efficient and has reached the end of its expected and useful life. This project would provide for the installation of a new HVAC split system and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing equipment and all required connections to utilities. | BOULDER CITY MUSEUM MAINTENANCE | 9951 | TCA | M&H | Museums | Boulder City | 1996 | 9200 | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0841PLM1 | WATER HEATER REPLACEMENT | 0841 | There is a 30 gallon gas-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | BOULDER CITY MUSEUM MAINTENANCE | 9951 | TCA | M&H | Museums | Boulder City | 1996 | 9200 | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0841ADA2 | ADA UPGRADES | 0841 | ADA regulations pertaining to building access, route of travel and restrooms has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances, route of travel inside the building and restrooms. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | BOULDER CITY MUSEUM MAINTENANCE | 9951 | TCA | M&H | Museums | Boulder City | 1996 | 9200 | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 500
0841SFT1 | EMERGENCY EYE WASH STATION REFURBISHMENT | 0841 | The emergency eye wash station is original to the building and the domestic water supply piping should be scheduled for replacement. The galvanized pipe is rusting on the inside and contaminating the water rendering the station useless. This project would provide for the removal of the existing piping and installation of new copper domestic water supply. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | BOULDER CITY MUSEUM MAINTENANCE | 9951 | TCA | M&H | Museums | Boulder City | 1996 | 9200 | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 500
1437EXT3 | EXTERIOR FINISHES | 1437 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | WATER TOWER | 9932 | TCA | M&H | NSRM | Carson City | 1987 | 400 | 2017-09-12 | Four to Ten Years | Long-Term Needs | 3 | 4000
1416INT1 | INTERIOR FINISHES | 1416 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This work will be mostly located in the ticket office and ticket counter rooms on the North side of the building. | WABUSKA DEPOT | 9932 | TCA | M&H | NSRM | Carson City | 1906 | 1920 | 2017-09-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4800
1416ELE1 | ELECTRICAL UPGRADE | 1416 | The building was constructed without electrical service. After relocating the structure to it's current location, the electrical system within the building has been retrofitted and rewired as the needs of the agency have changed over the years. This project would provide funding for the entire system to be upgraded to meet the evolving needs of the building. | WABUSKA DEPOT | 9932 | TCA | M&H | NSRM | Carson City | 1906 | 1920 | 2017-09-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 28800
1416EXT3 | EXTERIOR FINISHES | 1416 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | WABUSKA DEPOT | 9932 | TCA | M&H | NSRM | Carson City | 1906 | 1920 | 2017-09-12 | Four to Ten Years | Long-Term Needs | 3 | 19200
1416HVA1 | HVAC INSTALLATION | 1416 | The building does not have any heating, ventilation and air conditioning (HVAC) equipment. At the time of the survey of 2008, there was a portable propane fired heater available to heat portions of the building. This is not an efficient source of heat and the extreme changes in temperature will cause accelerated deterioration of this historical building. It is recommended that the building be retrofitted with an HVAC system to maintain constant temperatures in the building. Along with this equipment, insulation should be installed according to current standards to ensure energy efficiency. An R-19 wall and R-38 ceiling insulation is suggested. The regulated indoor temperatures will slow down the deterioration of the building and provide comfort for the occupants. The estimate has been inflated to provide for costs related to design and construction of a building on the National Register of Historical Buildings. | WABUSKA DEPOT | 9932 | TCA | M&H | NSRM | Carson City | 1906 | 1920 | 2017-09-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 75000
1416ENR1 | LIGHTING UPGRADE | 1416 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts to current standards, resulting in increased efficiency and reduced costs associated with illumination. Any electrical wiring upgrades are not included in this estimate. | WABUSKA DEPOT | 9932 | TCA | M&H | NSRM | Carson City | 1906 | 1920 | 2017-09-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5760
1416SFT1 | FIRE SPRINKLER INSTALLATION | 1416 | This building does not have an automatic fire suppression system. Nevada State Fire Marshal NAC 477.915 (c) requires buildings having a floor area exceeding 12,000 s.f. on any floor or 24,000 s.f. on all floors, or which contain a B or R-1 occupancy, be scheduled for installation of an automatic fire suppression system during the next remodeling of, or addition to the building. Backflow prevention is included in this estimate. This building is classified as a B occupancy. This project is in design under CIP 07-S03 and the estimate is based off of that project. This project or a portion thereof was previously recommended in the FCA report dated 01/13/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/17/2008. | WABUSKA DEPOT | 9932 | TCA | M&H | NSRM | Carson City | 1906 | 1920 | 2017-09-12 | Immediate to Two Years | Currently Critical | 1 | 34560
1647INT1 | INTERIOR FINISHES | 1647 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | COMFORT STATION | 9932 | TCA | M&H | NSRM | Carson City | 1990 | 373 | 2017-09-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1865
1647EXT2 | REPLACE ROOF | 1647 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. The extreme temperature fluctuations throughout the year, consistent wind and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next two to four years with a 50 year asphalt composition roofing shingle and new underlayments. Color to match the other structures on site This project or a portion thereof was previously recommended in the FCA report dated 01/13/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/17/2008. | COMFORT STATION | 9932 | TCA | M&H | NSRM | Carson City | 1990 | 373 | 2017-09-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5595
1647EXT3 | EXTERIOR FINISHES | 1647 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | COMFORT STATION | 9932 | TCA | M&H | NSRM | Carson City | 1990 | 373 | 2017-09-12 | Four to Ten Years | Long-Term Needs | 3 | 3730
9932ELE2 | POLE LIGHTING INSTALLATION | 9932 | This site houses historical documents and irreplaceable artifacts related to the history of the V&T Railroad and the Comstock region as well as expensive machinery in the Restoration Shop. There is not enough lighting around the site which may be contributing to recent thefts. This project would provide funding for purchase and installation of sixteen 30 foot tall light poles including 30" diameter raised concrete bases, electrical trenching, conduit, wiring and connections to existing utilities. These will be installed around the entire perimeter of the site and in the parking areas. | NEVADA STATE RAILROAD MUSEUM CC SITE | 9932 | TCA | M&H | NSRM | Carson City | 0 |  | 2017-09-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 147264
9932SEC2 | REPLACE EXTERIOR DOORS AND OPENERS | 9932 | Problems exist with the exit doors and overhead doors at the Annex, Annex Addition, and Restoration Shop. Most of the doors are original equipment. Repairs to these doors is difficult because the doors are no longer manufactured or they are custom sizes. This project recommends replacing the overhead doors with motorized equipment and controls. The exit doors should be replaced with a commercial grade door system with locks to match the existing site master lock system. Estimates are based on 10 overhead doors, at $8,000.00 each, and 8 exit doors at $4,000.00 each. This project or a portion thereof was previously recommended in the FCA report dated 01/13/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/17/2008. | NEVADA STATE RAILROAD MUSEUM CC SITE | 9932 | TCA | M&H | NSRM | Carson City | 0 |  | 2017-09-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 112000
9932ELE1 | ELECTRICAL UPGRADE | 9932 | The buildings at the site share a common electrical transformer and feed off the main service panel. The main panel and sub panels for the Annex and Restoration Shop are at their maximum capacity. This project recommends replacing and upgrading the main service panel and sub panels at the Annex, Annex Addition and Restoration Shop to provide needed additional capacity. This estimate assumes that the existing underground conduit feed could be used, therefore, no earthwork is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 01/13/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/17/2008. | NEVADA STATE RAILROAD MUSEUM CC SITE | 9932 | TCA | M&H | NSRM | Carson City | 0 |  | 2017-09-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 100000
9932SIT3 | PAVE FIRE ACCESS ROAD | 9932 | The site is served by dirt and gravel fire access roads, which are often impassable in inclement weather. The 2006 International Fire Code 503.2 addresses requirements for all-weather access roads. This project would provide for the installation of asphalt concrete paving and compacted base on the fire access road surrounding the site. Final acceptance falls to the responding fire authority, which should be consulted for additional local requirements if required prior to beginning design and construction. Additional comments by the Fire Marshal's office may impact final cost. The unit costs were adjusted for a thicker base and finish to support the loads of response equipment. 5" of asphalt and 8" of base was used to generate this estimate. This project or a portion thereof was previously recommended in the FCA report dated 01/13/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/17/2008. | NEVADA STATE RAILROAD MUSEUM CC SITE | 9932 | TCA | M&H | NSRM | Carson City | 0 |  | 2017-09-12 | Immediate to Two Years | Currently Critical | 1 | 195000
9932SEC1 | INSTALL SECURITY ALARM SYSTEM | 9932 | This site houses historical documents and irreplaceable artifacts related to the history of the V&T Railroad and the Comstock region. There is no security alarm to protect these items. This project would provide for the installation of a sitewide security system. The alarm controls should be centrally located in the Interpretive Center and encompass the Annex buildings, Restoration Shop, Wabuska Depot and Nelson House. Costs were based on the total square footage of the buildings. This project or a portion thereof was previously recommended in the FCA report dated 01/13/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/17/2008. | NEVADA STATE RAILROAD MUSEUM CC SITE | 9932 | TCA | M&H | NSRM | Carson City | 0 |  | 2017-09-12 | Immediate to Two Years | Currently Critical | 1 | 127940
9932SIT6 | SIGN REPLACEMENT | 9932 | The sign for the Railroad Museum on highway 395 is old, dilapidated and in need of replacement. Staff reported that 75% of the visitors to the museum are drive-by visitors. The new sign should be designed for better curb appeal in order to attract visitors to the museum. This project would provide funding for removal and disposal of the existing sign and replacement the sign with an aesthetically pleasing. The new sign may need to conform to Carson City and NDOT requirements due to the location on Highway 395. | NEVADA STATE RAILROAD MUSEUM CC SITE | 9932 | TCA | M&H | NSRM | Carson City | 0 |  | 2017-09-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
9932SFT1 | INSTALL FIRE ALARM SYSTEM | 9932 | This site houses historical documents and irreplaceable artifacts related to the history of the V&T Railroad and the Comstock region. There is no fire alarm to protect these items. This project would provide for the installation of a site wide alarm system and upgrade to the existing system where applicable. The alarm controls should be centrally located in the Interpretive Center and encompass the Annex buildings, Restoration Shop, Wabuska Depot and Nelson House. Costs were based on the total square footage of the buildings. This project or a portion thereof was previously recommended in the FCA report dated 01/13/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/17/2008. | NEVADA STATE RAILROAD MUSEUM CC SITE | 9932 | TCA | M&H | NSRM | Carson City | 0 |  | 2017-09-12 | Immediate to Two Years | Currently Critical | 1 | 153528
9932SIT5 | FENCE REPLACEMENT | 9932 | The wood split rail fencing around certain areas of the site is reaching the end of its expected life. This fencing serves to keep visitors off of planted areas as well as directing people to proper walkways when traveling to and from the buildings. This project would provide funding for removal and installation of 1,320 lineal feet of two rail, 3' high cedar fencing. | NEVADA STATE RAILROAD MUSEUM CC SITE | 9932 | TCA | M&H | NSRM | Carson City | 0 |  | 2017-09-12 | Four to Ten Years | Long-Term Needs | 3 | 19140
9932SIT7 | SIDEWALK INSTALLATION | 9932 | There is no sidewalk from the Chamber of Commerce building to the existing walkways at the Railroad Museum. This building is an information center for visitors on activities in Carson City including the adjacent Railroad Museum. The staff has indicated that there is a need for a sidewalk between these buildings. This project would provide for the installation of 800 SF of 4" thick Portland Cement concrete sidewalk. | NEVADA STATE RAILROAD MUSEUM CC SITE | 9932 | TCA | M&H | NSRM | Carson City | 0 |  | 2017-09-12 | Four to Ten Years | Long-Term Needs | 3 | 8000
9932SIT9 | SLURRY SEAL ASPHALT PAVING | 9932 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site wide including access roads and parking areas. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 100,000 square feet of asphalt area was used to generate this estimate. | NEVADA STATE RAILROAD MUSEUM CC SITE | 9932 | TCA | M&H | NSRM | Carson City | 0 |  | 2017-09-12 | Four to Ten Years | Long-Term Needs | 3 | 60000
9932SIT8 | TURNTABLE RESTORATION | 9932 | The railroad turntable located on the south side of the site is in need of re-leveling and restoration. The structure is vital to the movement of the railroad cars and engines. It is in desperate need of repair and rehabilitation. This project would provide funding to bring the structure back to a restored fully functioning condition including timber restoration or replacement and leveling. | NEVADA STATE RAILROAD MUSEUM CC SITE | 9932 | TCA | M&H | NSRM | Carson City | 0 |  | 2017-09-12 | Immediate to Two Years | Currently Critical | 1 | 150000
9932SIT4 | STORAGE BUILDING | 9932 | There are a couple of fenced areas on the west side of the site for storage of rail cars, equipment and other miscellaneous items for use in the restoration efforts. The equipment is exposed to the elements and subject to theft and vandalism. This project recommends construction of a 60' x 120' storage building to provide more adequate storage for this equipment. An engineered steel building was used for this estimate. | NEVADA STATE RAILROAD MUSEUM CC SITE | 9932 | TCA | M&H | NSRM | Carson City | 0 |  | 2017-09-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 576000
0104INT1 | INTERIOR FINISHES | 0104 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | NELSON HOUSE | 9932 | TCA | M&H | NSRM | Carson City | 1935 | 720 | 2017-09-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3600
0104EXT3 | EXTERIOR FINISHES | 0104 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | NELSON HOUSE | 9932 | TCA | M&H | NSRM | Carson City | 1935 | 720 | 2017-09-12 | Four to Ten Years | Long-Term Needs | 3 | 7200
0104SFT1 | FIRE SPRINKLER INSTALLATION | 0104 | This building does not have an automatic fire suppression system. Nevada State Fire Marshal NAC 477.915 (c) requires buildings having a floor area exceeding 12,000 s.f. on any floor or 24,000 s.f. on all floors, or which contain a B or R occupancy, be scheduled for installation of an automatic fire suppression system during the next remodeling of, or addition to the building. Backflow prevention is included in this estimate. This building is classified as a R occupancy. CIP 07-S03 does not currently encompass this building, but it is in the process of being added as an alternate. The estimate is based off of that project. | NELSON HOUSE | 9932 | TCA | M&H | NSRM | Carson City | 1935 | 720 | 2017-09-12 | Immediate to Two Years | Currently Critical | 1 | 12960
0969EXT2 | EXTERIOR FINISHES | 0969 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | ANNEX | 9932 | TCA | M&H | NSRM | Carson City | 1978 | 13600 | 2017-09-12 | Four to Ten Years | Long-Term Needs | 3 | 24000
0969INT2 | INSTALL CONCRETE WALKWAYS | 0969 | The building interior has a mix of dirt and concrete floors. This project recommends concrete flat work be installed for the main walkways between the rail cars. This project would provide for the installation of 4,000 SF of 4" thick concrete sidewalk. This project or a portion thereof was previously recommended in the FCA report dated 01/13/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/17/2008. | ANNEX | 9932 | TCA | M&H | NSRM | Carson City | 1978 | 13600 | 2017-09-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 40000
0969EXT1 | REROOF BUILDING | 0969 | Half of the building was re-roofed recently with a single-ply membrane system. The remaining original metal roof was in fair condition at the time of the survey. The rest of this building should be re-roofed as soon as possible to match the age and type of membrane as close as possible. This project or a portion thereof was previously recommended in the FCA report dated 01/13/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/17/2008. | ANNEX | 9932 | TCA | M&H | NSRM | Carson City | 1978 | 13600 | 2017-09-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 90000
0969INT1 | INSTALL BUILDING INSULATION | 0969 | This building has no insulation. The temperature extremes are contributing to accelerated decay of the contents, which include railroad cars and other historical artifacts awaiting restoration and/or display. This project will install batt insulation in the walls and ceilings to help moderate temperature fluctuations. It may be possible to use a foamed-in system to fill the cavities where applicable; costs are similar to the batt insulation provided for in this project. This project or a portion thereof was previously recommended in the FCA report dated 01/13/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/17/2008. | ANNEX | 9932 | TCA | M&H | NSRM | Carson City | 1978 | 13600 | 2017-09-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 42000
0861EXT3 | EXTERIOR FINISHES | 0861 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | JACOBSEN INTERPRETIVE CENTER | 9932 | TCA | M&H | NSRM | Carson City | 1988 | 10536 | 2017-09-12 | Four to Ten Years | Long-Term Needs | 3 | 105360
0861ADA1 | INTERIOR ADA RAMP UPGRADE | 0861 | There is an ADA ramp inside the building on the North side that provides access to the main floor of the museum. The ramp does not fully meet ADA requirements, specifically the slope is greater than 1:12. This project would provide for removing the existing ramp and replacing it with a new ADA compliant ramp. Americans with Disabilities Act Accessibility Guidelines (ADAAG) Section 4.8 - 1998 was referenced for this project. | JACOBSEN INTERPRETIVE CENTER | 9932 | TCA | M&H | NSRM | Carson City | 1988 | 10536 | 2017-09-12 | Immediate to Two Years | Currently Critical | 1 | 50000
0861INT2 | CARPET REPLACEMENT | 0861 | The carpet in the staff office and souvenir shop is showing signs of extreme wear. It is recommended that the carpet be replaced with heavy duty commercial grade carpet in the next two to three years. | JACOBSEN INTERPRETIVE CENTER | 9932 | TCA | M&H | NSRM | Carson City | 1988 | 10536 | 2017-09-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4200
0861INT3 | JANITORS CLOSET REPAIR | 0861 | The mop sink in the Janitors Closet is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | JACOBSEN INTERPRETIVE CENTER | 9932 | TCA | M&H | NSRM | Carson City | 1988 | 10536 | 2017-09-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
0861EXT4 | GUTTER REPLACEMENT | 0861 | The existing gutter and downspouts around the building have numerous joints that have proven impossible to seal against leaks. There is also a large section of gutter missing on the west elevation. This project would replace the existing segmented gutter with seamless gutter and downspouts. | JACOBSEN INTERPRETIVE CENTER | 9932 | TCA | M&H | NSRM | Carson City | 1988 | 10536 | 2017-09-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
0861INT1 | INTERIOR FINISHES | 0861 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | JACOBSEN INTERPRETIVE CENTER | 9932 | TCA | M&H | NSRM | Carson City | 1988 | 10536 | 2017-09-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 52680
0969HVA3 | HVAC INSTALLATION | 0969 | This building is used to restore historical artifacts and equipment. There is inadequate heating, no cooling and no humidification control in the building, which can adversely affect the lifespan of the artifacts and equipment. It is recommended that the heating equipment be upgraded and cooling equipment installed to maintain minimum and maximum temperatures in the building. The regulated indoor temperatures will slow down the deterioration of the building and equipment as well as provide comfort for the occupants. This project also recommends the installation of a humidification control system for the building. This project should be implemented concurrent with or following the "Building Insulation" project. | ANNEX | 9932 | TCA | M&H | NSRM | Carson City | 1978 | 13600 | 2017-09-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 250000
0861HVA1 | HVAC SYSTEM REPLACEMENT | 0861 | This building is used to store and display historical artifacts and equipment. There is inadequate heating, no cooling and no humidification control in the building, which can adversely affect the lifespan of the artifacts and equipment. Of the four suspended heaters, two are due for replacement. It is recommended that the heating equipment be upgraded and cooling equipment installed to maintain minimum and maximum temperatures in the building. The regulated indoor temperatures will slow down the deterioration of the building and equipment as well as provide comfort for the occupants. This project also recommends the installation of a humidification control system for the building and replacement of the non-operational ceiling fans. This project or a portion thereof was previously recommended in the FCA report dated 01/13/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/17/2008. | JACOBSEN INTERPRETIVE CENTER | 9932 | TCA | M&H | NSRM | Carson City | 1988 | 10536 | 2017-09-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 200000
0861SFT1 | FIRE SPRINKLER INSTALLATION | 0861 | This building does not have an automatic fire suppression system. Nevada State Fire Marshal NAC 477.915 (c) requires buildings having a floor area exceeding 12,000 s.f. on any floor or 24,000 s.f. on all floors, or which contain a B or R-1 occupancy, be scheduled for installation of an automatic fire suppression system during the next remodeling of, or addition to the building. Backflow prevention is included in this estimate. This building is partially classified as a B occupancy. This project is in design under CIP 07-S03 and the estimate is based off of that project. This project or a portion thereof was previously recommended in the FCA report dated 01/13/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/17/2008. | JACOBSEN INTERPRETIVE CENTER | 9932 | TCA | M&H | NSRM | Carson City | 1988 | 10536 | 2017-09-12 | Immediate to Two Years | Currently Critical | 1 | 189648
0861ELE1 | LIGHTING UPGRADE | 0861 | The museum's existing lighting fixtures are a mixture of T-8 and T-12 ballasted fluorescent lights, high pressure lighting, and track display units. This project will upgrade general lighting fixtures in the offices and common areas to T-8 lamps with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. The project provides a modular track lighting system for display areas, permitting the option of general or pinpoint lighting, depending on the illumination needs at the time. Additional funds are included to provide color corrected and specialty lights for these new fixtures. Occupancy sensors will be installed in restrooms and other low occupancy areas for additional savings. This project or a portion thereof was previously recommended in the FCA report dated 01/13/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/17/2008. | JACOBSEN INTERPRETIVE CENTER | 9932 | TCA | M&H | NSRM | Carson City | 1988 | 10536 | 2017-09-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 84288
0861PLM1 | WATER HEATER REPLACEMENT | 0861 | The average life span of a water heater is eight to ten years. The existing 17 gallon electric water heater in the building has reached the end of its expected life and is not energy efficient. It is recommended that a new gas appliance be installed for more efficient use of energy. This estimate includes removal and disposal of the old water heater and: 100 feet of gas pipe, fittings, couplers, and labor for installation. | JACOBSEN INTERPRETIVE CENTER | 9932 | TCA | M&H | NSRM | Carson City | 1988 | 10536 | 2017-09-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0861SFT2 | EGRESS LIGHTING UPGRADE | 0861 | The existing emergency lights are old and in need of replacement. This project would provide for the replacement of the emergency lights inside of the facility. | JACOBSEN INTERPRETIVE CENTER | 9932 | TCA | M&H | NSRM | Carson City | 1988 | 10536 | 2017-09-12 | Immediate to Two Years | Currently Critical | 1 | 3000
0971HVA2 | HVAC INSTALLATION | 0971 | The building does not have any heating, ventilation and air conditioning (HVAC) equipment. It is recommended that the building be retrofitted with an HVAC system to maintain constant temperatures in the building. Along with this equipment, insulation should be installed according to current standards to ensure energy efficiency. An R-19 wall and R-38 ceiling insulation is suggested and recommended in another project. | ANNEX ADDITION | 9932 | TCA | M&H | NSRM | Carson City | 1997 | 19000 | 2017-09-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 300000
0971EXT1 | EXTERIOR FINISHES | 0971 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | ANNEX ADDITION | 9932 | TCA | M&H | NSRM | Carson City | 1997 | 19000 | 2017-09-12 | Four to Ten Years | Long-Term Needs | 3 | 38000
0971ENR1 | LIGHTING UPGRADE | 0971 | The existing lighting fixtures are a mix of the older fluorescent type and metal halide lamps. This project will upgrade fluorescent fixtures to T-8 lamps with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. Additional light fixtures are also included in this estimate. Any electrical wiring upgrades are not included in this estimate. | ANNEX ADDITION | 9932 | TCA | M&H | NSRM | Carson City | 1997 | 19000 | 2017-09-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 57000
0969SFT2 | SMOKE DETECTOR UPGRADE | 0969 | According to NAC 477.915 (3), "Upon failure of a smoke detector which is powered by a battery and installed in a building owned or occupied by the state, the smoke detector must be replaced by a smoke detector which is connected to the wiring of the building and has a battery as a backup source of power." The existing smoke detectors appeared to not be working and additional smoke detectors should be installed throughout the building. | ANNEX | 9932 | TCA | M&H | NSRM | Carson City | 1978 | 13600 | 2017-09-12 | Immediate to Two Years | Currently Critical | 1 | 6000
0971INT1 | INSTALL BUILDING INSULATION | 0971 | This building has no insulation. The temperature extremes are contributing to accelerated decay of the contents, which include railroad cars and other historical artifacts awaiting restoration and/or display. This project will install batt insulation in the walls and ceilings to help moderate temperature fluctuations. It may be possible to use a foamed-in system to fill the cavities where applicable; costs are similar to the batt insulation provided for in this project. R-19 for walls and R-38 for ceilings is recommended. This project or a portion thereof was previously recommended in the FCA report dated 01/13/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/17/2008. | ANNEX ADDITION | 9932 | TCA | M&H | NSRM | Carson City | 1997 | 19000 | 2017-09-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 66500
0971INT2 | INSTALL INTERIOR CONCRETE WALKWAYS | 0971 | The majority of the building interior has dirt floors. This project recommends concrete flat work be installed for the main walkways between the rail cars. This project would provide for the installation of 3,200 SF of 4" thick concrete sidewalk. This project or a portion thereof was previously recommended in the FCA report dated 01/13/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/17/2008. | ANNEX ADDITION | 9932 | TCA | M&H | NSRM | Carson City | 1997 | 19000 | 2017-09-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 32000
0970ENR1 | LIGHTING UPGRADE | 0970 | The existing lighting fixtures are a mix of the older fluorescent type and metal halide lamps. This project will upgrade fluorescent fixtures to T-8 lamps with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. Additional light fixtures are also included in this estimate. Any electrical wiring upgrades are not included in this estimate. | RESTORATION SHOP | 9932 | TCA | M&H | NSRM | Carson City | 1980 | 6400 | 2017-09-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 21000
0969ENR1 | LIGHTING UPGRADE | 0969 | The existing lighting fixtures are a mix of the older fluorescent type and metal halide lamps. This project will upgrade fluorescent fixtures to T-8 lamps with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. Additional light fixtures are also included in this estimate. Any electrical wiring upgrades are not included in this estimate. | ANNEX | 9932 | TCA | M&H | NSRM | Carson City | 1978 | 13600 | 2017-09-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 36000
0970EXT2 | EXTERIOR FINISHES | 0970 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | RESTORATION SHOP | 9932 | TCA | M&H | NSRM | Carson City | 1980 | 6400 | 2017-09-12 | Four to Ten Years | Long-Term Needs | 3 | 14000
0970SFT1 | SMOKE DETECTOR UPGRADE | 0970 | According to NAC 477.915 (3), "Upon failure of a smoke detector which is powered by a battery and installed in a building owned or occupied by the state, the smoke detector must be replaced by a smoke detector which is connected to the wiring of the building and has a battery as a backup source of power." The existing smoke detectors appeared to not be working and additional smoke detectors should be installed throughout the building. | RESTORATION SHOP | 9932 | TCA | M&H | NSRM | Carson City | 1980 | 6400 | 2017-09-12 | Immediate to Two Years | Currently Critical | 1 | 5000
0970HVA1 | HVAC UPGRADE | 0970 | This building is used to restore historical artifacts and equipment. There is inadequate heating, no cooling and no humidification control in the building, which can adversely affect the lifespan of the artifacts and equipment. It is recommended that the heating equipment be upgraded and cooling equipment installed to maintain minimum and maximum temperatures in the building. The regulated indoor temperatures will slow down the deterioration of the building and equipment as well as provide comfort for the occupants. This project also recommends the installation of a humidification control system for the building. | RESTORATION SHOP | 9932 | TCA | M&H | NSRM | Carson City | 1980 | 6400 | 2017-09-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 150000
0971ENV1 | HAZARDOUS MATERIALS CONTAINMENT | 0971 | There is a maintenance office and shop in the south-east corner of the building. This area has two hazardous storage containers, but is in need of two more to maintain OSHA compliance. This project provides funding for the purchase of two hazardous storage containers for this shop area. | ANNEX ADDITION | 9932 | TCA | M&H | NSRM | Carson City | 1997 | 19000 | 2017-09-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
2128INT3 | INTERIOR FINISHES | 2128 | The interior finishes are in fair condition. Most of the walls and ceilings are unfinished wood, but there are painted walls and ceilings in the restrooms and the shop areas. It is recommended that the finished interior walls and ceilings be painted at least once in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | EAST ELY RAILROAD FREIGHT BARN | 9857 | TCA | M&H | Museums | Ely | 1906 | 12865 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
2128INT2 | FLOORING REPLACEMENT - FREIGHT OFFICE | 2128 | The "Battleship" linoleum flooring in the Freight Office is damaged and reaching the end of its useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new "Battleship" linoleum. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 06/03/2002. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/25/2011. | EAST ELY RAILROAD FREIGHT BARN | 9857 | TCA | M&H | Museums | Ely | 1906 | 12865 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8400
2128CUL1 | KITCHEN INSTALLATION | 2128 | The building does not have any culinary equipment. There are many special events held in the Freight Barn each year that benefit the museum through exposure and rental fees. Equipping the building with culinary equipment would provide additional accommodations for future special events. This project recommends installing mid range, high quality culinary equipment, a sink, cabinets and the plumbing and electrical utilities that they would require. | EAST ELY RAILROAD FREIGHT BARN | 9857 | TCA | M&H | Museums | Ely | 1906 | 12865 | 2017-11-07 | Four to Ten Years | Long-Term Needs | 3 | 75000
2128EXT3 | WINDOW REPLACEMENT | 2128 | The windows are original, single pane construction in a wooden frame. These older windows are drafty, not energy efficient and the wooden frames have deteriorated significantly. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 6 units including wooden frames and includes additional costs for the unique historical nature of the building. Removal and disposal of the existing windows is included in this estimate. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements for this building. | EAST ELY RAILROAD FREIGHT BARN | 9857 | TCA | M&H | Museums | Ely | 1906 | 12865 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
2128EXT4 | EXTERIOR DECK REPAIRS | 2128 | The building has a boardwalk on the street side of the building and a loading dock on the track side. They were recently refurbished with new wood planks that were nailed to the framing. The nails are proving to be insufficient and should be replaced with screws. As the wood ages, it pushes the nails out and causes a safety hazard. This project provides for removing the nails and replacing them with deck screws along the entire boardwalk and loading dock. | EAST ELY RAILROAD FREIGHT BARN | 9857 | TCA | M&H | Museums | Ely | 1906 | 12865 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
2128ENR1 | INSULATE BUILDING | 2128 | This building has no insulation. The temperature extremes are contributing to accelerated decay of the contents, which include historical artifacts awaiting restoration and/or on display. This project will install batt insulation in the walls and ceilings to help moderate temperature fluctuations. It may be possible to use a foamed-in system to fill the cavities where applicable; costs are similar to the batt insulation provided for in this project. This project should be implemented before or concurrent with the HVAC System Installation project and coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. | EAST ELY RAILROAD FREIGHT BARN | 9857 | TCA | M&H | Museums | Ely | 1906 | 12865 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 45027
2128HVA1 | HVAC SYSTEM INSTALLATION | 2128 | This building is equipped with a wood burning stove in the freight office and two wall mounted electric heaters in the restrooms and does not have any cooling equipment. The rest of the building is not conditioned space. Future plans for the building include interactive displays, a community center, and special events which would all benefit from adding heating and cooling for the entire building. This project would provide for replacing the existing heaters with roof mounted propane fired packaged units that provide heating as well as air conditioning to the entire building. Propane gas service will be required and is included in the cost. This project should be implemented after or concurrent with the Insulate Building project and coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 06/03/2002. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/25/2011. | EAST ELY RAILROAD FREIGHT BARN | 9857 | TCA | M&H | Museums | Ely | 1906 | 12865 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 77190
2128ENR2 | LIGHTING UPGRADE | 2128 | The existing lighting fixtures are the older fluorescent and incandescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts and compact fluorescent lights are suggested. Occupancy sensors will be installed in restrooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. | EAST ELY RAILROAD FREIGHT BARN | 9857 | TCA | M&H | Museums | Ely | 1906 | 12865 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19297
2128ADA1 | ADA SIGNAGE | 2128 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required and that the restroom ADA signs be moved to a compliant location. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | EAST ELY RAILROAD FREIGHT BARN | 9857 | TCA | M&H | Museums | Ely | 1906 | 12865 | 2017-11-07 | Immediate to Two Years | Currently Critical | 1 | 1500
2128EXT2 | EXTERIOR FINISHES | 2128 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the metal panels and wood and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 9-10 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | EAST ELY RAILROAD FREIGHT BARN | 9857 | TCA | M&H | Museums | Ely | 1906 | 12865 | 2017-11-07 | Four to Ten Years | Long-Term Needs | 3 | 64325
2128ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 2128 | This building does not contain a drinking fountain. It is recommended to install a drinking fountain for the comfort of the occupants. The 2006 IBC Section 1109.5 states where a water fountain is provided, at least half should be accessible. This project would provide funding for the purchase and installation of an accessible fixed high/ low ADA drinking fountain. | EAST ELY RAILROAD FREIGHT BARN | 9857 | TCA | M&H | Museums | Ely | 1906 | 12865 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
2227STR1 | STRUCTURAL REPAIRS | 2227 | Due to the age of the building and the structural codes at the time, the structural system may be deficient and should be evaluated and repaired. Some shoring work has been done in the basement by applying gunite to the foundation walls, but no other major structural upgrades have taken place since the State acquired the building in 1992. The estimate is a general figure representing a likely scenario of installing blocking, steel structural ties, cables. etc... to increase the lateral and vertical load resistance. An evaluation and design must be conducted by a licensed structural engineer, of which the costs are not included in this estimate. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 06/03/2002. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/25/2011. | EAST ELY RAILROAD DEPOT | 9857 | TCA | M&H | Museums | Ely | 1907 | 8600 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 125000
2227EXT4 | SHED ROOF REPLACEMENT | 2227 | The metal roof on the north elevation of the building was in poor condition at the time of the survey and had active leaks. This shed roof partially covers the boarding platform and has a gutter and downspout system that is in poor condition. When the gutters leak, water pools up and freezes on the boarding platform creating a safety hazard. The gutters and downspouts around the rest of the building are also in poor condition with active leaks. It is recommended to re-roof the metal shed roof and repair or replace the gutters and downspouts around the entire building. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 06/03/2002. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/25/2011. | EAST ELY RAILROAD DEPOT | 9857 | TCA | M&H | Museums | Ely | 1907 | 8600 | 2017-11-07 | Immediate to Two Years | Currently Critical | 1 | 25000
2227EXT5 | EXTERIOR FINISHES | 2227 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting the wood trim and soffits, power washing and painting the stucco, cleaning and sealing the stone masonry and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted, sealed and caulked in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. | EAST ELY RAILROAD DEPOT | 9857 | TCA | M&H | Museums | Ely | 1907 | 8600 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 43000
2227ENR1 | LIGHTING UPGRADE | 2227 | The existing lighting fixtures are the older fluorescent and incandescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts and compact fluorescent lights are suggested. Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. | EAST ELY RAILROAD DEPOT | 9857 | TCA | M&H | Museums | Ely | 1907 | 8600 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12900
2128SFT3 | FIRE SUPPRESSION SYSTEM INSTALLATION | 2128 | This building houses irreplaceable records for the site dating back to the early 1900s. The square footage of the building exceeds 12,000 square feet and does not have an automatic fire suppression system. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 or R-2 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 06/03/2002. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/25/2011. | EAST ELY RAILROAD FREIGHT BARN | 9857 | TCA | M&H | Museums | Ely | 1906 | 12865 | 2017-11-07 | Immediate to Two Years | Currently Critical | 1 | 90055
2227INT1 | INTERIOR FINISHES | 2227 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. | EAST ELY RAILROAD DEPOT | 9857 | TCA | M&H | Museums | Ely | 1907 | 8600 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 43000
2227EXT3 | WINDOW REPLACEMENT | 2227 | The windows are original, single pane construction in a wooden frame. These older windows are drafty, not energy efficient and the wooden frames have deteriorated significantly. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 44 units including wooden frames and includes additional costs for the unique historical nature of the building. Removal and disposal of the existing windows is included in this estimate. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements for this building. This project or a portion thereof was previously recommended in the FCA report dated 06/03/2002. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/25/2011. | EAST ELY RAILROAD DEPOT | 9857 | TCA | M&H | Museums | Ely | 1907 | 8600 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 66000
2227HVA1 | HVAC SYSTEM UPGRADE | 2227 | The existing HVAC system consists of electric baseboard heaters and several window mounted air conditioners. The electric heaters are inefficient and the air conditioners only cover small areas of the building. There is a need for cooling equipment throughout the building to provide a comfortable interior environment in the summer. This project would provide for replacing the existing equipment with a central HVAC system including exterior ground mounted propane fired packaged units that provide heating as well as air conditioning and installing duct work and controls. Propane gas service will be required and is included in the cost. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 06/03/2002. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/25/2011. | EAST ELY RAILROAD DEPOT | 9857 | TCA | M&H | Museums | Ely | 1907 | 8600 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 172000
2227ADA1 | ADA AUDIO/ VISUAL PRESENTATION | 2227 | The Railroad Depot is open to the public for tours and train rides. The second floor is home to most of the historical Depot artifacts and where a large portion of the tour takes place. There is no ADA access to this area. This project would provide for an ADA accessible location inside the lower level of the building for an audio / visual (A/V) presentation of the inaccessible portions of the Depot and site. This project includes funds for an audio / visual consultant to outline and document the exhibits and purchase and installation of all required A/V equipment including signage, TDD equipment and minor remodeling of the public area of the building as required to accommodate this program. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. The 2006 IBC, ICC/ANSI A117.1 - 2003, NRS 338.180 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) was used as a reference for this project. | EAST ELY RAILROAD DEPOT | 9857 | TCA | M&H | Museums | Ely | 1907 | 8600 | 2017-11-07 | Immediate to Two Years | Currently Critical | 1 | 25000
9856ADA1 | ADA ACCESS / ROUTE OF TRAVEL UPGRADES | 9856 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical and mental limitations. There are numerous areas between the sidewalk and the main entry doors that do not comply with ADA guidelines. The sidewalks, stairway and entry landing are not compliant and should be scheduled for repairs. Due to the slope at the entry landing, the adjacent ramps will require modifications to meet the new elevation of the landing. The stairway will need to be completely rebuilt. If the handrails are re-used, proper returns will need to be retrofitted onto them. Directional signage from the parking spaces to the entry should be included as well. The 2006 IBC, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. There are deficiencies in the accessible route from the bus stop and the parking spaces to the entry stairs and accessible ramp. These accessible elements are under the purview of UNR and should be addressed to provide the public with an ADA accessible route from the parking, bus stop and entrance into the building. | NEVADA HISTORICAL SOCIETY SITE | 9856 | TCA | M&H | HistSoc | Reno | 0 |  | 2018-08-04 | Immediate to Two Years | Currently Critical | 1 | 150000
0401SFT4 | EXIT SIGN UPGRADES | 0401 | The existing exit signs in the building are older types and should be replaced with new self-illuminated or LED style signs with battery-backed internal systems. The estimate is based on purchasing and installing 22 exit signs at $450 each. IBC - 2006 Chapter 10 was referenced for this project. | NEVADA HISTORICAL SOCIETY | 9856 | TCA | M&H | HistSoc | Reno | 1968 | 22200 | 2018-08-04 | Immediate to Two Years | Currently Critical | 1 | 9900
0401SFT2 | STAIR LANDING INSTALLATION | 0401 | There are a total of five exterior stairways coming out of the building, not including the one at the south side main entrance. Four of these stairways do not have a bottom landing. This does not comply with 2006 IBC Section 1009.4 which describes the requirements for landings at stairways including that the width and length of the landing shall not be less than the width of the stairway. The fifth stairway has a bottom landing that slopes towards the stairway and the building. This landing is on the east entrance and creates a situation where water pools up and freezes creating a slipping hazard. This project addresses installing four new landings designed to current code and removing and replacing the landing at the east entrance. | NEVADA HISTORICAL SOCIETY | 9856 | TCA | M&H | HistSoc | Reno | 1968 | 22200 | 2018-08-04 | Immediate to Two Years | Currently Critical | 1 | 7500
0401SFT5 | ROOF HATCH REPLACEMENT | 0401 | The roof hatch is original to the building and has reached the end of its useful life. The compression spring operators do not function properly, the latches and handles are worn and the seals and flashing have deteriorated. A faulty roof hatch is a safety hazard to anyone accessing the roof. This project would provide for removal and disposal of the existing roof hatch and purchase and installation of a new roof hatch. | NEVADA HISTORICAL SOCIETY | 9856 | TCA | M&H | HistSoc | Reno | 1968 | 22200 | 2018-08-04 | Immediate to Two Years | Currently Critical | 1 | 3500
0401INT1 | INTERIOR FINISHES | 0401 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | NEVADA HISTORICAL SOCIETY | 9856 | TCA | M&H | HistSoc | Reno | 1968 | 22200 | 2018-08-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 111000
0401SFT3 | FIRE SUPPRESSION SYSTEM REPLACEMENT | 0401 | There is a Halon automatic fire suppression system in a portion of the building. This system is outdated and the chemical it uses has been phased out. This project recommends replacing the existing system with a double-interlock pre-action fire suppression system and implementing a comprehensive testing and service schedule. Removal and disposal of the existing system is included in the estimate. | NEVADA HISTORICAL SOCIETY | 9856 | TCA | M&H | HistSoc | Reno | 1968 | 22200 | 2018-08-04 | Immediate to Two Years | Currently Critical | 1 | 250000
0401EXT5 | EXTERIOR DOOR REPLACEMENT | 0401 | The exterior metal door assembly on the south side public entrance is damaged from age and general wear and tear and has reached the end of it's expected life. This project would provide for the replacement of the south double door entry assembly with new metal doors, frames and hardware. Removal and disposal of the existing doors is included in this estimate. | NEVADA HISTORICAL SOCIETY | 9856 | TCA | M&H | HistSoc | Reno | 1968 | 22200 | 2018-08-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0401INT4 | HIGH DENSITY STORAGE SYSTEM INSTALLATION | 0401 | The static shelving in the archive area has reached capacity and will no longer be able to meet storage demands. Leased space and other offsite storage space has already been utilized to handle the overflow. In order to maintain control and security of the artifacts it is recommended to replace the existing shelving with a new high density storage system as opposed to utilizing the offsite storage facilities. The new system will store two to three times as much material in the same amount of space. The estimate includes removal and disposal of existing static shelving and purchase and installation of a high density storage system. | NEVADA HISTORICAL SOCIETY | 9856 | TCA | M&H | HistSoc | Reno | 1968 | 22200 | 2018-08-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 125000
0401EXT3 | EXTERIOR FINISHES | 0401 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 8-10 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NEVADA HISTORICAL SOCIETY | 9856 | TCA | M&H | HistSoc | Reno | 1968 | 22200 | 2018-08-04 | Four to Ten Years | Long-Term Needs | 3 | 111000
0401ENR2 | LIGHTING UPGRADE | 0401 | There are still some older fluorescent type lighting fixtures in the building including T-12's and older T-8's that are not energy efficient. This project will upgrade these fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, conference rooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | NEVADA HISTORICAL SOCIETY | 9856 | TCA | M&H | HistSoc | Reno | 1968 | 22200 | 2018-08-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8500
0401PLM1 | WATER HEATER REPLACEMENT | 0401 | There is a 30 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new on-demand electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | NEVADA HISTORICAL SOCIETY | 9856 | TCA | M&H | HistSoc | Reno | 1968 | 22200 | 2018-08-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0401SFT7 | EXPLOSION-PROOF REFRIGERATOR/ FREEZER | 0401 | This project would provide for the purchase and installation of two explosion-proof refrigerator/ freezer units. The existing unit has reached capacity and staff reported a need for two additional units. These units protect the chemicals or substances stored inside the unit from explosions outside the unit as well as protecting the exterior environment from explosions inside the unit. The units must be hardwired to the electrical system to prevent a short or overheating a coil which could ignite a flammable or explosive substance stored inside. Additional costs are included for an electrician to hard-wire the units to the electrical system. | NEVADA HISTORICAL SOCIETY | 9856 | TCA | M&H | HistSoc | Reno | 1968 | 22200 | 2018-08-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 17000
0401SFT6 | HIGH DENSITY STORAGE SYSTEM REPAIRS | 0401 | The existing high density storage system in the archive area is not functioning properly and is a safety hazard. The electrical and mechanical elements of the system are aged, compromising the safety of the staff and volunteers. The system has a safety feature which prevents the shelves from moving when a person is in the aisle. The electronics and sensors for this safety feature are failing and pose a very dangerous situation for a person working in the aisles. There are also shelves at the ends of the system that do not open fully. It is recommended to refurbish the entire storage system. The estimate includes removal and disposal of existing electrical and mechanical parts and purchase and installation of new parts to restore the system to a safe and fully functioning system. | NEVADA HISTORICAL SOCIETY | 9856 | TCA | M&H | HistSoc | Reno | 1968 | 22200 | 2018-08-04 | Immediate to Two Years | Currently Critical | 1 | 25000
0401INT3 | JANITORS CLOSET REPAIRS | 0401 | The mop sink in the Janitors Closet is mounted adjacent to gypsum board and showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | NEVADA HISTORICAL SOCIETY | 9856 | TCA | M&H | HistSoc | Reno | 1968 | 22200 | 2018-08-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
0401ADA2 | ADA SIGNAGE | 0401 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | NEVADA HISTORICAL SOCIETY | 9856 | TCA | M&H | HistSoc | Reno | 1968 | 22200 | 2018-08-04 | Immediate to Two Years | Currently Critical | 1 | 1200
0401ELE1 | PROVIDE CLEARANCE AT ELECTRICAL PANELS | 0401 | There are electrical panels in the building which do not have proper clear floor space around them. The 2006 IFC section 605.3 states that, "A working space of not less than 30 inches in width, 36 inches in depth and 78 inches in height shall be provided in front of electrical service equipment. Where the electrical service equipment is wider than 30 inches, the working space shall not be less than the width of the equipment. No storage of any materials shall be located within the designated working space." This project would provide funds to relocate the janitors equipment and other items currently blocking the working space. | NEVADA HISTORICAL SOCIETY | 9856 | TCA | M&H | HistSoc | Reno | 1968 | 22200 | 2018-08-04 | Immediate to Two Years | Currently Critical | 1 | 250
0401INT2 | FLOORING REPAIRS | 0401 | The painted and sealed concrete floor in the addition portion of the building is damaged and reaching the end of its useful life. It is recommended to refurbish the floor by stripping the existing finish, repairing any cracks, painting and sealing in order to extend its useful life. This project would provide for refurbishing the floor in the next 2-3 years. | NEVADA HISTORICAL SOCIETY | 9856 | TCA | M&H | HistSoc | Reno | 1968 | 22200 | 2018-08-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 49500
0401EXT4 | DOOR AWNING INSTALLATION | 0401 | The exterior door on the east elevation is the main entrance for staff and volunteers. They must use this entrance to open the building and disable the alarm. During inclement weather, snow and ice builds up on and around the door and impedes its function. This makes it difficult and dangerous to get in and out of the building. It is recommended to retrofit the door with a metal awning to protect this entrance from the elements. The awning should span the full width of the concrete landing and include a gutter that ties into the adjacent downspout. This project also includes relocating the exterior light from its current location to a position below the awning. | NEVADA HISTORICAL SOCIETY | 9856 | TCA | M&H | HistSoc | Reno | 1968 | 22200 | 2018-08-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3500
0401SEC1 | SECURITY SYSTEM UPGRADE | 0401 | The buildings security system is limited and outdated and the intercom system through the telephones does not meet staff requirements. There a few security cameras and alarmed doors, but this is not sufficient to protect the people, priceless artifacts, manuscripts, photographs and library collections in the building. The only intercom system is the speakerphones on the telephones. Staff noted that the speakers are not loud enough and they are not located in the most necessary areas. This project addresses upgrading the security and communications systems in the building. | NEVADA HISTORICAL SOCIETY | 9856 | TCA | M&H | HistSoc | Reno | 1968 | 22200 | 2018-08-04 | Immediate to Two Years | Currently Critical | 1 | 222000
2027EXT1 | EXTERIOR FINISHES | 2027 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are sanding, priming and painting, cleaning and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NEVADA STATE MUSEUM - NORTH ANNEX | 9907 | TCA | M&H | Museums | Carson City | 1955 | 8500 | 2021-02-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 42500
2027INT3 | INTERIOR FINISHES | 2027 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | NEVADA STATE MUSEUM - NORTH ANNEX | 9907 | TCA | M&H | Museums | Carson City | 1955 | 8500 | 2021-02-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 42500
2027HVA2 | REPLACE HVAC SYSTEM | 2027 | The existing roof mounted HVAC unit was installed in 1999 and will be reaching the end of it's expected life within the next 7-8 years. This project would provide for a new roof mounted package HVAC unit to be installed including all required connections to existing utilities and ducting. Removal and disposal or the existing unit is included in this estimate. | NEVADA STATE MUSEUM - NORTH ANNEX | 9907 | TCA | M&H | Museums | Carson City | 1955 | 8500 | 2021-02-26 | Four to Ten Years | Long-Term Needs | 3 | 75000
2027EXT3 | ROOF REPLACEMENT | 2027 | The roof on this building was in fair at the time of the survey (Feb. 2015). The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of a 15 year time period for this installation. It is recommended that this building be scheduled for re-roofing in the next 4 years to be consistent with the newer roofing program and the end of the warranty period. This project or a portion there of was previously recommended in the FCA report dated 04/30/2004 and 6/6/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 2/11/2015. | NEVADA STATE MUSEUM - NORTH ANNEX | 9907 | TCA | M&H | Museums | Carson City | 1955 | 8500 | 2021-02-26 | Four to Ten Years | Long-Term Needs | 3 | 42500
2027INT0 | REPLACE RESTROOM FLOORING | 2027 | The existing flooring in the lower level ADA accessible restrooms is vinyl composition tile (VCT). This creates a potential unsanitary condition and increases maintenance and also is showing signs of wear. This project would provide for removal of the existing VCT and installation of a slip resistant sheet vinyl. This project or a portion there of was previously recommended in the FCA report dated 6/6/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 2/11/2015. | NEVADA STATE MUSEUM - NORTH ANNEX | 9907 | TCA | M&H | Museums | Carson City | 1955 | 8500 | 2021-02-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3600
2027INT2 | CARPET REPLACEMENT | 2027 | The interior carpet floor covering on the lower level and upper level is showing signs of wear. Several areas are worn, tears are evident, and it has reached the end of it's expected life. This project would replace the existing broad loom carpet with carpet tile. Carpet tile would allow for future replacement of only those sections of carpet that are worn or damaged without the need to remove the entire carpet. This project or a portion there of was previously recommended in the FCA report dated 04/30/2004 and 6/6/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 2/11/2015. | NEVADA STATE MUSEUM - NORTH ANNEX | 9907 | TCA | M&H | Museums | Carson City | 1955 | 8500 | 2021-02-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
2027ADA3 | ADA ACCESSIBLE COUNTERTOP REPLACEMENT | 2027 | The plastic laminate base cabinet, countertop and sink in the docent lounge does not meet the ADA requirements. It is currently 36" above the finish floor and is not accessible. This room is used by a variety of people and should have barrier free access to the room and it's amenities. This project addresses removal and replacement of the plastic laminate base cabinet, countertop and sink to bring them into compliance with the NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards For Accessible Design which were used for reference on this project. The project includes the removal of the of the base cabinet, countertop and sink, and installation of a new plastic laminate cabinet system and sink. The cabinet should be sized accordingly to provide 18" of clearance between the cabinet and the exit door pull handle. Minor gypsum board repair and painting is included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 6/6/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 2/11/2015. | NEVADA STATE MUSEUM - NORTH ANNEX | 9907 | TCA | M&H | Museums | Carson City | 1955 | 8500 | 2021-02-26 | Immediate to Two Years | Currently Critical | 1 | 5000
2027INT5 | REMODEL UPPER LEVEL RESTROOMS | 2027 | The existing upper level Men's and Women's restrooms are showing their age and are in need of an upgrade. This project would provide for new fixtures and finishes to be installed including toilets, sinks faucets, toilet partitions and countertops. The existing tile cold remain but it is recommended that the existing tile be removed and replaced with new floor and wall tile. Removal and disposal of the existing fixtures is included in this estimate. | NEVADA STATE MUSEUM - NORTH ANNEX | 9907 | TCA | M&H | Museums | Carson City | 1955 | 8500 | 2021-02-26 | Four to Ten Years | Long-Term Needs | 3 | 40000
2944EXT1 | INTERIOR / EXTERIOR FINISHES / GLAZING MAINTENANCE | 2944 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior and interior of the building excluding the roof. Included in the cost are painting of the exposed steel structure, caulking of the glazing panels and annual cleaning of the glazing panels inside and out. It is recommended that these items be assessed on an annual basis and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | DEMA GUINN CONCOURSE | 9907 | TCA | M&H | Museums | Carson City | 2008 | 3949 | 2021-02-26 | Immediate to Two Years | Currently Critical | 1 | 39490
2563LGT1 | PAINT WATER TANK | 2563 | It is important to maintain the finish, weather resistance and appearance of the tank. This project recommends work to protect the exterior tank envelope, including sand blasting, painting, staining, or other applied finishes and other penetrations to maintain the tank in good, weather tight condition. This project should be performed on a cyclical basis. This project or a portion there of was previously recommended in the FCA report dated 03/01/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/07/2013. | INDIAN HILLS WATER TOWER | 9874 | TCA | M&H | Museums | Carson City | 1981 | 530 | 2021-02-26 | Four to Ten Years | Long-Term Needs | 3 | 15000
9874SIT3 | SHRUB REMOVAL | 9874 | There are some shrubs and trees along the south side of the building which are too close to the exterior wall. This project would provide for the removal of the shrubs and trimming of the trees along the south side of the facility. | NEVADA STATE MUSEUM INDIAN HILLS SITE | 9874 | TCA | M&H | Museums | Carson City | 0 |  | 2021-02-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 750
9907SIT3 | CRACK FILL / SEAL ASPHALT PAVING | 9907 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the paving site wide including access roads and parking areas. Striping is included in this estimate. This project should be scheduled on a 4 year cyclical basis to maintain the integrity of the paving and prevent premature failure. | NEVADA STATE MUSEUM COMPLEX - CC SITE | 9907 | TCA | M&H | Museums | Carson City | 1871 |  | 2021-02-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5136
9852SIT1 | ASPHALT CONCRETE PAVING REHABILITATION | 9852 | The existing asphalt concrete paving is in poor shape. There are large cracks and areas of alligatoring and is showing signs of failure. This project would provide for the removal and replacement of AC paving and sealing of the entire paved surface. Also included is ADA accessible parking, striping, signage and wheel stops. 30,000 square feet was used to generate this estimate. This project should be implemented within the next two years. | MARJORIE RUSSELL RESEARCH CENTER SITE | 9852 | TCA | M&H | Museums | Carson City | 1968 |  | 2021-02-26 | Immediate to Two Years | Currently Critical | 1 | 120000
9852SIT2 | DRAINAGE / LANDSCAPE IMPROVEMENTS | 9852 | The west side of the building has some areas in need of drainage improvements where the roof drainage down spouts terminate at grade. This project would provide for down spout extensions to a gravel drywell capable of handling runoff from rain and snow melt. This project also addresses the recommended removal of the planter areas on the north side of the facility as the exterior grade is at the same level as the floor and glazing panels. | MARJORIE RUSSELL RESEARCH CENTER SITE | 9852 | TCA | M&H | Museums | Carson City | 1968 |  | 2021-02-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
9874SIT2 | ASPHALT CONCRETE REHABILITATION | 9874 | The existing paved parking area is in poor condition. Signs of paving failure are evident with large cracks and alligatoring visible. This project recommends filling in the cracks, remove and replace damaged areas, extend the paved area to the edge of the building and applying a slurry seal and re-striping the onsite parking area and access road. The re-striping should include ADA parking/striping, loading zones and accessible route of travel from parking to the Warehouse Building. This project or a portion there of was previously recommended in the FCA report dated 03/01/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/07/2013. | NEVADA STATE MUSEUM INDIAN HILLS SITE | 9874 | TCA | M&H | Museums | Carson City | 0 |  | 2021-02-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 70000
0208SIT2 | REMOVE PLANTERS | 0208 | This building has planters across the front of the building that extend up onto the exterior wall. This practice promotes water infiltration through the side of the building and has been known to cause mold growth along the exterior walls of buildings. This project recommends that the planters be removed as soon as feasible and replaced with xeriscaping. This project or a portion there of was previously recommended in the FCA report dated 02/12/2003 and 03/01/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/28/2013. | MARJORIE RUSSELL RESEARCH CENTER | 9852 | TCA | M&H | Museums | Carson City | 1968 | 6000 | 2021-02-26 | Immediate to Two Years | Currently Critical | 1 | 2000
0208INT3 | REPLACE CABINETS | 0208 | The wood cabinets located in warehouse are used to store and protects artifacts. These cabinets are in poor shape, prone to fire and water damaged, the plywood is falling apart, doors do not close properly and the artifacts are subject to the environmental elements. Poor-quality storage enclosures accelerate the deterioration of the materials they are intended to protect. This project would provide for the purchase of 30 steel cabinets which will provide a stable environment for archived and stored items. This project or a portion there of was previously recommended in the FCA report dated 03/01/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/28/2013. | MARJORIE RUSSELL RESEARCH CENTER | 9852 | TCA | M&H | Museums | Carson City | 1968 | 6000 | 2021-02-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 54000
0208HVA2 | EXHAUST HOOD INSTALLATION | 0208 | The building contains an electric stove top in the kitchen area. The 2012 Uniform Mechanical code requires an exhaust hood to be installed. This project would provide for the purchase and installation of exhaust hood including the required ducting to the exterior of building. This project or a portion there of was previously recommended in the FCA report dated 03/01/2006 . It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/28/2013. | MARJORIE RUSSELL RESEARCH CENTER | 9852 | TCA | M&H | Museums | Carson City | 1968 | 6000 | 2021-02-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
0208ENR1 | EXTERIOR ENERGY RETROFIT | 0208 | The building is constructed of concrete masonry units (CMU) with no insulation. The windows are original to the building, and of single pane construction. Buildings of this type are not energy efficient. This project recommends adding an exterior insulation and finish system (EIFS) over the CMU, replacing the storefront window systems and doors with a dual pane insulated storefront window system and removing and replacing the windows in the rear of the building. This work will make the building more energy efficient. This project or a portion there of was previously recommended in the FCA report dated 02/12/2003 and 03/01/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/28/2013. | MARJORIE RUSSELL RESEARCH CENTER | 9852 | TCA | M&H | Museums | Carson City | 1968 | 6000 | 2021-02-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 72000
0208INT1 | REPLACE COUNTERTOPS | 0208 | The kitchen countertops are plastic laminate and original to the building. Age and constant use have contributed to the deterioration. The laminate is starting to separate from the substrate. This project would provide for the removal and installation of new plastic laminate countertops. This project or a portion there of was previously recommended in the FCA report dated 03/01/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/28/2013. | MARJORIE RUSSELL RESEARCH CENTER | 9852 | TCA | M&H | Museums | Carson City | 1968 | 6000 | 2021-02-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 750
0208INT2 | INTERIOR PAINTING | 0208 | The interior finishes on the walls are in fair to poor condition. The ceilings show minor water stains from past water leaks. This project would provide for the painting of the interior walls and ceiling. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project should be completed in the next two years. This project or a portion there of was previously recommended in the FCA report dated 03/01/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/28/2013. | MARJORIE RUSSELL RESEARCH CENTER | 9852 | TCA | M&H | Museums | Carson City | 1968 | 6000 | 2021-02-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
0208HVA1 | HVAC SYSTEM REPLACEMENT | 0208 | The three HVAC roof top units are over 20+ years old. They are not energy efficient, need constant repairs and have reached the end of their expected and useful life. This project would provide for installation of three new HVAC packaged units and cleaning of the existing duct work. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. This project or a portion there of was previously recommended in the FCA report dated 02/12/2003 and 03/01/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/28/2013. | MARJORIE RUSSELL RESEARCH CENTER | 9852 | TCA | M&H | Museums | Carson City | 1968 | 6000 | 2021-02-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 90000
0208ADA3 | INSTALL LEVER DOOR HARDWARE | 0208 | The existing doors in this facility have locking knob-type door hardware and do not meet the requirements for ADA accessibility. ICC/ANSI A117.1-12009 section 404.2.7 requires door handles to have a shape that is easy to grasp with one hand and does not require tight grasping, pinching or twisting of the wrist to operate. This project would provide for the purchase and installation of lever action hardware to be placed on all the interior doors. Typical of 5 doors. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 02/12/2003 and 03/01/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/28/2013. | MARJORIE RUSSELL RESEARCH CENTER | 9852 | TCA | M&H | Museums | Carson City | 1968 | 6000 | 2021-02-26 | Immediate to Two Years | Currently Critical | 1 | 1500
0208INT4 | WAREHOUSE FLOOR FINISH | 0208 | The warehouse concrete floor area is painted and/or stained and has floor mounted electrical duplex outlets throughout. The painted and/or stained floor in the warehouse is showing signs of wear. The concrete area around the floor mounted electrical outlets has been chipped away causing a tripping hazard. This project would provide for patching the concrete around the electrical outlets and the painting of the floor surface with a paint designed for use on concrete. Included in the estimate is prep work as needed. This project or a portion there of was previously recommended in the FCA report dated 03/01/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/28/2013. | MARJORIE RUSSELL RESEARCH CENTER | 9852 | TCA | M&H | Museums | Carson City | 1968 | 6000 | 2021-02-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
0208PLM1 | REPLACE WATER HEATER | 0208 | The water heater tank is showing signs of wear and deterioration. It appears this appliance is original to the building and has reached the end of its expected life. This project would provide for the purchase and installation of a new 75 gallon gas fired water heater tank including seismic bracing and drain pan. Removal and disposal of the existing tank is included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 03/01/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/28/2013. | MARJORIE RUSSELL RESEARCH CENTER | 9852 | TCA | M&H | Museums | Carson City | 1968 | 6000 | 2021-02-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0208EXT3 | EXTERIOR FINISHES | 0208 | It is important to maintain the finish, weather resistance and appearance of the building. The exterior finishes on the building is starting to peel and bluster. This project would provide funding to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. This project will protect the building envelope. This project would not be required if the exterior energy retrofit project is implemented. This project should be completed in the next two years. This project or a portion there of was previously recommended in the FCA report dated 02/12/2003 and 03/01/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/28/2013. | MARJORIE RUSSELL RESEARCH CENTER | 9852 | TCA | M&H | Museums | Carson City | 1968 | 6000 | 2021-02-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18000
0205INT5 | INTERIOR FINISHES | 0205 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | NEVADA STATE MUSEUM | 9907 | TCA | M&H | Museums | Carson City | 1871 | 45763 | 2021-02-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 221865
0208EXT2 | REPLACE GUTTERS AND DOWNSPOUTS | 0208 | The building's gutters have been damaged and show wear and tear from environmental conditions. Many are leaking. In several locations, downspouts have been damaged or are missing. This project would provide for the purchase and installation of seamless gutters and down spouts to divert the water away from the building and building entrances and exits. This project or a portion there of was previously recommended in the FCA report dated 03/01/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/28/2013. | MARJORIE RUSSELL RESEARCH CENTER | 9852 | TCA | M&H | Museums | Carson City | 1968 | 6000 | 2021-02-26 | Four to Ten Years | Long-Term Needs | 3 | 5000
0208SFT4 | SEISMIC GAS SHUT OFF VALVE | 0208 | Agreements reached between the Nevada Risk Management Office and the State of Nevada's Insurance Underwriter require Seismic Gas Shutoff Valves (SGSV's) on all gas services to all State buildings. This project would install a SGSV to the gas line serving the building. This project or a portion there of was previously recommended in the FCA report dated 03/01/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/28/2013. | MARJORIE RUSSELL RESEARCH CENTER | 9852 | TCA | M&H | Museums | Carson City | 1968 | 6000 | 2021-02-26 | Immediate to Two Years | Currently Critical | 1 | 3000
0205INT8 | REMODEL UPPER LEVEL & BASEMENT RESTROOMS | 0205 | The existing Men's and Women's restrooms are in need of remodeling due to age and use. This project would provide for the remodeling of two Men's and two Women's restrooms in the basement and upper level including but not limited to new plumbing fixtures partitions, accessories, flooring and painting. If space permits, ADA accessible elements should be incorporated into the design as much as feasible but the main level of the museum does have ADA accessible Men's and Women's restrooms for the public and employees. It is recommended that ADA directional signage be installed to provide location details to ADA accessible restrooms. | NEVADA STATE MUSEUM | 9907 | TCA | M&H | Museums | Carson City | 1871 | 45763 | 2021-02-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 40000
0205EXT2 | EXTERIOR FINISHES | 0205 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are sanding, priming and painting, cleaning and pointing the sandstone masonry as needed and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NEVADA STATE MUSEUM | 9907 | TCA | M&H | Museums | Carson City | 1871 | 45763 | 2021-02-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 310359
0205INT7 | JANITOR CLOSET FRP INSTALLATION | 0205 | There are three janitor closets with floor sinks with a gypsum board surround that is damaged by moisture. This project would provide for the installation of a fiberglass reinforced panel (FRP) on the walls adjacent to the floor / mop sinks. | NEVADA STATE MUSEUM | 9907 | TCA | M&H | Museums | Carson City | 1871 | 45763 | 2021-02-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1800
0205HVA3 | HVAC SYSTEM REPLACEMENT | 0205 | The existing HVAC system components have or are close to reaching the end of their expected life. The gas fired boiler is about 25 years old as well as the 33 fan coil units. The roof mounted chiller is over ten years old and all of this equipment is not energy efficient. This project would provide for the installation of a new gas fired boiler, and 33 fan coil units as well as a new energy management system including controls and VFD's. Some modifications to the ducting system in the basement area are included in this estimate. | NEVADA STATE MUSEUM | 9907 | TCA | M&H | Museums | Carson City | 1871 | 45763 | 2021-02-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 443370
0205INT6 | REPLACE CARPET TILES | 0205 | The existing carpet tiles on the upper level are worn and are in need of replacement. This project would provide for the installation of new commercial grade carpet tiles at the upper level of the museum. Removal and disposal of the existing carpet is included in this estimate. A total of 3,000 square feet was used for this estimate. | NEVADA STATE MUSEUM | 9907 | TCA | M&H | Museums | Carson City | 1871 | 45763 | 2021-02-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18000
0208SFT3 | JANITOR CLOSET WALL PROTECTION | 0208 | The mop sink in the Janitor's Closet is mounted adjacent to gypsum board that is showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. This project or a portion there of was previously recommended in the FCA report dated 03/01/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/28/2013. | MARJORIE RUSSELL RESEARCH CENTER | 9852 | TCA | M&H | Museums | Carson City | 1968 | 6000 | 2021-02-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0860PLM1 | SEPTIC TANK SERVICE | 0860 | The septic tank has not been inspected or pumped for the past 10 years according to staff. This project would provide for the septic tank to be inspected and pumped. This project should be done on a cyclical basis. This project or a portion there of was previously recommended in the FCA report dated 03/01/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/07/2013. | INDIAN HILLS WAREHOUSE | 9874 | TCA | M&H | Museums | Carson City | 1980 | 15440 | 2021-02-26 | Immediate to Two Years | Currently Critical | 1 | 750
0859EXT1 | EXTERIOR FINISHES | 0859 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. This building should be painted in the next year. This project or a portion there of was previously recommended in the FCA report dated 02/12/2003 and 03/01/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/07/2013. | INDIAN HILLS PUMP HOUSE | 9874 | TCA | M&H | Museums | Carson City | 1981 | 400 | 2021-02-26 | Immediate to Two Years | Currently Critical | 1 | 2000
0859EXT2 | INSTALL LANDING | 0859 | The entrance door to the pump house does not have an exterior concrete landing. IBC-2003 Chapter 1008.1.4 requires a landing on each side of a door. Landings shall be at the door elevation on each side. This project would provide for the installation of a concrete landing not less than the width of the door and 44 inches for the length in travel. This project or a portion there of was previously recommended in the FCA report dated 03/01/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/07/2013. | INDIAN HILLS PUMP HOUSE | 9874 | TCA | M&H | Museums | Carson City | 1981 | 400 | 2021-02-26 | Immediate to Two Years | Currently Critical | 1 | 500
0860EXT1 | EXTERIOR ENERGY RETROFIT | 0860 | The building is constructed of concrete masonry units (CMU) with no insulation. Buildings of this type are not energy efficient. This project would provide for the purchase and installation of adding an exterior insulating finish system (EIFS) over the CMU and replacing the exterior doors. This work will make the building more energy efficient and should concur at the same time the HVAC renovation occurs. This project or a portion there of was previously recommended in the FCA report dated 02/12/2003 and 03/01/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/07/2013. | INDIAN HILLS WAREHOUSE | 9874 | TCA | M&H | Museums | Carson City | 1980 | 15440 | 2021-02-26 | Four to Ten Years | Long-Term Needs | 3 | 310000
0860HVA1 | HVAC UPGRADE / INSTALLATION | 0860 | The warehouse section is equipped with six hanging gas force furnaces and no air-conditioning. Two of the furnaces were not working properly at the time of the survey. During accreditation by the American Association of Museums (AAM) in 2003, it was recommended that the warehouse area have an HVAC system for maintaining a proper interior environment for artifact storage. This project would provide for a complete HVAC system to be installed in the building including air handlers, duct work, connections to existing utilities seismic bracing and an energy managements system. Design of the system is not included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 03/01/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/07/2013. | INDIAN HILLS WAREHOUSE | 9874 | TCA | M&H | Museums | Carson City | 1980 | 15440 | 2021-02-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 231600
0860PLM2 | SINK DRAINAGE / WASTE PIPE | 0860 | The 2012 UPC requires "all plumbing fixtures, drains, appurtenances and appliances used to receive or discharge liquid wastes or sewage shall be directly connected to the sanitary drainage system." The sink located in the south warehouse drains directly into the field adjacent to the structure. This project would provide for the drainage system of the sink to be connected to the sanitary drainage line. This project or a portion there of was previously recommended in the FCA report dated 03/01/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/07/2013. | INDIAN HILLS WAREHOUSE | 9874 | TCA | M&H | Museums | Carson City | 1980 | 15440 | 2021-02-26 | Immediate to Two Years | Currently Critical | 1 | 1200
0860STR1 | MEZZANINE ASSESSMENT | 0860 | The mezzanine contains numerous code and safety issues including but not limited to access stairs, guardrails and handrails, ceiling height, systems and structural loading of the floor. This project recommends a structural assessment of the entire mezzanine due to lack of drawings or information on the construction. This project or a portion there of was previously recommended in the FCA report dated 03/01/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/07/2013. | INDIAN HILLS WAREHOUSE | 9874 | TCA | M&H | Museums | Carson City | 1980 | 15440 | 2021-02-26 | Immediate to Two Years | Currently Critical | 1 | 1500
0860EXT0 | RAIN GUTTER INSTALLATION | 0860 | The building does not have any rain gutters and down spouts to prevent water from flooding around the building especially at entrance and exit pathways. This can cause damage to the exterior finish of the building. This project would provide for the purchase and installation of seamless gutters and down spouts to divert the water away from the building and building entrances and exits. This project or a portion there of was previously recommended in the FCA report dated 03/01/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/07/2013. | INDIAN HILLS WAREHOUSE | 9874 | TCA | M&H | Museums | Carson City | 1980 | 15440 | 2021-02-26 | Four to Ten Years | Long-Term Needs | 3 | 2500
0860EXT7 | EXTERIOR PAINTING / FINISHES | 0860 | It is important to maintain the finish, weather resistance and appearance of the building. The exterior finishes on the building is starting to peel and blister. This project would provide for protection of the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. This project or a portion there of was previously recommended in the FCA report dated 03/01/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/07/2013. | INDIAN HILLS WAREHOUSE | 9874 | TCA | M&H | Museums | Carson City | 1980 | 15440 | 2021-02-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 46320
0860SFT4 | CONCRETE REPAIR - EPOXY SYSTEM | 0860 | The concrete floors in the building have cracks, some over an inch wide, in several locations. The cracks create safety issues when pulling/pushing a cart. This project would provide for cleaning and epoxy sealing of the cracks in the concrete floor. This project or a portion there of was previously recommended in the FCA report dated 02/12/2003 and 03/01/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/07/2013. | INDIAN HILLS WAREHOUSE | 9874 | TCA | M&H | Museums | Carson City | 1980 | 15440 | 2021-02-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0860INT1 | LEVER ACTION DOOR HANDLE INSTALLATION | 0860 | The existing doors in this facility have locking knob-type door hardware. The locks on the doors are sticking and do not operate properly. This project would provide for the purchase and installation of locking lever action door handles to be placed on all the doors in the building. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 03/01/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/07/2013. | INDIAN HILLS WAREHOUSE | 9874 | TCA | M&H | Museums | Carson City | 1980 | 15440 | 2021-02-26 | Immediate to Two Years | Currently Critical | 1 | 7500
0860SEC1 | INTERCOM AND CAMERA INSTALLATION | 0860 | The building is surrounded by a 6’chain link fence. There is an access gate to enter the site and buildings. The gate is kept locked for security reasons. There should be communication from the gate to the office area. This project would provide funding for the purchase and installation of a surveillance and communication system from the gate to the office area including a camera and intercom with connections to utilities as required. This project or a portion there of was previously recommended in the FCA report dated 03/01/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/07/2013. | INDIAN HILLS WAREHOUSE | 9874 | TCA | M&H | Museums | Carson City | 1980 | 15440 | 2021-02-26 | Four to Ten Years | Long-Term Needs | 3 | 10000
0860SFT7 | INSTALL SEISMIC GAS SHUT OFF VALVE | 0860 | The State's Underwriter recommends installing a Seismic Gas Shutoff Valve on each gas service to improve the insurability of State facilities. The valves are installed between the gas meter and the building or equipment served to shut off the gas supply in the event of an earthquake. This project would provide for a seismic gas shutoff valve on the gas line serving the building. This project or a portion there of was previously recommended in the FCA report dated 03/01/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/07/2013. | INDIAN HILLS WAREHOUSE | 9874 | TCA | M&H | Museums | Carson City | 1980 | 15440 | 2021-02-26 | Immediate to Two Years | Currently Critical | 1 | 3500
0860SFT5 | FIRE-RATED DOOR ASSEMBLY | 0860 | The building has a 1-hour fire wall assembly located between the warehouse and staging area. The existing set of double doors are not fire rated. The double door does not meet the criteria of IBC -2012 Chapter 715. This project would provide for purchase and installation of a new 1- hour fire rated double door and frame assembly including smoke seals and all hardware. Removal of the existing door and painting of the new door are included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 03/01/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/07/2013. | INDIAN HILLS WAREHOUSE | 9874 | TCA | M&H | Museums | Carson City | 1980 | 15440 | 2021-02-26 | Immediate to Two Years | Currently Critical | 1 | 3800
2106EXT1 | GUTTER AND DOWNSPOUT INSTALLATION | 2106 | The building does not have rain gutters and down spouts at all building entrances and patios. During times of inclement weather, water pours off of the metal roof down onto public and private entrances and patios causing concerns for safety. Water damage to certain areas of the building may occur if the water is not directed away from the building exterior. This project would provide for the purchase and installation of seamless gutters and down spouts to divert the water away from the building entrances and patios and the exterior finishes of the building. This project or a portion thereof was previously recommended in the FCA report dated 06/07/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/10/2012. | SOUTHERN NEVADA VETERANS HOME | 9889 | VetSvc | VetSvc |  | Boulder City | 2000 | 83960 | 2012-04-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 21000
2106EXT6 | DRIP EDGE INSTALLATION | 2106 | There are areas around the perimeter of the building where the foundation does not line up properly with the exterior insulation and finish system (EIFS) and there is no drip edge at the bottom of the EIFS. In many of these areas, there are gaps large enough to allow rodents and insects to enter the walls and infest the building. This condition also allows moisture to penetrate the walls which will lead to premature failure of the walls and possibly mold related issues. This project recommends installing a drip edge to direct water away from the building and flashing and caulking as needed around the entire perimeter of the building to close all of the gaps. | SOUTHERN NEVADA VETERANS HOME | 9889 | VetSvc | VetSvc |  | Boulder City | 2000 | 83960 | 2012-04-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9400
2106EXT5 | EXTERIOR FINISHES | 2106 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SOUTHERN NEVADA VETERANS HOME | 9889 | VetSvc | VetSvc |  | Boulder City | 2000 | 83960 | 2012-04-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 419800
2106ENR1 | ENERGY MANAGEMENT SYSTEM REPLACEMENT | 2106 | The YAMAS energy management system is original to the building and should be scheduled for replacement. Replacement parts for performing routine and emergency maintenance are not made anymore and the system has recently had numerous failures. In a facility of this type, it is imperative that the conditioned spaces are properly controlled at all times. This project would provide for the removal and disposal of the existing YAMAS energy management system and replacement with new equipment including all required connections to utilities and equipment. | SOUTHERN NEVADA VETERANS HOME | 9889 | VetSvc | VetSvc |  | Boulder City | 2000 | 83960 | 2012-04-10 | Immediate to Two Years | Currently Critical | 1 | 30000
2106EXT7 | ROOF REPAIRS | 2106 | The metal roofing system has leaks in the valleys, at roof penetrations, translucent skylights and other areas where the caulking and sealant has deteriorated. This project would provide for sealing and caulking of these areas particularly the 183 boots around the pipe penetrations. | SOUTHERN NEVADA VETERANS HOME | 9889 | VetSvc | VetSvc |  | Boulder City | 2000 | 83960 | 2012-04-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
2106INT3 | DOOR HARDWARE REPLACEMENT | 2106 | The panic hardware mechanisms on the interior doors are reaching the end of their expected life and should be scheduled for replacement. The mechanisms are damaged from age and general wear and tear and are beginning to fail. This project would provide for the replacement of the panic hardware throughout the building with new panic hardware. Removal and disposal of the existing mechanisms is included in this estimate. | SOUTHERN NEVADA VETERANS HOME | 9889 | VetSvc | VetSvc |  | Boulder City | 2000 | 83960 | 2012-04-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
2106SFT6 | FIRE ALARM SYSTEM UPGRADE | 2106 | This building is equipped with an automatic fire detection and alarm system that was installed in 2000. It is recommended that the system be scheduled to be upgraded in approximately 10 years to ensure the safety of the occupants. Also, according to NAC 477.917 "If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure". When completed, the new system will provide visual, as well as audible notification, in accordance with the version of the IBC that is adopted at the time and the State Fire Marshal's requirements at the time. | SOUTHERN NEVADA VETERANS HOME | 9889 | VetSvc | VetSvc |  | Boulder City | 2000 | 83960 | 2012-04-10 | Four to Ten Years | Long-Term Needs | 3 | 335840
2106SFT1 | JANITORS CLOSET REPAIRS JANITORS CLOSET REPAIRS | 2106 | The mop sinks in the Janitors Closets are mounted adjacent to gypsum board and are showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. Typical of 24 Janitors Closets. This project or a portion thereof was previously recommended in the FCA report dated 06/07/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/10/2012. | SOUTHERN NEVADA VETERANS HOME | 9889 | VetSvc | VetSvc |  | Boulder City | 2000 | 83960 | 2012-04-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 33600
2106SFT5 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 2106 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 06/07/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/10/2012. | SOUTHERN NEVADA VETERANS HOME | 9889 | VetSvc | VetSvc |  | Boulder City | 2000 | 83960 | 2012-04-10 | Immediate to Two Years | Currently Critical | 1 | 4000
2106INT2 | INTERIOR FINISHES | 2106 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SOUTHERN NEVADA VETERANS HOME | 9889 | VetSvc | VetSvc |  | Boulder City | 2000 | 83960 | 2012-04-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 419800
3112EXT1 | EXTERIOR FINISHES | 3112 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | VEHICLE SHADE STRUCTURE | 9889 | VetSvc | VetSvc |  | Boulder City | 2009 | 2160 | 2012-04-10 | Four to Ten Years | Long-Term Needs | 3 | 2160
9889SIT3 | CRACK FILL & SEAL ASPHALT PAVING | 9889 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the paving site wide including the access road, parking areas and the vehicle storage area. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 90,000 square feet of asphalt area was used to generate this estimate. | SOUTHERN NEVADA VETERANS HOME SITE | 9889 | VetSvc | VetSvc |  | Boulder City | 2000 |  | 2012-04-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 54000
9889ENR1 | EXTERIOR SOLAR SITE LIGHTING UPGRADE | 9889 | There are 25 existing light poles around the site with 34 total light fixtures attached. The existing light fixtures are the older 400 watt metal halide type and are not energy efficient. This project will upgrade the fixtures to higher efficiency LED exterior lights with solar panels for power. | SOUTHERN NEVADA VETERANS HOME SITE | 9889 | VetSvc | VetSvc |  | Boulder City | 2000 |  | 2012-04-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 85000
2105ADA3 | KITCHEN ADA UPGRADE | 2105 | The kitchenette does not meet the Americans with Disabilities Act (ADA) requirements. It is recommended to upgrade some of the features of the room for compliance with accessibility standards for employees. This project would provide funding for construction of an accessible sink and faucet and an accessible path of travel throughout the room. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | CHAPEL | 9890 | VetSvc | VetSvc |  | Boulder City | 1999 | 4800 | 2012-04-12 | Immediate to Two Years | Currently Critical | 1 | 2000
2105ADA1 | ADA SIGNAGE | 2105 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 06/09/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/12/2012. | CHAPEL | 9890 | VetSvc | VetSvc |  | Boulder City | 1999 | 4800 | 2012-04-12 | Immediate to Two Years | Currently Critical | 1 | 1500
2105EXT2 | ROOF REPAIRS | 2105 | The standing seam metal roofing and the single ply roof membrane on this building have active leaks on the north side of the building. The roof is 12 years old and should be under warranty. If the warranty is no longer valid, the estimate would provide for a licensed roofing contractor to repair the leaks. | CHAPEL | 9890 | VetSvc | VetSvc |  | Boulder City | 1999 | 4800 | 2012-04-12 | Immediate to Two Years | Currently Critical | 1 | 7500
2105EXT3 | ROOF REPLACEMENT | 2105 | The roof on this building was in fair to poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1999. It is recommended that this building be re-roofed in the next 6-8 years to be consistent with the roofing program and the end of the warranty period. | CHAPEL | 9890 | VetSvc | VetSvc |  | Boulder City | 1999 | 4800 | 2012-04-12 | Four to Ten Years | Long-Term Needs | 3 | 57600
2105EXT5 | EXTERIOR DOOR HARDWARE REPLACEMENT | 2105 | The sliding glass doors on the south side of the building are damaged from age and general wear and require new hardware. The doors are used frequently by the staff and the public and are currently very difficult to operate. This project would provide for the replacement of the sliding glass door hardware including the handles, rollers, strikes and bumpers. | CHAPEL | 9890 | VetSvc | VetSvc |  | Boulder City | 1999 | 4800 | 2012-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
2105ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 2105 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | CHAPEL | 9890 | VetSvc | VetSvc |  | Boulder City | 1999 | 4800 | 2012-04-12 | Immediate to Two Years | Currently Critical | 1 | 4000
2105SIT1 | SITE BOLLARDS | 2105 | There is a loading/unloading area for visitors along the north side of the building. There are two pillars that have one or two 4" diameter roof drain downspouts protruding beyond the edge of the curb. This project recommends the installation of 4-8" diameter pipe bollards filled with concrete on each side of the pillars to protect the downspouts. This project or a portion thereof was previously recommended in the FCA report dated 06/09/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/12/2012. | CHAPEL | 9890 | VetSvc | VetSvc |  | Boulder City | 1999 | 4800 | 2012-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
2105INT3 | CEILING TILE REPLACEMENT | 2105 | The ceiling in the building is mostly covered with a suspended ceiling system. The ceiling tiles in the system are damaged and stained and some are coming loose from the substrate. This project would provide for the replacement of the ceiling tiles. Removal and disposal of the existing tiles is included in this estimate. | CHAPEL | 9890 | VetSvc | VetSvc |  | Boulder City | 1999 | 4800 | 2012-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
2105EXT1 | EXTERIOR FINISHES | 2105 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 06/09/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/12/2012. | CHAPEL | 9890 | VetSvc | VetSvc |  | Boulder City | 1999 | 4800 | 2012-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24000
2105INT2 | FLOORING REPLACEMENT | 2105 | The VCT (vinyl composite tile) and carpet in the building are damaged and have reached the end of their useful life. It is recommended that the flooring be replaced immediately. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the next 1-2 years. This project or a portion thereof was previously recommended in the FCA report dated 06/09/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/12/2012. | CHAPEL | 9890 | VetSvc | VetSvc |  | Boulder City | 1999 | 4800 | 2012-04-12 | Immediate to Two Years | Currently Critical | 1 | 33600
2105INT1 | INTERIOR FINISHES | 2105 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 06/09/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/12/2012. | CHAPEL | 9890 | VetSvc | VetSvc |  | Boulder City | 1999 | 4800 | 2012-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24000
2105EXT4 | WINDOW REPLACEMENT | 2105 | The windows are original, dual pane construction in metal frames. These older windows are drafty and not energy efficient. Several panes have detached from the aluminum frames and are sliding down. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of approximately 100 units. Removal and disposal of the existing windows is included in this estimate. | CHAPEL | 9890 | VetSvc | VetSvc |  | Boulder City | 1999 | 4800 | 2012-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 70000
2997PLM1 | WATER TREATMENT SYSTEM INSTALLATION | 2997 | The existing plumbing and HVAC systems are not equipped with a water treatment system. Failure to treat the water causes wear and tear on the domestic water supply lines, plumbing fixtures and HVAC equipment. This project would provide for the purchase and installation of water softeners/ treatment systems to serve all of the mechanical and plumbing equipment. This project would also provide for a chemical treatment program including an updated chemicals control system, service and employee training provided by a qualified water treatment vendor. The annual maintenance fee charged by the water treatment vendor would be determined after an investigation of the water system is complete. These annual costs are not included in this project cost. For budgeting purposes, a $12,000 fee is suggested. | MAINTENANCE/OFFICE BUILDING | 9890 | VetSvc | VetSvc |  | Boulder City | 2009 | 4444 | 2012-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
2997ENR1 | CANOPY INSTALLATION | 2997 | The south facing elevation has no protection from the sun. Staff noted that the metal doors get so hot that you cannot touch them with bare hands and that there is an enormous heat load coming through the windows and doors even in winter months. This project would provide for installing a canopy along the entire south elevation to block the direct sunlight against the building. The new structure will have new concrete footings, steel framing and a metal standing seam roof. Design fees are not included in this estimate. | MAINTENANCE/OFFICE BUILDING | 9890 | VetSvc | VetSvc |  | Boulder City | 2009 | 4444 | 2012-04-12 | Four to Ten Years | Long-Term Needs | 3 | 135000
9890SIT5 | ASPHALT PAVING REPAIRS | 9890 | There are several areas of asphalt paving that are damaged and in need of repairs. The asphalt is rolling up on itself as cars push it against the curb creating a thick mass of extra asphalt on the edge of the road. The cause of the problem may be a poor asphalt mix or too much asphalt placed in these areas. This project would provide for removing and replacing the damaged areas of asphalt. Disposal of the existing asphalt is included in this estimate. | SOUTHERN NV. VETERANS MEMORIAL CEMETERY | 9890 | VetSvc | VetSvc |  | Boulder City | 0 |  | 2012-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
2998EXT2 | ROOF REPAIRS | 2998 | The standing seam metal roof on this structure had active leaks at the time of the survey. The leaks were evidenced by broken light fixtures under the roof which were filled with water. It is recommended that the roof structure is repaired immediately to prevent further damage to equipment which it is supposed to protect. | OPEN METAL CANOPY | 9890 | VetSvc | VetSvc |  | Boulder City | 2009 | 4200 | 2012-04-12 | Immediate to Two Years | Currently Critical | 1 | 7500
2998EXT1 | EXTERIOR FINISHES | 2998 | It is important to maintain the finish, weather resistance, and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | OPEN METAL CANOPY | 9890 | VetSvc | VetSvc |  | Boulder City | 2009 | 4200 | 2012-04-12 | Four to Ten Years | Long-Term Needs | 3 | 8400
9890SIT4 | CRACK FILL & SEAL ASPHALT PAVING | 9890 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the paving site wide including access roads and parking areas. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 225,000 square feet of asphalt area was used to generate this estimate. | SOUTHERN NV. VETERANS MEMORIAL CEMETERY | 9890 | VetSvc | VetSvc |  | Boulder City | 0 |  | 2012-04-12 | Four to Ten Years | Long-Term Needs | 3 | 135000
2997EXT1 | EXTERIOR FINISHES | 2997 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MAINTENANCE/OFFICE BUILDING | 9890 | VetSvc | VetSvc |  | Boulder City | 2009 | 4444 | 2012-04-12 | Four to Ten Years | Long-Term Needs | 3 | 22220
9890SIT6 | CONCRETE SWALE INSTALLATION | 9890 | The site has a drainage problem at the southwest corner of the new maintenance yard. During inclement weather, the rain accumulates in several areas adjacent to the perimeter fence and where materials are stored within the fence. This standing water also causes premature deterioration of the paving and other landscape improvements in the area. This project would provide for installation of a concrete swale outside of the perimeter fence to sufficiently carry the water away from the property. | SOUTHERN NV. VETERANS MEMORIAL CEMETERY | 9890 | VetSvc | VetSvc |  | Boulder City | 0 |  | 2012-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
2997INT1 | INTERIOR FINISHES | 2997 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | MAINTENANCE/OFFICE BUILDING | 9890 | VetSvc | VetSvc |  | Boulder City | 2009 | 4444 | 2012-04-12 | Four to Ten Years | Long-Term Needs | 3 | 22220
3147INT1 | INTERIOR FINISHES | 3147 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | ADMINISTRATION BUILDING | 9890 | VetSvc | VetSvc |  | Boulder City | 2012 | 2741 | 2012-04-12 | Four to Ten Years | Long-Term Needs | 3 | 13705
3147EXT1 | EXTERIOR FINISHES | 3147 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming, and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | ADMINISTRATION BUILDING | 9890 | VetSvc | VetSvc |  | Boulder City | 2012 | 2741 | 2012-04-12 | Four to Ten Years | Long-Term Needs | 3 | 13705
3150EXT1 | EXTERIOR FINISHES | 3150 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming, and painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | OUTDOOR COMMITTAL BLDG | 9890 | VetSvc | VetSvc |  | Boulder City | 2012 | 691 | 2012-04-12 | Four to Ten Years | Long-Term Needs | 3 | 3455
0614EXT1 | EXTERIOR FINISHES | 0614 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | STORAGE SHELTER | 9889 | VetSvc | VetSvc |  | Boulder City | 2001 | 624 | 2012-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 624
1944EXT1 | EXTERIOR FINISHES | 1944 | The exterior finishes are in good condition; however, the exposed glue laminated beams finish is in poor condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, sealing of CMU or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 2 - 3 years and is recommended on a cyclical basis based on environmental conditions. | CEMETERY PUBLIC INFORMATION OFFICE | 9898 | VetSvc | VetSvc |  | Fernley | 1990 | 576 | 2020-06-16 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2880
1944INT2 | INTERIOR FINISHES | 1944 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2 to 3 years and every 8 - 9 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | CEMETERY PUBLIC INFORMATION OFFICE | 9898 | VetSvc | VetSvc |  | Fernley | 1990 | 576 | 2020-06-16 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2880
1944SFT1 | WATER HEATER SEISMIC BRACING | 1944 | The water heater is not properly seismically anchored to the structure. This project would provide funding for seismic bracing of the water heater to the structure. | CEMETERY PUBLIC INFORMATION OFFICE | 9898 | VetSvc | VetSvc |  | Fernley | 1990 | 576 | 2020-06-16 | Immediate to Two Years | Currently Critical | 1 | 150
1943EXT1 | STOREFRONT / SLOPED GLAZING REPLACEMENT | 1943 | The storefront glazing system shows significant signs of failure due to age, exposure, broken seals around the glazing panels, and water infiltration. This project would provide for a complete replacement of the storefront glazing and framing. Removal and disposal of the existing system is included in this estimate. This project should be implemented concurrently with the CMU DECORATIVE BLOCK REPLACEMENT and EXTERIOR/INTERIOR FINISHES projects. This project or a portion thereof was previously recommended in the FCA report dated 12/08/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/16/2020. | CEMETERY PAVILION | 9898 | VetSvc | VetSvc |  | Fernley | 1990 | 576 | 2020-06-16 | Two to Four Years | Necessary - Not Yet Critical | 2 | 40000
2036EXT2 | EXTERIOR FINISHES | 2036 | The exterior conditions are in poor condition. There is significant spalling and efflorescence on the CMU decorative block that need to be treated and the exterior surfaces need to be sealed. It is important to maintain the finish, weather resistance, and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, sealing of CMU or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented within the next 2 - 3 years and is recommended on a cyclical basis based on environmental conditions. | CEMETERY STORAGE 2 | 9898 | VetSvc | VetSvc |  | Fernley | 1997 | 144 | 2020-06-16 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
2035EXT1 | EXTERIOR FINISHES | 2035 | The prefinished metal panel exterior finishes are in good condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including sealing and caulking around flashing, fixtures, and other penetrations to maintain the metal building in good, weather tight condition. It is recommended that this project be implemented in the next 8 - 9 years and is recommended on a cyclical basis based on environmental conditions. | CEMETERY STORAGE 1 | 9898 | VetSvc | VetSvc |  | Fernley | 1994 | 1152 | 2020-06-16 | Four to Ten Years | Long-Term Needs | 3 | 2304
1943EXT3 | CMU DECORATIVE BLOCK REPLACEMENT | 1943 | The CMU block supporting the storefront glazing system shows significant spalling and efflorescence. Visually, the appearance does not meet the expectations required to conduct veteran memorial services. This project would provide for a complete replacement of the CMU block. Removal and disposal of the existing system is included in this estimate. This project should be implemented concurrently with the STOREFRONT / SLOPED GLAZING REPLACEMENT and EXTERIOR/INTERIOR FINISHES projects. | CEMETERY PAVILION | 9898 | VetSvc | VetSvc |  | Fernley | 1990 | 576 | 2020-06-16 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
1943EXT2 | EXTERIOR/INTERIOR FINISHES | 1943 | The overall condition of the interior and exterior finishes is poor. A complete refurbishment is needed to meet the expectations required to conduct veteran memorial services. It is important to maintain the finish, weather resistance, and appearance of the structure. This project recommends work to protect the pavilion, other than the roof, including painting, staining, sealing of the wood structure or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the pavilion in good, weather tight condition. It is recommended that this project be implemented in the next 2 - 3 years and is recommended on a cyclical basis based on environmental conditions. This project should be implemented concurrently with the CMU DECORATIVE BLOCK REPLACEMENT and STOREFRONT / SLOPED GLAZING REPLACEMENT projects. | CEMETERY PAVILION | 9898 | VetSvc | VetSvc |  | Fernley | 1990 | 576 | 2020-06-16 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14400
1942EXT3 | ROOF REPLACEMENT | 1942 | The corrugated metal roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2 - 3 years with a standing seam metal roofing system and new vinyl faced insulation. This estimate includes removal and disposal of the old roofing system. | CEMETERY WELDING/STORAGE SHOP | 9898 | VetSvc | VetSvc |  | Fernley | 1990 | 1152 | 2020-06-16 | Two to Four Years | Necessary - Not Yet Critical | 2 | 21700
1942EXT4 | EXTERIOR FINISHES | 1942 | The exterior finishes on the wood siding portion of the exterior and exterior doors is in poor condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project recommends work to protect the exterior building envelope other than the roof, including caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that the building exterior be re-assessed in the next 2 - 3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CEMETERY WELDING/STORAGE SHOP | 9898 | VetSvc | VetSvc |  | Fernley | 1990 | 1152 | 2020-06-16 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3500
1942SIT3 | INSTALL PIPE BOLLARDS | 1942 | The building is surrounded by asphalt paving. This project would add 8" diameter pipe bollards to protect the exterior of the building and external utility riser connections. 12 pipe bollards was used to generate this estimate. This project or a portion thereof was previously recommended in the FCA report dated 12/08/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/16/2020. | CEMETERY WELDING/STORAGE SHOP | 9898 | VetSvc | VetSvc |  | Fernley | 1990 | 1152 | 2020-06-16 | Four to Ten Years | Long-Term Needs | 3 | 7200
1942ENR2 | LIGHTING UPGRADE | 1942 | The building lighting fixtures are older fluorescent units and not energy efficient. This project will upgrade lighting fixtures to T-8 lamps with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. Sensors should be installed in low occupancy areas for additional savings. This project or a portion thereof was previously recommended in the FCA report dated 12/08/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/16/2020. | CEMETERY WELDING/STORAGE SHOP | 9898 | VetSvc | VetSvc |  | Fernley | 1990 | 1152 | 2020-06-16 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2300
2499SFT1 | EGRESS DOOR INSTALLATION | 2499 | The office space on the south side of the building has only one entry/exit point through the public lobby. For security reasons, an additional exit is needed so all of the office space has an alternate exit for emergency situations. This project would provide all required demolition, installation, patching, and painting. | ADMINISTRATION OFFICE | 9898 | VetSvc | VetSvc |  | Fernley | 2004 | 2160 | 2020-06-16 | Immediate to Two Years | Currently Critical | 1 | 15000
2499LGT1 | EXTERIOR FINISHES | 2499 | The exterior finishes are in good condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, sealing of CMU or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 8 - 9 years and is recommended on a cyclical basis based on environmental conditions. . | ADMINISTRATION OFFICE | 9898 | VetSvc | VetSvc |  | Fernley | 2004 | 2160 | 2020-06-16 | Four to Ten Years | Long-Term Needs | 3 | 10800
2499INT2 | INTERIOR FINISHES | 2499 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4 to 5 years and every 8 to 10 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | ADMINISTRATION OFFICE | 9898 | VetSvc | VetSvc |  | Fernley | 2004 | 2160 | 2020-06-16 | Four to Ten Years | Long-Term Needs | 3 | 10800
2500EXT1 | EXTERIOR FINISHES | 2500 | The exterior finishes are in good condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, sealing of CMU or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 8 - 9 years and is recommended on a cyclical basis based on environmental conditions. | MAINTENANCE SHOP | 9898 | VetSvc | VetSvc |  | Fernley | 2004 | 1872 | 2020-06-16 | Four to Ten Years | Long-Term Needs | 3 | 28000
2500INT1 | INTERIOR FINISHES | 2500 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings of the office and restroom be painted at least once in the next 4 to 5 years and every 8 - 10 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | MAINTENANCE SHOP | 9898 | VetSvc | VetSvc |  | Fernley | 2004 | 1872 | 2020-06-16 | Four to Ten Years | Long-Term Needs | 3 | 2000
2499SIT1 | ADA SIGNAGE & STRIPING | 2499 | The ADA provides for accessibility to sites and services for people with physical limitations. The ADA parking area and passenger loading area are missing proper signage and striping to comply with ADA requirements. There is a missing "No Parking" sign at the ADA parking area and the striping has faded. This project would provide for striping, purchase and installation of the sign, and any other necessary upgrades to the parking area. The 2018 IBC, ICC/ANSI A117.1, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as a reference for this project. | ADMINISTRATION OFFICE | 9898 | VetSvc | VetSvc |  | Fernley | 2004 | 2160 | 2020-06-16 | Immediate to Two Years | Currently Critical | 1 | 4400
2500ELE1 | GFCI OUTLET INSTALLATION | 2500 | The existing receptacles in the restroom appear to be standard duplex receptacles and may not be GFCI protected. The 2017 NEC 210.8 requires all locations within 6 feet of a water source, garages, accessory buildings, and outdoors shall have GFCI protection. This project would provide for removing the standard receptacles and installing GFCI receptacles. | MAINTENANCE SHOP | 9898 | VetSvc | VetSvc |  | Fernley | 2004 | 1872 | 2020-06-16 | Immediate to Two Years | Currently Critical | 1 | 50
9898SIT2 | SLURRY SEAL PAVING | 9898 | It is important to maintain the asphalt concrete paving for the site. This project would provide for minor crack filling and slurry sealing of the paving. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 65,000 square feet of asphalt area was used to generate this estimate. This project or a portion thereof was previously recommended in the FCA report dated 12/08/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/16/2020. | NORTHERN VETERANS MEMORIAL CEMETERY SITE | 9898 | VetSvc | VetSvc |  | Fernley | 1990 |  | 2020-06-16 | Two to Four Years | Necessary - Not Yet Critical | 2 | 102000
9924SIT3 | PATCH, CRACK FILL AND SLURRY SEAL ASPHALT PAVEMENT | 9924 | The existing asphalt pavement is in poor to fair condition. There are areas that are in need of removal and replacement, crack filling and sealing. This project would provide for the removal and replacement of damaged asphalt pavement on the east side of the site and crack filling and a slurry seal of the west and south paved parking area. Striping including ADA accessible signage, parking, loading and boat inspection spaces and wheel stops are included in this estimate. Also included are concrete filled bollards to be installed around the HVAC unit by the Dispatch Office. Sealing of the asphalt paving also should be scheduled on a cyclical basis of every 3 to 5 years to maintain the integrity of the paving. A figure of 60 cents a square foot for sealing could be used for cyclical pavement sealing which is not included in this estimate. | DEPARTMENT OF WILDLIFE REGIONAL SITE | 9924 | Wildlife |  |  | Reno | 1960 |  | 2009-04-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 120000
9924SIT4 | PERIMETER FENCE & VEHICLE GATE REPAIRS | 9924 | The chain link perimeter fence has several areas that are in need of repair. The vehicle gate is not operating properly. This project would provide for a new electric vehicle gate to be installed along with repair or replacement of damaged sections of fencing. A three wire barbed fence is also recommended to be installed along the top of the chain link fence to prevent vandalism from occurring inside of the facility. | DEPARTMENT OF WILDLIFE REGIONAL SITE | 9924 | Wildlife |  |  | Reno | 1960 |  | 2009-04-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
9924SIT5 | SHRUB AND TREE REMOVAL | 9924 | There are several shrubs and trees that are in need of removal to prevent damage to the structures on site. This project would provide for the trimming and / or removal of the trees along the main office building, the storage building along the east side of the site and removal of the trees and shrubs along the fence line. | DEPARTMENT OF WILDLIFE REGIONAL SITE | 9924 | Wildlife |  |  | Reno | 1960 |  | 2009-04-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0277SFT4 | SMOKE DETECTOR UPGRADE | 0277 | The smoke detectors in the building are reaching the end of their expected life and do not meet current standards. It is recommended that the smoke detectors be scheduled for replacement. State Fire Marshal NAC 477.915 (3) requires that smoke detectors be connected to the building wiring with a battery backup. This project would provide funding for the purchase and installation of smoke detectors. | NDOW REGIONAL OFFICE/ANNEX | 9924 | Wildlife |  |  | Reno | 1963 | 14720 | 2009-04-07 | Immediate to Two Years | Currently Critical | 1 | 4000
0278ADA2 | ADA ACCESSIBLE SIGNAGE | 0278 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2006 IBC, ICC/ANSI A117.1 - 2003 and the most current version of the Americans With Disabilities Act Accessible Guidelines (ADAAG) was used as a reference for this project. | RADIO SHOP/DISPATCH OFFICE | 9924 | Wildlife |  |  | Reno | 1969 | 1152 | 2009-04-07 | Immediate to Two Years | Currently Critical | 1 | 600
0277EXT3 | ROOF REPLACEMENT | 0277 | The roof on the Hunter Education Addition area of this building was in fair to poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1990. It is recommended that this building be re-roofed in the next two years to be consistent with the roofing program and the end of the warranty period. | NDOW REGIONAL OFFICE/ANNEX | 9924 | Wildlife |  |  | Reno | 1963 | 14720 | 2009-04-07 | Immediate to Two Years | Currently Critical | 1 | 73230
0277ADA3 | ADA ACCESSIBLE RAMP MODIFICATIONS | 0277 | This facility has an ADA accessible ramp located on the south side of the building. The ramp does not have a proper landing, slope or handrails. This project would provide for an upgrade to the ramp to make it fully ADA compliant. The 2006 IBC, ICC/ANSI A117.1 - 2003 and the most current version of the Americans With Disabilities Act Accessible Guidelines (ADAAG) was used as a reference for this project. This project should coincide with the recommended pavement project. | NDOW REGIONAL OFFICE/ANNEX | 9924 | Wildlife |  |  | Reno | 1963 | 14720 | 2009-04-07 | Immediate to Two Years | Currently Critical | 1 | 15000
0277PLM2 | WATER HEATER REPLACEMENT | 0277 | There is a 30 gallon electric water heater in the mechanical room that was installed in 2005. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 5-6 years. It is recommended that a new gas-fired water heater be installed for more efficient use of energy. This estimate includes: 100 feet of gas pipe, fittings, couplers, and labor for installation. | NDOW REGIONAL OFFICE/ANNEX | 9924 | Wildlife |  |  | Reno | 1963 | 14720 | 2009-04-07 | Four to Ten Years | Long-Term Needs | 3 | 3000
0277SFT7 | REMOVE AND REPLACE EAST RAMP AND STAIRS | 0277 | There is a ramp along the northeast side of the building which exceeds 12% slope. The stairs and handrails also are not up to current building code requirements. This project would provide for the removal of the existing ramp and stairs and installation of a new ramp, stairs and handrails per Chapter 10, 2006 IBC. This estimate is for concrete construction. | NDOW REGIONAL OFFICE/ANNEX | 9924 | Wildlife |  |  | Reno | 1963 | 14720 | 2009-04-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0277SFT2 | REPAIR / REPLACE FUSIBLE LINKS | 0277 | The building has two 1-hour Firefly coiling doors with fusible links that are connected to the fire alarm system. Both of the fusible links are not currently operating. This project would provide for repair and/or replacement of the damaged fusible links to ensure proper functioning of the fire rated doors. | NDOW REGIONAL OFFICE/ANNEX | 9924 | Wildlife |  |  | Reno | 1963 | 14720 | 2009-04-07 | Immediate to Two Years | Currently Critical | 1 | 3000
0277PLM1 | WATER HEATER REPLACEMENT | 0277 | There is a 12 gallon electric water heater in the Hunter's Education portion of the building which was installed in 2000. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed for more efficient use of energy. The closet has gas service stubbed into it. This estimate includes: 10 feet of gas pipe, fittings, couplers, and labor for installation. | NDOW REGIONAL OFFICE/ANNEX | 9924 | Wildlife |  |  | Reno | 1963 | 14720 | 2009-04-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
0277EXT4 | WINDOW REPLACEMENT | 0277 | The windows in the older portion of the building are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 75 units. Removal and disposal of the existing windows is included in this estimate. | NDOW REGIONAL OFFICE/ANNEX | 9924 | Wildlife |  |  | Reno | 1963 | 14720 | 2009-04-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 75000
0277HVA1 | HVAC EQUIPMENT REPLACEMENT | 0277 | There are fourteen separate HVAC units servicing the building. They were installed at various times, but are all at least ten years old. Each unit serves a particular portion of the building which causes the conditioned spaces to be unbalanced and forces some of the units to be overworked. These older units are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of a new central HVAC system to provide conditioning for the entire building. The new system will most likely include altering the existing duct work and adding new duct work. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. This also includes an energy management system to be installed as part of this project. | NDOW REGIONAL OFFICE/ANNEX | 9924 | Wildlife |  |  | Reno | 1963 | 14720 | 2009-04-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 441600
0277INT1 | INTERIOR FINISHES | 0277 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | NDOW REGIONAL OFFICE/ANNEX | 9924 | Wildlife |  |  | Reno | 1963 | 14720 | 2009-04-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 73600
0278EXT2 | ROOF REPLACEMENT | 0278 | The standing seam metal roof on this building was in poor condition at the time of the survey and had active leaks. It is recommended that this building be re-roofed in the next one to two years with a new standing seam metal roofing system. This estimate includes removal and disposal of the old roofing material. | RADIO SHOP/DISPATCH OFFICE | 9924 | Wildlife |  |  | Reno | 1969 | 1152 | 2009-04-07 | Immediate to Two Years | Currently Critical | 1 | 17280
0278ADA1 | ADA ACCESSIBLE ENTRANCE RAMP | 0278 | The building has an ADA accessible ramp and handrails that does not meet current code requirements. It is recommended that the ramp, stairs and handrails be replaced. This project would provide for removal and replacement of the existing ADA accessible ramp and handrails. The 2006 IBC, ICC/ANSI A117.1 - 2003 and the most current version of the Americans With Disabilities Act Accessible Guidelines (ADAAG) was used as a reference for this project. | RADIO SHOP/DISPATCH OFFICE | 9924 | Wildlife |  |  | Reno | 1969 | 1152 | 2009-04-07 | Immediate to Two Years | Currently Critical | 1 | 35000
0278EXT1 | EXTERIOR FINISHES | 0278 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is the sealing and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | RADIO SHOP/DISPATCH OFFICE | 9924 | Wildlife |  |  | Reno | 1969 | 1152 | 2009-04-07 | Four to Ten Years | Long-Term Needs | 3 | 3456
0278INT1 | INTERIOR FINISHES | 0278 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to three years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. The square footage cost is reduced for this building because some of the walls are unfinished and other walls are covered with wallpaper. | RADIO SHOP/DISPATCH OFFICE | 9924 | Wildlife |  |  | Reno | 1969 | 1152 | 2009-04-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3456
0277SFT5 | INSTALL SEISMIC GAS SHUT-OFF VALVE | 0277 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. | NDOW REGIONAL OFFICE/ANNEX | 9924 | Wildlife |  |  | Reno | 1963 | 14720 | 2009-04-07 | Immediate to Two Years | Currently Critical | 1 | 4000
0277EXT2 | EXTERIOR FINISHES | 0277 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is painting the masonry and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted, sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NDOW REGIONAL OFFICE/ANNEX | 9924 | Wildlife |  |  | Reno | 1963 | 14720 | 2009-04-07 | Four to Ten Years | Long-Term Needs | 3 | 73600
0277SFT1 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0277 | The building is a B occupancy per the 2006 IBC and exceeds 12,000 square feet. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. | NDOW REGIONAL OFFICE/ANNEX | 9924 | Wildlife |  |  | Reno | 1963 | 14720 | 2009-04-07 | Immediate to Two Years | Currently Critical | 1 | 206080
0277INT5 | JANITORS CLOSET REPAIRS | 0277 | The mop sink in the Janitor Closet is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | NDOW REGIONAL OFFICE/ANNEX | 9924 | Wildlife |  |  | Reno | 1963 | 14720 | 2009-04-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
0277PLM3 | RESTROOM UPGRADE | 0277 | The Men's and Women's restrooms on the east side of the building are of original construction and they are due for an upgrade. This project would provide for a remodel of both Men's and Women's restrooms. The remodel may include, but is not limited to, new sinks, toilets, piping, hardware, mirrors, fixtures, partitions, cabinetry, flooring and paint. A lump sum of $16,000 has been included in this estimate for hazardous materials abatement if it is determined that there is asbestos in the flooring adhesive. | NDOW REGIONAL OFFICE/ANNEX | 9924 | Wildlife |  |  | Reno | 1963 | 14720 | 2009-04-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 33000
0277SFT3 | EXIT SIGN UPGRADE | 0277 | The existing exit signs in this building are older types and should be replaced with new self-illuminated or LED style signs with battery-backed internal systems. IBC - 2006 Chapter 10 was referenced for this project. | NDOW REGIONAL OFFICE/ANNEX | 9924 | Wildlife |  |  | Reno | 1963 | 14720 | 2009-04-07 | Immediate to Two Years | Currently Critical | 1 | 6750
0277ADA1 | ADA ACCESSIBLE WATER FOUNTAIN | 0277 | This building contains a water fountain. The 2006 IBC Chapter 11, Section 1109.5 states where a water fountain is provided, at least half should be accessible. This project would provide funding for the purchase and installation of a new accessible fixed high/ low ADA drinking fountain. The 2006 IBC, ICC/ANSI A117.1 - 2003 and the most current version of the Americans With Disabilities Act Accessible Guidelines (ADAAG) was used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 07/15/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/07/2009. | NDOW REGIONAL OFFICE/ANNEX | 9924 | Wildlife |  |  | Reno | 1963 | 14720 | 2009-04-07 | Immediate to Two Years | Currently Critical | 1 | 4000
0277ELE1 | ELECTRICAL UPGRADE | 0277 | This building was constructed before the high demand for electrical services were needed for computers and other electrical devices. As time has progressed, the buildings electrical demand and system has changed. It is utilized to its current maximum potential. The electrical panels and receptacles are at their limit and staff has indicated some of the old wiring and fixtures has been damaged and does not meet today's code requirements. It is recommended the entire system be upgraded to meet the evolving needs of the building including three-phase power, switchgear, wiring, panels and fixtures as required. This project is recommended to be done as soon as possible. | NDOW REGIONAL OFFICE/ANNEX | 9924 | Wildlife |  |  | Reno | 1963 | 14720 | 2009-04-07 | Immediate to Two Years | Currently Critical | 1 | 294400
0277INT2 | FLOORING REPLACEMENT | 0277 | The carpet and VCT (vinyl composite tile) flooring in the building is damaged and reaching the end of its useful life. It is recommended that the carpet and VCT flooring be replaced. This project would provide for removal and disposal of the carpet and VCT and installation of new carpet and 12x12 VCT with a 6" base. | NDOW REGIONAL OFFICE/ANNEX | 9924 | Wildlife |  |  | Reno | 1963 | 14720 | 2009-04-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 132480
0277INT3 | CEILING TILE REPLACEMENT | 0277 | The original 1963 construction portion of the building has adhered acoustical tiles on the ceiling. A large portion of the ceiling tiles are damaged and stained. This project would provide for the replacement of the acoustical tiles. Removal and disposal of the existing ceiling tiles is included in this estimate. The tiles and / or the adhesive may contain asbestos containing material (ACM) and remediation of ACM is not included in this estimate. | NDOW REGIONAL OFFICE/ANNEX | 9924 | Wildlife |  |  | Reno | 1963 | 14720 | 2009-04-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30251
0277ADA4 | ADA ACCESSIBLE SIGNAGE | 0277 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. Some of the signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed or replaced where required. The 2006 IBC, ICC/ANSI A117.1 - 2003 and the most current version of the Americans With Disabilities Act Accessible Guidelines (ADAAG) was used as a reference for this project. | NDOW REGIONAL OFFICE/ANNEX | 9924 | Wildlife |  |  | Reno | 1963 | 14720 | 2009-04-07 | Immediate to Two Years | Currently Critical | 1 | 1200
0277SFT6 | HANDRAIL MODIFICATION / INSTALLATION | 0277 | The stair handrails at the front entrance stairs do not meet code for safety or accessibility. There should be two intermediate handrails for the stairs due to the width of the stairs and the existing stairs do not have the proper extensions. This project recommends the installation of two additional handrails on the stairs, with proper returns and supports and modifications to the existing handrails to meet code. The 2006 IBC, ICC/ANSI A117.1 - 2003 and the most current version of the Americans With Disabilities Act Accessible Guidelines (ADAAG) was used as a reference for this project. | NDOW REGIONAL OFFICE/ANNEX | 9924 | Wildlife |  |  | Reno | 1963 | 14720 | 2009-04-07 | Immediate to Two Years | Currently Critical | 1 | 3000
0278ENR1 | LIGHTING UPGRADE | 0278 | The existing lighting fixtures in the Radio Shop are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts to current standards, resulting in increased efficiency and reduced costs associated with illumination. Any electrical wiring upgrades are not included in this estimate. | RADIO SHOP/DISPATCH OFFICE | 9924 | Wildlife |  |  | Reno | 1969 | 1152 | 2009-04-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1438
0278SFT1 | EXTERIOR LANDING INSTALLATION | 0278 | There is an exterior door from the Radio Shop which swings out over a step and does not have a proper landing. This does not comply with 2006 IBC Section 1008.1 which describes the requirements for landings including that the landing must be less than 1/2" below the threshold. This project addresses installing a landing designed to current code. | RADIO SHOP/DISPATCH OFFICE | 9924 | Wildlife |  |  | Reno | 1969 | 1152 | 2009-04-07 | Immediate to Two Years | Currently Critical | 1 | 1000
0277INT4 | BREAK ROOM REMODEL | 0277 | The kitchenette and associated casework in the employee break room are original to the building, dating to 1972. The quality of construction and installation were inadequate for the high usage at this facility, and the casework and counter tops are delaminating and failing. This project recommends the replacement of the existing counters, casework, and associated hardware and fixtures with heavy duty, quality components. The casework should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product over a moisture resistant underlayment to minimize swelling and damage from water exposure. This estimate includes disposal of the existing materials. | NDOW REGIONAL OFFICE/ANNEX | 9924 | Wildlife |  |  | Reno | 1963 | 14720 | 2009-04-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0277HVA2 | HVAC ALTERATIONS | 0277 | The building has two areas which do not have appropriate heating and cooling service. The Staff Biologist Office does not have supply or return ducting resulting in an unconditioned space that is uncomfortably warm or cold year round. The server room does not have sufficient cooling to accommodate the high heat output from the computer equipment which will cause the equipment to prematurely fail. It is recommended to install supply and return ducting to the office and to provide additional cooling to the server room. This project includes all required connections to existing utilities. This project should be coordinated with the HVAC replacement project. | NDOW REGIONAL OFFICE/ANNEX | 9924 | Wildlife |  |  | Reno | 1963 | 14720 | 2009-04-07 | Immediate to Two Years | Currently Critical | 1 | 3500
0277ENR1 | LIGHTING UPGRADE | 0277 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts to current standards, resulting in increased efficiency and reduced costs associated with illumination. Any electrical wiring upgrades are not included in this estimate. This project should be coordinated with the electrical upgrade project. This project or a portion thereof was previously recommended in the FCA report dated 07/15/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/07/2009. | NDOW REGIONAL OFFICE/ANNEX | 9924 | Wildlife |  |  | Reno | 1963 | 14720 | 2009-04-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 36800
0659ENR1 | LIGHTING UPGRADE | 0659 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts to current standards, resulting in increased efficiency and reduced costs associated with illumination. Any electrical wiring upgrades are not included in this estimate. | STORAGE #3 | 9924 | Wildlife |  |  | Reno | 1993 | 2400 | 2009-04-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
0659EXT1 | EXTERIOR FINISHES | 0659 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is the sealing and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | STORAGE #3 | 9924 | Wildlife |  |  | Reno | 1993 | 2400 | 2009-04-07 | Four to Ten Years | Long-Term Needs | 3 | 4800
0634EXT1 | EXTERIOR FINISHES | 0634 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is the sealing and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | STORAGE #1 - COMMUNICATIONS | 9924 | Wildlife |  |  | Reno |  | 600 | 2009-04-07 | Four to Ten Years | Long-Term Needs | 3 | 1200
0703EXT1 | EXTERIOR FINISHES | 0703 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is the sealing and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | STORAGE #2 | 9924 | Wildlife |  |  | Reno |  | 600 | 2009-04-07 | Four to Ten Years | Long-Term Needs | 3 | 1200
1438EXT2 | EXTERIOR FINISHES | 1438 | It is important to maintain the finish, weather resistance, energy efficiency and appearance of the building. This project would provide funding to protect the exterior of the metal building. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | DEPT. OF WILDLIFE BOAT STORAGE FACILITY | 9902 | Wildlife |  |  | Fallon | 1993 | 2250 | 2009-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
1438PLM1 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 1438 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. | DEPT. OF WILDLIFE BOAT STORAGE FACILITY | 9902 | Wildlife |  |  | Fallon | 1993 | 2250 | 2009-06-11 | Immediate to Two Years | Currently Critical | 1 | 3500
1438EXT1 | REPLACE OVERHEAD COILING DOORS | 1438 | Three of the four 10'x12' overhead coiling doors are damaged and do not function properly. Exposure, wind and vehicle collisions have caused the doors to bend, crack and lose their finish. They are original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead coiling doors and replacement with new manually operated overhead coiling doors. This project or a portion thereof was previously recommended in the FCA report dated 10/25/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/11/2009. | DEPT. OF WILDLIFE BOAT STORAGE FACILITY | 9902 | Wildlife |  |  | Fallon | 1993 | 2250 | 2009-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
1438SFT1 | EXTERIOR LANDING INSTALLATION | 1438 | Section 1008.1 of the 2006 IBC describes the requirements for doors including floor elevations and landings. The floor or landing shall be at the same elevation on each side of the door, the exterior landing shall not exceed a 2-percent slope and shall have a length measured in the direction of travel of not less than 44 inches. The landing at the door on the west side of the building does not comply with this code and poses a safety hazard. This project would provide for the installation of a compliant landing for the door. | DEPT. OF WILDLIFE BOAT STORAGE FACILITY | 9902 | Wildlife |  |  | Fallon | 1993 | 2250 | 2009-06-11 | Immediate to Two Years | Currently Critical | 1 | 500
1438ENR1 | LIGHTING UPGRADE | 1438 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts to current standards, resulting in increased efficiency and reduced costs associated with illumination. Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | DEPT. OF WILDLIFE BOAT STORAGE FACILITY | 9902 | Wildlife |  |  | Fallon | 1993 | 2250 | 2009-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
9902SFT1 | BACKFLOW PREVENTION | 9902 | State Health Law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of back siphonage or backpressure. This project allows for the installation of double check valves or reduced pressure principle backflow preventers as appropriate to the hazard and in appropriate locations near the potential source of contamination. Costs include an above ground vault, and allowance for 200 feet of 1" conduit to provide power for freeze protection. | NDOW WESTERN REGION FALLON OFFICE SITE | 9902 | Wildlife |  |  | Fallon | 0 |  | 2009-06-11 | Immediate to Two Years | Currently Critical | 1 | 25000
9902SIT2 | ASPHALT PAVING INSTALLATION | 9902 | The gravel parking areas on the site should be scheduled for paving. The inclement weather in the area causes deterioration to the grade including potholes and negative drainage areas. This project would provide asphalt concrete paving to replace the gravel areas. The estimate includes grading, 6" base, compaction and installation of 4" thick asphalt concrete paving. 11,500 square feet of gravel area was used to generate this estimate. This project or a portion thereof was previously recommended in the FCA report dated 10/25/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/11/2009. | NDOW WESTERN REGION FALLON OFFICE SITE | 9902 | Wildlife |  |  | Fallon | 0 |  | 2009-06-11 | Four to Ten Years | Long-Term Needs | 3 | 57500
9902SIT1 | SLURRY SEAL ASPHALT PAVING | 9902 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site wide including access roads, parking areas and the maintenance yard. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 3,500 square feet of asphalt area was used to generate this estimate. | NDOW WESTERN REGION FALLON OFFICE SITE | 9902 | Wildlife |  |  | Fallon | 0 |  | 2009-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2625
0633EXT5 | EXTERIOR DOOR REPLACEMENT | 0633 | The exterior metal doors are damaged from age and general wear and tear and have reached the end of their expected life. There have been continuous maintenance problems with the connections between the door closers and the frames. This project would provide for the replacement of four exterior doors with new metal doors, frames and hardware. Removal and disposal of the existing doors is included in this estimate. | WESTERN REGION FALLON FIELD OFFICE | 9902 | Wildlife |  |  | Fallon | 1974 | 3120 | 2009-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
0633ENV1 | PEST CONTROL | 0633 | There are numerous signs throughout this building of insect infestation including ants. Due to the potential risk of disease and damage to the building, this project provides for treatment and clean up of the insects by a licensed pest control business. It is recommended that the building be treated in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain control of the pests. | WESTERN REGION FALLON FIELD OFFICE | 9902 | Wildlife |  |  | Fallon | 1974 | 3120 | 2009-06-11 | Immediate to Two Years | Currently Critical | 1 | 1000
0633EXT3 | EXTERIOR FINISHES | 0633 | It is important to maintain the finish, weather resistance, energy efficiency and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | WESTERN REGION FALLON FIELD OFFICE | 9902 | Wildlife |  |  | Fallon | 1974 | 3120 | 2009-06-11 | Four to Ten Years | Long-Term Needs | 3 | 31200
0633STR1 | STRUCTURAL ASSESSMENT | 0633 | The foundation wall on the north facing elevation is showing significant water damage. The moisture has been weeping through the concrete from below the floor slab. The saturated concrete is crumbling and may be compromising the integrity of the structural system. This project recommends that a licensed structural engineer perform a structural investigation to assess the extent of the damage and recommend a plan to mitigate it. Future projects would be based on this report. | WESTERN REGION FALLON FIELD OFFICE | 9902 | Wildlife |  |  | Fallon | 1974 | 3120 | 2009-06-11 | Immediate to Two Years | Currently Critical | 1 | 2500
0633INT1 | INTERIOR FINISHES | 0633 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next four to five years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | WESTERN REGION FALLON FIELD OFFICE | 9902 | Wildlife |  |  | Fallon | 1974 | 3120 | 2009-06-11 | Four to Ten Years | Long-Term Needs | 3 | 15600
0633SFT3 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0633 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. | WESTERN REGION FALLON FIELD OFFICE | 9902 | Wildlife |  |  | Fallon | 1974 | 3120 | 2009-06-11 | Immediate to Two Years | Currently Critical | 1 | 3500
0633ENR4 | WINDOW REPLACEMENT | 0633 | The windows are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 20 units. Removal and disposal of the existing windows is included in this estimate. | WESTERN REGION FALLON FIELD OFFICE | 9902 | Wildlife |  |  | Fallon | 1974 | 3120 | 2009-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0633SFT1 | FIRE RATED DOOR REPAIRS | 0633 | Two fire rated doors have been removed from their original locations on the two north-west offices. The doors should be reattached to ensure the safety of the occupants by maintaining the original fire separations. | WESTERN REGION FALLON FIELD OFFICE | 9902 | Wildlife |  |  | Fallon | 1974 | 3120 | 2009-06-11 | Immediate to Two Years | Currently Critical | 1 | 500
0633ADA1 | ADA SIGNAGE | 0633 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2006 IBC, ICC/ANSI A117.1 - 2003 and the most current version of the Americans With Disabilities Act Accessible Guidelines (ADAAG) was used as a reference for this project. | WESTERN REGION FALLON FIELD OFFICE | 9902 | Wildlife |  |  | Fallon | 1974 | 3120 | 2009-06-11 | Immediate to Two Years | Currently Critical | 1 | 1200
0633ENR1 | LIGHTING UPGRADE | 0633 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts to current standards, resulting in increased efficiency and reduced costs associated with illumination. Occupancy sensors will be installed in restrooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | WESTERN REGION FALLON FIELD OFFICE | 9902 | Wildlife |  |  | Fallon | 1974 | 3120 | 2009-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6240
0633SFT2 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0633 | The building is a B occupancy per the 2006 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. | WESTERN REGION FALLON FIELD OFFICE | 9902 | Wildlife |  |  | Fallon | 1974 | 3120 | 2009-06-11 | Immediate to Two Years | Currently Critical | 1 | 43680
0633EXT2 | ROOF REPLACEMENT | 0633 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next two to three years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing and underlayments. This project or a portion thereof was previously recommended in the FCA report dated 10/25/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/11/2009. | WESTERN REGION FALLON FIELD OFFICE | 9902 | Wildlife |  |  | Fallon | 1974 | 3120 | 2009-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 46800
0633ENR2 | HVAC EQUIPMENT & SUPPORT REPLACEMENT | 0633 | The two HVAC roof top units are original to the building dating back to 1981. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of new HVAC packaged units with an economizer system and cleaning of the existing duct work and grilles and recommisioning. This project also would provide for the investigation and repairs if needed for the HVAC support structure. It is recommended that a licensed engineer review existing conditions and make recommendations for remediation. The estimate also includes removal and disposal of the existing HVAC units and all required connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 10/25/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/11/2009. | WESTERN REGION FALLON FIELD OFFICE | 9902 | Wildlife |  |  | Fallon | 1974 | 3120 | 2009-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 40000
0633ENR3 | WATER HEATER REPLACEMENT | 0633 | There is a 28 gallon gas-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 5-6 years. It is recommended that a new energy efficient gas-fired water heater be installed. | WESTERN REGION FALLON FIELD OFFICE | 9902 | Wildlife |  |  | Fallon | 1974 | 3120 | 2009-06-11 | Four to Ten Years | Long-Term Needs | 3 | 1500
0260INT3 | INTERIOR FINISHES | 0260 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 1/1/2002. It has been amended accordingly to reflect conditions observed during the most recent survey date of 2/25/2010. | NDOW REGIONAL OFFICE | 9878 | Wildlife |  |  | Las Vegas | 1967 | 5344 | 2010-02-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25660
0260INT2 | FLOORING REPLACEMENT | 0260 | The VCT (vinyl composite tile), sheet vinyl and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the next two to three years. It is likely that the mastic used for the VCT and linoleum has asbestos in it. This estimate includes additional funds for proper asbestos abatement including removal, disposal and monitoring. This project or a portion thereof was previously recommended in the FCA report dated 1/1/2002. It has been amended accordingly to reflect conditions observed during the most recent survey date of 2/25/2010. | NDOW REGIONAL OFFICE | 9878 | Wildlife |  |  | Las Vegas | 1967 | 5344 | 2010-02-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 40000
0260ENR5 | EXTERIOR INSULATION & FINISH SYSTEM | 0260 | The building is constructed of brick masonry with no insulation. Buildings of this type are not energy efficient. This project recommends adding an exterior insulation and finish system (EIFS) over the brick masonry. The estimate is based on $10.00 per square foot for the EIFS. It is recommended that this project be coordinated with the exterior door and window replacement projects. This project or a portion thereof was previously recommended in the FCA report dated 1/1/2002. It has been amended accordingly to reflect conditions observed during the most recent survey date of 2/25/2010. | NDOW REGIONAL OFFICE | 9878 | Wildlife |  |  | Las Vegas | 1967 | 5344 | 2010-02-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
0260PLM1 | RESTROOM REMODEL | 0260 | The restroom fixtures in the four restrooms other than the ADA restroom are older and in overall poor condition. The finishes, fixtures, cabinets, sinks, toilets, mirrors and exhaust fans are showing signs of wear and deterioration. This project would provide for a complete remodel of the restrooms. The removal and disposal of the existing fixtures and finishes is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 1/1/2002. It has been amended accordingly to reflect conditions observed during the most recent survey date of 2/25/2010. | NDOW REGIONAL OFFICE | 9878 | Wildlife |  |  | Las Vegas | 1967 | 5344 | 2010-02-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0260ENR1 | LIGHTING UPGRADE | 0260 | The existing lighting fixtures are the older fluorescent type and are not energy efficient. The existing lighting also needs to be redesigned to accommodate the buildings current usage. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, conference rooms and other low occupancy areas for additional savings and fixture locations will be altered based on current needs. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 1/1/2002. It has been amended accordingly to reflect conditions observed during the most recent survey date of 2/25/2010. | NDOW REGIONAL OFFICE | 9878 | Wildlife |  |  | Las Vegas | 1967 | 5344 | 2010-02-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12830
0260ENR2 | WINDOW REPLACEMENT | 0260 | The windows are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 30 units. Removal and disposal of the existing windows is included in this estimate. It is recommended that this project be coordinated with the EIFS project. This project or a portion thereof was previously recommended in the FCA report dated 1/1/2002. It has been amended accordingly to reflect conditions observed during the most recent survey date of 2/25/2010. | NDOW REGIONAL OFFICE | 9878 | Wildlife |  |  | Las Vegas | 1967 | 5344 | 2010-02-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
0260EXT1 | GUTTER INSTALLATION AND EAVE REPAIRS | 0260 | The building does not have gutters or downspouts to control the runoff from the roof. The water currently sheet drains off the roof causing flooding and erosion to the flower beds and grade around the building. The fascia, trim and soffits are damaged and should be repaired at the same time. This project would provide funding for the installation of a seamless gutter and downspout system for the building and repairing or replacing the fascia, trim and soffits as needed. This project or a portion thereof was previously recommended in the FCA report dated 1/1/2002. It has been amended accordingly to reflect conditions observed during the most recent survey date of 2/25/2010. | NDOW REGIONAL OFFICE | 9878 | Wildlife |  |  | Las Vegas | 1967 | 5344 | 2010-02-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 22500
0260SFT1 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0260 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of LED exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2006 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 1/1/2002. It has been amended accordingly to reflect conditions observed during the most recent survey date of 2/25/2010. | NDOW REGIONAL OFFICE | 9878 | Wildlife |  |  | Las Vegas | 1967 | 5344 | 2010-02-25 | Immediate to Two Years | Currently Critical | 1 | 2500
0260EXT3 | ROOF REPLACEMENT | 0260 | The ballasted roof on this building was in fair condition at the time of the survey. Based on age it should be scheduled for replacement in the next two to three years with a single-ply roofing membrane system which will bring the roof into the Statewide roofing warranty and preventative maintenance agreement program. This estimate includes removal and disposal of the old roofing. This project or a portion thereof was previously recommended in the FCA report dated 1/1/2002. It has been amended accordingly to reflect conditions observed during the most recent survey date of 2/25/2010. | NDOW REGIONAL OFFICE | 9878 | Wildlife |  |  | Las Vegas | 1967 | 5344 | 2010-02-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 76980
0260ENR3 | EXTERIOR DOOR REPLACEMENT | 0260 | The existing exterior wood doors appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement of the wood doors with new metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. This project does not include the storefront system doors at the entrance to the building. This project or a portion thereof was previously recommended in the FCA report dated 1/1/2002. It has been amended accordingly to reflect conditions observed during the most recent survey date of 2/25/2010. | NDOW REGIONAL OFFICE | 9878 | Wildlife |  |  | Las Vegas | 1967 | 5344 | 2010-02-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
0260ADA1 | ADA SIGNAGE | 0260 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2003 were referenced for this project. | NDOW REGIONAL OFFICE | 9878 | Wildlife |  |  | Las Vegas | 1967 | 5344 | 2010-02-25 | Immediate to Two Years | Currently Critical | 1 | 1000
0260SFT4 | EXTERIOR LANDING INSTALLATION | 0260 | There is an out-swinging exterior door from the building which swings out over a step and does not have a landing. This does not comply with 2006 IBC Section 1008.1 which requires a proper landing and for the landing to be not more than 1/2" below the threshold. This project would provide for the installation of a compliant landing for the door. | NDOW REGIONAL OFFICE | 9878 | Wildlife |  |  | Las Vegas | 1967 | 5344 | 2010-02-25 | Immediate to Two Years | Currently Critical | 1 | 500
0260PLM3 | WATER HEATER REPLACEMENT | 0260 | There is a 15 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed for more efficient use of energy. This estimate includes: 100 feet of gas pipe, fittings, couplers, and labor for installation. Removal and disposal of the existing equipment is included in this estimate. | NDOW REGIONAL OFFICE | 9878 | Wildlife |  |  | Las Vegas | 1967 | 5344 | 2010-02-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0260EXT4 | EXTERIOR FINISHES | 0260 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the masonry, sanding, priming and painting the wood siding, and caulking of the windows, flashing, fixtures, and all other penetrations. It is recommended that the building be sealed, painted, and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 1/1/2002. It has been amended accordingly to reflect conditions observed during the most recent survey date of 2/25/2010. | NDOW REGIONAL OFFICE | 9878 | Wildlife |  |  | Las Vegas | 1967 | 5344 | 2010-02-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35924
0260PLM2 | BACKFLOW PREVENTION | 0260 | State Health Law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of back siphonage or backpressure. This project allows for the installation of double check valves or reduced pressure principle backflow preventers as appropriate to the hazard and in appropriate locations near the potential source of contamination. Costs include an above ground vault and allowance for 200 feet of 1" conduit to provide power for freeze protection. | NDOW REGIONAL OFFICE | 9878 | Wildlife |  |  | Las Vegas | 1967 | 5344 | 2010-02-25 | Immediate to Two Years | Currently Critical | 1 | 25000
0260SFT3 | FIRE ALARM SYSTEM INSTALLATION | 0260 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2006 Section 7, the 2006 International Fire Code and NAC 477.917. | NDOW REGIONAL OFFICE | 9878 | Wildlife |  |  | Las Vegas | 1967 | 5344 | 2010-02-25 | Immediate to Two Years | Currently Critical | 1 | 35924
0260SFT2 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0260 | The building is a B occupancy per the 2006 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. | NDOW REGIONAL OFFICE | 9878 | Wildlife |  |  | Las Vegas | 1967 | 5344 | 2010-02-25 | Immediate to Two Years | Currently Critical | 1 | 71848
0260ENR4 | HVAC EQUIPMENT REPLACEMENT | 0260 | The three ground mounted HVAC packaged units are showing signs of wear. They are not energy efficient and have reached the end of their expected and useful life. There is no energy management system (EMS) for the building. This project would provide for installation of an EMS, three new HVAC packaged units and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | NDOW REGIONAL OFFICE | 9878 | Wildlife |  |  | Las Vegas | 1967 | 5344 | 2010-02-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 45000
0260SFT5 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0260 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. | NDOW REGIONAL OFFICE | 9878 | Wildlife |  |  | Las Vegas | 1967 | 5344 | 2010-02-25 | Immediate to Two Years | Currently Critical | 1 | 4000
0260EXT5 | ROOF ALTERATIONS | 0260 | The tree on the northwest side of the building is touching the roof eave and will eventually damage the roof. The tree will continue to grow and potentially cause leaks in the roof and structural damage. The tree provides shade to the building and is a positive environmental feature for the site. This project would provide for altering the roof in order to accommodate the tree. A structural design will be necessary to ensure that the eave loads are properly transferred and it is recommended that this project be coordinated with the roofing project. | NDOW REGIONAL OFFICE | 9878 | Wildlife |  |  | Las Vegas | 1967 | 5344 | 2010-02-25 | Immediate to Two Years | Currently Critical | 1 | 7500
0704SFT3 | FIRE ALARM SYSTEM INSTALLATION | 0704 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2006 Section 7, the 2006 International Fire Code and NAC 477.917. | WILDLIFE OFFICE ANNEX | 9878 | Wildlife |  |  | Las Vegas | 1971 | 1740 | 2010-02-25 | Immediate to Two Years | Currently Critical | 1 | 11200
0704ADA1 | ADA RESTROOM UPGRADE | 0704 | The building does not have an accessible restroom. The existing restroom does not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring, and paint. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2003 were referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 1/1/2002. It has been amended accordingly to reflect conditions observed during the most recent survey date of 2/25/2010. | WILDLIFE OFFICE ANNEX | 9878 | Wildlife |  |  | Las Vegas | 1971 | 1740 | 2010-02-25 | Immediate to Two Years | Currently Critical | 1 | 25000
0704INT3 | INTERIOR FINISHES | 0704 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | WILDLIFE OFFICE ANNEX | 9878 | Wildlife |  |  | Las Vegas | 1971 | 1740 | 2010-02-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
0704ADA2 | ADA SIGNAGE | 0704 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2003 were referenced for this project. | WILDLIFE OFFICE ANNEX | 9878 | Wildlife |  |  | Las Vegas | 1971 | 1740 | 2010-02-25 | Immediate to Two Years | Currently Critical | 1 | 600
0704PLM3 | WATER HEATER REPLACEMENT | 0704 | There is a 15 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 3-4 years. It is recommended that a new gas-fired water heater be installed for more efficient use of energy. This estimate includes: 100 feet of gas pipe, fittings, couplers, and labor for installation. Removal and disposal of the existing equipment is included in this estimate. | WILDLIFE OFFICE ANNEX | 9878 | Wildlife |  |  | Las Vegas | 1971 | 1740 | 2010-02-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0704SFT2 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0704 | The building is a B occupancy per the 2006 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. | WILDLIFE OFFICE ANNEX | 9878 | Wildlife |  |  | Las Vegas | 1971 | 1740 | 2010-02-25 | Immediate to Two Years | Currently Critical | 1 | 22400
0704SFT4 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0704 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. | WILDLIFE OFFICE ANNEX | 9878 | Wildlife |  |  | Las Vegas | 1971 | 1740 | 2010-02-25 | Immediate to Two Years | Currently Critical | 1 | 4000
0704EXT6 | EXTERIOR FINISHES | 0704 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the masonry, sanding, priming and painting the wood siding and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | WILDLIFE OFFICE ANNEX | 9878 | Wildlife |  |  | Las Vegas | 1971 | 1740 | 2010-02-25 | Four to Ten Years | Long-Term Needs | 3 | 12000
0704EXT5 | EXTERIOR DOOR REPLACEMENT | 0704 | The exterior metal doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the doors with new metal doors, frames and hardware. Removal and disposal of the existing doors is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 1/1/2002. It has been amended accordingly to reflect conditions observed during the most recent survey date of 2/25/2010. | WILDLIFE OFFICE ANNEX | 9878 | Wildlife |  |  | Las Vegas | 1971 | 1740 | 2010-02-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
0704SFT1 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0704 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2006 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 1/1/2002. It has been amended accordingly to reflect conditions observed during the most recent survey date of 2/25/2010. | WILDLIFE OFFICE ANNEX | 9878 | Wildlife |  |  | Las Vegas | 1971 | 1740 | 2010-02-25 | Immediate to Two Years | Currently Critical | 1 | 2500
0704ENR1 | EXTERIOR INSULATION & FINISH SYSTEM | 0704 | The building is constructed of brick masonry with no insulation. Buildings of this type are not energy efficient. This project recommends adding an exterior insulation and finish system (EIFS) over the brick masonry. The estimate is based on $10.00 per square foot for the EIFS. It is recommended that this project be coordinated with the exterior door and window replacement projects. This project or a portion thereof was previously recommended in the FCA report dated 1/1/2002. It has been amended accordingly to reflect conditions observed during the most recent survey date of 2/25/2010. | WILDLIFE OFFICE ANNEX | 9878 | Wildlife |  |  | Las Vegas | 1971 | 1740 | 2010-02-25 | Immediate to Two Years | Currently Critical | 1 | 16000
0704ENR2 | WINDOW REPLACEMENT | 0704 | The windows are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 11 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 1/1/2002. It has been amended accordingly to reflect conditions observed during the most recent survey date of 2/25/2010. | WILDLIFE OFFICE ANNEX | 9878 | Wildlife |  |  | Las Vegas | 1971 | 1740 | 2010-02-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11000
0704ENR3 | HVAC EQUIPMENT REPLACEMENT | 0704 | The FAU unit is showing signs of wear. It is not energy efficient and has reached the end of its expected and useful life. There is no energy management system (EMS) for the building. This project would provide for installation of an EMS, a new FAU unit and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC unit and all required connections to utilities. The air conditioning condenser is fairly new and not included in this project. | WILDLIFE OFFICE ANNEX | 9878 | Wildlife |  |  | Las Vegas | 1971 | 1740 | 2010-02-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
0704EXT1 | INSTALL RAIN GUTTERS REPAIR/REPLACE FASCIA | 0704 | The building does not have gutters or downspouts to control the runoff from the roof. The water currently sheet drains off the roof causing flooding and erosion to the flower beds and grade around the building. The fascia, trim and soffits should be repaired at the same time. This project would provide funding for the installation of a seamless gutter and downspout system for the building and repairing or replacing the fascia, trim and soffits as needed. This project or a portion thereof was previously recommended in the FCA report dated 1/1/2002. It has been amended accordingly to reflect conditions observed during the most recent survey date of 2/25/2010. | WILDLIFE OFFICE ANNEX | 9878 | Wildlife |  |  | Las Vegas | 1971 | 1740 | 2010-02-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
0704EXT3 | ROOF REPLACEMENT | 0704 | The asphalt composition shingle roof on this building was in fair condition at the time of the survey. It is recommended that this building be re-roofed in the next 7-10 years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. | WILDLIFE OFFICE ANNEX | 9878 | Wildlife |  |  | Las Vegas | 1971 | 1740 | 2010-02-25 | Four to Ten Years | Long-Term Needs | 3 | 24000
2464INT1 | INTERIOR FINISHES | 2464 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 10/11/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/11/2012. | HATCHERY RESIDENCE #3 | 9897 | Wildlife |  |  | Boulder City | 2005 | 2350 | 2012-04-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11750
2469EXT1 | EXTERIOR FINISHES | 2469 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 10/11/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/11/2012. | UPPER REARING BUILDING | 9897 | Wildlife |  |  | Boulder City | 2005 | 34000 | 2012-04-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 34000
2468EXT1 | EXTERIOR FINISHES | 2468 | It is important to maintain the finish, weather resistance, and appearance of the structure. This project would provide funding to protect the exterior of the structure. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the structure be painted and sealed in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 10/11/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/11/2012. | HATCHERY FEED BINS | 9897 | Wildlife |  |  | Boulder City | 2005 | 500 | 2012-04-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
2466HVA1 | CONDENSATE LINE REPAIRS | 2466 | The building has two roof-mounted evaporative coolers that are leaking water and damaging the roof. The condensate lines have leaks in them and since the water is untreated, it is staining the standing seam metal roof and will cause corrosion and rusting if left unrepaired. This project would provide for replacement of the condensate lines to prevent any further damage. | HATCHERY SHOP / FEED STORAGE | 9897 | Wildlife |  |  | Boulder City | 2005 | 5360 | 2012-04-11 | Immediate to Two Years | Currently Critical | 1 | 1000
2464SFT1 | FIRE SEPARATION UPGRADE | 2464 | Section R309.2 of the 2012 International Residential Code states that, "The garage shall be separated from the residence and its attic area by not less than 1/2" Type X gypsum board applied to the garage side." The attic access in the ceiling of the garage is only covered by a piece of plywood which does not meet this requirement. Without the proper fire-rated assembly between the garage and the attic, the safety of the occupants and the protection of the structure are compromised. This project would provide for the purchase and installation of the gypsum board at the attic access to meet the requirements of the code. | HATCHERY RESIDENCE #3 | 9897 | Wildlife |  |  | Boulder City | 2005 | 2350 | 2012-04-11 | Immediate to Two Years | Currently Critical | 1 | 500
2464PLM1 | WATER HEATER REPLACEMENT | 2464 | There is a 40 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 4-5 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | HATCHERY RESIDENCE #3 | 9897 | Wildlife |  |  | Boulder City | 2005 | 2350 | 2012-04-11 | Four to Ten Years | Long-Term Needs | 3 | 1500
2464EXT1 | EXTERIOR FINISHES | 2464 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 10/11/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/11/2012. | HATCHERY RESIDENCE #3 | 9897 | Wildlife |  |  | Boulder City | 2005 | 2350 | 2012-04-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11750
2470EXT1 | EXTERIOR FINISHES | 2470 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting of the EIFS and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | LAUGHLIN WILDLIFE FIELD OFFICE | 9838 | Wildlife |  |  | Laughlin | 2004 | 2700 | 2012-04-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 13500
2470SFT1 | FIRE SUPPRESSION SYSTEM INSTALLATION | 2470 | The building is a B occupancy per the 2006 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 or R-2 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. | LAUGHLIN WILDLIFE FIELD OFFICE | 9838 | Wildlife |  |  | Laughlin | 2004 | 2700 | 2012-04-11 | Immediate to Two Years | Currently Critical | 1 | 37800
2470INT1 | INTERIOR FINISHES | 2470 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | LAUGHLIN WILDLIFE FIELD OFFICE | 9838 | Wildlife |  |  | Laughlin | 2004 | 2700 | 2012-04-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 13500
2465SFT1 | FIRE SEPARATION UPGRADE | 2465 | Section R309.2 of the 2012 International Residential Code states that, "The garage shall be separated from the residence and its attic area by not less than 1/2" Type X gypsum board applied to the garage side." The attic access in the ceiling of the garage is only covered by a piece of plywood which does not meet this requirement. Without the proper fire-rated assembly between the garage and the attic, the safety of the occupants and the protection of the structure are compromised. This project would provide for the purchase and installation of the gypsum board at the attic access to meet the requirements of the code. | HATCHERY RESIDENCE #4 | 9897 | Wildlife |  |  | Boulder City | 2005 | 2350 | 2012-04-11 | Immediate to Two Years | Currently Critical | 1 | 500
2465PLM1 | WATER HEATER REPLACEMENT | 2465 | There is a 40 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 4-5 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | HATCHERY RESIDENCE #4 | 9897 | Wildlife |  |  | Boulder City | 2005 | 2350 | 2012-04-11 | Four to Ten Years | Long-Term Needs | 3 | 1500
2465INT1 | INTERIOR FINISHES | 2465 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 10/11/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/11/2012. | HATCHERY RESIDENCE #4 | 9897 | Wildlife |  |  | Boulder City | 2005 | 2350 | 2012-04-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11750
2466EXT1 | EXTERIOR FINISHES | 2466 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 10/11/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/11/2012. | HATCHERY SHOP / FEED STORAGE | 9897 | Wildlife |  |  | Boulder City | 2005 | 5360 | 2012-04-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5360
2465EXT1 | EXTERIOR FINISHES | 2465 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 10/11/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/11/2012. | HATCHERY RESIDENCE #4 | 9897 | Wildlife |  |  | Boulder City | 2005 | 2350 | 2012-04-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11750
2470ENR1 | HVAC EQUIPMENT REPLACEMENT | 2470 | The two HVAC roof top AC units serving the Vehicle Storage Garage are over 20 years old. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of two new HVAC units and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | LAUGHLIN WILDLIFE FIELD OFFICE | 9838 | Wildlife |  |  | Laughlin | 2004 | 2700 | 2012-04-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14000
2466INT1 | INTERIOR FINISHES | 2466 | The interior finishes are in fair condition. It is recommended that the painted interior walls be painted at least once in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. The open framed walls and ceilings with exposed insulation should be covered by netting to prevent the birds from destroying the insulation. Alternatively, the walls could be covered by gypsum board and painted at an increased cost. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 10/11/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/11/2012. | HATCHERY SHOP / FEED STORAGE | 9897 | Wildlife |  |  | Boulder City | 2005 | 5360 | 2012-04-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 26800
9897LGT1 | CRACK FILL & SEAL ASPHALT PAVING | 9897 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the paving site wide including access roads, parking areas and maintenance yards. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 162,000 square feet of asphalt area was used to generate this estimate. This project or a portion thereof was previously recommended in the FCA report dated 10/11/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/11/2012. | LAKE MEAD FISH HATCHERY SITE | 9897 | Wildlife |  |  | Boulder City | 1972 |  | 2012-04-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 97200
9838SIT1 | CRACK FILL & SEAL ASPHALT PAVING | 9838 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the paving site wide including access roads, parking areas and vehicle storage areas. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 32,000 square feet of asphalt area was used to generate this estimate. | LAUGHLIN WILDLIFE FIELD OFFICE SITE | 9838 | Wildlife |  |  | Laughlin | 0 |  | 2012-04-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19200
0655SFT1 | DIESEL FUEL TANK SHUTOFF REPLACEMENT | 0655 | The existing emergency shutoff switch for the diesel fuel tank and delivery system is due for replacement. The switch is over 30 years old, does not have a sign to identify it, and is difficult to locate. This project would replace the existing switch with a new mushroom switch and install clear signage to identify and locate the switch. | VISITATION/HATCHERY BUILDING | 9897 | Wildlife |  |  | Boulder City | 2005 | 26430 | 2012-04-11 | Immediate to Two Years | Currently Critical | 1 | 1500
0657EXT1 | EXTERIOR FINISHES | 0657 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 10/11/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/11/2012. | HATCHERY FIRE PUMP STATION | 9897 | Wildlife |  |  | Boulder City | 2005 | 176 | 2012-04-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 176
0656EXT1 | EXTERIOR FINISHES | 0656 | It is important to maintain the finish, weather resistance, and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 10/11/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/11/2012. | LOWER REARING SHADE SHELTER | 9897 | Wildlife |  |  | Boulder City |  | 23760 | 2012-04-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 23760
0655EXT1 | EXTERIOR FINISHES | 0655 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Approximately 1/8 of the exterior of the building is sealed concrete masonry units, the rest is steel framing with metal siding. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 10/11/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/11/2012. | VISITATION/HATCHERY BUILDING | 9897 | Wildlife |  |  | Boulder City | 2005 | 26430 | 2012-04-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 52524
0655ELE1 | GENERATOR REPLACEMENT | 0655 | The raceways have automatic monitors controlling the PH levels, oxygen levels and automatic fish feeders. Water is apportioned between the hatchery and residences after it enters the system through an aeration tower. During power outages, water is re-circulated back to the aeration tower and a portion of this contaminated water eventually ends up at the tap of the residences and the water in the raceways becomes potentially deadly for the fish. The building has a back-up generator system to prevent this hazard that was installed in 1973. The generator is constantly breaking down and has been rebuilt several times. The exhaust mufflers are within 6" from the wood timbers on the exterior of the building and should be re-routed. This project would provide for a new diesel powered 375 KVA generator including required connections to utility systems and relocating the exhaust mufflers. This project or a portion thereof was previously recommended in the FCA report dated 10/11/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/11/2012. | VISITATION/HATCHERY BUILDING | 9897 | Wildlife |  |  | Boulder City | 2005 | 26430 | 2012-04-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 150000
0655INT1 | INTERIOR FINISHES | 0655 | The interior finishes are in fair condition. Approximately 3,500 square feet of the building is finished with painted gypsum board. It is recommended that the painted interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 10/11/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/11/2012. | VISITATION/HATCHERY BUILDING | 9897 | Wildlife |  |  | Boulder City | 2005 | 26430 | 2012-04-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 17500
0654SFT1 | FIRE SEPARATION UPGRADE | 0654 | Section R309.2 of the 2012 International Residential Code states that, "The garage shall be separated from the residence and its attic area by not less than 1/2" Type X gypsum board applied to the garage side." The attic access in the ceiling of the garage is only covered by a piece of plywood which does not meet this requirement. Without the proper fire-rated assembly between the garage and the attic, the safety of the occupants and the protection of the structure are compromised. This project would provide for the purchase and installation of the gypsum board at the attic access to meet the requirements of the code. | HATCHERY RESIDENCE #1 | 9897 | Wildlife |  |  | Boulder City | 2005 | 2350 | 2012-04-11 | Immediate to Two Years | Currently Critical | 1 | 500
0654PLM1 | WATER HEATER REPLACEMENT | 0654 | There is a 40 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 4-5 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | HATCHERY RESIDENCE #1 | 9897 | Wildlife |  |  | Boulder City | 2005 | 2350 | 2012-04-11 | Four to Ten Years | Long-Term Needs | 3 | 1500
0654INT1 | INTERIOR FINISHES | 0654 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 10/11/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/11/2012. | HATCHERY RESIDENCE #1 | 9897 | Wildlife |  |  | Boulder City | 2005 | 2350 | 2012-04-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11750
0907SFT1 | FIRE SEPARATION UPGRADE | 0907 | Section R309.2 of the 2012 International Residential Code states that, "The garage shall be separated from the residence and its attic area by not less than 1/2" Type X gypsum board applied to the garage side." The attic access in the ceiling of the garage is only covered by a piece of plywood which does not meet this requirement. Without the proper fire-rated assembly between the garage and the attic, the safety of the occupants and the protection of the structure are compromised. This project would provide for the purchase and installation of the gypsum board at the attic access to meet the requirements of the code. | HATCHERY RESIDENCE #2 | 9897 | Wildlife |  |  | Boulder City | 2005 | 2350 | 2012-04-11 | Immediate to Two Years | Currently Critical | 1 | 500
0655SFT2 | EXIT SIGN AND EGRESS LIGHTING INSTALLATION | 0655 | The building does not have emergency lighting and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 08/18/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/06/2016. | VISITATION/HATCHERY BUILDING | 9897 | Wildlife |  |  | Boulder City | 2005 | 26430 | 2012-04-11 | Immediate to Two Years | Currently Critical | 1 | 6715
0914EXT1 | EXTERIOR FINISHES | 0914 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 10/11/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/11/2012. | NORTH EQUIPMENT STORAGE | 9897 | Wildlife |  |  | Boulder City |  | 1050 | 2012-04-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1050
0906EXT1 | EXTERIOR FINISHES | 0906 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 10/11/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/11/2012. | FILTER BUILDING | 9897 | Wildlife |  |  | Boulder City | 2005 | 417 | 2012-04-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2085
0907PLM1 | WATER HEATER REPLACEMENT | 0907 | There is a 40 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 4-5 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | HATCHERY RESIDENCE #2 | 9897 | Wildlife |  |  | Boulder City | 2005 | 2350 | 2012-04-11 | Four to Ten Years | Long-Term Needs | 3 | 1500
0907EXT1 | EXTERIOR FINISHES | 0907 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 10/11/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/11/2012. | HATCHERY RESIDENCE #2 | 9897 | Wildlife |  |  | Boulder City | 2005 | 2350 | 2012-04-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11750
0907INT1 | INTERIOR FINISHES | 0907 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 10/11/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/11/2012. | HATCHERY RESIDENCE #2 | 9897 | Wildlife |  |  | Boulder City | 2005 | 2350 | 2012-04-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11750
0912EXT1 | EXTERIOR FINISHES | 0912 | It is important to maintain the finish, weather resistance, and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 10/11/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/11/2012. | OUTFLOW SHED | 9897 | Wildlife |  |  | Boulder City | 1975 | 176 | 2012-04-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 352
0654EXT1 | EXTERIOR FINISHES | 0654 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 10/11/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/11/2012. | HATCHERY RESIDENCE #1 | 9897 | Wildlife |  |  | Boulder City | 2005 | 2350 | 2012-04-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11750
0913EXT1 | EXTERIOR/ INTERIOR FINISHES | 0913 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 10/11/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/11/2012. | HATCHERY WATER AERATION TOWER | 9897 | Wildlife |  |  | Boulder City | 2005 | 400 | 2012-04-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0661ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0661 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | NDOW AIRCRAFT HANGAR | 9900 | Wildlife |  |  | Minden | 1996 | 6400 | 2013-11-12 | Immediate to Two Years | Currently Critical | 1 | 4000
0661ADA1 | ADA PARKING SPACE | 0661 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. A concrete parking area and passenger loading area are necessary to comply with ADA requirements. This project would provide for a concrete van accessible ADA parking and loading space and walkway to the existing sidewalk. This will require regrading, installing P.C. concrete, striping, signage and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 07/07/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/12/2013. | NDOW AIRCRAFT HANGAR | 9900 | Wildlife |  |  | Minden | 1996 | 6400 | 2013-11-12 | Immediate to Two Years | Currently Critical | 1 | 2500
0661EXT1 | EXTERIOR FINISHES | 0661 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 07/07/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/12/2013. | NDOW AIRCRAFT HANGAR | 9900 | Wildlife |  |  | Minden | 1996 | 6400 | 2013-11-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6400
0661PLM1 | DOUBLE CHECK VALVE RELOCATION | 0661 | The existing double check valve serving the fire protection system is located in an underground vault. The valve is difficult to test and service. In addition, the test connections on the valve are corroding due to ground moisture. This project would raise the valve, install it in an above ground heated enclosure that will provide access for annual testing. Relocating the valve will require a new hydraulic analysis of the water supply. This project or a portion thereof was previously recommended in the FCA report dated 07/07/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/12/2013. | NDOW AIRCRAFT HANGAR | 9900 | Wildlife |  |  | Minden | 1996 | 6400 | 2013-11-12 | Immediate to Two Years | Currently Critical | 1 | 5000
0661ADA3 | ADA RESTROOM UPGRADE | 0661 | The designated unisex ADA accessible restroom is not fully compliant. There is no pipe protection and it is missing a grab bar. A partial retrofit is necessary. This project would provide funding to bring the restroom into full ADA compliance. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | NDOW AIRCRAFT HANGAR | 9900 | Wildlife |  |  | Minden | 1996 | 6400 | 2013-11-12 | Immediate to Two Years | Currently Critical | 1 | 1000
0661INT2 | INTERIOR FINISHES | 0661 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 07/07/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/12/2013. | NDOW AIRCRAFT HANGAR | 9900 | Wildlife |  |  | Minden | 1996 | 6400 | 2013-11-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
2213EXT1 | EXTERIOR/ INTERIOR FINISHES | 2213 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/29/2014. | CXT COMFORT STATION | 9965 | Wildlife |  |  | Overton | 2001 | 100 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
2221ADA1 | ADA SIGNAGE & STRIPING | 2221 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The concrete parking area and passenger loading area are missing proper signage and striping to comply with ADA requirements. This project would provide for striping, signage and any other necessary upgrades to the parking space. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/29/2014. | CXT ADA COMFORT STATION | 9965 | Wildlife |  |  | Overton | 2001 | 100 | 2014-01-29 | Immediate to Two Years | Currently Critical | 1 | 1000
2221EXT1 | EXTERIOR/ INTERIOR FINISHES | 2221 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. Additional costs are included for patching and repairing the damage caused by a recent impact. It is recommended that the building be repaired, sealed and caulked in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/29/2014. | CXT ADA COMFORT STATION | 9965 | Wildlife |  |  | Overton | 2001 | 100 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
9965EXT1 | EXTERIOR FINISHES, SHADE RAMADAS | 9965 | There are 7 steel shade ramadas throughout the site which are either 120 s.f., 240 s.f. or 576 s.f. for a total of 1,416 square feet. It is important to maintain the finish, weather resistance and appearance of the structures. This project would provide for painting of the structures and it is recommended that this project is scheduled on a cyclical basis to maintain the integrity of the structures. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/29/2014. | OVERTON WMA SITE | 9965 | Wildlife |  |  | Overton | 1967 |  | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2832
3030EXT3 | EXTERIOR DOOR REPLACEMENT | 3030 | The exterior metal doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the two door assemblies with new metal doors, frames and hardware. Removal and disposal of the existing doors is included in this estimate. | EMPLOYEE STORAGE - FIELD SHOP | 9965 | Wildlife |  |  | Overton | 0 | 1440 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
3030INT1 | INTERIOR FINISHES | 3030 | The interior finishes are in fair condition. It is recommended to paint the interior walls at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/29/2014. | EMPLOYEE STORAGE - FIELD SHOP | 9965 | Wildlife |  |  | Overton | 0 | 1440 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7200
3030EXT1 | EXTERIOR FINISHES | 3030 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units, staining the wood siding and trim and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/29/2014. | EMPLOYEE STORAGE - FIELD SHOP | 9965 | Wildlife |  |  | Overton | 0 | 1440 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7200
9965SIT3 | CARPORT STRUCTURE INSTALLATION | 9965 | There is a need for a carport structure in the maintenance area. The trucks and agricultural equipment are exposed to the sun causing preventable damage and maintenance costs. This project would provide a steel carport 24' x 100' to be constructed on the east side of the yard. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/29/2014. | OVERTON WMA SITE | 9965 | Wildlife |  |  | Overton | 1967 |  | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 60000
3030EXT2 | ROOF REPLACEMENT | 3030 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. Several shingles had blown off and many others were partially detached and failing. It is recommended that this building be re-roofed in the next 1-2 years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. | EMPLOYEE STORAGE - FIELD SHOP | 9965 | Wildlife |  |  | Overton | 0 | 1440 | 2014-01-29 | Immediate to Two Years | Currently Critical | 1 | 17280
9965SIT5 | FENCE REPLACEMENT | 9965 | The majority of the fencing around the maintenance yard has failed and is due for replacement. This project recommends the installation of a 6 foot high 6 gauge wire perimeter chain link fence around the entire site with two 14' wide gates with hardware. The cost estimate also includes demolition and disposal of the existing fence. | OVERTON WMA SITE | 9965 | Wildlife |  |  | Overton | 1967 |  | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 42000
9965SIT6 | CXT RESTROOM INSTALLATION | 9965 | The restroom building on the site has been demolished leaving no restroom facilities for the maintenance staff. This project would provide for the purchase and installation of an ADA compliant precast CXT or similar unisex comfort station to be located adjacent to the Maintenance Shop. | OVERTON WMA SITE | 9965 | Wildlife |  |  | Overton | 1967 |  | 2014-01-29 | Immediate to Two Years | Currently Critical | 1 | 20000
9965SIT7 | TREE TRIMMING | 9965 | There are many large cottonwood trees on the site that have not been trimmed recently. They have grown to the extent that they are a safety hazard due to dead branches falling or the entire tree falling in areas where visitors frequent. This project would trim, prune or remove the trees to ensure the safety of visitors and maintain the health of the trees. | OVERTON WMA SITE | 9965 | Wildlife |  |  | Overton | 1967 |  | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
9965SIT4 | DIVERSION DAM REPAIRS | 9965 | There is a diversion dam on the north side of the site that was built in the 1940's and is due for major repairs or replacement. There is no catwalk above the dam to do repairs and maintenance from and several of the mechanical parts are worn and broken. One of the locks is not functioning correctly and is currently held in place with a block of wood. The gates are worn and the concrete is deteriorating. This project would provide for refurbishing the entire dam structure to ensure that the wildlife management area has the hydraulic controls that are necessary. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/29/2014. | OVERTON WMA SITE | 9965 | Wildlife |  |  | Overton | 1967 |  | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 150000
0639PLM1 | WATER HEATER REPLACEMENT | 0639 | There is a 50 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | WMA SUPERVISOR'S RESIDENCE | 9965 | Wildlife |  |  | Overton | 1966 | 1600 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0660ELE1 | ELECTRICAL UPGRADE | 0660 | This building was constructed before the high demand for electrical services were needed for computers and vehicle repair equipment. As time has progressed, the buildings electrical demand and system has changed. It is utilized to its current maximum potential. The electrical panels and receptacles are at their limit. It is recommended the entire system be upgraded to meet the evolving needs of the building. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/29/2014. | WMA MAINTENANCE SHOP | 9965 | Wildlife |  |  | Overton | 1988 | 2400 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 28800
0641EXT2 | DEMOLISH STRUCTURE | 0641 | The structure is over 70 years of age and is a safety hazard. The structural system has failed and the building should no longer be in use in any way. The main structural posts have detached from their footings, bolts are missing from the structural attachments, and the roof system has failed. This project would provide funding for the demolition and disposal of the building. | EQUIPMENT STORAGE | 9965 | Wildlife |  |  | Overton | 1940 | 2600 | 2014-01-29 | Immediate to Two Years | Currently Critical | 1 | 26000
0640EXT3 | WINDOW REPLACEMENT | 0640 | The windows are original, single pane construction in a wooden frame. These older windows are drafty, not energy efficient and the wooden frames have deteriorated significantly. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 3 units including wooden frames. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/29/2014. | EMPLOYEE STORAGE | 9965 | Wildlife |  |  | Overton | 1940 | 375 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2100
0660ENR1 | WINDOW REPLACEMENT | 0660 | The windows are original, dual pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 4 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/29/2014. | WMA MAINTENANCE SHOP | 9965 | Wildlife |  |  | Overton | 1988 | 2400 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0640EXT2 | EXTERIOR DOOR REPLACEMENT | 0640 | The existing exterior wood door appears to be original to the building. It is damaged from age and general wear and tear. This project would provide for the replacement of the wood door with a new metal door, frame and hardware. Removal and disposal of the existing door and painting of the new door is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/29/2014. | EMPLOYEE STORAGE | 9965 | Wildlife |  |  | Overton | 1940 | 375 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
0640EXT4 | ROOF REPLACEMENT | 0640 | The corrugated metal roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a standing seam metal roofing system. This estimate includes removal and disposal of the old roofing. | EMPLOYEE STORAGE | 9965 | Wildlife |  |  | Overton | 1940 | 375 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
0639EXT4 | EXTERIOR FINISHES | 0639 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | WMA SUPERVISOR'S RESIDENCE | 9965 | Wildlife |  |  | Overton | 1966 | 1600 | 2014-01-29 | Four to Ten Years | Long-Term Needs | 3 | 8000
0915INT1 | INTERIOR FINISHES | 0915 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/29/2014. | OIL STORAGE SHED | 9965 | Wildlife |  |  | Overton | 2000 | 100 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
0915ENR1 | LIGHTING UPGRADE | 0915 | The existing sodium halide pole light on the exterior of the building is broken and is not energy efficient. This project will upgrade the fixture to a more energy efficient high-pressure sodium or LED lamp. These types of lights will provide better illumination and save energy. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/29/2014. | OIL STORAGE SHED | 9965 | Wildlife |  |  | Overton | 2000 | 100 | 2014-01-29 | Immediate to Two Years | Currently Critical | 1 | 2500
0915EXT1 | EXTERIOR FINISHES | 0915 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the door and metal trim and caulking and sealing the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and sealed in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/29/2014. | OIL STORAGE SHED | 9965 | Wildlife |  |  | Overton | 2000 | 100 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
0916EXT1 | EXTERIOR FINISHES | 0916 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/29/2014. | GRANARY | 9965 | Wildlife |  |  | Overton | 1940 | 314 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 942
0918EXT3 | EXTERIOR FINISHES | 0918 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | CHECK STATION (FEE BOOTH) | 9965 | Wildlife |  |  | Overton | 2000 | 120 | 2014-01-29 | Four to Ten Years | Long-Term Needs | 3 | 600
0918ADA1 | ADA PARKING SPACE | 0918 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. A concrete parking area and passenger loading area are necessary to comply with ADA requirements. This project would provide for a concrete van accessible ADA parking and loading space and walkway to the existing sidewalk. This will require regrading, installing P.C. concrete, striping, signage and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/29/2014. | CHECK STATION (FEE BOOTH) | 9965 | Wildlife |  |  | Overton | 2000 | 120 | 2014-01-29 | Immediate to Two Years | Currently Critical | 1 | 2500
0918INT1 | INTERIOR FINISHES | 0918 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/29/2014. | CHECK STATION (FEE BOOTH) | 9965 | Wildlife |  |  | Overton | 2000 | 120 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 600
0640EXT1 | EXTERIOR FINISHES | 0640 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/29/2014. | EMPLOYEE STORAGE | 9965 | Wildlife |  |  | Overton | 1940 | 375 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1875
0639INT4 | INTERIOR FINISHES | 0639 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 4-5 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | WMA SUPERVISOR'S RESIDENCE | 9965 | Wildlife |  |  | Overton | 1966 | 1600 | 2014-01-29 | Four to Ten Years | Long-Term Needs | 3 | 8000
0660EXT3 | OVERHEAD DOOR REPLACEMENT | 0660 | There are two 10'x14' and one 10'x12' overhead doors which are damaged and do not function properly. Exposure and wind have caused the doors to bend, crack and lose their finish. They are original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead coiling doors and replacement with new manually operated overhead coiling doors. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/29/2014. | WMA MAINTENANCE SHOP | 9965 | Wildlife |  |  | Overton | 1988 | 2400 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0660ENR2 | HVAC EQUIPMENT REPLACEMENT | 0660 | The HVAC system was installed in 1988 and is original to the building. It consists of two propane-fired furnaces and four wall mounted evaporative coolers. The system is not energy efficient and has reached the end of its expected and useful life. This project would provide for installation of a new HVAC system and cleaning of the existing duct work and grilles. The new system shall be designed to significantly reduce electrical and natural gas usage in order to comply with the 2009 IECC and ASHRAE 90.1 and to reduce utility costs. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/29/2014. | WMA MAINTENANCE SHOP | 9965 | Wildlife |  |  | Overton | 1988 | 2400 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 36000
0660EXT1 | EXTERIOR FINISHES | 0660 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/29/2014. | WMA MAINTENANCE SHOP | 9965 | Wildlife |  |  | Overton | 1988 | 2400 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4800
2336EXT1 | HISTORIC BUILDING MAINTENANCE | 2336 | The wood structure is over 75 years old and there are numerous areas where the wood is splitting, warping and deteriorating. This project would provide for sealing the wood and repairing the roof as needed. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements, which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | LOG RANCH BUILDING #1 | 9953 | Wildlife |  |  | Kirch WMA | 1920 | 460 | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6900
2331ADA2 | ADA ACCESSIBLE PATH OF TRAVEL | 2331 | The ADA provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the restroom are necessary to comply with ADA accessibility requirements. This project would provide for a concrete van accessible ADA parking and loading space and concrete walkway to the existing sidewalk. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. 750 square feet of concrete was used for this estimate. | BLM RESTROOM #2 | 9953 | Wildlife |  |  | Kirch WMA | 2000 | 70 | 2016-06-08 | Immediate to Two Years | Currently Critical | 1 | 30000
2331ADA1 | ADA SIGNAGE | 2331 | ADA regulations pertaining to building access, route of travel and restrooms has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms and sign contrast and finish. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | BLM RESTROOM #2 | 9953 | Wildlife |  |  | Kirch WMA | 2000 | 70 | 2016-06-08 | Immediate to Two Years | Currently Critical | 1 | 450
2331EXT1 | EXTERIOR/ INTERIOR FINISHES | 2331 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | BLM RESTROOM #2 | 9953 | Wildlife |  |  | Kirch WMA | 2000 | 70 | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
2332EXT1 | EXTERIOR/ INTERIOR FINISHES | 2332 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | BLM RESTROOM #3 | 9953 | Wildlife |  |  | Kirch WMA | 2000 | 70 | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
2332ADA2 | ADA ACCESSIBLE PATH OF TRAVEL | 2332 | The ADA provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the restroom are necessary to comply with ADA accessibility requirements. This project would provide for a concrete van accessible ADA parking and loading space and concrete walkway to the existing sidewalk. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. 750 square feet of concrete was used for this estimate. | BLM RESTROOM #3 | 9953 | Wildlife |  |  | Kirch WMA | 2000 | 70 | 2016-06-08 | Immediate to Two Years | Currently Critical | 1 | 30000
2332ADA1 | ADA SIGNAGE | 2332 | ADA regulations pertaining to building access, route of travel and restrooms has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | BLM RESTROOM #3 | 9953 | Wildlife |  |  | Kirch WMA | 2000 | 70 | 2016-06-08 | Immediate to Two Years | Currently Critical | 1 | 450
2333EXT1 | EXTERIOR FINISHES | 2333 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | RAMADA #1 | 9953 | Wildlife |  |  | Kirch WMA | 2000 | 140 | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 560
2330ADA1 | ADA SIGNAGE | 2330 | ADA regulations pertaining to building access, route of travel and restrooms has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | BLM RESTROOM #1 | 9953 | Wildlife |  |  | Kirch WMA | 2000 | 70 | 2016-06-08 | Immediate to Two Years | Currently Critical | 1 | 450
2335EXT1 | EXTERIOR FINISHES | 2335 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | RAMADA #3 | 9953 | Wildlife |  |  | Kirch WMA | 2000 | 140 | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 560
2328EXT1 | EXTERIOR/ INTERIOR FINISHES | 2328 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | CXT RESTROOM #4 - CAMPGROUND | 9953 | Wildlife |  |  | Kirch WMA | 2000 | 120 | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2400
2337EXT1 | HISTORIC BUILDING MAINTENANCE | 2337 | The wood structure is over 75 years old and there are numerous areas where the wood is splitting, warping and deteriorating. This project would provide for sealing the wood and repairing the roof as needed. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements, which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | LOG RANCH BUILDING #2 | 9953 | Wildlife |  |  | Kirch WMA | 1920 | 700 | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
2334EXT1 | EXTERIOR FINISHES | 2334 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | RAMADA #2 | 9953 | Wildlife |  |  | Kirch WMA | 2000 | 140 | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 560
2330EXT1 | EXTERIOR/ INTERIOR FINISHES | 2330 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | BLM RESTROOM #1 | 9953 | Wildlife |  |  | Kirch WMA | 2000 | 70 | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
2330ADA2 | ADA ACCESSIBLE PATH OF TRAVEL | 2330 | The ADA provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the restroom are necessary to comply with ADA accessibility requirements. This project would provide for a concrete van accessible ADA parking and loading space and concrete walkway to the existing sidewalk. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. 750 square feet of concrete was used for this estimate. | BLM RESTROOM #1 | 9953 | Wildlife |  |  | Kirch WMA | 2000 | 70 | 2016-06-08 | Immediate to Two Years | Currently Critical | 1 | 30000
2329ADA1 | ADA SIGNAGE | 2329 | ADA regulations pertaining to building access, route of travel and restrooms has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | CXT RESTROOM #5 | 9953 | Wildlife |  |  | Kirch WMA | 2000 | 120 | 2016-06-08 | Immediate to Two Years | Currently Critical | 1 | 450
2329ADA2 | ADA ACCESSIBLE PATH OF TRAVEL | 2329 | The ADA provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the restroom are necessary to comply with ADA accessibility requirements. This project would provide for a concrete van accessible ADA parking and loading space and concrete walkway to the existing sidewalk. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. 750 square feet of concrete was used for this estimate. | CXT RESTROOM #5 | 9953 | Wildlife |  |  | Kirch WMA | 2000 | 120 | 2016-06-08 | Immediate to Two Years | Currently Critical | 1 | 30000
2326ADA2 | ADA ACCESSIBLE PATH OF TRAVEL | 2326 | The ADA provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the restroom are necessary to comply with ADA accessibility requirements. This project would provide for a concrete van accessible ADA parking and loading space and concrete walkway to the existing sidewalk. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. 750 square feet of concrete was used for this estimate. | CXT RESTROOM #2 - CAMPGROUND | 9953 | Wildlife |  |  | Kirch WMA | 2000 | 120 | 2016-06-08 | Immediate to Two Years | Currently Critical | 1 | 30000
2328ADA1 | ADA SIGNAGE | 2328 | ADA regulations pertaining to building access, route of travel and restrooms has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | CXT RESTROOM #4 - CAMPGROUND | 9953 | Wildlife |  |  | Kirch WMA | 2000 | 120 | 2016-06-08 | Immediate to Two Years | Currently Critical | 1 | 450
2328ADA2 | ADA ACCESSIBLE PATH OF TRAVEL | 2328 | The ADA provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the restroom are necessary to comply with ADA accessibility requirements. This project would provide for a concrete van accessible ADA parking and loading space and concrete walkway to the existing sidewalk. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. 750 square feet of concrete was used for this estimate. | CXT RESTROOM #4 - CAMPGROUND | 9953 | Wildlife |  |  | Kirch WMA | 2000 | 120 | 2016-06-08 | Immediate to Two Years | Currently Critical | 1 | 30000
2327ADA2 | ADA ACCESSIBLE PATH OF TRAVEL | 2327 | The ADA provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the restroom are necessary to comply with ADA accessibility requirements. This project would provide for a concrete van accessible ADA parking and loading space and concrete walkway to the existing sidewalk. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. 750 square feet of concrete was used for this estimate. | CXT RESTROOM #3 - CAMPGROUND | 9953 | Wildlife |  |  | Kirch WMA | 2000 | 120 | 2016-06-08 | Immediate to Two Years | Currently Critical | 1 | 30000
2327ADA1 | ADA SIGNAGE | 2327 | ADA regulations pertaining to building access, route of travel and restrooms has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms and sign contrast and finish. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | CXT RESTROOM #3 - CAMPGROUND | 9953 | Wildlife |  |  | Kirch WMA | 2000 | 120 | 2016-06-08 | Immediate to Two Years | Currently Critical | 1 | 450
2327EXT1 | EXTERIOR/ INTERIOR FINISHES | 2327 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | CXT RESTROOM #3 - CAMPGROUND | 9953 | Wildlife |  |  | Kirch WMA | 2000 | 120 | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2400
2326ADA1 | ADA SIGNAGE | 2326 | ADA regulations pertaining to building access, route of travel and restrooms has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms and sign contrast and finish. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | CXT RESTROOM #2 - CAMPGROUND | 9953 | Wildlife |  |  | Kirch WMA | 2000 | 120 | 2016-06-08 | Immediate to Two Years | Currently Critical | 1 | 450
2326EXT1 | EXTERIOR/ INTERIOR FINISHES | 2326 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | CXT RESTROOM #2 - CAMPGROUND | 9953 | Wildlife |  |  | Kirch WMA | 2000 | 120 | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2400
2325ADA1 | ADA SIGNAGE | 2325 | ADA regulations pertaining to building access, route of travel and restrooms has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | CXT RESTROOM #1 - CAMPGROUND | 9953 | Wildlife |  |  | Kirch WMA | 2000 | 120 | 2016-06-08 | Immediate to Two Years | Currently Critical | 1 | 450
2329EXT1 | EXTERIOR/ INTERIOR FINISHES | 2329 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | CXT RESTROOM #5 | 9953 | Wildlife |  |  | Kirch WMA | 2000 | 120 | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2400
2325EXT1 | EXTERIOR/ INTERIOR FINISHES | 2325 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | CXT RESTROOM #1 - CAMPGROUND | 9953 | Wildlife |  |  | Kirch WMA | 2000 | 120 | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2400
9953SIT2 | ACCESS BRIDGE REPLACEMENT | 9953 | The Tule access bridge crosses a ditch at the site, providing access to the opposite side of the site for recreation. The structure is older, in poor condition, and could become a safety issue. This project recommends the installation of a concrete box culvert and walkway to replace the bridge. The new installation will last longer and be less susceptible to damage by water flows. This project or a portion thereof was previously recommended in the FCA report dated 05/24/2002 and 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | KIRCH WMA SITE | 9953 | Wildlife |  |  | Kirch WMA |  |  | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
3677EXT1 | EXTERIOR FINISHES | 3677 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | RESIDENCE #2 | 9953 | Wildlife |  |  | Kirch WMA | 2013 | 1650 | 2016-06-08 | Four to Ten Years | Long-Term Needs | 3 | 16500
9953SIT6 | FENCE REPLACEMENT | 9953 | This site is home to some endangered species. The habitat is tightly managed to protect them. Feral horses and stray cattle must be kept out. The perimeter fencing for the wildlife management area is a juniper pole fence, which is aging. The fence posts are losing their integrity and failing. This project recommends replacing the fence with steel posts and wildlife stranded wire. The estimate is based on approximately 50 miles of fencing. This project or a portion thereof was previously recommended in the FCA report dated 05/24/2002 and 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | KIRCH WMA SITE | 9953 | Wildlife |  |  | Kirch WMA |  |  | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 300000
3677ENV1 | PEST CONTROL | 3677 | There are numerous rodent droppings in the crawl space throughout this building. Due to the potential risk of disease, this project provides for treatment and clean up of the rodent droppings by a licensed pest control business. | RESIDENCE #2 | 9953 | Wildlife |  |  | Kirch WMA | 2013 | 1650 | 2016-06-08 | Immediate to Two Years | Currently Critical | 1 | 1000
9953SIT5 | IRRIGATION SYSTEM REPLACEMENT | 9953 | The campground is served by a well, which provides water for campers and the irrigation. A drip irrigation system was installed at the campground to provide water for trees and shrubs, but problems with water quality and other issues adversely affected the effectiveness of the system. This project recommends removing the existing system and replacing it with a new drip irrigation system including backflow prevention, filters, and self-cleaning bubblers and valves. Following installation, trees and shrubs should be reintroduced to the campground area. This project or a portion thereof was previously recommended in the FCA report dated 05/24/2002 and 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | KIRCH WMA SITE | 9953 | Wildlife |  |  | Kirch WMA |  |  | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
9953SFT1 | EXTERIOR STAIR HANDRAIL INSTALLATION | 9953 | There is a set of stairs on the west side of the office which are lacking handrails. This project would provide for the installation of a 1-1/2 inch tube steel handrail to be installed on each side of the stairs. Chapter 10 of the 2012 IBC was used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | KIRCH WMA SITE | 9953 | Wildlife |  |  | Kirch WMA |  |  | 2016-06-08 | Immediate to Two Years | Currently Critical | 1 | 5000
9953ADA1 | BOAT DOCK AND RAMP REPLACEMENT | 9953 | The boat docks and concrete ramps are approaching the end of their expected life and should be scheduled for replacement due to extreme climatic conditions and use. The concrete ramps are cracking and spalling. It is important for the concrete to be in good shape to insure proper traction for tow vehicles and to prevent accidents. This project would provide for the purchase and installation of 3 new ADA compliant boat docks and concrete ramps. Removal and disposal of the existing concrete ramps and docks are included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | KIRCH WMA SITE | 9953 | Wildlife |  |  | Kirch WMA |  |  | 2016-06-08 | Immediate to Two Years | Currently Critical | 1 | 450000
3677SIT1 | REMOVE SPRINKLERED LAWN WITHIN 3' OF BUILDING | 3677 | The house has considerable damage to the siding from lawn sprinklers wetting the siding. This project would create drip irrigated planters within three feet of the house and relocate sprinklers so they do not wet the house. | RESIDENCE #2 | 9953 | Wildlife |  |  | Kirch WMA | 2013 | 1650 | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6600
9953SIT8 | HAZARDOUS COMMUNICATION PROGRAM | 9953 | Due to the storage of hazardous materials, this site shall comply with IFC 2012 Chapter 4 Emergency Planning and Preparedness, and have a written Hazardous Materials Management Plan, including but not limited to, Section 5003 Safety Data Sheets, Section 406 Employee Training and Response Procedures and Section 407 Hazard Communication. Chapter 50 Section 5001 will provide additional assistance in devising and implementing a hazardous communication program. | KIRCH WMA SITE | 9953 | Wildlife |  |  | Kirch WMA |  |  | 2016-06-08 | Immediate to Two Years | Currently Critical | 1 | 2000
3677INT1 | INTERIOR FINISHES | 3677 | It is recommended to paint the interior walls and ceilings at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | RESIDENCE #2 | 9953 | Wildlife |  |  | Kirch WMA | 2013 | 1650 | 2016-06-08 | Four to Ten Years | Long-Term Needs | 3 | 16500
0945EXT3 | ROOF REPLACEMENT | 0945 | The corrugated metal roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a standing seam metal roofing system. This estimate includes removal and disposal of the old roofing. | EQUIPMENT SHED | 9953 | Wildlife |  |  | Kirch WMA | 1960 | 1200 | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14400
0944EXT1 | HISTORIC BUILDING MAINTENANCE | 0944 | The wood structure is over 87 years old and there are numerous areas where the wood is splitting, warping and deteriorating. This is also an exhibit for the park and requires maintenance. This project would provide for sealing the wood and repairing the roof as needed. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements, which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SLAUGHTER HOUSE | 9953 | Wildlife |  |  | Kirch WMA | 1930 | 700 | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10500
0945ENV1 | SPILL CONTAINMENT | 0945 | The Equipment Shed does not have a method for containing spills or leakage from drums. This project would add secondary containment pallets for all containers in the building and install placards on the building exterior. | EQUIPMENT SHED | 9953 | Wildlife |  |  | Kirch WMA | 1960 | 1200 | 2016-06-08 | Immediate to Two Years | Currently Critical | 1 | 6500
0942EXT1 | EXTERIOR FINISHES | 0942 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | SEED SILO | 9953 | Wildlife |  |  | Kirch WMA | 1960 | 200 | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1120
0945EXT1 | EXTERIOR FINISHES | 0945 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | EQUIPMENT SHED | 9953 | Wildlife |  |  | Kirch WMA | 1960 | 1200 | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2400
0644INT2 | INTERIOR FINISHES | 0644 | It is recommended to paint the interior walls and ceilings at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and adequately prepared to receive the coating. An epoxy-based paint should be utilized in wet areas for durability. | KIRCH WMA PUMP HOUSE | 9953 | Wildlife |  |  | Kirch WMA | 1992 | 100 | 2016-06-08 | Four to Ten Years | Long-Term Needs | 3 | 1000
0943SFT1 | SAFETY CABINETS | 0943 | The building contains many different herbicides, pesticides and other hazardous products located on open shelves and on the floor. This does not meet OSHA standards or IFC for hazardous materials containment. This project would provide for two self-closing hazardous storage containers in the building and install placards on the building’s exterior in accordance with OSHA 1910.106 (d) and IFC Chapter 57 Section 5704.3.2.1.3. | CHEMICAL STORAGE SHED | 9953 | Wildlife |  |  | Kirch WMA | 1960 | 240 | 2016-06-08 | Immediate to Two Years | Currently Critical | 1 | 10000
0644ELE2 | LIGHTING UPGRADE | 0644 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | KIRCH WMA PUMP HOUSE | 9953 | Wildlife |  |  | Kirch WMA | 1992 | 100 | 2016-06-08 | Four to Ten Years | Long-Term Needs | 3 | 800
0644ELE3 | GFCI OUTLETS | 0644 | The existing receptacles in the Kirch WMA Pump House and outside are standard duplex receptacles. The 2011 (NEC) National Electrical Code 210.8 requires these locations to have Ground Fault Circuit Interrupter (GFCI) protection. This project would provide for removing the standard receptacles and installing GFCI receptacles. | KIRCH WMA PUMP HOUSE | 9953 | Wildlife |  |  | Kirch WMA | 1992 | 100 | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 800
0645ENV1 | HAZARDOUS MATERIALS STORAGE | 0645 | The Oil Storage Building contains hazardous materials (i.e. gas, batteries, herbicides and pesticides). Per IFC 2012 Hazardous Materials, and in accordance with NFPA; where hazardous materials are stored, dispensed or used, Section 5003 states the proper use and application is to have mechanical exhaust and ventilation, and hazard identification signs shall be installed. Refer to Section 5004 and 5005 for the proper use and setup. It is important to comply with all applicable codes. This project would provide for all requirements in IFC 2012, to include Section 105 permits and inspections through the State Fire Marshal’s Office and the State Public Works Division. | OIL STORAGE BUILDING | 9953 | Wildlife |  |  | Kirch WMA | 1960 | 150 | 2016-06-08 | Immediate to Two Years | Currently Critical | 1 | 30000
0645SFT1 | EXPLOSION PROOF INTERIOR LED LIGHTING | 0645 | The existing lighting fixtures are the incandescent type, and are not energy efficient or explosion proof. This project will upgrade fixtures to higher efficiency units with longer life cycles and will be explosion proof. 4' LEDs in class 1 explosion proof fixtures are suggested. Occupancy sensors will be installed for additional savings. Electrical wiring upgrades have not been included in this estimate. | OIL STORAGE BUILDING | 9953 | Wildlife |  |  | Kirch WMA | 1960 | 150 | 2016-06-08 | Immediate to Two Years | Currently Critical | 1 | 2000
0645ENV2 | PROVIDE HAZARDOUS MATERIALS CONTAINMENT | 0645 | At the time of the survey, there were oil drums stored in the Oil Storage Building as well as propane tanks, gas cans and aerosol cans stored in the same area. This does not meet OSHA standards for proper storage containment. The oil drums should be stored on OSHA approved drum spill pallets in order to protect the environment from spills or leaks. The project will provide for two OSHA approved drum spill pallets capable of storing two drums each and purchasing an OSHA approved storage cabinet for miscellaneous items such as the gas cans. According to OSHA 1910.106 (d), a proper storage container shall be provided for flammable or combustible liquids in drums or other containers (including flammable aerosols) not exceeding 60 gallons individual capacity and those portable tanks not exceeding 660 gallons individual capacity. | OIL STORAGE BUILDING | 9953 | Wildlife |  |  | Kirch WMA | 1960 | 150 | 2016-06-08 | Immediate to Two Years | Currently Critical | 1 | 15000
0645SFT2 | BATTERY STORAGE | 0645 | Section 608 of the 2012 IFC explains the requirements for stationary storage of battery systems. This project will provide funding for the proper way to store, charge and/or use batteries indoors. IFC Section 608 states batteries shall have safety caps, spill control and neutralization, mechanical ventilation and/or cabinet ventilation, supervision over the mechanical ventilation, building or cabinet signage, seismically braced, and a smoke alarm. This project would provide funding for the requirement of Section 608 of the 2012 IFC. | OIL STORAGE BUILDING | 9953 | Wildlife |  |  | Kirch WMA | 1960 | 150 | 2016-06-08 | Immediate to Two Years | Currently Critical | 1 | 25000
0943ENV1 | HAZARDOUS MATERIALS STORAGE UPGRADE | 0943 | The Chemical Storage Shed contains hazardous materials (i.e. herbicides and pesticides). Per IFC 2012 Hazardous Materials, and in accordance with NFPA; where hazardous materials are stored, dispensed or used, Section 5003 states the proper use and application is to have mechanical exhaust and ventilation, and hazard identification signs shall be installed. Refer to Section 5004 and 5005 for the proper use and setup. It is important to comply with all applicable codes. This project would provide for all requirements in IFC 2012, to include Section 105 permits and inspections through the State Fire Marshal’s Office and the State Public Works Division. | CHEMICAL STORAGE SHED | 9953 | Wildlife |  |  | Kirch WMA | 1960 | 240 | 2016-06-08 | Immediate to Two Years | Currently Critical | 1 | 30000
0643EXT2 | ROOF REPLACEMENT | 0643 | The standing seam metal roof on this building was in poor condition at the time of the survey and had active leaks. It is recommended that this building be re-roofed in the next 1-2 years with a new single-ply roofing system which will be installed directly over the existing metal roof. This will allow the roof to qualify for the statewide roofing program warranty and preventative maintenance agreement. | SHOP/ BUNKHOUSE/ OFFICE | 9953 | Wildlife |  |  | Kirch WMA | 1969 | 1250 | 2016-06-08 | Immediate to Two Years | Currently Critical | 1 | 15000
0644ELE1 | WIRING CLEANUP | 0644 | The wiring in the Kirch WMA Pump House is disorganized and not in proper electrical boxes. This creates a safety issue during repairs or upgrades. This project would provide for organization, proper labeling and for the wiring to be placed in electrical boxes per NEC 2011. | KIRCH WMA PUMP HOUSE | 9953 | Wildlife |  |  | Kirch WMA | 1992 | 100 | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
0643ELE1 | GFCI DUPLEX OUTLET REPLACEMENT | 0643 | There are several outlets in the restroom, kitchen and garage that are not GFCI protected. These outlets should be changed to GFCI type outlets per the NEC. This project would provide for the purchase and installation of GFCI duplex outlets. | SHOP/ BUNKHOUSE/ OFFICE | 9953 | Wildlife |  |  | Kirch WMA | 1969 | 1250 | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
0643ELE2 | ELECTRICAL AND COMMUNICATIONS UPGRADE | 0643 | This building was constructed before the high demand for electrical services were needed for computers, communications systems and other electrical devices. As time has progressed, the buildings electrical demand and communications system has changed. The electrical system is utilized to its current maximum potential and the communications system is outdated. The electrical panels, switches and receptacles are at their limit. It is recommended to upgrade the entire electrical system and communications system to meet the evolving needs of the building. | SHOP/ BUNKHOUSE/ OFFICE | 9953 | Wildlife |  |  | Kirch WMA | 1969 | 1250 | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 31250
0643SFT4 | SITE BOLLARDS | 0643 | The building has a propane tank that provides fuel for the heaters. The propane tank does not have adequate bollard coverage. Per IFC 2012 Section 312 Vehicle Impact Protection, there needs to be steel posts installed, not less than 4 inches in diameter and filled with concrete. The spacing shall not be more than 4 feet between posts on center and located not less than 3 feet from each gas tank. This project would provide funding for eight new bollards to be located around the other bollards. | SHOP/ BUNKHOUSE/ OFFICE | 9953 | Wildlife |  |  | Kirch WMA | 1969 | 1250 | 2016-06-08 | Immediate to Two Years | Currently Critical | 1 | 8000
0643INT4 | KITCHEN REMODEL | 0643 | The kitchen is in fair to poor condition. The cabinets and equipment are showing signs of general wear and tear and have approached the end of their expected life. This project recommends the replacement of the existing kitchen cabinets, counters, fixtures and equipment with mid range, high quality components. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | SHOP/ BUNKHOUSE/ OFFICE | 9953 | Wildlife |  |  | Kirch WMA | 1969 | 1250 | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0643PLM1 | WATER HEATER REPLACEMENT | 0643 | There is a 50 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | SHOP/ BUNKHOUSE/ OFFICE | 9953 | Wildlife |  |  | Kirch WMA | 1969 | 1250 | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
0643EXT1 | EXTERIOR FINISHES | 0643 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations and removing the dirt and rocks around the perimeter of the building. The dirt and rocks are reacting with the metal panels and causing premature deterioration of the metal. It is recommended that the work is done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | SHOP/ BUNKHOUSE/ OFFICE | 9953 | Wildlife |  |  | Kirch WMA | 1969 | 1250 | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12500
0644EXT2 | ROOF REPLACEMENT | 0644 | The asphalt roll roofing was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 4-5 years with a new single-ply roofing system. This will allow the roof to qualify for the statewide roofing warranty and preventative maintenance agreement programs. | KIRCH WMA PUMP HOUSE | 9953 | Wildlife |  |  | Kirch WMA | 1992 | 100 | 2016-06-08 | Four to Ten Years | Long-Term Needs | 3 | 1200
0643INT2 | VCT FLOORING REPLACEMENT | 0643 | The VCT flooring in the Bunkhouse is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. 250 square feet of floor area was used to generate this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | SHOP/ BUNKHOUSE/ OFFICE | 9953 | Wildlife |  |  | Kirch WMA | 1969 | 1250 | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2250
0945EXT2 | EXTERIOR SIDING REPLACEMENT | 0945 | The corrugated metal panels covering the building are original and should be scheduled for replacement. Many of the panels are damaged from general wear and tear. This project would provide for the removal and the disposal of the existing panels and the replacement with new pre-painted metal panels. | EQUIPMENT SHED | 9953 | Wildlife |  |  | Kirch WMA | 1960 | 1200 | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5100
0643SFT2 | EXIT SIGN AND EGRESS LIGHTING INSTALLATION | 0643 | The building does not have emergency lighting and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | SHOP/ BUNKHOUSE/ OFFICE | 9953 | Wildlife |  |  | Kirch WMA | 1969 | 1250 | 2016-06-08 | Immediate to Two Years | Currently Critical | 1 | 1250
0642INT2 | INTERIOR REMODEL AND FIRE SUPPRESSION | 0642 | The interior fixtures and finishes are in general disrepair and the building is due for a complete remodel. This project would provide for the removal and replacement of the flooring, doors and frames, cabinetry, trim and baseboards and any other interior finishes and fixtures in need of replacement. When a remodel is conducted per 2012 IBC, NAC 477.915 (2) states, R occupancy, be scheduled for installation of an automatic fire suppression system during the next remodeling of or addition to the building. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. | KIRCH WMA RESIDENCE | 9953 | Wildlife |  |  | Kirch WMA | 1964 | 1900 | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 123500
0642EXT5 | EXTERIOR FINISHES | 0642 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | KIRCH WMA RESIDENCE | 9953 | Wildlife |  |  | Kirch WMA | 1964 | 1900 | 2016-06-08 | Four to Ten Years | Long-Term Needs | 3 | 19000
0642INT1 | INTERIOR FINISHES | 0642 | It is recommended that the interior walls and ceilings be painted at least once in the next three to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | KIRCH WMA RESIDENCE | 9953 | Wildlife |  |  | Kirch WMA | 1964 | 1900 | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19000
0943SFT2 | EXPLOSION PROOF INTERIOR LED LIGHTING | 0943 | The existing lighting fixtures are the incandescent type, and are not energy efficient or explosion proof. This project will upgrade fixtures to higher efficiency units with longer life cycles and will be explosion proof. 4' LEDs in class 1 explosion proof fixtures are suggested. Occupancy sensors will be installed for additional savings. Electrical wiring upgrades have not been included in this estimate. | CHEMICAL STORAGE SHED | 9953 | Wildlife |  |  | Kirch WMA | 1960 | 240 | 2016-06-08 | Immediate to Two Years | Currently Critical | 1 | 2000
0644SFT1 | PROVIDE CLEARANCE AT ELECTRICAL PANELS | 0644 | There is an electrical panel in the building which does not have the proper floor clearance. The 2012 IFC Section 605.3 states, a working space of not less than 30 inches in width, 36 inches in depth and 78 inches in height shall be provided in front of electrical service equipment. Where the electrical service equipment is wider than 30 inches, the working space shall not be less than the width of the equipment. No storage of any materials shall be located within the designated working space. This project would provide funds to relocate the shelf and other items currently blocking the working space. | KIRCH WMA PUMP HOUSE | 9953 | Wildlife |  |  | Kirch WMA | 1992 | 100 | 2016-06-08 | Immediate to Two Years | Currently Critical | 1 | 2000
0645EXT1 | EXTERIOR FINISHES | 0645 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations and removing the dirt and rocks around the perimeter of the building. The dirt and rocks are reacting with the metal panels and causing premature deterioration of the metal. It is recommended that the work is done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | OIL STORAGE BUILDING | 9953 | Wildlife |  |  | Kirch WMA | 1960 | 150 | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0643INT1 | INTERIOR FINISHES | 0643 | It is recommended that the interior walls and ceilings be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | SHOP/ BUNKHOUSE/ OFFICE | 9953 | Wildlife |  |  | Kirch WMA | 1969 | 1250 | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12500
0941EXT1 | HISTORICAL BUILDING MAINTENANCE | 0941 | The wood structure is over 87 years old and there are numerous areas where the wood is splitting, warping and deteriorating. This is also an exhibit for the park and requires maintenance. This project would provide for sealing the wood and repairing the roof as needed. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements, which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | OLD RANCH SCHOOL HOUSE | 9953 | Wildlife |  |  | Kirch WMA | 1930 | 650 | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 665
0643EXT3 | CONCRETE APRON INSTALLATION | 0643 | The building has two vehicle garage doors that don’t have exterior concrete aprons. This project would provide for the installation of two new 4" thick concrete slab-on-grade aprons at the vehicle garage doors. Removal and disposal of the existing concrete is included in this estimate. | SHOP/ BUNKHOUSE/ OFFICE | 9953 | Wildlife |  |  | Kirch WMA | 1969 | 1250 | 2016-06-08 | Four to Ten Years | Long-Term Needs | 3 | 2400
0943EXT1 | EXTERIOR FINISHES | 0943 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations and removing the dirt and rocks around the perimeter of the building. The dirt and rocks are reacting with the metal panels and causing premature deterioration of the metal. It is recommended that the work is done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | CHEMICAL STORAGE SHED | 9953 | Wildlife |  |  | Kirch WMA | 1960 | 240 | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2400
0643SFT1 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0643 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. | SHOP/ BUNKHOUSE/ OFFICE | 9953 | Wildlife |  |  | Kirch WMA | 1969 | 1250 | 2016-06-08 | Immediate to Two Years | Currently Critical | 1 | 4000
0643ADA2 | ADA SIGNAGE & STRIPING | 0643 | The ADA provides for accessibility to sites and services for people with physical limitations. The concrete parking area and passenger loading area are missing proper signage and striping to comply with ADA requirements. This project would provide for striping, signage and any other necessary upgrades to the parking space. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | SHOP/ BUNKHOUSE/ OFFICE | 9953 | Wildlife |  |  | Kirch WMA | 1969 | 1250 | 2016-06-08 | Immediate to Two Years | Currently Critical | 1 | 3500
0643ENR1 | LIGHTING UPGRADE | 0643 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | SHOP/ BUNKHOUSE/ OFFICE | 9953 | Wildlife |  |  | Kirch WMA | 1969 | 1250 | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
0643SFT3 | SMOKE AND CARBON MONOXIDE ALARM INSTALLATION | 0643 | Section 907.2.11 of the 2012 IBC and 2012 IFC explains the requirements for smoke alarms in dwelling units including installing and maintaining smoke alarms in each sleeping room and on the ceiling or wall outside of each separate sleeping area in the immediate vicinity of bedrooms. IFC 2012 Section 908.7 carbon monoxide alarms group I or R occupancies located in a building containing a fuel-burning appliance or in a building which has an attached garage shall be equipped with single-station carbon monoxide alarm. The carbon monoxide alarm shall be listed as complying with UL 2034 and be installed and maintained in accordance with NFPA 720 and the manufacturer’s instructions. State Fire Marshal NAC 477.915 (3) requires that smoke detectors and carbon monoxide alarms be connected to the wiring of the building with a battery backup. This project would provide funding for the purchase and installation of a smoke alarm and combo smoke alarm and carbon monoxide alarm in accordance with these codes. | SHOP/ BUNKHOUSE/ OFFICE | 9953 | Wildlife |  |  | Kirch WMA | 1969 | 1250 | 2016-06-08 | Immediate to Two Years | Currently Critical | 1 | 2500
0644EXT1 | EXTERIOR FINISHES | 0644 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is cleaning the vinyl siding and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be cleaned and caulked in the next 5-7 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | KIRCH WMA PUMP HOUSE | 9953 | Wildlife |  |  | Kirch WMA | 1992 | 100 | 2016-06-08 | Four to Ten Years | Long-Term Needs | 3 | 1000
0643ADA1 | ADA RESTROOM REMODEL | 0643 | The restroom in the Office is original to the building, not ADA compliant and in overall poor condition. This project would provide for a complete remodel including a wider door, new sink, toilet, plumbing jacket, shower, grab bars, floor and wall finishes and all hardware required to be ADA compliant. Minor remodeling of the space may be required. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 20010 were referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | SHOP/ BUNKHOUSE/ OFFICE | 9953 | Wildlife |  |  | Kirch WMA | 1969 | 1250 | 2016-06-08 | Immediate to Two Years | Currently Critical | 1 | 25000
2297ADA3 | BREAK ROOM REMODEL ADA | 2297 | The kitchenette and associated cabinets in the employee break room are original to the building. This project recommends the replacement of the existing kitchen countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. An ADA accessible sink should be provided. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards for Accessible Design should be incorporated into the design. This estimate includes removal and disposal of the existing materials. | EASTERN REGION NDOW OFFICE BUILDING | 9880 | Wildlife |  |  | Elko | 2002 | 9000 | 2016-07-05 | Immediate to Two Years | Currently Critical | 1 | 15000
2298SFT4 | BATTERY STORAGE | 2298 | Section 608 of the 2012 IFC explains the requirements for stationary storage of battery systems. Batteries shall have safety caps, spill control and neutralization, mechanical ventilation and/or cabinet ventilation, supervision over the mechanical ventilation, building or cabinet signage, seismically braced and a smoke alarm. This project will provide funding for the requirements of Section 608 of the 2012 IFC proper way to store, charge and/or use batteries indoors. This project or a portion thereof was previously recommended in the FCA report dated 09/28/2005 and 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/05/2016. | EASTERN REGION NDOW GARAGE | 9880 | Wildlife |  |  | Elko | 2002 | 5200 | 2016-07-05 | Immediate to Two Years | Currently Critical | 1 | 25000
2298ENV1 | LIGHTING UPGRADE | 2298 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | EASTERN REGION NDOW GARAGE | 9880 | Wildlife |  |  | Elko | 2002 | 5200 | 2016-07-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 41600
2298ENV2 | SPILL CONTAINMENT | 2298 | The Garage does not have a method for containing spills or leakage from drums. This project would add secondary containment pallets for all containers in the building and install placards on the building’s exterior. | EASTERN REGION NDOW GARAGE | 9880 | Wildlife |  |  | Elko | 2002 | 5200 | 2016-07-05 | Immediate to Two Years | Currently Critical | 1 | 6500
2298HVA2 | EVAPORATIVE COOLER INSTALLATION | 2298 | The Garage has no central cooling system and is uncomfortably warm in the summer. It is recommended to install four evaporative coolers in the building to ensure a comfortable work environment. This project would provide for the purchase and installation of four evaporative coolers including all required connections to existing utilities. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/05/2016. | EASTERN REGION NDOW GARAGE | 9880 | Wildlife |  |  | Elko | 2002 | 5200 | 2016-07-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
2298SFT8 | ANCHOR SHELVES | 2298 | OSHA recommends that the bottom of all columns be furnished with column base plates, and be anchored to the floor with anchor bolts capable of resisting the forces caused by the loads on the shelving unit. Per OSHA standard 1926.250(a)(1), All materials stored in tiers shall be stacked, racked, blocked, interlocked, or otherwise secured to prevent sliding, falling or collapse. This project would provide for a licensed contractor to install anchor bolts and properly secure the shelving units to the floor and to the other shelves. This project should be overseen by a licensed engineer or architect. | EASTERN REGION NDOW GARAGE | 9880 | Wildlife |  |  | Elko | 2002 | 5200 | 2016-07-05 | Immediate to Two Years | Currently Critical | 1 | 10000
2298SFT7 | HAZARDOUS MATERIALS STORAGE | 2298 | The Garage contains hazardous materials (i.e. gasoline, herbicides and pesticides). Per IFC 2012 Hazardous Materials, and in accordance with NFPA; where hazardous materials are stored, dispensed or used, Section 5003 states the proper use and application is to have mechanical exhaust and ventilation, and hazard identification signs shall be installed. Refer to Section 5004 and 5005 for the proper use and setup. It is important to comply with all applicable codes. This project would provide for all requirements in IFC 2012, to include Section 105 permits and inspections through the SFMO and the SPWD. | EASTERN REGION NDOW GARAGE | 9880 | Wildlife |  |  | Elko | 2002 | 5200 | 2016-07-05 | Immediate to Two Years | Currently Critical | 1 | 30000
2298SFT1 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 2298 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/28/2005 and 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/05/2016. | EASTERN REGION NDOW GARAGE | 9880 | Wildlife |  |  | Elko | 2002 | 5200 | 2016-07-05 | Immediate to Two Years | Currently Critical | 1 | 5000
2298SFT2 | SAFETY CABINETS | 2298 | Flammable or combustible liquids in drums or other containers (including flammable aerosols) not exceeding 60 gallons individual capacity and those portable tanks not exceeding 660 gallons individual capacity, shall have a proper storage container, OSHA 1910.106 (7) (d). This project will provide two OSHA approved storage cabinets for gasoline, aerosol cans and other flammable items. This project or a portion thereof was previously recommended in the FCA report dated 09/28/2005 and 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/05/2016. | EASTERN REGION NDOW GARAGE | 9880 | Wildlife |  |  | Elko | 2002 | 5200 | 2016-07-05 | Immediate to Two Years | Currently Critical | 1 | 10000
2298HVA1 | HEATER INSTALLATION | 2298 | The Garage is currently unheated, making for unpleasant working conditions in colder weather. Natural gas is stubbed up outside of the building. This project would provide for the installation of two 25 KBTU suspended heaters in the shop area. The estimate includes installing a gas meter, seismic gas shut off valve, gas piping and seismic supports, and electrical connections. This project or a portion thereof was previously recommended in the FCA report dated 09/28/2005 and 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/05/2016. | EASTERN REGION NDOW GARAGE | 9880 | Wildlife |  |  | Elko | 2002 | 5200 | 2016-07-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24000
2297ADA2 | ADA SHOWER UPGRADE | 2297 | The current shower pan and surround are cracked and in poor condition at the time of the survey. This project would provide for one ADA compliant stainless steel shower cabinet to be installed to provide shower facilities for the disabled. Included in this estimate is the installation of one stainless steel ADA compliant shower cabinet unit complete with accessible plumbing fixtures, seat, etc. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | EASTERN REGION NDOW OFFICE BUILDING | 9880 | Wildlife |  |  | Elko | 2002 | 9000 | 2016-07-05 | Immediate to Two Years | Currently Critical | 1 | 25000
2298SFT6 | HOUSEKEEPING STORAGE | 2298 | The Garage has miscellaneous items stacked in aisles, passageways and blocking egress. Items currently on shelving units are unsafely stacked. OSHA 1926.250(a)(3) states Aisles and passageways shall be kept clear to provide for the free and safe movement of material handling equipment or employees. Such areas shall be kept in good repair 1926.250(c) Housekeeping Storage areas shall be kept free from accumulation of materials that constitute hazards from tripping, fire, explosion, or pest harborage. This project would provide funding to comply with OSHA standards. It is recommended that the employer develop a maintenance and inspection program for storage, which include keeping aisles clear and providing sufficient clearance for material handling equipment, ensuring storage shelves are properly aligned, plum, and level, per manufacturer’s instructions, as well as encouraging employees to promptly report any damage to storage shelves. | EASTERN REGION NDOW GARAGE | 9880 | Wildlife |  |  | Elko | 2002 | 5200 | 2016-07-05 | Immediate to Two Years | Currently Critical | 1 | 4000
2297EXT2 | ROOF REPLACEMENT | 2297 | The single-ply and standing seam metal roof on this building was in fair condition at the time of the survey. It is recommended that this building be re-roofed in the next 4-5 years with a new single-ply roofing system including installing single-ply roofing directly over the existing metal roof. This will allow the roof to qualify for the statewide roofing program warranty and preventative maintenance agreement. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/05/2016. | EASTERN REGION NDOW OFFICE BUILDING | 9880 | Wildlife |  |  | Elko | 2002 | 9000 | 2016-07-05 | Four to Ten Years | Long-Term Needs | 3 | 108000
2298SFT5 | PROVIDE CLEARANCE AT ELECTRICAL PANELS | 2298 | There are electrical panels in the building which do not have proper clear floor space around them. The 2012 IFC Section 605.3 states A working space of not less than 30 inches in width, 36 inches in depth and 78 inches in height shall be provided in front of electrical service equipment. Where the electrical service equipment is wider than 30 inches, the working space shall not be less than the width of the equipment. No storage of any materials shall be located within the designated working space. This project would provide funds to relocate the tables, microwaves and other items currently blocking the working space. | EASTERN REGION NDOW GARAGE | 9880 | Wildlife |  |  | Elko | 2002 | 5200 | 2016-07-05 | Immediate to Two Years | Currently Critical | 1 | 250
2297ADA1 | ADA SIGNAGE | 2297 | ADA regulations pertaining to building access, route of travel and restrooms has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/ pictograms; and sign contrast and finish. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances, route of travel inside the building and restrooms. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/05/2016. | EASTERN REGION NDOW OFFICE BUILDING | 9880 | Wildlife |  |  | Elko | 2002 | 9000 | 2016-07-05 | Immediate to Two Years | Currently Critical | 1 | 2500
2297ENR3 | LIGHTING UPGRADE | 2297 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | EASTERN REGION NDOW OFFICE BUILDING | 9880 | Wildlife |  |  | Elko | 2002 | 9000 | 2016-07-05 | Four to Ten Years | Long-Term Needs | 3 | 72000
2297INT4 | CEILING TILE REPLACEMENT | 2297 | The building has a suspended acoustical tile ceiling system. A number of the ceiling tiles are damaged and stained from leaks in the boiler and roofing systems. This project would provide for the replacement of the suspended acoustical ceiling tiles that are damaged or stained. Removal and disposal of the existing ceiling system is included in this estimate. | EASTERN REGION NDOW OFFICE BUILDING | 9880 | Wildlife |  |  | Elko | 2002 | 9000 | 2016-07-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
2297ENR1 | WATER HEATER REPLACEMENT | 2297 | There is a 50 gallon gas-fired water heater in the building. The average life span of a water heater is 8-10 years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next year. It is recommended that a new energy efficient gas-fired water heater be installed. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/05/2016. | EASTERN REGION NDOW OFFICE BUILDING | 9880 | Wildlife |  |  | Elko | 2002 | 9000 | 2016-07-05 | Immediate to Two Years | Currently Critical | 1 | 1750
2297PLM1 | WATER TREATMENT SYSTEM INSTALLATION | 2297 | The existing plumbing and HVAC systems are not equipped with a water treatment system. Failure to treat the water causes wear and tear on the domestic water supply lines, plumbing fixtures and HVAC equipment. This project would provide for the purchase and installation of water softeners/ treatment systems to serve all of the mechanical and plumbing equipment. This project would also provide for a chemical treatment program including an updated chemicals control system, service and employee training provided by a qualified water treatment vendor. The annual maintenance fee charged by the water treatment vendor would be determined after an investigation of the water system is complete. These annual costs are not included in this project cost. For budgeting purposes, a $12,000 annual maintenance fee is suggested. | EASTERN REGION NDOW OFFICE BUILDING | 9880 | Wildlife |  |  | Elko | 2002 | 9000 | 2016-07-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
2297ENV3 | GUTTER DOWNSPOUT REPLACEMENT | 2297 | The existing cast iron with no-hub downspouts on the North side of the building are located between the CMU exterior wall and an interior gypsum wallboard. At the time of the survey there was evidence of water leaking from the downspouts. This is due to cracks created when water freezes inside the downspouts. This project would remove the damaged downspouts and no-hubs and reinstall and relocate the downspouts to the outside of the building with a thermostatic controlled heat tape. | EASTERN REGION NDOW OFFICE BUILDING | 9880 | Wildlife |  |  | Elko | 2002 | 9000 | 2016-07-05 | Immediate to Two Years | Currently Critical | 1 | 12000
2297SFT3 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 2297 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | EASTERN REGION NDOW OFFICE BUILDING | 9880 | Wildlife |  |  | Elko | 2002 | 9000 | 2016-07-05 | Immediate to Two Years | Currently Critical | 1 | 5000
2297EXT1 | EXTERIOR FINISHES | 2297 | It is important to maintain the finish, weather resistance, energy efficiency and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the masonry and stone, painting the EIFS and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/05/2016. | EASTERN REGION NDOW OFFICE BUILDING | 9880 | Wildlife |  |  | Elko | 2002 | 9000 | 2016-07-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 90000
2297ENR2 | ENERGY MANAGEMENT SYSTEM INSTALLATION | 2297 | The YAMAS energy management system is original to the building and should be scheduled for replacement. Replacement parts for performing routine and emergency maintenance are not made any more , the system has recently had numerous failures and the system is too old to perform software updates. This project would provide for the removal and disposal of the existing YAMAS energy management system and replacement with new equipment including all required connections to utilities and equipment. | EASTERN REGION NDOW OFFICE BUILDING | 9880 | Wildlife |  |  | Elko | 2002 | 9000 | 2016-07-05 | Immediate to Two Years | Currently Critical | 1 | 30000
2297HVA3 | BOILER REPLACEMENT | 2297 | There are two hot water boilers servicing the building. They are original to the building dating back to 2002. The life expectancy of these units is 20 to 25 years with proper maintenance and water treatment programs. Replacement parts for performing routine and emergency maintenance are hard to find for this old equipment. The controls and mixing valves should be replaced for the same reasons. This project would provide for the removal and disposal of the existing boilers, controls and mixing valves and replacement with new equipment including all required connections to utilities and equipment. The estimate is based on a 300 MBH output hot water boiler. | EASTERN REGION NDOW OFFICE BUILDING | 9880 | Wildlife |  |  | Elko | 2002 | 9000 | 2016-07-05 | Four to Ten Years | Long-Term Needs | 3 | 100000
2297SFT4 | FIRE & SECURITY ALARM SYSTEM REPLACEMENT | 2297 | This building is equipped with an outdated automatic fire detection and alarm system. Due to the age of the systems, parts cannot be obtained and do not comply with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. According to NAC 477.917 If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. When completed, the new system will comply with the 2012 IBC Chapter 9, Section 907 and the SFMO requirements. | EASTERN REGION NDOW OFFICE BUILDING | 9880 | Wildlife |  |  | Elko | 2002 | 9000 | 2016-07-05 | Immediate to Two Years | Currently Critical | 1 | 72000
2297INT1 | INTERIOR FINISHES | 2297 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and adequately prepared to receive the coating. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/05/2016. | EASTERN REGION NDOW OFFICE BUILDING | 9880 | Wildlife |  |  | Elko | 2002 | 9000 | 2016-07-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 90000
2297INT3 | FLOORING REPLACEMENT | 2297 | The VCT and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the next 2-3 years. | EASTERN REGION NDOW OFFICE BUILDING | 9880 | Wildlife |  |  | Elko | 2002 | 9000 | 2016-07-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 72000
2298EXT1 | EXTERIOR FINISHES | 2298 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is caulking and sealing the flashing, fixtures and all other penetrations and painting of the rollup doors. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/05/2016. | EASTERN REGION NDOW GARAGE | 9880 | Wildlife |  |  | Elko | 2002 | 5200 | 2016-07-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 52000
9880SFT1 | HAZARDOUS COMMUNICATION PROGRAM | 9880 | Due to the storage of hazardous materials, this site shall comply with IFC 2012 Chapter 4 Emergency Planning and Preparedness and have a written Hazardous Materials Management Plan, including but not limited to, Section 5003 Safety Data Sheets, Section 406 Employee Training and Response Procedures and Section 407 Hazard Communication. Chapter 50 Section 5001 will provide additional assistance in devising and implementing a hazardous communication program. | EASTERN REGION WILDLIFE OFFICE SITE | 9880 | Wildlife |  |  | Elko | 2002 |  | 2016-07-05 | Immediate to Two Years | Currently Critical | 1 | 2000
9880SIT1 | SITE BOLLARDS | 9880 | The site has parking in the rear of the Office building near the AC units. The garage building has five sectional overhead doors. These areas are in need of bollards to protect the AC units and the garage building. This project would provide funding for 18 eight inch diameter bollards to be located on each side of the garage sectional overhead doors and in front of the AC units. This project or a portion thereof was previously recommended in the FCA report dated 09/28/2005 and 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/05/2016. | EASTERN REGION WILDLIFE OFFICE SITE | 9880 | Wildlife |  |  | Elko | 2002 |  | 2016-07-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18000
9880ADA1 | ADA SIDEWALK REPLACEMENT | 9880 | The concrete sidewalks around the building are in need of replacement. They have cracks and are spalling. This project would provide for the removal and replacement of the concrete sidewalks. 1,500 SF of 4" thick concrete was used for this estimate. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | EASTERN REGION WILDLIFE OFFICE SITE | 9880 | Wildlife |  |  | Elko | 2002 |  | 2016-07-05 | Immediate to Two Years | Currently Critical | 1 | 22500
9880SIT5 | PARKING LOT STRIPING | 9880 | It is important to maintain the striping on the pavement at the site. This project would provide for the necessary striping and painting of the curbs and parking spaces. An ADA parking and loading space emblem will be painted on the concrete that is designated for ADA parking. This project should be scheduled on a 2 year cyclical basis to maintain the integrity of the striping, painting and ADA designation. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | EASTERN REGION WILDLIFE OFFICE SITE | 9880 | Wildlife |  |  | Elko | 2002 |  | 2016-07-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
9880SIT4 | VALLEY GUTTER REPAIRS | 9880 | The concrete valley gutter running through the parking lot is deteriorated and failing. There is significant spalling in many areas that will require complete replacement. The rest of the gutter requires patching and sealing. This project addresses removal and replacement of damaged areas and repairs as needed. 350 SF of 4" thick concrete gutter was used for this estimate. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/05/2016. | EASTERN REGION WILDLIFE OFFICE SITE | 9880 | Wildlife |  |  | Elko | 2002 |  | 2016-07-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
9882PLM1 | WELL INSTALLATION | 9882 | The 19 fish raceways receive water from both Spring Creek and Snake Creek. The water flows through the raceways and eventually flows back into Snake Creek. At times during the summer months and during droughts, the water from the creeks are unable to meet demands. This project recommends drilling a new well and installing new pumping equipment to serve the water demands of the site. Estimates are based on a maximum of 300 feet of drilling. | SPRING CREEK FISH REARING STATION SITE | 9882 | Wildlife |  |  | Baker | 0 |  | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 400000
0664HVA1 | HVAC EQUIPMENT REPLACEMENT | 0664 | The 84,000 BTUs heating system was installed in 1993. It is not energy efficient and has reached the end of its expected and useful life. This project would provide for the installation of a new HVAC split system and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing equipment and all required connections to utilities. | S.C. REARING STATION RES. #1, NORTH | 9882 | Wildlife |  |  | Baker | 1950 | 1008 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0665HVA1 | HEATER INSTALLATION | 0665 | The building is currently unheated, making for unpleasant working conditions in colder weather. This project would provide for the installation of two 25KBTU suspended heaters in the building. The estimate includes installing a gas meter, seismic gas shut off valve, gas piping and seismic supports and electric connections. | S.C. REARING STATION STORAGE/SHOP | 9882 | Wildlife |  |  | Baker | 1964 | 1343 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24000
0665ENR1 | LIGHTING UPGRADE | 0665 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | S.C. REARING STATION STORAGE/SHOP | 9882 | Wildlife |  |  | Baker | 1964 | 1343 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10744
0666ADA2 | ADA SHOWER UPGRADE | 0666 | This project would provide for an ADA compliant stainless steel shower cabinet to be installed to provide shower facilities for the disabled. Included in this estimate is the installation of a stainless steel ADA compliant shower cabinet unit complete with accessible plumbing fixtures, seats, etc. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | S.C. REARING STATION OFFICE & GARAGE | 9882 | Wildlife |  |  | Baker | 1949 | 768 | 2016-07-06 | Immediate to Two Years | Currently Critical | 1 | 25000
0665EXT4 | OVERHEAD DOOR REPLACEMENT | 0665 | There are two 8'x8' overhead coiling doors in the building which are damaged and do not function properly. They are original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead garage doors and replacement with new automatic openers and insulated garage doors. Removal and disposal of the existing garage doors is included in this estimate. | S.C. REARING STATION STORAGE/SHOP | 9882 | Wildlife |  |  | Baker | 1964 | 1343 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14000
0667EXT3 | GUTTER INSTALLATION | 0667 | The building does not have gutters or downspouts to control the runoff from the roof. The water currently drains off the roof causing extensive erosion to the built-up dirt slope around the foundation. This will eventually lead to failure of the foundation undermining the integrity of the entire structure. This project would provide funding for the installation of a seamless gutter and downspout system for the building. | S.C. REARING STATION RESIDENCE GARAGE | 9882 | Wildlife |  |  | Baker | 1972 | 768 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
0667ENR1 | INSULATE BUILDING | 0667 | The building is not insulated and is not energy efficient. This project will install batt insulation (R19) in the walls and (R38) on the ceilings and will be covered with impermeable vinyl interior surface to help moderate temperature fluctuations. | S.C. REARING STATION RESIDENCE GARAGE | 9882 | Wildlife |  |  | Baker | 1972 | 768 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11520
0665SFT1 | EXTERIOR LANDING INSTALLATION | 0665 | The landing at the door on the building does not comply with code and poses a safety hazard. Section 1008.1 of the 2012 IBC describes the requirements for doors including floor elevations and landings. The floor or landing shall be at the same elevation on each side of the door and the exterior landing shall not exceed a 2-percent slope and shall have a length measured in the direction of travel of not less than 44 inches. This project would provide for the installation of compliant landing for the door. | S.C. REARING STATION STORAGE/SHOP | 9882 | Wildlife |  |  | Baker | 1964 | 1343 | 2016-07-06 | Immediate to Two Years | Currently Critical | 1 | 2500
0665SIT2 | SITE DRAINAGE UPGRADES | 0665 | The grade does not slope away effectively from the building. Water has pooled against the foundation. In the winter months, as the water freezes against the foundation, over time, this can cause damage to the foundation. It is recommended per IBC 1804.3 Site Grading the ground immediately adjacent to the foundation shall be sloped away from the building at a slope of not less than one vertical in 20 units horizontal (5-percent slope) for a minimum distance of 10 feet (3048 mm) measured perpendicular to the face of the wall. This project would create a 5% slope away from the building. Additional drainage swales and French Drains shall be installed, as needed. It is recommended that the grading be completed within 2-3 years. | S.C. REARING STATION STORAGE/SHOP | 9882 | Wildlife |  |  | Baker | 1964 | 1343 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0665INT1 | BUILDING INSULATION | 0665 | The building is not insulated and is not energy efficient. This project will install batt insulation (R19) in the walls and (R38) on the ceilings and will be covered with impermeable vinyl interior surface to help moderate temperature fluctuations. This project or a portion thereof was previously recommended in the FCA report dated 08/18/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/06/2016. | S.C. REARING STATION STORAGE/SHOP | 9882 | Wildlife |  |  | Baker | 1964 | 1343 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20145
0667SIT3 | SITE DRAINAGE UPGRADES | 0667 | The grade does not slope away effectively from the building. Water has pooled against the foundation. In the winter months, as the water freezes against the foundation, over time, this can cause damage to the foundation. It is recommended per IBC 1804.3 Site Grading the ground immediately adjacent to the foundation shall be sloped away from the building at a slope of not less than one vertical in 20 units horizontal (5-percent slope) for a minimum distance of 10 feet (3048 mm) measured perpendicular to the face of the wall. This project would create a 5% slope away from the building. Additional drainage swales and French Drains shall be installed, as needed. It is recommended that the grading be completed within 2-3 years. | S.C. REARING STATION RESIDENCE GARAGE | 9882 | Wildlife |  |  | Baker | 1972 | 768 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0664SIT2 | SITE DRAINAGE UPGRADES | 0664 | The grade does not slope away effectively from the building. Water has pooled against the foundation. In the winter months, as the water freezes against the foundation, over time, this can cause damage to the foundation. It is recommended per IBC 1804.3 Site Grading the ground immediately adjacent to the foundation shall be sloped away from the building at a slope of not less than one vertical in 20 units horizontal (5-percent slope) for a minimum distance of 10 feet (3048 mm) measured perpendicular to the face of the wall. This project would create a 5% slope away from the building. Additional drainage swales and French Drains shall be installed, as needed. It is recommended that the grading be completed within 2-3 years. | S.C. REARING STATION RES. #1, NORTH | 9882 | Wildlife |  |  | Baker | 1950 | 1008 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0667EXT4 | EXTERIOR FINISHES | 0667 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking, sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | S.C. REARING STATION RESIDENCE GARAGE | 9882 | Wildlife |  |  | Baker | 1972 | 768 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1536
0664SIT3 | REMOVE SPRINKLERED LAWN WITHIN 3' OF BUILDING | 0664 | The house has considerable damage to the siding from lawn sprinklers wetting the siding. This project would create drip irrigated planters within three feet of the house and relocate sprinklers so they do not wet the house. | S.C. REARING STATION RES. #1, NORTH | 9882 | Wildlife |  |  | Baker | 1950 | 1008 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0664SIT1 | REPLACE CONCRETE WALK | 0664 | The existing concrete sidewalks are cracked, spalling and present a tripping hazard to pedestrians. Exposure to the weather has contributed to the damage and deterioration. It is believed the concrete is part of the original construction. This project would provide funding for the removal and disposal of the existing concrete and the installation of a 42" wide x 25' long section of concrete sidewalk. This project should coincide with other concrete work recommended for the site. This project or a portion thereof was previously recommended in the FCA report dated 08/18/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/06/2016. | S.C. REARING STATION RES. #1, NORTH | 9882 | Wildlife |  |  | Baker | 1950 | 1008 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
0948EXT2 | EXTERIOR FINISHES | 0948 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | S.C. REARING STATION SHED #1 | 9882 | Wildlife |  |  | Baker | 1950 | 144 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1440
0664EXT2 | EXTERIOR FINISHES | 0664 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is cleaning the vinyl siding and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be cleaned and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | S.C. REARING STATION RES. #1, NORTH | 9882 | Wildlife |  |  | Baker | 1950 | 1008 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10080
0667ENR2 | WINDOW REPLACEMENT | 0667 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 4 units. Removal and disposal of the existing windows is included in this estimate. | S.C. REARING STATION RESIDENCE GARAGE | 9882 | Wildlife |  |  | Baker | 1972 | 768 | 2016-07-06 | Four to Ten Years | Long-Term Needs | 3 | 6000
0949SFT1 | EXTERIOR LANDING INSTALLATION | 0949 | There is an exterior door on the building that does not have a landing. This does not comply with 2012 IBC Section 1008.1, which requires a proper landing and for the landing to not be more than 1/2" below the threshold. This project would provide for the installation of compliant landings. | S.C. REARING STATION DOMESTIC WELL SHED | 9882 | Wildlife |  |  | Baker | 1980 | 120 | 2016-07-06 | Immediate to Two Years | Currently Critical | 1 | 1500
0949ELE1 | WIRING CLEANUP | 0949 | The wiring in the Domestic Well Shed is disorganized and not in proper electrical boxes. This creates a safety issue during repairs or upgrades. This project would provide for organization, proper labeling and for the wiring to be placed electrical boxes per NEC 2011. | S.C. REARING STATION DOMESTIC WELL SHED | 9882 | Wildlife |  |  | Baker | 1980 | 120 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
0949EXT3 | ROOF REPLACEMENT | 0949 | The asphalt roll roofing on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayment. This estimate includes removal and disposal of the old roofing. | S.C. REARING STATION DOMESTIC WELL SHED | 9882 | Wildlife |  |  | Baker | 1980 | 120 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1440
0949ELE2 | GFCI OUTLETS | 0949 | The existing receptacle in the Domestic Well Shed is a standard duplex receptacle. The 2011 NEC 210.8 requires this location to have Ground Fault Circuit Interrupter (GFCI) protection. This project would provide for removing the standard receptacle and installing GFCI receptacle. | S.C. REARING STATION DOMESTIC WELL SHED | 9882 | Wildlife |  |  | Baker | 1980 | 120 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 400
0664EXT3 | ROOF REPLACEMENT | 0664 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayment. This estimate includes removal and disposal of the old roofing. | S.C. REARING STATION RES. #1, NORTH | 9882 | Wildlife |  |  | Baker | 1950 | 1008 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12096
0664INT2 | INTERIOR REMODEL | 0664 | The interior fixtures and finishes are in general disrepair and the building is due for a complete remodel. This project would provide for removal and replacement of the flooring, doors and frames, cabinetry, trim, baseboards, kitchen and any other interior finishes and fixtures in need of replacement. | S.C. REARING STATION RES. #1, NORTH | 9882 | Wildlife |  |  | Baker | 1950 | 1008 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50400
0664PLM1 | WATER HEATER REPLACEMENT | 0664 | There is a 40 gallon propane-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 8-10 years. It is recommended that a new propane-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | S.C. REARING STATION RES. #1, NORTH | 9882 | Wildlife |  |  | Baker | 1950 | 1008 | 2016-07-06 | Four to Ten Years | Long-Term Needs | 3 | 1750
0949EXT2 | EXTERIOR FINISHES | 0949 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the flashing and fixtures and all other penetrations. It is recommended that the building be painted in the next 2-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | S.C. REARING STATION DOMESTIC WELL SHED | 9882 | Wildlife |  |  | Baker | 1980 | 120 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1200
0666SFT5 | FLUE REPAIRS | 0666 | The flue on this building has an improper support strap, is too close to combustibles and doesn’t have the proper clearances. The heater flue, the support strap and the distances of the flue to the fascia do not comply with IFGC 2012, IBC 2012, IMC 2012 chapter 8, chimneys and vents or the Manufacturers Specification for installation instructions. It is recommended that all flues throughout the building be installed per the manufacturers specifications IFGC 2012, IBC 2012 and IMC 2012. | S.C. REARING STATION OFFICE & GARAGE | 9882 | Wildlife |  |  | Baker | 1949 | 768 | 2016-07-06 | Immediate to Two Years | Currently Critical | 1 | 2000
0667SIT1 | TREE REMOVAL | 0667 | A deciduous tree is growing next to the garage foundation between the two roll up doors. The tree in time will cause damage to the foundation and flooring. This tree should be removed before damage occurs to the foundation and flooring. This project would provide funding to remove the tree and its roots. This project or a portion thereof was previously recommended in the FCA report dated 08/18/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/06/2016. | S.C. REARING STATION RESIDENCE GARAGE | 9882 | Wildlife |  |  | Baker | 1972 | 768 | 2016-07-06 | Immediate to Two Years | Currently Critical | 1 | 4000
0666SFT4 | SAFETY CABINETS | 0666 | The building contains many different paints, stains, and other hazardous products located on open shelves and on the floor. This does not meet OSHA standards or IFC for hazardous materials containment. This project would provide for two self-closing hazardous storage containers in the building and install placards on the building exterior in accordance with OSHA 1910.106 (d) and IFC Chapter 57 Section 5704.3.2.1.3. | S.C. REARING STATION OFFICE & GARAGE | 9882 | Wildlife |  |  | Baker | 1949 | 768 | 2016-07-06 | Immediate to Two Years | Currently Critical | 1 | 10000
0666EXT3 | ROOF REPLACEMENT | 0666 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayment. This estimate includes removal and disposal of the old roofing. | S.C. REARING STATION OFFICE & GARAGE | 9882 | Wildlife |  |  | Baker | 1949 | 768 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9216
0948EXT3 | EXTERIOR SIDING REPLACEMENT | 0948 | The existing Lap siding is in poor condition and will no longer hold paint and is due for replacement. This project recommends removing the Lap siding and replacing it with new T1-11 siding finished with an oil-based stain or paint. | S.C. REARING STATION SHED #1 | 9882 | Wildlife |  |  | Baker | 1950 | 144 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3600
0666SIT4 | SITE DRAINAGE UPGRADES | 0666 | The grade does not slope away effectively from the building. Water has pooled against the foundation. In the winter months, as the water freezes against the foundation, over time, this can cause damage to the foundation. It is recommended per IBC 1804.3 Site Grading the ground immediately adjacent to the foundation shall be sloped away from the building at a slope of not less than one vertical in 20 units horizontal (5-percent slope) for a minimum distance of 10 feet (3048 mm) measured perpendicular to the face of the wall. This project would create a 5% slope away from the building. Additional drainage swales and French Drains shall be installed, as needed. It is recommended that the grading be completed within 2-3 years. | S.C. REARING STATION OFFICE & GARAGE | 9882 | Wildlife |  |  | Baker | 1949 | 768 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0667EXT2 | CONCRETE APRON | 0667 | The area in front of the garage doors is grass. To make garage access more convenient, it is recommended that a 24' x 20' concrete apron be poured in front of the garage doors. This project would provide for the funding to pour a 24' x 20' concrete apron including any required grading and soil preparation. This project or a portion thereof was previously recommended in the FCA report dated 08/18/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/06/2016. | S.C. REARING STATION RESIDENCE GARAGE | 9882 | Wildlife |  |  | Baker | 1972 | 768 | 2016-07-06 | Four to Ten Years | Long-Term Needs | 3 | 12000
0666ADA1 | ADA RESTROOM UPGRADE | 0666 | The building does not have an accessible restroom. The existing restroom does not meet the ADA requirements. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom. Items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | S.C. REARING STATION OFFICE & GARAGE | 9882 | Wildlife |  |  | Baker | 1949 | 768 | 2016-07-06 | Immediate to Two Years | Currently Critical | 1 | 15000
0666EXT4 | EXTERIOR FINISHES | 0666 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | S.C. REARING STATION OFFICE & GARAGE | 9882 | Wildlife |  |  | Baker | 1949 | 768 | 2016-07-06 | Immediate to Two Years | Currently Critical | 1 | 7680
0666SFT6 | CONCRETE APRON REPLACEMENT | 0666 | The exterior concrete apron outside of the building has extensive cracking and is due for replacement. This project would provide for the installation of a new 120 square foot 4" thick concrete slab-on-grade apron. Removal and disposal of the existing concrete is included in this estimate. | S.C. REARING STATION OFFICE & GARAGE | 9882 | Wildlife |  |  | Baker | 1949 | 768 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1200
0666SFT3 | EXIT SIGN AND EGRESS LIGHTING INSTALLATION | 0666 | The building does not have emergency lighting and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC 2012 Chapter 10 was referenced for this project. | S.C. REARING STATION OFFICE & GARAGE | 9882 | Wildlife |  |  | Baker | 1949 | 768 | 2016-07-06 | Immediate to Two Years | Currently Critical | 1 | 3840
0665EXT3 | EXTERIOR FINISHES | 0665 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 08/18/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/06/2016. | S.C. REARING STATION STORAGE/SHOP | 9882 | Wildlife |  |  | Baker | 1964 | 1343 | 2016-07-06 | Immediate to Two Years | Currently Critical | 1 | 13430
0665EXT2 | WINDOW REPLACEMENT | 0665 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 6 units. Removal and disposal of the existing windows is included in this estimate. | S.C. REARING STATION STORAGE/SHOP | 9882 | Wildlife |  |  | Baker | 1964 | 1343 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
0666ENR1 | REPLACE WINDOWS | 0666 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 14 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 08/18/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/06/2016. | S.C. REARING STATION OFFICE & GARAGE | 9882 | Wildlife |  |  | Baker | 1949 | 768 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 21000
0666SFT1 | SMOKE/ CARBON MONOXIDE ALARM INSTALLATION | 0666 | There are no smoke detectors or carbon monoxide detectors in the building. State Fire Marshal NAC 477.915 (3) requires that smoke detectors and carbon monoxide alarms be connected to the wiring of the building with a battery backup. This project would provide funding for the purchase and installation of a smoke alarm and combo smoke alarm and carbon monoxide alarm in accordance with the applicable building codes. This project or a portion thereof was previously recommended in the FCA report dated 08/18/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/06/2016. | S.C. REARING STATION OFFICE & GARAGE | 9882 | Wildlife |  |  | Baker | 1949 | 768 | 2016-07-06 | Immediate to Two Years | Currently Critical | 1 | 2000
0665EXT1 | CONCRETE APRON REPLACEMENT | 0665 | The building is missing an exterior concrete apron outside the roll up door bays. This project would provide for the installation of two new 120 square foot 4" thick concrete slab-on-grade aprons. | S.C. REARING STATION STORAGE/SHOP | 9882 | Wildlife |  |  | Baker | 1964 | 1343 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2400
0947EXT3 | ROOF REPLACEMENT | 0947 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayment. This estimate includes removal and disposal of the old roofing. | S.C. REARING STATION RES. #2, SOUTH | 9882 | Wildlife |  |  | Baker | 1950 | 1008 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12096
0667HVA1 | HEATER INSTALLATION | 0667 | The building is currently unheated, making for unpleasant working conditions in colder weather. This project would provide for the installation of two 25KBTU suspended heaters in the building. The estimate includes installing a gas meter, seismic gas shut off valve, gas piping and seismic supports and electric connections. | S.C. REARING STATION RESIDENCE GARAGE | 9882 | Wildlife |  |  | Baker | 1972 | 768 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24000
0947PLM1 | WATER HEATER REPLACEMENT | 0947 | There is a 40 gallon propane-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 8-10 years. It is recommended that a new propane-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | S.C. REARING STATION RES. #2, SOUTH | 9882 | Wildlife |  |  | Baker | 1950 | 1008 | 2016-07-06 | Four to Ten Years | Long-Term Needs | 3 | 1750
0947SIT3 | SITE DRAINAGE UPGRADES | 0947 | The grade does not slope away effectively from the building. Water has pooled against the foundation. In the winter months, as the water freezes against the foundation, over time, this can cause damage to the foundation. It is recommended per IBC 1804.3 Site Grading the ground immediately adjacent to the foundation shall be sloped away from the building at a slope of not less than one vertical in 20 units horizontal (5-percent slope) for a minimum distance of 10 feet (3048 mm) measured perpendicular to the face of the wall. This project would create a 5% slope away from the building. Additional drainage swales and French Drains shall be installed, as needed. It is recommended that the grading be completed within 2-3 years. | S.C. REARING STATION RES. #2, SOUTH | 9882 | Wildlife |  |  | Baker | 1950 | 1008 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0947EXT2 | EXTERIOR FINISHES | 0947 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is cleaning the vinyl siding and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be cleaned and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | S.C. REARING STATION RES. #2, SOUTH | 9882 | Wildlife |  |  | Baker | 1950 | 1008 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10080
0947SIT4 | REMOVE SPRINKLERED LAWN WITHIN 3' OF BUILDING | 0947 | The house has considerable damage to the siding from lawn sprinklers wetting the siding. This project would create drip irrigated planters within three feet of the house and relocate the sprinklers so they do not wet the house. | S.C. REARING STATION RES. #2, SOUTH | 9882 | Wildlife |  |  | Baker | 1950 | 1008 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0947SIT1 | SIDEWALK REPLACEMENT | 0947 | The existing concrete sidewalks are cracked, spalling and present a tripping hazard to pedestrians. Exposure to the weather has contributed to the damage and deterioration. It is believed the concrete is part of the original construction. This project would provide funding for the removal and disposal of the existing concrete and the installation of a 42" wide x 25' long section of concrete sidewalk. This project or a portion thereof was previously recommended in the FCA report dated 08/18/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/06/2016. | S.C. REARING STATION RES. #2, SOUTH | 9882 | Wildlife |  |  | Baker | 1950 | 1008 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
0947SIT2 | TREE REMOVAL | 0947 | A deciduous tree is growing next to the foundation of the residence. The tree in time will cause damage to the foundation. This tree should be removed before damage occurs to the foundation. This project would provide funding for the removal of the tree and roots. This project or a portion thereof was previously recommended in the FCA report dated 08/18/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/06/2016. | S.C. REARING STATION RES. #2, SOUTH | 9882 | Wildlife |  |  | Baker | 1950 | 1008 | 2016-07-06 | Immediate to Two Years | Currently Critical | 1 | 4000
0948EXT1 | REPLACE ROOF | 0948 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayment. This estimate includes removal and disposal of the old roofing. This project or a portion thereof was previously recommended in the FCA report dated 08/18/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/06/2016. | S.C. REARING STATION SHED #1 | 9882 | Wildlife |  |  | Baker | 1950 | 144 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1728
0948ENR1 | LIGHTING UPGRADE | 0948 | The existing lighting fixture is the older incandescent type, and is not energy efficient. This project will upgrade the fixture to a higher efficiency LED unit with a longer life cycle. An occupancy sensor will be installed for additional savings. Any electrical wiring upgrades are not included in this estimate. | S.C. REARING STATION SHED #1 | 9882 | Wildlife |  |  | Baker | 1950 | 144 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 144
0948INT2 | CONCRETE FOUNDATION | 0948 | At the time of this survey, the shed’s floor was unfinished and was dirt. This project would provide for the installation of a 4" thick concrete floor and a landing outside the front door of the building. The 2012 IBC Section 1008.1 was used as a reference for this project. | S.C. REARING STATION SHED #1 | 9882 | Wildlife |  |  | Baker | 1950 | 144 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14400
0947INT1 | INTERIOR REMODEL | 0947 | The interior fixtures and finishes are in general disrepair and the building is due for a complete remodel. This project would provide for the removal and replacement of the flooring, doors and frames, cabinetry, trim, baseboards, kitchen and any other interior finishes and fixtures in need of replacement excluding the bathroom. | S.C. REARING STATION RES. #2, SOUTH | 9882 | Wildlife |  |  | Baker | 1950 | 1008 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50400
2940EXT2 | ROOF REPLACEMENT | 2940 | The corrugated metal roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 4-5 years with a standing seam metal roofing system. This estimate includes the removal and the disposal of the old roof. | NDOW STORAGE SHED | 9947 | Wildlife |  |  | Cathedral Gorge | 2004 | 420 | 2017-04-05 | Four to Ten Years | Long-Term Needs | 3 | 6300
2940EXT3 | GARAGE DOOR REPLACEMENT | 2940 | The garage door is constructed of metal and is original to the building. It has deteriorated from weather exposure over time. It is recommended that a new garage door be installed. This estimate includes the removal and the disposal of the existing garage door. | NDOW STORAGE SHED | 9947 | Wildlife |  |  | Cathedral Gorge | 2004 | 420 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
2940SFT1 | EXTERIOR LANDING INSTALLATION | 2940 | Section R311.4.3 of the 2018 IBC describes the requirements for landings at exterior doors. The landing shall not be more than 7 3/4 inches below the top of the threshold and shall have a minimum dimension of 36 inches measured in the direction of travel. There are two doors that do not comply with this code and pose a safety hazard. This project would provide for the installation of compliant landings for each door. | NDOW STORAGE SHED | 9947 | Wildlife |  |  | Cathedral Gorge | 2004 | 420 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
2940EXT1 | EXTERIOR FINISHES | 2940 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof. This shall include sealing or other applied finishes, caulking around flashing, fixtures, and other penetrations to keep the building in a weather tight condition. It is recommended that this project be implemented in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | NDOW STORAGE SHED | 9947 | Wildlife |  |  | Cathedral Gorge | 2004 | 420 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4200
2942EXT1 | EXTERIOR/ INTERIOR FINISHES | 2942 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing of the precast concrete, and caulking of the flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CXT COMFORT STATION #1 - SOUTH | 9954 | Wildlife |  |  | Key Pittman WMA | 2007 | 56 | 2017-04-06 | Four to Ten Years | Long-Term Needs | 3 | 1120
3029EXT1 | EXTERIOR FINISHES | 3029 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/06/2017. | WMA STORAGE BUILDING | 9954 | Wildlife |  |  | Key Pittman WMA | 0 | 300 | 2017-04-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
3028ADA1 | ADA SIGNAGE & STRIPING | 3028 | The ADA provides for accessibility to sites and services for people with physical limitations. The concrete parking area and passenger loading area are missing proper signage and striping to comply with ADA requirements. This project would provide for striping, signage and any other necessary upgrades to the parking space. NRS 338.180, IBC - 2018, ICC/ANSI A117.1 and Americans with ADAAG were referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/06/2017. | CXT COMFORT STATION #2 - NORTH | 9954 | Wildlife |  |  | Key Pittman WMA | 0 | 112 | 2017-04-06 | Immediate to Two Years | Currently Critical | 1 | 3500
3029ELE1 | GFCI OUTLETS | 3029 | The existing receptacle is a standard duplex receptacle. The 2011 NEC 210.8 requires this location to be GFCI protected. This project would provide for removing the standard receptacle and installing a GFCI receptacle. | WMA STORAGE BUILDING | 9954 | Wildlife |  |  | Key Pittman WMA | 0 | 300 | 2017-04-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 400
3029SFT1 | SAFETY CABINETS | 3029 | The storage building contains many different paints, stains, pesticides, and other hazardous products on open shelves and on the floor. This does not meet OSHA standards for hazardous materials containment. This project would provide two hazardous storage containers in the building and install placards on the building exterior in accordance with OSHA 1910.106 (d). This project or a portion thereof was previously recommended in the FCA report dated 11/03/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/06/2017. | WMA STORAGE BUILDING | 9954 | Wildlife |  |  | Key Pittman WMA | 0 | 300 | 2017-04-06 | Immediate to Two Years | Currently Critical | 1 | 5000
3029ENR1 | LIGHTING UPGRADE | 3029 | The existing lighting fixtures are the older fluorescent type and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | WMA STORAGE BUILDING | 9954 | Wildlife |  |  | Key Pittman WMA | 0 | 300 | 2017-04-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 350
9954ELE1 | WIRING CLEANUP | 9954 | The wiring at the electrical panel and feeding the wellhead is disorganized, not in conduit, and does not have exterior grade cover plates or boxes. This creates a safety issue due to the moist environment. This project would provide for wiring organization and placement into electrical boxes, conduit to be added, and for the proper labeling per NEC 2017. | KEY PITTMAN WMA SITE | 9954 | Wildlife |  |  | Key Pittman WMA | 0 |  | 2017-04-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
3028EXT1 | EXTERIOR/ INTERIOR FINISHES | 3028 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing of the precast concrete, and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/06/2017. | CXT COMFORT STATION #2 - NORTH | 9954 | Wildlife |  |  | Key Pittman WMA | 0 | 112 | 2017-04-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2240
0647SIT1 | TREE AND SHRUB PRUNING/ REMOVAL | 0647 | There are several trees that are in need of removal to prevent damage to the Maintenance Shop. This project would provide for the trimming and/ or removal of the trees along the Maintenance Shop building and removal of the trees along the fence line. | MAINTENANCE SHOP | 9954 | Wildlife |  |  | Key Pittman WMA |  | 1200 | 2017-04-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0647ENR3 | EXTERIOR EIFS INSTALLATION | 0647 | The Maintenance Shop is an uninsulated concrete masonry unit structure. This project would provide for the installation of an exterior insulation and finish system which would reduce energy consumption resulting in energy cost savings. This project is recommended to be done in conjunction with the HVAC and Lighting Upgrade projects. An acrylic based finish is recommended due to the climate and extreme temperature fluctuations. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/06/2017. | MAINTENANCE SHOP | 9954 | Wildlife |  |  | Key Pittman WMA |  | 1200 | 2017-04-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 28800
0647EXT2 | ROOF/ STRUCTURE REPLACEMENT | 0647 | The roof framing and the rolled asphalt roofing on this building were in poor condition at the time of the survey. The framing is rotted and failing. It is particularly noticeable at the main ridge beam which is cracked. It is recommended that the entire roof structure be replaced including structural supports replacing it with a new composition roofing system including the underlayment. This estimate includes removal and disposal of the old framing and roofing system. Engineering of the roof structure will be required and a $5,000 allowance is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/06/2017. | MAINTENANCE SHOP | 9954 | Wildlife |  |  | Key Pittman WMA |  | 1200 | 2017-04-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 101841
0647ENV1 | PEST CONTROL | 0647 | There are numerous rodent droppings throughout this building. Due to the potential risk of disease, this project provides for treatment and cleanup of the rodent droppings by a licensed pest control business. | MAINTENANCE SHOP | 9954 | Wildlife |  |  | Key Pittman WMA |  | 1200 | 2017-04-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
0647EXT3 | OVERHEAD DOOR REPLACEMENT | 0647 | There are two overhead coiling doors which are damaged and do not function properly. Exposure and wind have caused the doors to bend, crack, and lose their finish. They are original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead coiling doors and the replacement with new manually operated overhead coiling doors. | MAINTENANCE SHOP | 9954 | Wildlife |  |  | Key Pittman WMA |  | 1200 | 2017-04-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14000
0647ENR1 | WINDOW REPLACEMENT | 0647 | The windows are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 3 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/06/2017. | MAINTENANCE SHOP | 9954 | Wildlife |  |  | Key Pittman WMA |  | 1200 | 2017-04-06 | Immediate to Two Years | Currently Critical | 1 | 4500
0648EXT1 | EXTERIOR FINISHES | 0648 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/06/2017. | CHICKEN COOP | 9954 | Wildlife |  |  | Key Pittman WMA |  | 168 | 2017-04-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1680
0647HVA1 | HVAC INSTALLATION | 0647 | The building has no central cooling or heating system and is uncomfortably warm in the summer and cold in the winter. It is recommended to install a 3 ton fuel fired packaged HVAC unit complete with ducting, diffusers, as required, and connection to the existing fuel tank. This project should be coordinated with the Exterior EIFS Installation project. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/06/2017. | MAINTENANCE SHOP | 9954 | Wildlife |  |  | Key Pittman WMA |  | 1200 | 2017-04-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
0647ENR2 | LIGHTING UPGRADE | 0647 | The existing lighting fixtures are the older fluorescent type and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/06/2017. | MAINTENANCE SHOP | 9954 | Wildlife |  |  | Key Pittman WMA |  | 1200 | 2017-04-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
0647SFT1 | EXTERIOR LANDING INSTALLATION | 0647 | There is an exterior door which swings out over a step and does not have a landing that complies with IBC 2018. IBC Section 1008 which requires a landing to be not more than 1/2" below the threshold. This project would provide for the installation of a compliant landing for the door. | MAINTENANCE SHOP | 9954 | Wildlife |  |  | Key Pittman WMA |  | 1200 | 2017-04-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0647INT1 | INTERIOR FINISHES | 0647 | The interior finishes are in fair condition. It is recommended that the interior CMU walls be sealed at least once in the next two to four years. Prior to sealing, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/06/2017. | MAINTENANCE SHOP | 9954 | Wildlife |  |  | Key Pittman WMA |  | 1200 | 2017-04-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
0903SFT4 | SMOKE ALARM INSTALLATION | 0903 | IRC 2018 Section R314 and R315.3 explains the requirements for smoke alarms in dwelling units. This includes: installing and maintaining smoke alarms in each sleeping room; having a carbon monoxide and smoke detector on the ceiling or wall outside of each sleeping area; in the immediate vicinity of bedrooms when an alteration, repair or addition requiring a permit occurs. IRC 2018, requires that smoke detectors and carbon monoxide alarms be UL rated. State Fire Marshal NAC 477.915 (3) requires that smoke detectors be connected to the wiring in a building and include a battery for emergency backup power. This project would provide funding for the purchase and installation of smoke alarms and carbon monoxide alarms in accordance with IRC and NAC laws. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/06/2017. | SUPERVISOR'S RESIDENCE | 9954 | Wildlife |  |  | Key Pittman WMA | 1959 | 1200 | 2017-04-06 | Immediate to Two Years | Currently Critical | 1 | 2000
0903INT2 | RESTROOM REMODEL | 0903 | One of the two restrooms in the residence is original to the building and in overall poor condition. The finishes, fixtures, cabinets, toilets, showers, and exhaust fans are showing signs of wear and deterioration. This project would provide for a complete remodel of the restroom. The removal and disposal of the existing fixtures and finishes is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/06/2017. | SUPERVISOR'S RESIDENCE | 9954 | Wildlife |  |  | Key Pittman WMA | 1959 | 1200 | 2017-04-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 40000
0904EXT1 | EXTERIOR FINISHES | 0904 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing of the concrete, and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/06/2017. | GRANARY | 9954 | Wildlife |  |  | Key Pittman WMA |  | 177 | 2017-04-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1770
0904SFT1 | EXTERIOR LANDING INSTALLATION | 0904 | Section 1008.1 of the 2018 IBC describes the requirements for doors including floor elevations and landings. The floor or landing shall be at the same elevation on each side of the door, the exterior landing shall not exceed a 2-percent slope and shall have a length measured in the direction of travel of not less than 44 inches. The landing for the door does not comply with this code and poses a safety hazard. This project would provide for the installation of a compliant landing for the door. | GRANARY | 9954 | Wildlife |  |  | Key Pittman WMA |  | 177 | 2017-04-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0903ENR2 | LIGHTING UPGRADE | 0903 | The existing lighting fixtures are the older incandescent type and are not energy efficient. This project will upgrade the fixtures to higher efficiency units with a longer life cycle. Compact fluorescent lamps are suggested. Electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/06/2017. | SUPERVISOR'S RESIDENCE | 9954 | Wildlife |  |  | Key Pittman WMA | 1959 | 1200 | 2017-04-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9600
0903EXT1 | EXTERIOR FINISHES | 0903 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing of the masonry, and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/06/2017. | SUPERVISOR'S RESIDENCE | 9954 | Wildlife |  |  | Key Pittman WMA | 1959 | 1200 | 2017-04-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
0903SFT1 | EXTERIOR STAIR REPLACEMENT | 0903 | The exterior concrete stairs near the garage do not comply with 2018 IBC Chapter 10. The treads and risers are not uniform in size and the stairway is missing handrails. This project would provide for the installation of a compliant stairway including handrails. Removal and disposal of the existing stairs is included in the estimate. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/06/2017. | SUPERVISOR'S RESIDENCE | 9954 | Wildlife |  |  | Key Pittman WMA | 1959 | 1200 | 2017-04-06 | Immediate to Two Years | Currently Critical | 1 | 9000
0903SFT2 | INTERIOR DOOR REPLACEMENT | 0903 | The door to the stairway leading to the basement swings out over the stairs. This is a safety hazard and does not comply with 2018 IBC Chapter 10. This project would provide for reversing the swing on the door. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/06/2017. | SUPERVISOR'S RESIDENCE | 9954 | Wildlife |  |  | Key Pittman WMA | 1959 | 1200 | 2017-04-06 | Immediate to Two Years | Currently Critical | 1 | 1000
0903ENR1 | WINDOW REPLACEMENT | 0903 | The windows are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 21 units and includes replacing the wood trim around each unit. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/06/2017. | SUPERVISOR'S RESIDENCE | 9954 | Wildlife |  |  | Key Pittman WMA | 1959 | 1200 | 2017-04-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 31500
0903HVA1 | HVAC EQUIPMENT REPLACEMENT | 0903 | The HVAC system is original to the building and should be scheduled for replacement. It is not energy efficient and has reached the end of its expected and useful life. The R-22 refrigerant in the cooling system is no longer EPA complaint and its production is mandated to be phased out completely by January 1, 2020. This project would provide for installation of a new HVAC system and cleaning of the existing duct work and grilles. This project includes the removal and disposal of the existing HVAC system and all required connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/06/2017. | SUPERVISOR'S RESIDENCE | 9954 | Wildlife |  |  | Key Pittman WMA | 1959 | 1200 | 2017-04-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0903PLM1 | WATER HEATER REPLACEMENT | 0903 | There is a 50 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | SUPERVISOR'S RESIDENCE | 9954 | Wildlife |  |  | Key Pittman WMA | 1959 | 1200 | 2017-04-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0904EXT2 | ROOF REPLACEMENT | 0904 | The roof framing and the corrugated metal roofing on this building were in poor condition at the time of the survey. The framing is rotted and many wood members are splitting. It is recommended that the framing and roofing be replaced in the next 2-3 years. This estimate includes removal and disposal of the old framing and roofing system. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/06/2017. | GRANARY | 9954 | Wildlife |  |  | Key Pittman WMA |  | 177 | 2017-04-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2655
0903INT3 | CONCRETE REPAIRS | 0903 | The concrete floor and walls in the basement are damaged from water infiltration and heaving. There are cracks and stains that should be repaired and cleaned. It is recommended that the concrete be cleaned and repaired in order to extend its useful life. This project would provide for cleaning the concrete, filling in the cracks, and applying a coat of sealant. It is recommended that this project be completed in the next 2-3 years. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/06/2017. | SUPERVISOR'S RESIDENCE | 9954 | Wildlife |  |  | Key Pittman WMA | 1959 | 1200 | 2017-04-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0903SFT3 | INTERIOR STAIR HANDRAIL REPLACEMENT | 0903 | The handrails for the stairway to the basement are older, not safe, and do not meet code. The gripping surfaces are incorrect and they are installed on only one side of the stairs. This project recommends the installation of handrails on both sides of the stairs, proper returns and supports in accordance with the 2018 IBC Chapter 10, Section 1012. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/06/2017. | SUPERVISOR'S RESIDENCE | 9954 | Wildlife |  |  | Key Pittman WMA | 1959 | 1200 | 2017-04-06 | Immediate to Two Years | Currently Critical | 1 | 12000
0903ENV1 | PEST CONTROL | 0903 | There are numerous rodent droppings throughout this building. Due to the potential risk of disease, this project provides for treatment and cleanup of the rodent droppings by a licensed pest control business. | SUPERVISOR'S RESIDENCE | 9954 | Wildlife |  |  | Key Pittman WMA | 1959 | 1200 | 2017-04-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
2127SFT6 | EXTERIOR LANDING INSTALLATION | 2127 | There is an exterior stairway at the rear of the building which does not have a landing. This does not comply with 2006 IBC Section 1008.1 which describes the requirements for landings including that the width of the landing shall not be less than the width of the stairway. This project addresses installing a landing designed to current code. | ELY WILDLIFE FIELD OFFICE | 9825 | Wildlife |  |  | Ely | 2000 | 1720 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
2127EXT2 | EXTERIOR FINISHES | 2127 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is cleaning and repairing the vinyl siding and caulking of the windows, painting, flashing, fixtures and all other penetrations. It is recommended that the building be cleaned, repaired and caulked in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | ELY WILDLIFE FIELD OFFICE | 9825 | Wildlife |  |  | Ely | 2000 | 1720 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8600
2127ADA1 | ADA SIGNAGE | 2127 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | ELY WILDLIFE FIELD OFFICE | 9825 | Wildlife |  |  | Ely | 2000 | 1720 | 2017-11-07 | Immediate to Two Years | Currently Critical | 1 | 600
2127INT1 | INTERIOR FINISHES | 2127 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | ELY WILDLIFE FIELD OFFICE | 9825 | Wildlife |  |  | Ely | 2000 | 1720 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8600
2127EXT1 | EXTERIOR SIDING REPLACEMENT | 2127 | This building has vinyl siding which is damaged and reaching the end of its useful life and should be scheduled for replacement. Some of the vinyl pieces are missing and others are cracked and warped. The siding is out of warranty and has been discontinued by the manufacturer. New siding will be required in the future to maintain the building in good weather tight condition. This project recommends removing the vinyl siding and replacing it with T1-11 panels finished with an oil-based stain or paint. Removal and disposal of the vinyl siding is including in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 06/03/2002. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | ELY WILDLIFE FIELD OFFICE | 9825 | Wildlife |  |  | Ely | 2000 | 1720 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25800
2231EXT1 | STABILIZE STRUCTURE | 2231 | The existing building is in poor condition. This project would provide for the sealing and protection of the exterior of the structure including roof and siding repairs and boarding up the large openings. It is recommended that this building be left in a state of arrested decay and not be used. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | CCC OFFICE | 9940 | Wildlife |  |  | Steptoe Valley | 1940 | 340 | 2017-11-07 | Four to Ten Years | Long-Term Needs | 3 | 1700
2228EXT1 | STABILIZE STRUCTURE | 2228 | The existing building is in poor condition. This project would provide for the sealing and protection of the exterior of the structure including roof and siding repairs and boarding up the large openings. It is recommended that this building be left in a state of arrested decay and not be used. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | HORSE BARN | 9940 | Wildlife |  |  | Steptoe Valley | 1930 | 3440 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 17200
2229EXT1 | STABILIZE STRUCTURE | 2229 | The existing building is in poor condition. This project would provide for the sealing and protection of the exterior of the structure including roof and siding repairs and boarding up the large openings. It is recommended that this building be left in a state of arrested decay and not be used. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | LOAFING SHED | 9940 | Wildlife |  |  | Steptoe Valley | 1930 | 1120 | 2017-11-07 | Four to Ten Years | Long-Term Needs | 3 | 5600
2127SFT4 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 2127 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2006 Chapter 10 was referenced for this project. | ELY WILDLIFE FIELD OFFICE | 9825 | Wildlife |  |  | Ely | 2000 | 1720 | 2017-11-07 | Immediate to Two Years | Currently Critical | 1 | 1000
2232EXT1 | STABILIZE STRUCTURE | 2232 | The existing building is in poor condition. This project would provide for the sealing and protection of the exterior of the structure including roof and siding repairs and boarding up the large openings. It is recommended that this building be left in a state of arrested decay and not be used. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | SHEARING SHED | 9940 | Wildlife |  |  | Steptoe Valley | 1920 | 1650 | 2017-11-07 | Four to Ten Years | Long-Term Needs | 3 | 8250
2127SFT1 | GFCI DUPLEX OUTLET REPLACEMENT | 2127 | One of the GFCI outlets in the restroom is damaged. The test and reset buttons did not work at the time of the survey which poses a safety hazard. This project would provide for the purchase and installation of a GFCI duplex outlet for the restroom. | ELY WILDLIFE FIELD OFFICE | 9825 | Wildlife |  |  | Ely | 2000 | 1720 | 2017-11-07 | Immediate to Two Years | Currently Critical | 1 | 300
2127SFT3 | FIRE SUPPRESSION SYSTEM INSTALLATION | 2127 | The building is a B occupancy per the 2006 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 or R-2 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. | ELY WILDLIFE FIELD OFFICE | 9825 | Wildlife |  |  | Ely | 2000 | 1720 | 2017-11-07 | Immediate to Two Years | Currently Critical | 1 | 12040
2127ENR1 | LIGHTING UPGRADE | 2127 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, conference rooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | ELY WILDLIFE FIELD OFFICE | 9825 | Wildlife |  |  | Ely | 2000 | 1720 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2580
2127PLM1 | WATER HEATER REPLACEMENT | 2127 | There is a 10 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new on-demand electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | ELY WILDLIFE FIELD OFFICE | 9825 | Wildlife |  |  | Ely | 2000 | 1720 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
2127SFT2 | FIRE ALARM SYSTEM INSTALLATION | 2127 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2006 Section 7 and the 2006 International Fire Code. | ELY WILDLIFE FIELD OFFICE | 9825 | Wildlife |  |  | Ely | 2000 | 1720 | 2017-11-07 | Immediate to Two Years | Currently Critical | 1 | 6880
2127ADA2 | ADA ACCESSIBLE COUNTER | 2127 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The front office has a service counter for the public to approach which does not meet current codes. Section 7.2 of the Americans with Disabilities Act Accessible Guidelines (ADAAG) states that the counter must have a portion which is at least 36" in length with a maximum height of 36" above the finish floor. This project will provide an accessible counter space in accordance with this requirement. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | ELY WILDLIFE FIELD OFFICE | 9825 | Wildlife |  |  | Ely | 2000 | 1720 | 2017-11-07 | Immediate to Two Years | Currently Critical | 1 | 1000
2230EXT2 | SIDING REPAIRS | 2230 | The wood siding on this building was in poor condition at the time of the survey. It is recommended that the wood siding be repaired in the next two to three years. The siding will require new wood planks in many areas but the existing wood should remain where possible. If any existing wood remains, the fasteners should be checked for security and replaced if needed. This estimate includes removal and disposal of the old siding. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | GRAIN STORAGE SHED | 9940 | Wildlife |  |  | Steptoe Valley | 1940 | 510 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1020
2239SFT2 | EXTERIOR LANDING INSTALLATION | 2239 | Section 1008.1 of the 2006 IBC describes the requirements for doors including floor elevations and landings. The floor or landing shall be at the same elevation on each side of the door, the exterior landing shall not exceed a 2-percent slope and shall have a length measured in the direction of travel of not less than 44 inches. The two exterior man doors do not have landings and pose a safety hazard. This project would provide for the installation of compliant landings for each door. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | BUNK HOUSE/STORAGE | 9940 | Wildlife |  |  | Steptoe Valley | 1970 | 350 | 2017-11-07 | Immediate to Two Years | Currently Critical | 1 | 500
2241EXT1 | EXTERIOR FINISHES | 2241 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. Also included is repairing the wood eaves and soffits as needed. It is recommended that the building be painted and repaired in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Please note that the siding appears to be a transite siding which may contain asbestos. Do not sand or otherwise disturb the siding without consulting a professional familiar with asbestos. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | STEPTOE VALLEY WMA OFFICE | 9940 | Wildlife |  |  | Steptoe Valley | 1930 | 1270 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19050
2241EXT2 | ROOF REPLACEMENT | 2241 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next one to two years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | STEPTOE VALLEY WMA OFFICE | 9940 | Wildlife |  |  | Steptoe Valley | 1930 | 1270 | 2017-11-07 | Immediate to Two Years | Currently Critical | 1 | 12700
2241ENR2 | WINDOW REPLACEMENT | 2241 | Some of the windows are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 5 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | STEPTOE VALLEY WMA OFFICE | 9940 | Wildlife |  |  | Steptoe Valley | 1930 | 1270 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3500
2241ENR1 | LIGHTING UPGRADE | 2241 | The existing lighting fixtures are the older incandescent or fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. Compact fluorescent lamps and F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, closets and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | STEPTOE VALLEY WMA OFFICE | 9940 | Wildlife |  |  | Steptoe Valley | 1930 | 1270 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1270
2241ADA1 | ADA ACCESSIBLE ENTRANCE UPGRADES | 2241 | The office is lacking an accessible entrance into the building and the existing stairs are not compliant with the building code. The building is open to the public during certain time periods and is also used as an office for Wildlife staff. This building is required to have an accessible entrance per the Americans with Disabilities Act (ADA) regulations. This project would provide for an accessible stairway, ramp and new door and hardware to provide access the building. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2003 were referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | STEPTOE VALLEY WMA OFFICE | 9940 | Wildlife |  |  | Steptoe Valley | 1930 | 1270 | 2017-11-07 | Immediate to Two Years | Currently Critical | 1 | 35000
2241INT2 | REPLACE BATHROOM FIXTURES | 2241 | The existing bathroom fixtures and finishes appear to be original and are in poor condition. This project would provide for the replacement of the bathroom fixtures including a toilet, sink, faucets and bathtub / shower combination unit. New flooring is included in this estimate. This bathroom would not need to be ADA accessible if the project for a new CXT comfort station is installed for public use adjacent to the office. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | STEPTOE VALLEY WMA OFFICE | 9940 | Wildlife |  |  | Steptoe Valley | 1930 | 1270 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
2240EXT1 | EXTERIOR FINISHES | 2240 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is cleaning the vinyl siding and caulking of the windows, flashing, fixtures and all other penetrations as well as repairing some damaged siding. It is recommended that the building be cleaned and caulked in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | RESIDENCE/BUNK HOUSE | 9940 | Wildlife |  |  | Steptoe Valley | 1970 | 920 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4600
2240INT1 | INTERIOR FINISHES | 2240 | The interior finishes are in fair condition. It is recommended that the interior walls and ceiling be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | RESIDENCE/BUNK HOUSE | 9940 | Wildlife |  |  | Steptoe Valley | 1970 | 920 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4600
2240EXT2 | ROOF REPLACEMENT | 2240 | The asphalt composition shingle roof on this building was in fair condition at the time of the survey. It is recommended that this building be re-roofed in the next two to three years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. | RESIDENCE/BUNK HOUSE | 9940 | Wildlife |  |  | Steptoe Valley | 1970 | 920 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9200
2241INT1 | INTERIOR FINISHES | 2241 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | STEPTOE VALLEY WMA OFFICE | 9940 | Wildlife |  |  | Steptoe Valley | 1930 | 1270 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6350
2240ENR1 | WINDOW REPLACEMENT | 2240 | The windows are original, dual pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 5 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | RESIDENCE/BUNK HOUSE | 9940 | Wildlife |  |  | Steptoe Valley | 1970 | 920 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3500
2236EXT1 | ROOF REPLACEMENT | 2236 | The rolled asphalt roofing on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next two to three years with new rolled asphalt roofing and new underlayments. This estimate includes removal and disposal of the old roofing. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | OLD GENERATOR/WOOD STORAGE BUILDING | 9940 | Wildlife |  |  | Steptoe Valley | 1950 | 350 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3500
2239EXT1 | ROOF REPLACEMENT | 2239 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next two to three years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | BUNK HOUSE/STORAGE | 9940 | Wildlife |  |  | Steptoe Valley | 1970 | 350 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3500
2238EXT2 | STABILIZE STRUCTURE | 2238 | The existing building is in poor condition. This project would provide for the sealing and protection of the exterior of the structure including roof and siding repairs and boarding up the large openings. It is recommended that this building be left in a state of arrested decay and not be used. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | EQUIPMENT STORAGE/GARAGE | 9940 | Wildlife |  |  | Steptoe Valley | 1940 | 710 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3550
2237EXT1 | DEMOLISH STRUCTURE | 2237 | The Log Dugout is over 100 years old and the structure has failed. The building is dilapidated and deteriorating and has reached the end of its useful life. This project would provide funding for the demolition of the building. Before demolition, the State Historic Preservation Office should be consulted due to the age of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | LOG DUGOUT | 9940 | Wildlife |  |  | Steptoe Valley | 1890 | 590 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5900
2236EXT2 | EXTERIOR FINISHES | 2236 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the masonry and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | OLD GENERATOR/WOOD STORAGE BUILDING | 9940 | Wildlife |  |  | Steptoe Valley | 1950 | 350 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1750
2230EXT1 | ROOF REPAIRS | 2230 | The corrugated metal roof on this building was in poor condition at the time of the survey. The temperature fluctuations throughout the year and consistent wind which blows the panels off are contributing factors to wear and deterioration. It is recommended that the corrugated roof be repaired in the next two to three years. The roof will require new corrugated panels in many areas but the existing panels should remain where possible. If any existing panels remain, the fasteners should be checked for security and replaced if needed. This estimate includes removal and disposal of the old roofing as required. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | GRAIN STORAGE SHED | 9940 | Wildlife |  |  | Steptoe Valley | 1940 | 510 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2550
2234EXT1 | STABILIZE STRUCTURE | 2234 | The existing building is in poor condition. This project would provide for the sealing and protection of the exterior of the structure including roof and siding repairs and boarding up the large openings. It is recommended that this building be left in a state of arrested decay and not be used. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | ICE HOUSE | 9940 | Wildlife |  |  | Steptoe Valley | 1930 | 200 | 2017-11-07 | Four to Ten Years | Long-Term Needs | 3 | 1000
2233EXT1 | EXTERIOR FINISHES | 2233 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is the caulking and sealing of the doors, windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | SHOP BUILDING | 9940 | Wildlife |  |  | Steptoe Valley | 1980 | 1200 | 2017-11-07 | Four to Ten Years | Long-Term Needs | 3 | 2400
2233SFT1 | EXTERIOR LANDING INSTALLATION | 2233 | Section 1008.1 of the 2006 IBC describes the requirements for doors including floor elevations and landings. The floor or landing shall be at the same elevation on each side of the door, the exterior landing shall not exceed a 2-percent slope and shall have a length measured in the direction of travel equal to or greater that the size of the door. The exterior man door does not have a landing and poses a safety hazard. This project would provide for the installation of a building code compliant landing for the door. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | SHOP BUILDING | 9940 | Wildlife |  |  | Steptoe Valley | 1980 | 1200 | 2017-11-07 | Immediate to Two Years | Currently Critical | 1 | 250
2233SIT1 | CONCRETE APRON INSTALLATION | 2233 | The vehicle garage door does not have an exterior concrete apron. The dirt in front of the door gets muddy and rutted requiring constant maintenance. This project would provide for the installation of a new 4" thick concrete slab-on-grade apron at the vehicle garage door. 200 square feet of concrete was used to generate this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | SHOP BUILDING | 9940 | Wildlife |  |  | Steptoe Valley | 1980 | 1200 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
2233ENR1 | WINDOW REPLACEMENT | 2233 | The windows are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 4 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | SHOP BUILDING | 9940 | Wildlife |  |  | Steptoe Valley | 1980 | 1200 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
2240INT2 | FLOORING REPLACEMENT | 2240 | The VCT (vinyl composite tile) and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the next two to three years. Additional costs have been added for abatement of any asbestos containing materials that may be present. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | RESIDENCE/BUNK HOUSE | 9940 | Wildlife |  |  | Steptoe Valley | 1970 | 920 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6440
2235EXT1 | STABILIZE STRUCTURE | 2235 | The existing building is in poor condition. This project would provide for the sealing and protection of the exterior of the structure including roof and siding repairs and boarding up the large openings. It is recommended that this building be left in a state of arrested decay and not be used. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | LOG CABIN | 9940 | Wildlife |  |  | Steptoe Valley | 1890 | 430 | 2017-11-07 | Four to Ten Years | Long-Term Needs | 3 | 2150
9825SIT5 | WEED ABATEMENT | 9825 | The site has areas that are covered with weeds especially in the rear storage area. This project would provide for the removal and disposal of the weeds on the site and treatment of the area with an herbicide to prevent future weed growth. | ELY WILDLIFE FIELD OFFICE SITE | 9825 | Wildlife |  |  | Ely | 2000 |  | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
9825ADA1 | ADA PARKING SIGN REPLACEMENT | 9825 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria and the existing parking sign is outdated. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances and replacing the parking sign. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | ELY WILDLIFE FIELD OFFICE SITE | 9825 | Wildlife |  |  | Ely | 2000 |  | 2017-11-07 | Immediate to Two Years | Currently Critical | 1 | 1500
9933SIT1 | WEED ABATEMENT | 9933 | Most of the site is covered with weeds. This project would provide for the removal and disposal of the weeds on the site and treatment of the area with an herbicide to control future weed growth. | ELY WILDLIFE OLD FIELD OFFICE SITE | 9933 | Wildlife |  |  | Ely |  |  | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
9940ENV1 | CXT COMFORT STATION INSTALLATION | 9940 | The Office area and several of the parking areas on the north side of the site do not have public restrooms. Given the distance of these locations from existing restroom facilities, health concerns exist due to visitors not using the restroom facilities at other areas. It is recommended that CXT or similar style unisex comfort stations be installed which meet current ADA requirements. This project would provide for the purchase and installation of three unisex CXT restrooms including an ADA compliant concrete parking and loading zone adjacent to the restrooms. One of the comfort stations is proposed to be installed adjacent to the office and should be coordinated with the ADA accessible parking proposed project. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | STEPTOE VALLEY WMA SITE | 9940 | Wildlife |  |  | Steptoe Valley |  |  | 2017-11-07 | Immediate to Two Years | Currently Critical | 1 | 60000
9825SIT1 | SEAL ASPHALT PAVING | 9825 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the paving site wide including the access roads and parking lot. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 10,000 square feet of asphalt area was used to generate this estimate. | ELY WILDLIFE FIELD OFFICE SITE | 9825 | Wildlife |  |  | Ely | 2000 |  | 2017-11-07 | Immediate to Two Years | Currently Critical | 1 | 5000
9940SFT1 | SAFETY SIGNAGE FOR OUTBUILDINGS | 9940 | For security and safety purposes it is recommended to install "Authorized Personnel Only" signs throughout the site. Signs should be placed at all outbuildings to encourage visitors to stay out. Many of the outbuildings are structurally unsound and some are historic. It should be encouraged to protect these buildings from vandalism or theft of materials. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | STEPTOE VALLEY WMA SITE | 9940 | Wildlife |  |  | Steptoe Valley |  |  | 2017-11-07 | Immediate to Two Years | Currently Critical | 1 | 5000
9940SIT1 | ACCESS ROAD REPAIRS | 9940 | It is important to maintain the dirt and gravel access roads on the site. Several stretches of road are washed-out or are deeply rutted making it difficult to access all the areas of the site and altering established drainage flows. This project would provide for purchasing type 2 sub-base material and grading the roads where needed. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the roads and prevent premature failure. 5,000 square yards of road area was used to generate this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | STEPTOE VALLEY WMA SITE | 9940 | Wildlife |  |  | Steptoe Valley |  |  | 2017-11-07 | Four to Ten Years | Long-Term Needs | 3 | 125000
9825SIT6 | CONSTRUCT STORAGE BUILDING | 9825 | There is a major lack of storage on the site to support the various functions conducted by the Wildlife staff. Game evidence is currently stored outside which does not preserve the evidence properly and presents a theft opportunity. Testing equipment, storage and supplies are stored in temporary metal containers at the rear of the site which are difficult to access and provide little security. A new storage building would also provide space for lab activities. Dissections and other lab work are currently taking place in the existing office which is not designed for this activity. This project would provide for the purchase and installation of a 40' x 60' engineered steel building on a concrete foundation including connection to the existing electrical, water, sewer and propane services. | ELY WILDLIFE FIELD OFFICE SITE | 9825 | Wildlife |  |  | Ely | 2000 |  | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 84000
9825SIT2 | EXTERIOR SOLAR SITE LIGHTING INSTALLATION | 9825 | There is no site lighting for the access road and parking area which is a security and safety concern. This project would provide for the installation of 4 solar powered LED exterior light fixtures, 20 foot tall poles and 30" diameter raised concrete bases. This installation will eliminate the need for trenching and electrical connections. | ELY WILDLIFE FIELD OFFICE SITE | 9825 | Wildlife |  |  | Ely | 2000 |  | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 26000
9825SIT4 | CARPORT STRUCTURE INSTALLATION | 9825 | There are approximately 10 state vehicles parked in the rear parking area at any given time including trucks, boats, trailers and quads. Some of these vehicles carry sensitive measuring and testing equipment which can deteriorate quickly due to exposure to the elements. This project would provide a steel carport capable of protecting 10 vehicles to be built on the east side of the site. | ELY WILDLIFE FIELD OFFICE SITE | 9825 | Wildlife |  |  | Ely | 2000 |  | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
9825SIT3 | VEHICLE GATE REPLACEMENT | 9825 | The site has a perimeter fence with a vehicle access gate to the south of the building. The manual sliding gate is not operating properly especially in the colder winter months. It is less than 20 feet wide which does not comply with the fire code. This project recommends the gates be upgraded to a motorized track system that can handle the freezing winter temperatures and meets the requirements of the fire code. The gates will be required to meet UL Standard 325, per NRS 405.270 and section 503.2.1 of the 2006 International Fire Code. | ELY WILDLIFE FIELD OFFICE SITE | 9825 | Wildlife |  |  | Ely | 2000 |  | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
9940ADA1 | ADA ACCESSIBLE PARKING | 9940 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. A concrete parking area and passenger loading area are necessary to comply with ADA requirements. This project would provide for a concrete van accessible ADA parking and loading space and walkway to the Office. This will require regrading, installing P.C. concrete, striping, signage and any other necessary upgrades. 500 square feet of P.C. concrete was used to generate this estimate. This project should coincide with the WMA Office ADA entrance project. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2003 were referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | STEPTOE VALLEY WMA SITE | 9940 | Wildlife |  |  | Steptoe Valley |  |  | 2017-11-07 | Immediate to Two Years | Currently Critical | 1 | 5000
9933SIT2 | ASPHALT PAVING INSTALLATION | 9933 | The access road and parking areas on the site are not paved. Any existing concrete or asphalt paving has deteriorated to the point of complete failure. This project would provide asphalt cement paving for a 20' wide access road and parking spaces. The estimate includes grading, 6" base, compaction and installation of 4" thick asphalt cement paving. | ELY WILDLIFE OLD FIELD OFFICE SITE | 9933 | Wildlife |  |  | Ely |  |  | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 37500
3023EXT1 | EXTERIOR/ INTERIOR FINISHES | 3023 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | COMMINS LAKE CXT RESTROOM #1 | 9940 | Wildlife |  |  | Steptoe Valley | 0 | 84 | 2017-11-07 | Four to Ten Years | Long-Term Needs | 3 | 840
3027SFT1 | SAFETY CABINETS | 3027 | The storage building contains many different paints, stains, pesticides and other hazardous products on open shelves and on the floor. This does not meet OSHA standards for hazardous materials containment. This project would provide two hazardous storage containers in the building and install placards on the building exterior in accordance with OSHA 1910.106 (d). This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | STORAGE BUILDING | 9940 | Wildlife |  |  | Steptoe Valley | 0 | 336 | 2017-11-07 | Immediate to Two Years | Currently Critical | 1 | 5000
3027EXT1 | EXTERIOR FINISHES | 3027 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations. Also, it is recommended that the earth to metal contact be removed to prevent premature failure of the siding. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | STORAGE BUILDING | 9940 | Wildlife |  |  | Steptoe Valley | 0 | 336 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 672
3026EXT1 | EXTERIOR/ INTERIOR FINISHES | 3026 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | COMMINS LAKE CXT RESTROOM #4 | 9940 | Wildlife |  |  | Steptoe Valley | 0 | 84 | 2017-11-07 | Four to Ten Years | Long-Term Needs | 3 | 840
3024EXT1 | EXTERIOR/ INTERIOR FINISHES | 3024 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | COMMINS LAKE CXT RESTROOM #2 | 9940 | Wildlife |  |  | Steptoe Valley | 0 | 84 | 2017-11-07 | Four to Ten Years | Long-Term Needs | 3 | 840
3025EXT1 | EXTERIOR/ INTERIOR FINISHES | 3025 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | COMMINS LAKE CXT RESTROOM #3 | 9940 | Wildlife |  |  | Steptoe Valley | 0 | 84 | 2017-11-07 | Four to Ten Years | Long-Term Needs | 3 | 840
0635EXT2 | WINDOW REPLACEMENT | 0635 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 10 units. Removal and disposal of the existing windows is included in this estimate. | OLD WILDLIFE ADMINISTRATIVE OFFICE | 9933 | Wildlife |  |  | Ely | 1955 | 1440 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
0636SFT2 | EXTERIOR LANDING INSTALLATION | 0636 | Section 1008.1 of the 2006 IBC describes the requirements for doors including floor elevations and landings. The floor or landing shall be at the same elevation on each side of the door, the exterior landing shall not exceed a 2-percent slope and shall have a length measured in the direction of travel of not less than 44 inches. The landing at the door on the north side of the building does not comply with this code and poses a safety hazard. This project would provide for the installation of a compliant landing for the door. | WILDLIFE STORAGE/GARAGE | 9933 | Wildlife |  |  | Ely | 1950 | 768 | 2017-11-07 | Immediate to Two Years | Currently Critical | 1 | 1000
0635ADA1 | ADA SIGNAGE | 0635 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | OLD WILDLIFE ADMINISTRATIVE OFFICE | 9933 | Wildlife |  |  | Ely | 1955 | 1440 | 2017-11-07 | Immediate to Two Years | Currently Critical | 1 | 500
0636EXT3 | OVERHEAD DOOR REPLACEMENT | 0636 | There are two 10'x10' overhead doors which are damaged and do not function properly. Exposure and wind have caused the doors to bend, crack and lose their finish. They are original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead doors and replacement with new manually operated coiling doors. | WILDLIFE STORAGE/GARAGE | 9933 | Wildlife |  |  | Ely | 1950 | 768 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
0636EXT2 | EXTERIOR DOOR REPLACEMENT | 0636 | The exterior metal man door is damaged from age and general wear and tear and has reached the end of its expected life. This project would provide for the replacement of the door assembly with a new metal door, frame and hardware. Removal and disposal of the existing door is included in this estimate. | WILDLIFE STORAGE/GARAGE | 9933 | Wildlife |  |  | Ely | 1950 | 768 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0635EXT3 | EXTERIOR DOOR REPLACEMENT | 0635 | The 3 exterior wood doors appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement of the wood doors with new metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | OLD WILDLIFE ADMINISTRATIVE OFFICE | 9933 | Wildlife |  |  | Ely | 1955 | 1440 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
0635ENR1 | LIGHTING UPGRADE | 0635 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, conference rooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | OLD WILDLIFE ADMINISTRATIVE OFFICE | 9933 | Wildlife |  |  | Ely | 1955 | 1440 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2160
0635INT3 | INTERIOR DOOR REPLACEMENT | 0635 | The interior doors in this building are hollow core units and are damaged or missing altogether. This project would provide for the installation of new solid core interior doors including frames, lever action door handles, hardware and paint. Removal and disposal of the existing doors is included in this cost estimate. A total of 5 interior doors was used in this estimate. | OLD WILDLIFE ADMINISTRATIVE OFFICE | 9933 | Wildlife |  |  | Ely | 1955 | 1440 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0635ELE1 | ELECTRICAL UPGRADE | 0635 | This building was constructed before the high demand for electrical services were needed for computers and other electrical devices. As time has progressed, the buildings electrical demand and system has changed. If occupied, it would be utilized to its current maximum potential. The electrical panels and receptacles would be at their limit. It is recommended the entire system be upgraded to meet the evolving needs of the building. | OLD WILDLIFE ADMINISTRATIVE OFFICE | 9933 | Wildlife |  |  | Ely | 1955 | 1440 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 28800
0636SFT1 | FIRE ALARM SYSTEM INSTALLATION | 0636 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2006 Section 7 and the 2006 International Fire Code. | WILDLIFE STORAGE/GARAGE | 9933 | Wildlife |  |  | Ely | 1950 | 768 | 2017-11-07 | Immediate to Two Years | Currently Critical | 1 | 3072
0636EXT1 | EXTERIOR FINISHES | 0636 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | WILDLIFE STORAGE/GARAGE | 9933 | Wildlife |  |  | Ely | 1950 | 768 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
0635SFT2 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0635 | The building is a B occupancy per the 2006 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 or R-2 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. | OLD WILDLIFE ADMINISTRATIVE OFFICE | 9933 | Wildlife |  |  | Ely | 1955 | 1440 | 2017-11-07 | Immediate to Two Years | Currently Critical | 1 | 10080
0635ENV1 | UNDERGROUND TANK REMOVAL | 0635 | At the south exterior wall there is an underground heating oil fuel tank that is no longer needed because new propane-fired equipment will be installed. This project allows for removal of the underground tank and associated soils surrounding the installation. | OLD WILDLIFE ADMINISTRATIVE OFFICE | 9933 | Wildlife |  |  | Ely | 1955 | 1440 | 2017-11-07 | Immediate to Two Years | Currently Critical | 1 | 15000
0635SFT4 | EXTERIOR LANDING INSTALLATION | 0635 | Section 1008.1 of the 2006 IBC describes the requirements for doors including floor elevations and landings. The floor or landing shall be at the same elevation on each side of the door, the exterior landing shall not exceed a 2-percent slope and shall have a length measured in the direction of travel of not less than 44 inches. The two doors on the east side of the building do not comply with this code and pose a safety hazard. This project would provide for the installation of a compliant landing for each door. | OLD WILDLIFE ADMINISTRATIVE OFFICE | 9933 | Wildlife |  |  | Ely | 1955 | 1440 | 2017-11-07 | Immediate to Two Years | Currently Critical | 1 | 2000
0635SFT1 | FIRE ALARM SYSTEM INSTALLATION | 0635 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2006 Section 7 and the 2006 International Fire Code. | OLD WILDLIFE ADMINISTRATIVE OFFICE | 9933 | Wildlife |  |  | Ely | 1955 | 1440 | 2017-11-07 | Immediate to Two Years | Currently Critical | 1 | 5760
0635HVA1 | HVAC EQUIPMENT REPLACEMENT | 0635 | The oil fired furnace is original to the building and is no longer operational. There is no other HVAC equipment in the building. This project would provide for installation of a new HVAC packaged unit to provide heating and cooling, cleaning of the existing duct work and replacement of the vent grilles. This project includes removal and disposal of the existing furnace and all required connections to utilities. Propane gas service will be required and is included in the cost. | OLD WILDLIFE ADMINISTRATIVE OFFICE | 9933 | Wildlife |  |  | Ely | 1955 | 1440 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 28800
0635INT2 | FLOORING REPLACEMENT | 0635 | The VCT (vinyl composite tile) and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the next 2-3 years. The flooring should be tested for asbestos containing materials (ACM) and additional costs should be added if it is necessary to abate it. | OLD WILDLIFE ADMINISTRATIVE OFFICE | 9933 | Wildlife |  |  | Ely | 1955 | 1440 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11520
0635PLM1 | PLUMBING SYSTEM REPLACEMENT | 0635 | The plumbing and waste system is older and in poor condition. Most of the system appears to be original to the building and should be scheduled for replacement. This project recommends replacing all of the water and sewer lines, the plumbing fixtures and the septic system. This estimate includes removal and disposal of the existing system as required. | OLD WILDLIFE ADMINISTRATIVE OFFICE | 9933 | Wildlife |  |  | Ely | 1955 | 1440 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
0635EXT4 | OVERHEAD DOOR REPLACEMENT | 0635 | There are two 8'x8' overhead doors on the east side of the building which are damaged and do not function properly. They are original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead doors and replacement with two new manually operated overhead doors. Removal and disposal of the existing doors is included in this estimate. | OLD WILDLIFE ADMINISTRATIVE OFFICE | 9933 | Wildlife |  |  | Ely | 1955 | 1440 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
0635EXT1 | EXTERIOR FINISHES | 0635 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls, wood trim and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | OLD WILDLIFE ADMINISTRATIVE OFFICE | 9933 | Wildlife |  |  | Ely | 1955 | 1440 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7200
0635INT1 | INTERIOR FINISHES | 0635 | The interior finishes are in fair to poor condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | OLD WILDLIFE ADMINISTRATIVE OFFICE | 9933 | Wildlife |  |  | Ely | 1955 | 1440 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7200
0635INT4 | CEILING REPLACEMENT | 0635 | The ceiling in the building is covered with acoustical ceiling tiles. The ceiling tiles are damaged and stained and some are coming loose from the substrate. This project would provide for the replacement of the ceiling tiles. Removal and disposal of the existing tiles is included in this estimate. The ceiling tiles and adhesive should be tested for asbestos containing materials (ACM) and additional costs should be added if it is necessary to abate it. | OLD WILDLIFE ADMINISTRATIVE OFFICE | 9933 | Wildlife |  |  | Ely | 1955 | 1440 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7200
0635SFT3 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0635 | There are no emergency egress lights or exit signs in the building. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2006 Chapter 10 was referenced for this project. | OLD WILDLIFE ADMINISTRATIVE OFFICE | 9933 | Wildlife |  |  | Ely | 1955 | 1440 | 2017-11-07 | Immediate to Two Years | Currently Critical | 1 | 1000
1667INT4 | KITCHEN REMODEL | 1667 | The kitchen is in fair to poor condition. The cabinets and equipment are showing signs of general wear and tear and are approaching the end of their expected life. This project recommends the replacement of the existing kitchen cabinets, counters, fixtures and equipment with mid range, high quality components. | HATCHERY RESIDENCE 2 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Four to Ten Years | Long-Term Needs | 3 | 35000
1667PLM1 | WATER HEATER REPLACEMENT | 1667 | There is a 50 gallon propane-fired water heater in the garage. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 3-4 years. It is recommended that a new propane-fired water heater be installed. | HATCHERY RESIDENCE 2 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1750
1667HVA1 | HVAC EQUIPMENT REPLACEMENT | 1667 | The HVAC system consists of a roof top evaporative cooler and gas fired furnace in the garage. These units are original to the building, installed in 1990. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installing new HVAC units and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | HATCHERY RESIDENCE 2 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 29580
1668EXT2 | REPLACE ROOF | 1668 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next one to two years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. This project or a portion thereof was previously recommended in the FCA report dated 08/09/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | HATCHERY RESIDENCE 3 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Immediate to Two Years | Currently Critical | 1 | 29580
1668EXT5 | WINDOW REPLACEMENT | 1668 | The windows are original, dual pane construction in a metal frame. These older windows are not energy efficient and many have broken seals. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 11 units. Removal and disposal of the existing windows is included in this estimate. | HATCHERY RESIDENCE 3 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11000
1668INT3 | REPLACE FLOOR COVERING | 1668 | The carpet and vinyl flooring in the building is damaged and reaching the end of its useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new carpet and vinyl flooring. This project or a portion thereof was previously recommended in the FCA report dated 08/09/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | HATCHERY RESIDENCE 3 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15776
1668INT1 | INTERIOR FINISHES | 1668 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 08/09/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | HATCHERY RESIDENCE 3 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9860
1668EXT4 | GUTTER INSTALLATION | 1668 | The building does not have gutters or downspouts to control the runoff from the roof. The water currently sheet drains off the roof causing erosion to the grade and damage to the siding. This project would provide funding for the installation of a seamless gutter and downspout system for the building. | HATCHERY RESIDENCE 3 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
1667EXT5 | WINDOW REPLACEMENT | 1667 | The windows are original, dual pane construction in a metal frame. These older windows are not energy efficient and many have broken seals. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 11 units. Removal and disposal of the existing windows is included in this estimate. | HATCHERY RESIDENCE 2 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11000
1668EXT3 | REMOVE SPRINKLERED LAWN WITHIN 3' OF BUILDING | 1668 | The house has considerable damage to the siding from lawn sprinklers wetting the siding. This project would create drip irrigated planters within three feet of the house and relocate sprinklers so they do not wet the house. Backflow prevention devices would be enclosed in a heated enclosure to prevent freezing. Existing hose bibs upstream of the backflow preventers would be relocated downstream of the valve. This project or a portion thereof was previously recommended in the FCA report dated 08/09/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | HATCHERY RESIDENCE 3 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
1667EXT4 | GUTTER INSTALLATION | 1667 | The building does not have gutters or downspouts to control the runoff from the roof. The water currently sheet drains off the roof causing erosion to the grade and damage to the siding. This project would provide funding for the installation of a seamless gutter and downspout system for the building. | HATCHERY RESIDENCE 2 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
1667INT3 | REPLACE FLOOR COVERING | 1667 | The carpet and vinyl flooring in the building is damaged and reaching the end of its useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new carpet and vinyl flooring. This project or a portion thereof was previously recommended in the FCA report dated 08/09/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | HATCHERY RESIDENCE 2 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15776
1667EXT1 | EXTERIOR FINISHES | 1667 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 08/09/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | HATCHERY RESIDENCE 2 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19720
1667INT1 | INTERIOR FINISHES | 1667 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 08/09/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | HATCHERY RESIDENCE 2 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9860
1667EXT2 | REPLACE ROOF | 1667 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next one to two years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. This project or a portion thereof was previously recommended in the FCA report dated 08/09/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | HATCHERY RESIDENCE 2 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Immediate to Two Years | Currently Critical | 1 | 29580
1667INT2 | RESTROOM REMODEL | 1667 | The two restrooms in the residence are original to the building and in overall poor condition. The finishes, fixtures, cabinets, toilets, showers and exhaust fans are showing signs of wear and deterioration. This project would provide for a complete remodel of the restrooms. The removal and disposal of the existing fixtures and finishes is included in this estimate. | HATCHERY RESIDENCE 2 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
1666PLM1 | WATER HEATER REPLACEMENT | 1666 | There is a 50 gallon propane-fired water heater in the garage. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 3-4 years. It is recommended that a new propane-fired water heater be installed. | HATCHERY RESIDENCE 1 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1750
1666HVA1 | HVAC EQUIPMENT REPLACEMENT | 1666 | The HVAC system consists of a roof top evaporative cooler and gas fired furnace in the garage. These units are original to the building, installed in 1990. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installing new HVAC units and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | HATCHERY RESIDENCE 1 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 29580
1666INT4 | KITCHEN REMODEL | 1666 | The kitchen is in fair to poor condition. The cabinets and equipment are showing signs of general wear and tear and are approaching the end of their expected life. This project recommends the replacement of the existing kitchen cabinets, counters, fixtures and equipment with mid range, high quality components. | HATCHERY RESIDENCE 1 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Four to Ten Years | Long-Term Needs | 3 | 35000
1666EXT5 | WINDOW REPLACEMENT | 1666 | The windows are original, dual pane construction in a metal frame. These older windows are not energy efficient and many have broken seals. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 11 units. Removal and disposal of the existing windows is included in this estimate. | HATCHERY RESIDENCE 1 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11000
1666EXT1 | EXTERIOR FINISHES | 1666 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 08/09/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | HATCHERY RESIDENCE 1 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19720
1666INT2 | RESTROOM REMODEL | 1666 | The two restrooms in the residence are original to the building and in overall poor condition. The finishes, fixtures, cabinets, toilets, showers and exhaust fans are showing signs of wear and deterioration. This project would provide for a complete remodel of the restrooms. The removal and disposal of the existing fixtures and finishes is included in this estimate. | HATCHERY RESIDENCE 1 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
1666INT1 | INTERIOR FINISHES | 1666 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 08/09/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | HATCHERY RESIDENCE 1 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9860
1667EXT3 | REMOVE SPRINKLERED LAWN WITHIN 3' OF BUILDING | 1667 | The house has considerable damage to the siding from lawn sprinklers wetting the siding. This project would create drip irrigated planters within three feet of the house and relocate sprinklers so they do not wet the house. Backflow prevention devices would be enclosed in a heated enclosure to prevent freezing. Existing hose bibs upstream of the backflow preventers would be relocated downstream of the valve. This project or a portion thereof was previously recommended in the FCA report dated 08/09/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | HATCHERY RESIDENCE 2 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
1669PLM1 | WATER HEATER REPLACEMENT | 1669 | There is a 50 gallon propane-fired water heater in the garage. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 3-4 years. It is recommended that a new propane-fired water heater be installed. | HATCHERY RESIDENCE 4 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1750
1670HVA1 | HVAC EQUIPMENT REPLACEMENT | 1670 | The HVAC system consists of a roof top evaporative condenser and gas fired furnace in the garage. These units are original to the building, installed in 1990. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installing new HVAC units and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | HATCHERY RESIDENCE 5 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 29580
1670INT4 | KITCHEN REMODEL | 1670 | The kitchen is in fair to poor condition. The cabinets and equipment are showing signs of general wear and tear and are approaching the end of their expected life. This project recommends the replacement of the existing kitchen cabinets, counters, fixtures and equipment with mid range, high quality components. | HATCHERY RESIDENCE 5 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Four to Ten Years | Long-Term Needs | 3 | 35000
1670INT2 | RESTROOM REMODEL | 1670 | The two restrooms in the residence are original to the building and in overall poor condition. The finishes, fixtures, cabinets, toilets, showers and exhaust fans are showing signs of wear and deterioration. This project would provide for a complete remodel of the restrooms. The removal and disposal of the existing fixtures and finishes is included in this estimate. | HATCHERY RESIDENCE 5 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
1670INT1 | INTERIOR FINISHES | 1670 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 08/09/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | HATCHERY RESIDENCE 5 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9860
1670EXT2 | REPLACE ROOF | 1670 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next one to two years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. This project or a portion thereof was previously recommended in the FCA report dated 08/09/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | HATCHERY RESIDENCE 5 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Immediate to Two Years | Currently Critical | 1 | 29580
1670EXT1 | EXTERIOR FINISHES | 1670 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 08/09/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | HATCHERY RESIDENCE 5 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19720
1670EXT3 | REMOVE SPRINKLERED LAWN WITHIN 3' OF BUILDING | 1670 | The house has considerable damage to the siding from lawn sprinklers wetting the siding. This project would create drip irrigated planters within three feet of the house and relocate sprinklers so they do not wet the house. Backflow prevention devices would be enclosed in a heated enclosure to prevent freezing. Existing hose bibs upstream of the backflow preventers would be relocated downstream of the valve. This project or a portion thereof was previously recommended in the FCA report dated 08/09/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | HATCHERY RESIDENCE 5 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
1670EXT4 | GUTTER INSTALLATION | 1670 | The building does not have gutters or downspouts to control the runoff from the roof. The water currently sheet drains off the roof causing erosion to the grade and damage to the siding. This project would provide funding for the installation of a seamless gutter and downspout system for the building. | HATCHERY RESIDENCE 5 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
1670INT3 | REPLACE FLOOR COVERING | 1670 | The carpet and vinyl flooring in the building is damaged and reaching the end of its useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new carpet and vinyl flooring. This project or a portion thereof was previously recommended in the FCA report dated 08/09/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | HATCHERY RESIDENCE 5 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15776
1670EXT5 | WINDOW REPLACEMENT | 1670 | The windows are original, dual pane construction in a metal frame. These older windows are not energy efficient and many have broken seals. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 11 units. Removal and disposal of the existing windows is included in this estimate. | HATCHERY RESIDENCE 5 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11000
1668PLM1 | WATER HEATER REPLACEMENT | 1668 | There is a 50 gallon propane-fired water heater in the garage. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 3-4 years. It is recommended that a new propane-fired water heater be installed. | HATCHERY RESIDENCE 3 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1750
1669HVA1 | HVAC EQUIPMENT REPLACEMENT | 1669 | The HVAC system consists of a roof top evaporative cooler and gas fired furnace in the garage. These units are original to the building, installed in 1990. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installing new HVAC units and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | HATCHERY RESIDENCE 4 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 29580
1668EXT1 | EXTERIOR FINISHES | 1668 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 08/09/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | HATCHERY RESIDENCE 3 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19720
1669INT4 | KITCHEN REMODEL | 1669 | The kitchen is in fair to poor condition. The cabinets and equipment are showing signs of general wear and tear and are approaching the end of their expected life. This project recommends the replacement of the existing kitchen cabinets, counters, fixtures and equipment with mid range, high quality components. | HATCHERY RESIDENCE 4 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Four to Ten Years | Long-Term Needs | 3 | 35000
1669INT3 | REPLACE FLOOR COVERING | 1669 | The carpet and vinyl flooring in the building is damaged and reaching the end of its useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new carpet and vinyl flooring. This project or a portion thereof was previously recommended in the FCA report dated 08/09/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | HATCHERY RESIDENCE 4 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15776
1669INT1 | INTERIOR FINISHES | 1669 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 08/09/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | HATCHERY RESIDENCE 4 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9860
1669EXT3 | REMOVE SPRINKLERED LAWN WITHIN 3' OF BUILDING | 1669 | The house has considerable damage to the siding from lawn sprinklers wetting the siding. This project would create drip irrigated planters within three feet of the house and relocate sprinklers so they do not wet the house. Backflow prevention devices would be enclosed in a heated enclosure to prevent freezing. Existing hose bibs upstream of the backflow preventers would be relocated downstream of the valve. This project or a portion thereof was previously recommended in the FCA report dated 08/09/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | HATCHERY RESIDENCE 4 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
1669EXT5 | WINDOW REPLACEMENT | 1669 | The windows are original, dual pane construction in a metal frame. These older windows are not energy efficient and many have broken seals. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 11 units. Removal and disposal of the existing windows is included in this estimate. | HATCHERY RESIDENCE 4 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11000
1669EXT2 | REPLACE ROOF | 1669 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next one to two years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. This project or a portion thereof was previously recommended in the FCA report dated 08/09/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | HATCHERY RESIDENCE 4 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Immediate to Two Years | Currently Critical | 1 | 29580
1668INT4 | KITCHEN REMODEL | 1668 | The kitchen is in fair to poor condition. The cabinets and equipment are showing signs of general wear and tear and are approaching the end of their expected life. This project recommends the replacement of the existing kitchen cabinets, counters, fixtures and equipment with mid range, high quality components. | HATCHERY RESIDENCE 3 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Four to Ten Years | Long-Term Needs | 3 | 35000
1668INT2 | RESTROOM REMODEL | 1668 | The two restrooms in the residence are original to the building and in overall poor condition. The finishes, fixtures, cabinets, toilets, showers and exhaust fans are showing signs of wear and deterioration. This project would provide for a complete remodel of the restrooms. The removal and disposal of the existing fixtures and finishes is included in this estimate. | HATCHERY RESIDENCE 3 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
1664EXT2 | ROOF REPLACEMENT | 1664 | The roof on this building was in poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 15 years. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof, and constant exposure to the sun are contributing factors to wear and deterioration. The current rolled asphalt roof was installed in 1990. It is recommended that this building be re-roofed with a single-ply roofing system in the next 2-3 years to be consistent with the roofing program. | HATCHERY WATER WELL PUMP HOUSE C2 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 256 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3840
1668HVA1 | HVAC EQUIPMENT REPLACEMENT | 1668 | The HVAC system consists of a roof top evaporative condenser and gas fired furnace in the garage. These units are original to the building, installed in 1990. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installing new HVAC units and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | HATCHERY RESIDENCE 3 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 29580
1666EXT2 | REPLACE ROOF | 1666 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next one to two years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. This project or a portion thereof was previously recommended in the FCA report dated 08/09/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | HATCHERY RESIDENCE 1 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Immediate to Two Years | Currently Critical | 1 | 29580
1669INT2 | RESTROOM REMODEL | 1669 | The two restrooms in the residence are original to the building and in overall poor condition. The finishes, fixtures, cabinets, toilets, showers and exhaust fans are showing signs of wear and deterioration. This project would provide for a complete remodel of the restrooms. The removal and disposal of the existing fixtures and finishes is included in this estimate. | HATCHERY RESIDENCE 4 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
1656ADA1 | ADA SIGNAGE | 1656 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2006 IBC, ICC/ANSI A117.1 - 2003, NRS 338.180 and the most current version of the Americans With Disabilities Act Accessible Guidelines (ADAAG) was used as a reference for this project | HATCHERY OFFICE/SHOP | 9905 | Wildlife |  |  | Mason Valley | 1990 | 12008 | 2019-06-11 | Immediate to Two Years | Currently Critical | 1 | 1800
1665ENR1 | LIGHTING UPGRADE | 1665 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts to current standards, resulting in increased efficiency and reduced costs associated with illumination. Any electrical wiring upgrades are not included in this estimate. | HATCHERY WATER WELL PUMP HOUSE A1 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 256 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 640
1658ENR1 | LIGHTING UPGRADE | 1658 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts to current standards, resulting in increased efficiency and reduced costs associated with illumination. Any electrical wiring upgrades are not included in this estimate. | HATCHERY DRY STORAGE | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1323 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3308
1657ENR1 | LIGHTING UPGRADE | 1657 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade T-12 lamps to T-8 lamps with electronic ballasts and upgrade the HID (high intensity discharge) lamps to current standards, resulting in increased efficiency and reduced costs associated with illumination and HVAC load. Any electrical wiring upgrades are not included in this estimate. | HATCHERY BUILDING | 9905 | Wildlife |  |  | Mason Valley | 1990 | 14855 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 37138
1657INT1 | INTERIOR FINISHES | 1657 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HATCHERY BUILDING | 9905 | Wildlife |  |  | Mason Valley | 1990 | 14855 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 74275
1657EXT2 | ROOF REPLACEMENT | 1657 | The roof on this building was in poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 15 years. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof, and constant exposure to the sun are contributing factors to wear and deterioration. The current rolled asphalt roof was installed in 1990. It is recommended that this building be re-roofed with a single-ply roofing system in the next two years to be consistent with the roofing program. | HATCHERY BUILDING | 9905 | Wildlife |  |  | Mason Valley | 1990 | 14855 | 2019-06-11 | Immediate to Two Years | Currently Critical | 1 | 222825
1657ADA1 | ADA SIGNAGE | 1657 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2006 IBC, ICC/ANSI A117.1 - 2003, NRS 338.180 and the most current version of the Americans With Disabilities Act Accessible Guidelines (ADAAG) was used as a reference for this project | HATCHERY BUILDING | 9905 | Wildlife |  |  | Mason Valley | 1990 | 14855 | 2019-06-11 | Immediate to Two Years | Currently Critical | 1 | 900
1657HVA1 | CHILLER CONTROL PROGRAMMING | 1657 | The electronic controller for the chillers is not functioning. The controller needs to be re-programmed by a qualified professional in order to achieve the energy efficiency of the equipment as well as to ensure that the building is consistently conditioned as needed. This project would provide for reprogramming the chiller controls. | HATCHERY BUILDING | 9905 | Wildlife |  |  | Mason Valley | 1990 | 14855 | 2019-06-11 | Immediate to Two Years | Currently Critical | 1 | 10000
1657EXT1 | EXTERIOR FINISHES | 1657 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the masonry and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HATCHERY BUILDING | 9905 | Wildlife |  |  | Mason Valley | 1990 | 14855 | 2019-06-11 | Four to Ten Years | Long-Term Needs | 3 | 74275
1657ELE1 | INSTALL ELECTRIC WATER HEATER | 1657 | The existing propane-fired water heater is permanently installed in the same room as the chillers. 2006 IMC 1106.2 prohibits open flame-producing devices in refrigeration rooms. This project would replace the existing gas fired equipment with electric equipment. | HATCHERY BUILDING | 9905 | Wildlife |  |  | Mason Valley | 1990 | 14855 | 2019-06-11 | Immediate to Two Years | Currently Critical | 1 | 1500
1656ADA2 | RACEWAY ADA ACCESS PROGRAM ACCESSIBILITY | 1656 | The Hatchery Raceway is open to the public for viewing fish rearing activities. There is not any designated ADA access to this area. This project would provide for an ADA accessible location inside of the public area of this building for an audio / visual (A/V) presentation of hatchery and raceway areas which may not be ADA accessible. This project includes funds for an audio / visual consultant to outline and document hatchery raceway operations and purchase and installation on all required A/V equipment including signage, TDD equipment and minor remodeling of the public area of the building as required to accommodate this program. The 2006 IBC, ICC/ANSI A117.1 - 2003, NRS 338.180 and the most current version of the Americans With Disabilities Act Accessible Guidelines (ADAAG) was used as a reference for this project. | HATCHERY OFFICE/SHOP | 9905 | Wildlife |  |  | Mason Valley | 1990 | 12008 | 2019-06-11 | Immediate to Two Years | Currently Critical | 1 | 20000
1659EXT1 | EXTERIOR FINISHES | 1659 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is the sealing and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HATCHERY VEHICLE STORAGE | 9905 | Wildlife |  |  | Mason Valley | 1990 | 5063 | 2019-06-11 | Four to Ten Years | Long-Term Needs | 3 | 7554
1656SFT1 | FIRE SUPPRESSION SYSTEM INSTALLATION | 1656 | The building is partially a B occupancy per the 2006 IBC and has a floor area greater than 12,000 square feet. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. | HATCHERY OFFICE/SHOP | 9905 | Wildlife |  |  | Mason Valley | 1990 | 12008 | 2019-06-11 | Immediate to Two Years | Currently Critical | 1 | 84056
1660EXT1 | EXTERIOR FINISHES | 1660 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is the sealing and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HATCHERY HAZMAT STORAGE | 9905 | Wildlife |  |  | Mason Valley | 1990 | 247 | 2019-06-11 | Four to Ten Years | Long-Term Needs | 3 | 741
1656INT1 | REPLACE CARPET AND TILE | 1656 | The carpet and VCT (vinyl composite tile) flooring in the Office is damaged and reaching the end of its useful life. It is recommended that the carpet and VCT flooring be replaced. This project would provide for removal and disposal of the carpet and VCT and installation of new 12x12 VCT with a 6" base. This project or a portion thereof was previously recommended in the FCA report dated 08/09/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | HATCHERY OFFICE/SHOP | 9905 | Wildlife |  |  | Mason Valley | 1990 | 12008 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 48000
1656EXT1 | REPLACE GUTTER | 1656 | The existing gutter on the shop eve has numerous joints that have proven impossible to seal against leaks. The leaking gutters will cause premature deterioration to the building finishes and the site hardscape. This project would replace the existing segmented gutter with seamless gutter. This project or a portion thereof was previously recommended in the FCA report dated 08/09/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | HATCHERY OFFICE/SHOP | 9905 | Wildlife |  |  | Mason Valley | 1990 | 12008 | 2019-06-11 | Four to Ten Years | Long-Term Needs | 3 | 6800
1656SFT3 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 1656 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2006 Chapter 10 was referenced for this project. | HATCHERY OFFICE/SHOP | 9905 | Wildlife |  |  | Mason Valley | 1990 | 12008 | 2019-06-11 | Immediate to Two Years | Currently Critical | 1 | 5000
1656INT3 | BREAK ROOM REMODEL | 1656 | The kitchenette and associated cabinets in the employee break room are original to the building. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and counter tops are delaminating and failing. This project recommends the replacement of the existing kitchen counters, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. This estimate includes disposal of the existing materials. | HATCHERY OFFICE/SHOP | 9905 | Wildlife |  |  | Mason Valley | 1990 | 12008 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
1656ELE1 | INCREASE PHONE CAPACITY AND ADD VOICE MAIL | 1656 | The existing phone switch is inadequate for the needs of the staff and currently does not offer voice mail. It is recommended that the switch be upgraded to add a voice mail module and ten new phone lines. To facilitate real time vendor access to the SCADA system and provide State employees with responsive access to email and data, the site should be provided with a high-speed internet connection as well. High-speed internet access costs are not included in the estimated costs for upgrading the phone switch. This project or a portion thereof was previously recommended in the FCA report dated 08/09/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | HATCHERY OFFICE/SHOP | 9905 | Wildlife |  |  | Mason Valley | 1990 | 12008 | 2019-06-11 | Four to Ten Years | Long-Term Needs | 3 | 10000
1656EXT2 | EXTERIOR FINISHES | 1656 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is the sealing and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HATCHERY OFFICE/SHOP | 9905 | Wildlife |  |  | Mason Valley | 1990 | 12008 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 36024
1656ENR1 | LIGHTING UPGRADE | 1656 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts to current standards, resulting in increased efficiency and reduced costs associated with illumination. Any electrical wiring upgrades are not included in this estimate. | HATCHERY OFFICE/SHOP | 9905 | Wildlife |  |  | Mason Valley | 1990 | 12008 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30020
1656EXT4 | OVERHEAD DOOR MOTOR INSTALLATION | 1656 | There are three 14'x16' overhead coiling doors which are manually operated. This project would provide for the installation of motors for the doors including remote operation, safety controls and connection to existing utilities. | HATCHERY OFFICE/SHOP | 9905 | Wildlife |  |  | Mason Valley | 1990 | 12008 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
1656ENV1 | DUST COLLECTION SYSTEM INSTALLATION | 1656 | The building has a woodshop area which does not have an adequate dust collection system. In order to reduce the possibility of damage or injury, each piece of equipment should have complete collection capability. This project recommends installing a new dust collection system. | HATCHERY OFFICE/SHOP | 9905 | Wildlife |  |  | Mason Valley | 1990 | 12008 | 2019-06-11 | Immediate to Two Years | Currently Critical | 1 | 20000
1656PLM2 | WATER HEATER REPLACEMENT | 1656 | There is a 50 gallon propane-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 8-10 years. It is recommended that a new propane-fired water heater be installed. | HATCHERY OFFICE/SHOP | 9905 | Wildlife |  |  | Mason Valley | 1990 | 12008 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1750
1656INT2 | INTERIOR FINISHES | 1656 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 08/09/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | HATCHERY OFFICE/SHOP | 9905 | Wildlife |  |  | Mason Valley | 1990 | 12008 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
1656SFT2 | FIRE ALARM SYSTEM INSTALLATION | 1656 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2006 Section 7 and the 2006 International Fire Code. | HATCHERY OFFICE/SHOP | 9905 | Wildlife |  |  | Mason Valley | 1990 | 12008 | 2019-06-11 | Immediate to Two Years | Currently Critical | 1 | 42028
1663INT1 | INTERIOR FINISHES | 1663 | The interior finishes are in fair condition. It is recommended that the interior walls be cleaned and sealed and that the ceiling be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. | HATCHERY WATER WELL PUMP HOUSE A2 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 311 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 778
1666EXT4 | GUTTER INSTALLATION | 1666 | The building does not have gutters or downspouts to control the runoff from the roof. The water currently sheet drains off the roof causing erosion to the grade and damage to the siding. This project would provide funding for the installation of a seamless gutter and downspout system for the building. | HATCHERY RESIDENCE 1 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
1666EXT3 | REMOVE SPRINKLERED LAWN WITHIN 3' OF BUILDING | 1666 | The house has considerable damage to the siding from lawn sprinklers wetting the siding. This project would create drip irrigated planters within three feet of the house and relocate sprinklers so they do not wet the house. Backflow prevention devices would be enclosed in a heated enclosure to prevent freezing. Existing hose bibs upstream of the backflow preventers would be relocated downstream of the valve. This project or a portion thereof was previously recommended in the FCA report dated 08/09/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | HATCHERY RESIDENCE 1 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
1665EXT1 | EXTERIOR FINISHES | 1665 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the masonry and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HATCHERY WATER WELL PUMP HOUSE A1 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 256 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1280
1665INT1 | INTERIOR FINISHES | 1665 | The interior finishes are in fair condition. It is recommended that the interior walls be cleaned and sealed and that the ceiling be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. | HATCHERY WATER WELL PUMP HOUSE A1 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 256 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 640
1670PLM1 | WATER HEATER REPLACEMENT | 1670 | There is a 50 gallon propane-fired water heater in the garage. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 3-4 years. It is recommended that a new propane-fired water heater be installed. | HATCHERY RESIDENCE 5 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1750
1665EXT2 | ROOF REPLACEMENT | 1665 | The roof on this building was in poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 15 years. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof, and constant exposure to the sun are contributing factors to wear and deterioration. The current rolled asphalt roof was installed in 1990. It is recommended that this building be re-roofed with a single-ply roofing system in the next 2-3 years to be consistent with the roofing program. | HATCHERY WATER WELL PUMP HOUSE A1 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 256 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3840
1669EXT1 | EXTERIOR FINISHES | 1669 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 08/09/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | HATCHERY RESIDENCE 4 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19720
1664ENR1 | LIGHTING UPGRADE | 1664 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts to current standards, resulting in increased efficiency and reduced costs associated with illumination. Any electrical wiring upgrades are not included in this estimate. | HATCHERY WATER WELL PUMP HOUSE C2 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 256 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 300
1664EXT1 | EXTERIOR FINISHES | 1664 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the masonry and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HATCHERY WATER WELL PUMP HOUSE C2 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 256 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1280
1664INT1 | INTERIOR FINISHES | 1664 | The interior finishes are in fair condition. It is recommended that the interior walls be cleaned and sealed and that the ceiling be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. | HATCHERY WATER WELL PUMP HOUSE C2 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 256 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 640
1658EXT1 | EXTERIOR FINISHES | 1658 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is the sealing and caulking of the windows, flashing, fixtures and all other penetrations and painting of the overhead doors. It is recommended that the building be caulked and sealed and the doors be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HATCHERY DRY STORAGE | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1323 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3969
1663EXT1 | EXTERIOR FINISHES | 1663 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the masonry and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HATCHERY WATER WELL PUMP HOUSE A2 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 311 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1555
1666INT3 | REPLACE FLOOR COVERING | 1666 | The carpet and vinyl flooring in the building is damaged and reaching the end of its useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new carpet and vinyl flooring. This project or a portion thereof was previously recommended in the FCA report dated 08/09/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | HATCHERY RESIDENCE 1 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15776
1663EXT2 | ROOF REPLACEMENT | 1663 | The roof on this building was in poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 15 years. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof, and constant exposure to the sun are contributing factors to wear and deterioration. The current rolled asphalt roof was installed in 1990. It is recommended that this building be re-roofed with a single-ply roofing system in the next 2-3 years to be consistent with the roofing program. | HATCHERY WATER WELL PUMP HOUSE A2 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 311 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4665
1662INT1 | INTERIOR FINISHES | 1662 | The interior finishes are in fair condition. It is recommended that the interior walls be cleaned and sealed and that the ceiling be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. | HATCHERY WATER WELL PUMP HOUSE C1 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 311 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 778
1662ENR1 | LIGHTING UPGRADE | 1662 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts to current standards, resulting in increased efficiency and reduced costs associated with illumination. Any electrical wiring upgrades are not included in this estimate. | HATCHERY WATER WELL PUMP HOUSE C1 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 311 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
1662EXT1 | EXTERIOR FINISHES | 1662 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the masonry and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HATCHERY WATER WELL PUMP HOUSE C1 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 311 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1555
1662EXT2 | ROOF REPLACEMENT | 1662 | The roof on this building was in poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 15 years. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof, and constant exposure to the sun are contributing factors to wear and deterioration. The current rolled asphalt roof was installed in 1990. It is recommended that this building be re-roofed with a single-ply roofing system in the next 2-3 years to be consistent with the roofing program. | HATCHERY WATER WELL PUMP HOUSE C1 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 311 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4665
1661ENV1 | REPLACE UNDERGROUND TANK | 1661 | The site emergency generators are served by a 1,000 gallon Fiberglas/steel underground fuel tank located between the well house and the above ground water tank. At the time of the previous site visit, the leak detection monitor was in alarm. This project would replace the existing tank with a 1,000 gallon above ground "ConVault" to serve the generators. The underground tank would be investigated for leakage and closed if none is found. This project does not include funds for site remediation. This project or a portion thereof was previously recommended in the FCA report dated 08/09/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | HATCHERY PUMP HOUSE B | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1160 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
1661HVA1 | HVAC EQUIPMENT REPLACEMENT | 1661 | The three HVAC roof top units and the ceiling mounted heater were installed in 1990. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of a new HVAC system and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | HATCHERY PUMP HOUSE B | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1160 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 34800
1661ENR1 | LIGHTING UPGRADE | 1661 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts to current standards, resulting in increased efficiency and reduced costs associated with illumination. Any electrical wiring upgrades are not included in this estimate. | HATCHERY PUMP HOUSE B | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1160 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2900
1661INT1 | INTERIOR FINISHES / CEILING REPAIR | 1661 | The interior finishes are in fair condition except for the damaged gypsum board ceiling . This project would provide for the removal and replacement of the damaged ceiling areas and painting. It is recommended that the interior walls be cleaned and sealed and that the ceiling be painted at least once in the next two years after the repairs are made. Prior to painting, all surfaces should be repaired and prepped. The roof replacement project must be done prior to the repairing of the ceiling. | HATCHERY PUMP HOUSE B | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1160 | 2019-06-11 | Immediate to Two Years | Currently Critical | 1 | 5800
1661EXT2 | ROOF REPLACEMENT | 1661 | The roof on this building was in poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 15 years. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof, and constant exposure to the sun are contributing factors to wear and deterioration. The current rolled asphalt roof was installed in 1990. It is recommended that this building be re-roofed with a single-ply roofing system in the next 1-2 years to be consistent with the roofing program. | HATCHERY PUMP HOUSE B | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1160 | 2019-06-11 | Immediate to Two Years | Currently Critical | 1 | 17400
1661EXT1 | EXTERIOR FINISHES | 1661 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the masonry and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HATCHERY PUMP HOUSE B | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1160 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5800
1663ENR1 | LIGHTING UPGRADE | 1663 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts to current standards, resulting in increased efficiency and reduced costs associated with illumination. Any electrical wiring upgrades are not included in this estimate. | HATCHERY WATER WELL PUMP HOUSE A2 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 311 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
1669EXT4 | GUTTER INSTALLATION | 1669 | The building does not have gutters or downspouts to control the runoff from the roof. The water currently sheet drains off the roof causing erosion to the grade and damage to the siding. This project would provide funding for the installation of a seamless gutter and downspout system for the building. | HATCHERY RESIDENCE 4 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
2979EXT1 | EXTERIOR FINISHES | 2979 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding for the sealing and painting of the exterior of the building. Included in the cost is sealing and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HATCHERY BULK FEED BIN | 9905 | Wildlife |  |  | Mason Valley | 1990 | 196 | 2019-06-11 | Four to Ten Years | Long-Term Needs | 3 | 1960
2460EXT2 | ROOF REPLACEMENT | 2460 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next one to two years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. | HATCHERY RESIDENCE 4 SHOP | 9905 | Wildlife |  |  | Mason Valley | 1991 | 480 | 2019-06-11 | Immediate to Two Years | Currently Critical | 1 | 7200
2460EXT1 | EXTERIOR FINISHES | 2460 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 08/09/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | HATCHERY RESIDENCE 4 SHOP | 9905 | Wildlife |  |  | Mason Valley | 1991 | 480 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4800
2460INT1 | INTERIOR FINISHES | 2460 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HATCHERY RESIDENCE 4 SHOP | 9905 | Wildlife |  |  | Mason Valley | 1991 | 480 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2400
2461EXT1 | EXTERIOR FINISHES | 2461 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HATCHERY MOWER SHED | 9905 | Wildlife |  |  | Mason Valley | 0 | 200 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 300
2978EXT2 | GUTTER INSTALLATION | 2978 | The building does not have gutters or downspouts to control the runoff from the roof. The water currently sheet drains off the roof causing extensive erosion to the rip-rap slope around the foundation. This will eventually lead to failure of the foundation undermining the integrity of the entire structure. This project would provide funding for the installation of a seamless gutter and downspout system for the building. | HATCHERY RACEWAY SHELTER | 9905 | Wildlife |  |  | Mason Valley | 1990 | 75600 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 45000
2977EXT1 | EXTERIOR FINISHES | 2977 | It is important to maintain the finish, weather resistance and appearance of the water tank. This project would provide for the painting of the water tank to maintain it in a good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | HATCHERY WATER TANK | 9905 | Wildlife |  |  | Mason Valley | 1990 | 531 | 2019-06-11 | Four to Ten Years | Long-Term Needs | 3 | 7500
2978EXT1 | EXTERIOR FINISHES | 2978 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding for the sealing and painting of the exterior of the building. Included in the cost is sealing and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HATCHERY RACEWAY SHELTER | 9905 | Wildlife |  |  | Mason Valley | 1990 | 75600 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18900
9905ENR2 | ENERGY SAVINGS PERFORMANCE CONTRACT | 9905 | This project would invite an Energy Services Company (ESCO) to provide an analysis of energy and water savings opportunities at the Hatchery site. The ESCO could then enter into an Energy Savings Performance Contract with the Department of Wildlife to implement approved energy savings projects. Monetary savings from the projects would be used in whole or in part to pay the ESCO services. Among the opportunities that exist are lighting retrofits, the use of water or ground source heat pumps or heat exchangers, and the use of overhead low intensity radiant heating in shop areas. This project or a portion thereof was previously recommended in the FCA report dated 08/09/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | MASON VALLEY HATCHERY SITE | 9905 | Wildlife |  |  | Mason Valley | 0 |  | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6500
9905ENV1 | RESIDENCE SEPTIC TANK SYSTEM MAINTENANCE | 9905 | There are 5 residences each with a 500 gallon septic tank and associated leach fields. They are in need of pumping to maintain the integrity of the leach lines and fields. This project would provide for the pumping of all 5 tanks. It is recommended that this project be scheduled on a cyclical basis based on usage. | MASON VALLEY HATCHERY SITE | 9905 | Wildlife |  |  | Mason Valley | 0 |  | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
9905ELE2 | REPLACE HATCHERY WATER MANAGEMENT COMPUTER SYSTEM | 9905 | The computer and software system for the hatchery operations monitors every aspect of fish hatching and rearing including but not limited to water flows, temperature, raceway flows, and well water flows to the main hatchery. This equipment is dated and is in need of an upgrade. There is not a backup to the system and if it fails, there could be losses to fish hatching and rearing operations. This project would provide for a new computer and upgrade the software system for fish hatchery operations. The main computer is located in Hatchery Office / Shop. It is recommended that this equipment be replaced in the next two years. | MASON VALLEY HATCHERY SITE | 9905 | Wildlife |  |  | Mason Valley | 0 |  | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
9905SIT3 | COOLING TOWER CONCRETE APRON REPAIR | 9905 | The cooling tower along the west side of the Hatchery building has a large sloped concrete apron which is showing signs of damage. There are cracks from settling and evidence of erosion occurring underneath the concrete. This may compromise the structural stability of the concrete foundation below the cooling tower. This project would provide for the necessary repairs to be made to prevent water infiltration and erosion. | MASON VALLEY HATCHERY SITE | 9905 | Wildlife |  |  | Mason Valley | 0 |  | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18000
9905ELE1 | RELOCATE RESIDENCE AREA PHONE VAULT | 9905 | The phone system in the housing area is subject to frequent outages due to lighting strikes. In addition, the main junction box is in a below ground vault, which subjects the terminations to corrosion due to ground moisture reducing the quality of service. This project would relocate the junction box to an above ground location and install lightning protection. This project or a portion thereof was previously recommended in the FCA report dated 08/09/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | MASON VALLEY HATCHERY SITE | 9905 | Wildlife |  |  | Mason Valley | 0 |  | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
9905ENV2 | INSTALL FUEL STORAGE TANKS | 9905 | The existing fuel tank adjacent to the vehicle storage building is a single-wall elevated fuel tank with a containment base. This project would install a 1,000 gallon gasoline and a 2,000 gallon diesel "ConVault" above ground tank and dispenser including all wiring, piping, vents, and spill containment. | MASON VALLEY HATCHERY SITE | 9905 | Wildlife |  |  | Mason Valley | 0 |  | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24000
9905SIT2 | REMOVE & REPLACE,CRACK FILL AND SLURRY SEAL ASPHALT PAVEMENT | 9905 | There is approximately 327,150 Square feet of asphalt paving on the site. There are numerous areas that are damaged and the entire paved area is in need of a slurry seal. This project would provide for the removal and replacement of 260,550 square feet of pavement and crack fill and slurry sealing of 66,600 square feet of existing paving to remain. Striping is included in this estimate. Slurry sealing of the entire paved area is also recommended on a 5-7 year cycle to maintain the integrity of the paving on site. For budgeting purposes, a construction cost figure of 50 cents a square foot could be used for slurry sealing which is not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 07/15/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/07/2009. | MASON VALLEY HATCHERY SITE | 9905 | Wildlife |  |  | Mason Valley | 0 |  | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 817875
2477EXT1 | DEMOLISH STRUCTURE | 2477 | The Quonset Hut is dilapidated and deteriorating and has reached the end of its useful life. This project would provide funding for the demolition of the building. | MVWMA QUONSET HUT | 9904 | Wildlife |  |  | Mason Valley | 0 | 3000 | 2019-06-26 | Four to Ten Years | Long-Term Needs | 3 | 15000
2984EXT1 | EXTERIOR FINISHES | 2984 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is cleaning the vinyl siding and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be cleaned and caulked in the next 5-6 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project also includes costs for installing a 3'x3' concrete landing at the door. | MVWMA FILTER HOUSE 2 | 9904 | Wildlife |  |  | Mason Valley | 0 | 63 | 2019-06-26 | Four to Ten Years | Long-Term Needs | 3 | 500
2985INT1 | INTERIOR FINISHES | 2985 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | MVWMA RESIDENCE 4 GREENHOUSE | 9904 | Wildlife |  |  | Mason Valley | 0 | 64 | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 320
2983EXT1 | EXTERIOR FINISHES | 2983 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is cleaning the vinyl siding and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be cleaned and caulked in the next 5-6 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project also includes costs for installing a 3'x3' concrete landing at the door. | MVWMA FILTER HOUSE 1 | 9904 | Wildlife |  |  | Mason Valley | 0 | 63 | 2019-06-26 | Four to Ten Years | Long-Term Needs | 3 | 500
2986EXT1 | EXTERIOR FINISHES | 2986 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding and sealing and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-6 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MVWMA RESIDENCE 4 GAZEBO | 9904 | Wildlife |  |  | Mason Valley | 0 | 128 | 2019-06-26 | Four to Ten Years | Long-Term Needs | 3 | 1280
2985EXT1 | EXTERIOR FINISHES | 2985 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MVWMA RESIDENCE 4 GREENHOUSE | 9904 | Wildlife |  |  | Mason Valley | 0 | 64 | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
2473EXT1 | EXTERIOR FINISHES | 2473 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is the sealing and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MVWMA NORTH PUMP HOUSE | 9904 | Wildlife |  |  | Mason Valley | 1955 | 64 | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 160
2474EXT1 | DEMOLISH STRUCTURE | 2474 | The Old Goose Pens building is dilapidated and deteriorating and has reached the end of its useful life. This project would provide funding for the demolition of the building. | MVWMA OLD GOOSE PENS | 9904 | Wildlife |  |  | Mason Valley | 0 | 3000 | 2019-06-26 | Four to Ten Years | Long-Term Needs | 3 | 15000
2476EXT1 | DEMOLISH STRUCTURE | 2476 | The Barn/ Box Stalls building is dilapidated and deteriorating and has reached the end of its useful life. This project would provide funding for the demolition of the building. | MVWMA BARN/BOX STALLS | 9904 | Wildlife |  |  | Mason Valley | 0 | 1200 | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
2478EXT1 | EXTERIOR FINISHES | 2478 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide for painting and sealing of the interior and exterior of the structure. This project should be scheduled on a cyclical basis to maintain the integrity of the structure. | MVWMA EQUIPMENT MAINTENANCE BUILDING | 9904 | Wildlife |  |  | Mason Valley | 0 | 1500 | 2019-06-26 | Four to Ten Years | Long-Term Needs | 3 | 3000
2472EXT1 | DEMOLISH STRUCTURE | 2472 | The Storage Shed - West is dilapidated and deteriorating and has reached the end of its useful life. This project would provide funding for the demolition of the building. | MVWMA STORAGE SHED - WEST | 9904 | Wildlife |  |  | Mason Valley | 1955 | 960 | 2019-06-26 | Four to Ten Years | Long-Term Needs | 3 | 4800
2981EXT1 | EXTERIOR FINISHES | 2981 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is the painting, sealing and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted, caulked and sealed in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MVWMA MECHANICS SHOP | 9904 | Wildlife |  |  | Mason Valley | 0 | 480 | 2019-06-26 | Four to Ten Years | Long-Term Needs | 3 | 1440
2475EXT1 | DEMOLISH STRUCTURE | 2475 | The Residence 4 Storage Shed is dilapidated and deteriorating and has reached the end of its useful life. This project would provide funding for the demolition of the building. | MVWMA RESIDENCE 4 STORAGE SHED | 9904 | Wildlife |  |  | Mason Valley | 1955 | 1500 | 2019-06-26 | Four to Ten Years | Long-Term Needs | 3 | 7500
2981SFT1 | FIRE SUPPRESSION SYSTEM INSTALLATION | 2981 | This building does not have an automatic fire suppression system. It should be retrofitted with fire sprinklers during the next remodel or addition. NAC 477.917 states that: Existing buildings and structures: Additions, alterations and repairs. (NRS 477.030) 1. If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. 2. The State Fire Marshal will determine the value of the building or structure and the value of any additions, alterations and repairs. If the owner of the building disagrees with the value as determined by the State Fire Marshal, the owner of the building may engage a qualified and disinterested appraiser to ascertain the fair market value of the building or structure and the value of any additions, alterations and repairs. 3. As used in this section, “addition” means any extension or increase in the floor space or height of a building or structure. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. This project does not include a water storage tank for fire protection which may be required if existing water flows are not adequate. | MVWMA MECHANICS SHOP | 9904 | Wildlife |  |  | Mason Valley | 0 | 480 | 2019-06-26 | Immediate to Two Years | Currently Critical | 1 | 6720
2981EXT3 | WINDOW REPLACEMENT | 2981 | The windows are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 6 units. Removal and disposal of the existing windows is included in this estimate. | MVWMA MECHANICS SHOP | 9904 | Wildlife |  |  | Mason Valley | 0 | 480 | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
2981ENR1 | LIGHTING UPGRADE | 2981 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts to current standards, resulting in increased efficiency and reduced costs associated with illumination. Any electrical wiring upgrades are not included in this estimate. | MVWMA MECHANICS SHOP | 9904 | Wildlife |  |  | Mason Valley | 0 | 480 | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1200
2981EXT2 | EXTERIOR DOOR REPLACEMENT | 2981 | The existing exterior wood door is approaching the end of its expected life. It is damaged from age and general wear and tear. This project would provide for the replacement of the wood door with a new metal door, frame and hardware. Also, a 3'x3'x4" thick concrete landing is included in this project. Removal and disposal of the existing door and painting of the new door is included in this estimate. | MVWMA MECHANICS SHOP | 9904 | Wildlife |  |  | Mason Valley | 0 | 480 | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
2980EXT1 | EXTERIOR / INTERIOR FINISHES | 2980 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MVWMA CXT RESTROOM | 9904 | Wildlife |  |  | Mason Valley | 1990 | 81 | 2019-06-26 | Four to Ten Years | Long-Term Needs | 3 | 810
2982EXT1 | DEMOLISH STRUCTURE | 2982 | The Storage Building contains numerous code and safety issues including but not limited to damaged windows, broken or missing electrical fixtures, dry rot and possible structural damage due to the age of the building. The building is dilapidated and deteriorating and has reached the end of its useful life. This project would provide funding for the demolition of the building. | MVWMA STORAGE BUILDING | 9904 | Wildlife |  |  | Mason Valley | 0 | 96 | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 960
2471EXT1 | DEMOLISH STRUCTURE | 2471 | The Tack Shed/ Calf Barn is dilapidated and deteriorating and has reached the end of its useful life. This project would provide funding for the demolition of the building. | MVWMA TACK SHED/CALF BARN | 9904 | Wildlife |  |  | Mason Valley | 1955 | 1015 | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10150
9904ADA1 | INSTALL ADA ACCESSIBLE PARKING SPACE / ROUTE OF TRAVEL | 9904 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and route of travel to the office are necessary to comply with ADA accessibility requirements. This project would provide for a concrete van accessible ADA parking and loading space and concrete walkway to the existing sidewalk. This will require placement of P.C. concrete, regrading, signage, striping and any other necessary upgrades. The 2006 IBC, ICC/ANSI A117.1 - 2003 and the most current version of the Americans With Disabilities Act Accessible Guidelines (ADAAG) was used as a reference for this project. 750 square feet of concrete was used for this estimate. It is recommended that this project coincide with the paving project. | MASON VALLEY WMA SITE | 9904 | Wildlife |  |  | Mason Valley | 0 |  | 2019-06-26 | Immediate to Two Years | Currently Critical | 1 | 9000
9904PLM2 | WATER LINE REPLACEMENT | 9904 | The underground water line between the North Pump House and Residence #4 has reached the end of its expected life and should be scheduled for replacement. This project recommends the installation of 3/4" schedule 40 PVC pipe to replace the existing pipe. 1,500 lineal feet was used for this estimate. | MASON VALLEY WMA SITE | 9904 | Wildlife |  |  | Mason Valley | 0 |  | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 22500
9904SIT2 | ASPHALT PAVING INSTALLATION | 9904 | The parking area in front of the Office/ Headquarters is not paved. This project would provide asphalt cement paving for a 30,000 square foot parking lot. The estimate includes grading, 6" base, compaction, installation and striping of 4" thick asphalt cement paving. Design is not included in this estimate. | MASON VALLEY WMA SITE | 9904 | Wildlife |  |  | Mason Valley | 0 |  | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 150000
9904SIT1 | RELOCATE FIRE HOSE SHED | 9904 | Residence No. 3 has a shed housing a fire hose and valve for fire fighting. The shed is in disrepair and is isolated behind the residence in shrubs and is obstructed by equipment. This project would relocate the hose and valve to a cabinet in front of the residence in an accessible location. | MASON VALLEY WMA SITE | 9904 | Wildlife |  |  | Mason Valley | 0 |  | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
9904ENV1 | INSTALL CON-VAULTS AND CONCRETE FUELING APRON | 9904 | The existing fuel tanks are single wall steel supported on beams. The tanks and fueling dispensers have no effective secondary containment. This project would install a split tank or two separate Con-Vault tanks and dispensers along with a concrete fueling apron to prevent spills and contamination of the soil. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | MASON VALLEY WMA SITE | 9904 | Wildlife |  |  | Mason Valley | 0 |  | 2019-06-26 | Immediate to Two Years | Currently Critical | 1 | 40000
9904PLM1 | INSTALL 2-STAGE PROPANE REGULATORS | 9904 | NFPA 58 requires 2-stage pressure regulators on all fixed piping propane installations. Existing installations on the three residences and at the Mechanic's Shop have single stage regulation. This project would install a second stage regulator and relocate the tank at the Mechanic's Shop for proper clearance. Additionally, the heater in the Mechanic's Shop is installed with a flexible gas line penetrating the heater metal cabinet. This is a Plumbing Code Violation. This project will install a solid pipe nipple to project beyond the heater case for connection. | MASON VALLEY WMA SITE | 9904 | Wildlife |  |  | Mason Valley | 0 |  | 2019-06-26 | Immediate to Two Years | Currently Critical | 1 | 4000
0650EXT2 | ROOF REPLACEMENT | 0650 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next two to three years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. Replacement of the evaporative cooler should be completed prior to or at the same time. | MVWMA OFFICE/HEADQUARTERS | 9904 | Wildlife |  |  | Mason Valley | 1955 | 950 | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14250
0650SFT1 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0650 | The building is a B occupancy per the 2006 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. This project does not include a water storage tank for fire protection which may be required if existing water flows are not adequate. | MVWMA OFFICE/HEADQUARTERS | 9904 | Wildlife |  |  | Mason Valley | 1955 | 950 | 2019-06-26 | Immediate to Two Years | Currently Critical | 1 | 13300
0958SFT1 | STAIR HANDRAIL INSTALLATION | 0958 | The front entry stairs do not meet the 2006 IBC Chapter 10 building code. The stairs are missing a handrail. This project would provide for the installation of a new handrail for the stairs. | MVWMA RESIDENCE #3 | 9904 | Wildlife |  |  | Mason Valley | 1961 | 1400 | 2019-06-26 | Immediate to Two Years | Currently Critical | 1 | 500
0959EXT4 | ROOF REPLACEMENT | 0959 | The asphalt composition shingle roof on this building was in fair condition at the time of the survey. It is recommended that this building be re-roofed in the next four to five years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. | MVWMA RESIDENCE #4 | 9904 | Wildlife |  |  | Mason Valley | 1969 | 1600 | 2019-06-26 | Four to Ten Years | Long-Term Needs | 3 | 24000
0959EXT3 | WINDOW REPLACEMENT | 0959 | The windows are older, dual pane construction in a vinyl frame which are not energy efficient and are reaching the end of their expected life. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 17 units. Removal and disposal of the existing windows is included in this estimate. | MVWMA RESIDENCE #4 | 9904 | Wildlife |  |  | Mason Valley | 1969 | 1600 | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 17000
0959PLM2 | WATER HEATER REPLACEMENT | 0959 | There is a 50 gallon propane-fired water heater in the closet. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 8-10 years. It is recommended that a new propane-fired water heater be installed. | MVWMA RESIDENCE #4 | 9904 | Wildlife |  |  | Mason Valley | 1969 | 1600 | 2019-06-26 | Four to Ten Years | Long-Term Needs | 3 | 1750
0959INT2 | CEILING REPAIR | 0959 | The gypsum board in the closet ceiling is damaged and / or missing at the HVAC duct penetration. This project would provide for the repairs to the ceiling including installing new gypsum board and painting. It is recommended that this project be completed in the next two years. | MVWMA RESIDENCE #4 | 9904 | Wildlife |  |  | Mason Valley | 1969 | 1600 | 2019-06-26 | Immediate to Two Years | Currently Critical | 1 | 500
0962EXT1 | DEMOLISH STRUCTURE | 0962 | The Wood Shop contains numerous code and safety issues including but not limited to transite siding, broken windows, broken or missing electrical fixtures, dry rot and possible structural damage due to the age of the building. The building is dilapidated and deteriorating and has reached the end of its useful life. This project would provide funding for the demolition of the building. | MVWMA WOOD SHOP | 9904 | Wildlife |  |  | Mason Valley | 1955 | 640 | 2019-06-26 | Four to Ten Years | Long-Term Needs | 3 | 6400
0961EXT1 | DEMOLISH STRUCTURE | 0961 | The Garage is dilapidated and deteriorating and has reached the end of its useful life. There is evidence of roof leaks. This project would provide funding for the demolition of the building. | MVWMA GARAGE | 9904 | Wildlife |  |  | Mason Valley | 1955 | 1250 | 2019-06-26 | Four to Ten Years | Long-Term Needs | 3 | 6250
0959EXT2 | EXTERIOR FINISHES | 0959 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is the painting, sealing and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted, caulked and sealed in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MVWMA RESIDENCE #4 | 9904 | Wildlife |  |  | Mason Valley | 1969 | 1600 | 2019-06-26 | Four to Ten Years | Long-Term Needs | 3 | 8000
0959PLM1 | LANDSCAPE IRRIGATION | 0959 | Current landscape maintenance practices use excessive amounts of water to maintain the lawn and planter areas. This project would install a landscape irrigation system with an electronic controller to reduce water usage and maintain the excellent condition of the landscaping. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | MVWMA RESIDENCE #4 | 9904 | Wildlife |  |  | Mason Valley | 1969 | 1600 | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0959INT1 | INTERIOR FINISHES | 0959 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | MVWMA RESIDENCE #4 | 9904 | Wildlife |  |  | Mason Valley | 1969 | 1600 | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
0958PLM1 | WATER HEATER REPLACEMENT | 0958 | There is a 50 gallon propane-fired water heater in the garage. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new propane-fired water heater be installed. | MVWMA RESIDENCE #3 | 9904 | Wildlife |  |  | Mason Valley | 1961 | 1400 | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1750
0650HVA1 | REPLACE EVAPORATIVE COOLER | 0650 | The roof mounted evaporative cooler has been leaking and is problematic due to it's age. This project would provide for a new evaporative cooler to be installed including removal of the existing cooler and connections to the existing utilities. | MVWMA OFFICE/HEADQUARTERS | 9904 | Wildlife |  |  | Mason Valley | 1955 | 950 | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0956EXT1 | EXTERIOR FINISHES | 0956 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is cleaning the vinyl siding and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be cleaned and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MVWMA RESIDENCE #1 | 9904 | Wildlife |  |  | Mason Valley | 1961 | 1400 | 2019-06-26 | Four to Ten Years | Long-Term Needs | 3 | 7000
0955EXT3 | DO0R LANDING INSTALLATION | 0955 | The exterior door does not have a landing. This project would provide for the installation of a 3 foot by 3 foot concrete landing, 4 inches thick. | MVWMA PUMP HOUSE | 9904 | Wildlife |  |  | Mason Valley | 1965 | 200 | 2019-06-26 | Four to Ten Years | Long-Term Needs | 3 | 100
0955EXT2 | EXTERIOR FINISHES | 0955 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is the painting, sealing and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted, caulked and sealed in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MVWMA PUMP HOUSE | 9904 | Wildlife |  |  | Mason Valley | 1965 | 200 | 2019-06-26 | Four to Ten Years | Long-Term Needs | 3 | 600
0955PLM1 | WATER STORAGE TANK REPLACEMENT | 0955 | There is a 500 gallon water storage tank in the building. The average life span of a water storage tank is forty to fifty years. The tank was installed in 1965. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 3-4 years. This project would provide for a new water storage tank to be installed including connections to existing utilities. | MVWMA PUMP HOUSE | 9904 | Wildlife |  |  | Mason Valley | 1965 | 200 | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0954EXT1 | DEMOLISH STRUCTURE | 0954 | The Incubator House contains numerous code and safety issues including but not limited to bat infestation, broken or missing electrical fixtures, dry rot and possible structural damage. The exterior metal panels have blown off in the wind and there has been no attempt to repair the building. This has exposed the substrate and framing members to the elements. The building is dilapidated and deteriorating and has reached the end of its useful life. This project would provide funding for the demolition of the building. | MVWMA INCUBATOR HOUSE | 9904 | Wildlife |  |  | Mason Valley | 1968 | 512 | 2019-06-26 | Four to Ten Years | Long-Term Needs | 3 | 5120
0650INT2 | FLOORING REPLACEMENT | 0650 | The existing flooring is a mix of concrete and old vinyl composition tile (VCT) which is in extremely poor shape. This project would provide for new VCT to be installed throughout the building. Removal of the existing flooring is included in this estimate. This project should be implemented in the next two years. | MVWMA OFFICE/HEADQUARTERS | 9904 | Wildlife |  |  | Mason Valley | 1955 | 950 | 2019-06-26 | Immediate to Two Years | Currently Critical | 1 | 7600
0956INT1 | INTERIOR FINISHES | 0956 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next four to five years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | MVWMA RESIDENCE #1 | 9904 | Wildlife |  |  | Mason Valley | 1961 | 1400 | 2019-06-26 | Four to Ten Years | Long-Term Needs | 3 | 7000
0650EXT1 | EXTERIOR FINISHES | 0650 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. The estimate is based on 950 square feet at $10.00 per foot for the main building plus 800 square feet at $2.00 per foot for the trellis in front of the building. The estimate also provides for removing earth to wood contact by regrading around the exterior of the building. | MVWMA OFFICE/HEADQUARTERS | 9904 | Wildlife |  |  | Mason Valley | 1955 | 950 | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11100
0653EXT1 | DEMOLISH STRUCTURE | 0653 | The Oil Storage building is dilapidated and deteriorating and has reached the end of its useful life. This project would provide funding for the demolition of the building. | MVWMA OIL STORAGE | 9904 | Wildlife |  |  | Mason Valley | 1955 | 144 | 2019-06-26 | Four to Ten Years | Long-Term Needs | 3 | 720
0650ADA1 | ADA ACCESSIBILITY IMPROVEMENTS | 0650 | The office is lacking ADA accessibility components for providing barrier free access to the public. This project would provide for an ADA compliant ramp and door hardware at the main entrance to the building as well as remodeling of the existing restroom into a unisex ADA compliant facility and appropriate signage. This may include but is not limited to replacing all restroom fixtures, door and hardware, painting and installing fiberglass reinforced panels (FRP). The 2006 IBC, ICC/ANSI A117.1 - 2003 and the most current version of the Americans With Disabilities Act Accessible Guidelines (ADAAG) was used as a reference for this project. | MVWMA OFFICE/HEADQUARTERS | 9904 | Wildlife |  |  | Mason Valley | 1955 | 950 | 2019-06-26 | Immediate to Two Years | Currently Critical | 1 | 38500
0650SFT2 | FIRE ALARM SYSTEM INSTALLATION | 0650 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2006 Section 7 and the 2006 International Fire Code. | MVWMA OFFICE/HEADQUARTERS | 9904 | Wildlife |  |  | Mason Valley | 1955 | 950 | 2019-06-26 | Immediate to Two Years | Currently Critical | 1 | 3325
0650EXT4 | EXTERIOR DOOR REPLACEMENT | 0650 | The exterior wood doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the two exterior wood door assemblies with new metal doors, frames and hardware. Removal and disposal of the existing doors is included in this estimate. | MVWMA OFFICE/HEADQUARTERS | 9904 | Wildlife |  |  | Mason Valley | 1955 | 950 | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0650EXT3 | WINDOW REPLACEMENT | 0650 | The windows are original, dual pane construction in a wooden frame. These older windows are drafty, not energy efficient and the wooden frames have deteriorated significantly. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 7 units including wooden frames. Removal and disposal of the existing windows is included in this estimate. | MVWMA OFFICE/HEADQUARTERS | 9904 | Wildlife |  |  | Mason Valley | 1955 | 950 | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10500
0958EXT1 | EXTERIOR FINISHES | 0958 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is cleaning the vinyl siding and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be cleaned and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MVWMA RESIDENCE #3 | 9904 | Wildlife |  |  | Mason Valley | 1961 | 1400 | 2019-06-26 | Four to Ten Years | Long-Term Needs | 3 | 7000
0960EXT1 | EXTERIOR FINISHES | 0960 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide for painting and sealing of the interior and exterior of the structure. This project should be scheduled on a cyclical basis to maintain the integrity of the structure. | MVWMA EQUIPMENT SHED | 9904 | Wildlife |  |  | Mason Valley | 1955 | 1536 | 2019-06-26 | Four to Ten Years | Long-Term Needs | 3 | 3072
0650INT1 | INTERIOR FINISHES / CEILING REPAIRS | 0650 | The interior finishes are in fair condition. It is recommended that the interior walls and ceiling be painted at least once in the next two to three years. Prior to painting, all surfaces should be repaired and prepped. Repair to the damaged ceilings is also included in this estimate. | MVWMA OFFICE/HEADQUARTERS | 9904 | Wildlife |  |  | Mason Valley | 1955 | 950 | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4750
0957INT2 | KITCHEN REMODEL | 0957 | The kitchen is in fair to poor condition. The cabinets and equipment are showing signs of general wear and tear and are approaching the end of their expected life. This project recommends the replacement of the existing kitchen cabinets, counters, fixtures and equipment with mid range, high quality components. | MVWMA RESIDENCE #2 | 9904 | Wildlife |  |  | Mason Valley | 1961 | 1400 | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
0958INT1 | INTERIOR FINISHES | 0958 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next four to five years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | MVWMA RESIDENCE #3 | 9904 | Wildlife |  |  | Mason Valley | 1961 | 1400 | 2019-06-26 | Four to Ten Years | Long-Term Needs | 3 | 7000
0957PLM1 | WATER HEATER REPLACEMENT | 0957 | There is a 50 gallon propane-fired water heater in the garage. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new propane-fired water heater be installed. | MVWMA RESIDENCE #2 | 9904 | Wildlife |  |  | Mason Valley | 1961 | 1400 | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1750
0650ENR1 | LIGHTING UPGRADE | 0650 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts to current standards, resulting in increased efficiency and reduced costs associated with illumination. Any electrical wiring upgrades are not included in this estimate. | MVWMA OFFICE/HEADQUARTERS | 9904 | Wildlife |  |  | Mason Valley | 1955 | 950 | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2375
0957SFT1 | ENTRY STAIR HANDRAIL INSTALLATION | 0957 | The front entry stairs do not meet the 2006 IBC Chapter 10 building code. The stairs are missing a handrail. This project would provide for the installation of a new handrail on the stairs. | MVWMA RESIDENCE #2 | 9904 | Wildlife |  |  | Mason Valley | 1961 | 1400 | 2019-06-26 | Immediate to Two Years | Currently Critical | 1 | 500
0956SFT1 | ENTRY LANDING / STAIR / HANDRAIL INSTALLATION | 0956 | The front entry landing and stairs do not meet the 2006 IBC Chapter 10 building code. The landing is required to be a minimum of 36 inches and the stair risers are not equal. The stairs are missing a handrail. This project would provide for the installation of a new concrete landing, stairs and handrail. | MVWMA RESIDENCE #1 | 9904 | Wildlife |  |  | Mason Valley | 1961 | 1400 | 2019-06-26 | Immediate to Two Years | Currently Critical | 1 | 1500
0649EXT4 | EXTERIOR DOOR REPLACEMENT | 0649 | The existing exterior wood doors appear to be original to the building. They are damaged from age and general wear and tear and are in need of replacement to seal the building. This project would provide for the replacement of four wood doors with four new metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | MVWMA BROODER HOUSE | 9904 | Wildlife |  |  | Mason Valley | 1965 | 2880 | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0649EXT3 | WINDOW REPLACEMENT | 0649 | The windows are original, single pane construction in a metal frame. These older windows are damaged and in need of replacement to seal the building. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 2 units. Removal and disposal of the existing windows is included in this estimate. | MVWMA BROODER HOUSE | 9904 | Wildlife |  |  | Mason Valley | 1965 | 2880 | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
0649EXT1 | EXTERIOR FINISHES | 0649 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the concrete masonry, painting and caulking of the wood siding, windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painting and caulked in the next 3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MVWMA BROODER HOUSE | 9904 | Wildlife |  |  | Mason Valley | 1965 | 2880 | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14400
0957EXT6 | WINDOW REPLACEMENT | 0957 | The windows are older, dual pane construction in a vinyl frame which are not energy efficient and are reaching the end of their expected life. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 9 units. Removal and disposal of the existing windows is included in this estimate. | MVWMA RESIDENCE #2 | 9904 | Wildlife |  |  | Mason Valley | 1961 | 1400 | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
0957INT1 | INTERIOR FINISHES | 0957 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to three years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | MVWMA RESIDENCE #2 | 9904 | Wildlife |  |  | Mason Valley | 1961 | 1400 | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7000
0957EXT2 | EXTERIOR FINISHES | 0957 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is cleaning the vinyl siding and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be cleaned and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MVWMA RESIDENCE #2 | 9904 | Wildlife |  |  | Mason Valley | 1961 | 1400 | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7000
0957INT3 | FLOORING REPLACEMENT | 0957 | The carpet and sheet vinyl flooring in the building are showing signs of extreme wear. It is recommended that the carpet and sheet vinyl be replaced with heavy duty commercial grade carpet and VCT (vinyl composite tile) flooring in the next one to two years. | MVWMA RESIDENCE #2 | 9904 | Wildlife |  |  | Mason Valley | 1961 | 1400 | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11200
0957EXT5 | INSTALL PLANTER | 0957 | The Residence has relatively new vinyl siding. Along the rear and west side of the residence, the lawn grows right up to the house making it difficult to mow without damaging the siding. Watering the lawn also wets the siding causing premature deterioration. This project would remove the lawn within three feet of the residence and install a planter with drip irrigation. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | MVWMA RESIDENCE #2 | 9904 | Wildlife |  |  | Mason Valley | 1961 | 1400 | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
0957EXT4 | RESCREEN PATIO | 0957 | The screens on the patio are torn and damaged. They have reached the end of their expected life and should be scheduled for replacement. This project would replace the screens and the wood door to keep insects and other pests out of the patio. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | MVWMA RESIDENCE #2 | 9904 | Wildlife |  |  | Mason Valley | 1961 | 1400 | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1200
0957EXT1 | REPLACE ROOF | 0957 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next two to three years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | MVWMA RESIDENCE #2 | 9904 | Wildlife |  |  | Mason Valley | 1961 | 1400 | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 21000
0649EXT2 | ROOF REPLACEMENT | 0649 | The corrugated metal roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next two to three years with a standing seam metal roofing system. This estimate includes removal and disposal of the old roofing. | MVWMA BROODER HOUSE | 9904 | Wildlife |  |  | Mason Valley | 1965 | 2880 | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 28800
0956PLM1 | WATER HEATER REPLACEMENT | 0956 | There is a 50 gallon propane-fired water heater in the garage. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new 50 gallon propane-fired water heater be installed. | MVWMA RESIDENCE #1 | 9904 | Wildlife |  |  | Mason Valley | 1961 | 1400 | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1750
9881ELE1 | POWER LINE UPGRADE | 9881 | The main power line for the site is on the west side of the road and crosses the road to connect to the Office building. The pole is not tall enough to raise the lines above the height of large trucks and the line has been broken in the past. This project recommends working with the utility company to either provide a taller pole or bury the lines under the road. The estimate is based on the State providing all funding for the work. This project or a portion thereof was previously recommended in the FCA report dated 06/27/2012. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2020. | GALLAGHER FISH HATCHERY SITE | 9881 | Wildlife |  |  | Ruby Valley | 1940 |  | 2020-06-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24000
9881ADA1 | ADA PARKING AND PATH OF TRAVEL | 9881 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the office are necessary to comply with ADA accessibility requirements. This project would provide for a concrete van accessible ADA parking and loading space and concrete walkway / landing to the public entrance. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2018 IBC, ICC/ANSI A117.1, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. 750 square feet of concrete was used for this estimate. This project or a portion thereof was previously recommended in the FCA report dated 06/27/2012. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2020. | GALLAGHER FISH HATCHERY SITE | 9881 | Wildlife |  |  | Ruby Valley | 1940 |  | 2020-06-05 | Immediate to Two Years | Currently Critical | 1 | 18800
3141EXT1 | EXTERIOR FINISHES | 3141 | The exterior finishes are in good condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | VEHICLE STORAGE BUILDING | 9881 | Wildlife |  |  | Ruby Valley | 2006 | 4000 | 2020-06-05 | Four to Ten Years | Long-Term Needs | 3 | 4000
3144EXT1 | EXTERIOR FINISHES | 3144 | The exterior finishes are in good condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CONTROL BOX #2 | 9881 | Wildlife |  |  | Ruby Valley | 2006 | 162 | 2020-06-05 | Four to Ten Years | Long-Term Needs | 3 | 800
3146EXT1 | EXTERIOR FINISHES | 3146 | The exterior finishes are in good condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is cleaning the vinyl siding and caulking of the window, flashing, fixtures and all other penetrations. It is recommended that the building be cleaned and caulked in the next 8 - 9 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | RESIDENCE #2 GARAGE | 9881 | Wildlife |  |  | Ruby Valley | 2006 | 840 | 2020-06-05 | Four to Ten Years | Long-Term Needs | 3 | 1680
3146EXT2 | STRUCTURAL REPAIRS | 3146 | The southwest corner of the roof has been structurally damaged. The asphalt shingles are rippled and the fascia and soffit are severely damaged. The project would fund the removal of the shingles in this area, inspect and repair any trusses and roof sheathing, and replace the damaged fascia, cladding, and soffit. | RESIDENCE #2 GARAGE | 9881 | Wildlife |  |  | Ruby Valley | 2006 | 840 | 2020-06-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3500
3145EXT1 | EXTERIOR FINISHES | 3145 | The exterior finishes are in good condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is cleaning the vinyl siding and caulking of the window, flashing, fixtures and all other penetrations. It is recommended that the building be cleaned and caulked in the next 8 - 9 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | RESIDENCE #1 GARAGE | 9881 | Wildlife |  |  | Ruby Valley | 2006 | 840 | 2020-06-05 | Four to Ten Years | Long-Term Needs | 3 | 1680
3143EXT1 | EXTERIOR FINISHES | 3143 | The exterior finishes are in good condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CONTROL BOX #1 | 9881 | Wildlife |  |  | Ruby Valley | 2006 | 162 | 2020-06-05 | Four to Ten Years | Long-Term Needs | 3 | 800
3142INT1 | INTERIOR FINISHES | 3142 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. | EMERGENCY GENERATOR BUILDING | 9881 | Wildlife |  |  | Ruby Valley | 2006 | 640 | 2020-06-05 | Four to Ten Years | Long-Term Needs | 3 | 3200
3142ELE1 | ELECTRICAL SAFETY | 3142 | The main electrical switchgear meter section appears to only have a paper dead front in the electrical meter mount location. This may expose live bus conductors to those in the room. This needs to be investigated and corrections made, if necessary, by a qualified electrician. | EMERGENCY GENERATOR BUILDING | 9881 | Wildlife |  |  | Ruby Valley | 2006 | 640 | 2020-06-05 | Immediate to Two Years | Currently Critical | 1 | 400
3140EXT1 | EXTERIOR FINISHES | 3140 | The exterior finishes are in good condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | REARING BUILDING | 9881 | Wildlife |  |  | Ruby Valley | 2006 | 32264 | 2020-06-05 | Four to Ten Years | Long-Term Needs | 3 | 32264
3139EXT1 | EXTERIOR FINISHES | 3139 | The exterior finishes are in good condition. It is important to maintain the finish, weather resistance, and appearance of the water tank. This project would provide for the painting of the water tank and caulking of the joints to maintain it in a good, weather tight condition. It is recommended that this project be implemented in the next 8 - 9 years and is recommended on a cyclical basis based on environmental conditions. | WATER TANK | 9881 | Wildlife |  |  | Ruby Valley | 2006 | 200 | 2020-06-05 | Four to Ten Years | Long-Term Needs | 3 | 1000
3142EXT1 | EXTERIOR FINISHES | 3142 | The exterior finishes are in good condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is cleaning the vinyl siding and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be cleaned and caulked in the next 8 - 9 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | EMERGENCY GENERATOR BUILDING | 9881 | Wildlife |  |  | Ruby Valley | 2006 | 640 | 2020-06-05 | Four to Ten Years | Long-Term Needs | 3 | 1280
0922SFT2 | FIRE ALARM SYSTEM INSTALLATION | 0922 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2009 Section 7 and the 2018 International Fire Code. This project or a portion thereof was previously recommended in the FCA report dated 06/27/2012. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2020. | GALLAGHER FISH HATCHERY | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 5280 | 2020-06-05 | Immediate to Two Years | Currently Critical | 1 | 33100
0922PLM1 | WATER MAIN REPLACEMENT | 0922 | The main water intake for the hatchery is leaking inside the building and is not equipped with a shut-off valve. This project recommends replacing the water line with a new line and shut-off valve. The estimate includes temporary measures to control the water flow from the natural spring and removal and replacement of the piping. This project provides for an engineered system which will conform to all required environmental rules and regulations including NDEP. This project or a portion thereof was previously recommended in the FCA report dated 06/27/2012. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2020. | GALLAGHER FISH HATCHERY | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 5280 | 2020-06-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 59500
0934INT1 | INTERIOR FINISHES | 0934 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | GALLAGHER FISH HATCHERY RESIDENCE #6 | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 1100 | 2020-06-05 | Four to Ten Years | Long-Term Needs | 3 | 11000
0922HVA1 | AIR CONDITIONER REPLACEMENT | 0922 | The Food Preparation Room is cooled by an older portable evaporative air conditioner. The portable air conditioner is not sufficient to cool the entire space in the warmer months of the year. It is recommended to install an air conditioning system in this area to ensure that the temperature is properly regulated. This project would provide for the purchase and installation of a permanent air conditioner including all required connections to existing utilities. This project or a portion thereof was previously recommended in the FCA report dated 06/27/2012. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2020. | GALLAGHER FISH HATCHERY | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 5280 | 2020-06-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
0922EXT4 | BUILDING STRUCTURAL REPAIRS | 0922 | The south end of the building appears to be structurally settling. The east and west walls have large cracks. This project will fund the structural repairs to the exterior walls, foundation, floor slab, and structural roof repair caused by the cracked, discontinuous structural beams at both the east and west walls which support the roof framing. Repairs will include demolition and replacement of the existing exterior concrete wall panels at main wall cracks, developing expansion joints, repairing existing steel angle roof support ledgers, repairing various locations of perimeter concrete walls, foundation repairs, interior concrete floor slab repairs, structural roof repairs, and the interior walls will be prepped and repainted. This project is written in parallel with 2021 CIP 21248. This project should be implemented concurrently with the WATER INTRUSION REPAIRS project. | GALLAGHER FISH HATCHERY | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 5280 | 2020-06-05 | Immediate to Two Years | Currently Critical | 1 | 630000
0922ELE1 | EXTERIOR LIGHTING REPLACEMENT | 0922 | The building has incandescent lighting on its exterior, but the light fixtures are old, failing, and not energy efficient. This project would provide for the replacement of the exterior lighting fixtures with new LED light fixtures using existing wiring. | GALLAGHER FISH HATCHERY | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 5280 | 2020-06-05 | Four to Ten Years | Long-Term Needs | 3 | 3500
0922ELE2 | WATER INTRUSION REPAIRS | 0922 | Ground water is intermittently entering the building under the main electrical entrance in the northeast corner of the building and is a safety hazard. The apparent cause of the water intrusion is an underground spring located on the northwest side of the building. This project recommends repairs to the existing spring drainage system and installing a French drain around the building to protect the structure and electrical systems. This project is written in parallel with 2021 CIP 21248. This project should be implemented concurrently with the BUILDING STRUCTURAL REPAIRS project. | GALLAGHER FISH HATCHERY | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 5280 | 2020-06-05 | Immediate to Two Years | Currently Critical | 1 | 228000
0922HVA2 | EXHAUST VENTILATION FAN INSTALLATION | 0922 | There is no exhaust ventilation in the Food Preparation Room. The chemicals and food materials used in preparation of the fish food are pungent and an irritant to the personnel handling these materials. This project would provide for the purchase and installation of a new commercial grade exhaust fan work zone system and will include the connections to utilities. This project is written in parallel with 2021 CIP 21248. | GALLAGHER FISH HATCHERY | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 5280 | 2020-06-05 | Immediate to Two Years | Currently Critical | 1 | 28500
0928INT1 | INTERIOR FINISHES | 0928 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | GALLAGHER FISH HATCHERY RESIDENCE #2 | 9881 | Wildlife |  |  | Ruby Valley | 1956 | 1100 | 2020-06-05 | Four to Ten Years | Long-Term Needs | 3 | 5500
0922SFT3 | EXIT SIGN AND EGRESS LIGHTING INSTALLATION | 0922 | The building does not have any emergency lighting or exit signs. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2018 Chapter 10 was referenced for this project. This project is written in parallel with 2021 CIP 21248. This project or a portion thereof was previously recommended in the FCA report dated 06/27/2012. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2020. | GALLAGHER FISH HATCHERY | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 5280 | 2020-06-05 | Immediate to Two Years | Currently Critical | 1 | 19000
0927SIT1 | TRIM OR REMOVE TREES ADJOINING BUILDINGS | 0927 | Large trees are growing up against the structures. The trees move in windy conditions, rubbing the roof, which can cause premature failure of the roof system. The trees need pruning of all branches immediately above the roof and removal of dead branches that can fall and damage the roof. | GALLAGHER HATCHERY RESIDENCE #1 GARAGE | 9881 | Wildlife |  |  | Ruby Valley | 1956 | 288 | 2020-06-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
0927EXT3 | ROOF REPLACEMENT | 0927 | The asphalt composition shingle roof on this building was in fair condition at the time of the survey. It is recommended that this building be re-roofed in the next 6 - 8 years with a new 50 year asphalt composition shingle roof and new underlayment. This estimate includes removal and disposal of the old roofing system. | GALLAGHER HATCHERY RESIDENCE #1 GARAGE | 9881 | Wildlife |  |  | Ruby Valley | 1956 | 288 | 2020-06-05 | Four to Ten Years | Long-Term Needs | 3 | 5400
0927EXT2 | EXTERIOR FINISHES | 0927 | The exterior finishes are in poor condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting, and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2 - 3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | GALLAGHER HATCHERY RESIDENCE #1 GARAGE | 9881 | Wildlife |  |  | Ruby Valley | 1956 | 288 | 2020-06-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2900
0928SFT4 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0928 | This building is an R occupancy. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state regardless of occupancy having a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an "R" occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. | GALLAGHER FISH HATCHERY RESIDENCE #2 | 9881 | Wildlife |  |  | Ruby Valley | 1956 | 1100 | 2020-06-05 | Four to Ten Years | Long-Term Needs | 3 | 19800
0928EXT2 | WIND SCREEN REFURBISHMENT | 0928 | The finish on the front entry wind screen is severely weather checked and the lattice is missing slats. This project would fund refinishing the structure and replacing the wood lattice with vinyl. | GALLAGHER FISH HATCHERY RESIDENCE #2 | 9881 | Wildlife |  |  | Ruby Valley | 1956 | 1100 | 2020-06-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0926SFT1 | SMOKE ALARM & CARBON MONOXIDE ALARM INSTALLATION | 0926 | This building is lacking a carbon monoxide detection system and missing some smoke alarms. 2018 IRC R314 & R315, IFC 2018 Section 1103.8 & 1103.9 (Smoke Alarms & Carbon Monoxide Detection for Existing Buildings) define requirements in Dwelling Units and Sleeping Units (Group I & R Occupancies) for buildings containing fuel-burning appliances. The carbon monoxide alarms shall be listed as complying with UL 2034, be installed and maintained in accordance with NFPA 720 and the manufacturer’s instructions. This project would provide funding for the purchase and installation of carbon monoxide alarms in accordance with this code. | GALLAGHER FISH HATCHERY RESIDENCE #1 | 9881 | Wildlife |  |  | Ruby Valley | 1956 | 1100 | 2020-06-05 | Immediate to Two Years | Currently Critical | 1 | 1500
0928SFT2 | EXTERIOR STAIR HANDRAIL INSTALLATION | 0928 | The concrete exterior stairs at the entry are lacking a handrail as required in section R311.7.8 of the 2018 International Residential Code. This project would provide for a tubular steel framed handrail to be installed in accordance with the code. This project or a portion thereof was previously recommended in the FCA report dated 06/27/2012. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2020 | GALLAGHER FISH HATCHERY RESIDENCE #2 | 9881 | Wildlife |  |  | Ruby Valley | 1956 | 1100 | 2020-06-05 | Immediate to Two Years | Currently Critical | 1 | 3500
0926INT1 | INTERIOR FINISHES | 0926 | The interior finishes are in poor condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2 - 3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | GALLAGHER FISH HATCHERY RESIDENCE #1 | 9881 | Wildlife |  |  | Ruby Valley | 1956 | 1100 | 2020-06-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5500
0928EXT1 | EXTERIOR FINISHES | 0928 | The exterior finishes are in good condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is cleaning the vinyl siding and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be cleaned and caulked in the next 8 - 9 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | GALLAGHER FISH HATCHERY RESIDENCE #2 | 9881 | Wildlife |  |  | Ruby Valley | 1956 | 1100 | 2020-06-05 | Four to Ten Years | Long-Term Needs | 3 | 11000
0929EXT1 | EXTERIOR FINISHES | 0929 | The exterior finishes were in fair condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting, and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | GALLAGHER HATCHERY RESIDENCE #2 GARAGE | 9881 | Wildlife |  |  | Ruby Valley | 1956 | 288 | 2020-06-05 | Four to Ten Years | Long-Term Needs | 3 | 1440
0931EXT1 | EXTERIOR FINISHES | 0931 | The exterior finishes are in poor condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting, and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2 -3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | GALLAGHER HATCHERY RESIDENCE #3 GARAGE | 9881 | Wildlife |  |  | Ruby Valley | 1956 | 288 | 2020-06-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1440
0932INT2 | FLOORING REPLACEMENT | 0932 | The flooring in the residence is reaching the end of its useful life. It is recommended that all of the flooring in the residence be replaced. This project would provide for removal and disposal of the existing flooring and installation of new flooring. | GALLAGHER FISH HATCHERY RESIDENCE #4 | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 1100 | 2020-06-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12400
0932ENV1 | PEST CONTROL | 0932 | There are numerous signs throughout this residence of insect infestation including ants. Due to the potential risk of disease and damage to the building, this project provides for treatment and clean up of the insects by a licensed pest control business. It is recommended that the residence be treated in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain control of the pests. | GALLAGHER FISH HATCHERY RESIDENCE #4 | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 1100 | 2020-06-05 | Immediate to Two Years | Currently Critical | 1 | 1200
0935EXT2 | DEMOLISH STRUCTURE | 0935 | The structure is dilapidated, deteriorating, and is over 50 years of age. It is no longer in use. This project would provide funding for the demolition and disposal of the structure. | GALLAGHER HATCHERY SHADE SHELTER NORTH | 9881 | Wildlife |  |  | Ruby Valley | 1955 | 804 | 2020-06-05 | Four to Ten Years | Long-Term Needs | 3 | 1500
0932SFT2 | CARBON MONOXIDE DETECTOR INSTALLATION | 0932 | This building is lacking a carbon monoxide detection system. 2018 IRC R315, IFC 2018 Section 1109.3 (Carbon Monoxide Detection for Existing Buildings) and Section 915 carbon monoxide alarm requirements in Dwelling Units and Sleeping Units (Group I & R Occupancies) for buildings containing fuel-burning appliances. The carbon monoxide alarm(s) shall be listed as complying with UL 2034 and be installed and maintained in accordance with NFPA 720 and the manufacturer’s instructions. This project would provide funding for the purchase and installation of carbon monoxide alarms in accordance with this code. | GALLAGHER FISH HATCHERY RESIDENCE #4 | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 1100 | 2020-06-05 | Immediate to Two Years | Currently Critical | 1 | 900
0928SFT3 | CARBON MONOXIDE DETECTOR INSTALLATION | 0928 | This building is lacking a carbon monoxide detection system. 2018 IRC R315, IFC 2018 Section 1109.3 (Carbon Monoxide Detection for Existing Buildings) and Section 915 carbon monoxide alarm requirements in Dwelling Units and Sleeping Units (Group I & R Occupancies) for buildings containing fuel-burning appliances. The carbon monoxide alarm(s) shall be listed as complying with UL 2034 and be installed and maintained in accordance with NFPA 720 and the manufacturer’s instructions. This project would provide funding for the purchase and installation of carbon monoxide alarms in accordance with this code. | GALLAGHER FISH HATCHERY RESIDENCE #2 | 9881 | Wildlife |  |  | Ruby Valley | 1956 | 1100 | 2020-06-05 | Immediate to Two Years | Currently Critical | 1 | 900
0926SFT4 | BASEMENT EMERGENCY ESCAPE INSTALLATION | 0926 | An additional sleeping area has been added to the basement of the residence. Based on 2018 IRC R310.6 Exception which states that "New sleeping rooms created in an existing basement shall be provided with emergency escape..." it is recommended that an additional emergency escape be added in accordance to the R310 requirements. This project would create an approved escape through a modified window well or retrofitting the abandoned coal slide located on the south side of the residence. | GALLAGHER FISH HATCHERY RESIDENCE #1 | 9881 | Wildlife |  |  | Ruby Valley | 1956 | 1100 | 2020-06-05 | Immediate to Two Years | Currently Critical | 1 | 15000
0923SFT6 | INTERIOR STAIR HANDRAIL REPLACEMENT | 0923 | The interior stair handrails are older and do not meet code for safety. The gripping surfaces are incorrect, they are not continuous from the top to bottom landings and they are installed on only one side of the stair. This project recommends the installation of handrails on both sides of the stairs with proper returns and supports in accordance with the 2018 IBC Chapter 10, Section 1012. This project or a portion thereof was previously recommended in the FCA report dated 06/27/2012. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2020. | GALLAGHER FISH HATCHERY OFFICE & SHOP | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 3246 | 2020-06-05 | Immediate to Two Years | Currently Critical | 1 | 1500
0923ADA1 | ADA ENTRANCE AND PATH OF TRAVEL | 0923 | The existing exterior entrance door and threshold to the Office are not accessible and there is no accessible path of travel inside the building. This project would provide for a new accessible door and threshold assembly including removal of the existing door assembly and installation of the new accessible door assembly and a compliant path of travel throughout the upper floor and to the accessible restroom. ADA compliant signage is also included in this project. The 2018 IBC, ICC/ANSI A117.1, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 06/27/2012. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2020. | GALLAGHER FISH HATCHERY OFFICE & SHOP | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 3246 | 2020-06-05 | Immediate to Two Years | Currently Critical | 1 | 3500
0923EXT1 | EXTERIOR FINISHES | 0923 | The exterior finishes on the wood portion at the entry is in poor condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is cleaning and sealing the concrete, sanding, priming and painting the wood, and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and painted in the next 2 -3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | GALLAGHER FISH HATCHERY OFFICE & SHOP | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 3246 | 2020-06-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16230
0923EXT2 | OVERHEAD DOOR REPLACEMENT | 0923 | Three of the four 10'x14' overhead coiling doors are damaged and do not function properly. The other overhead door was recently replaced. Exposure and wind have caused the doors to bend, crack, and lose their finish. They are original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead coiling doors and replacement with new manually operated insulated overhead coiling doors. This project or a portion thereof was previously recommended in the FCA report dated 06/27/2012. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2020. | GALLAGHER FISH HATCHERY OFFICE & SHOP | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 3246 | 2020-06-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18000
0926SFT5 | WATER HEATER SEISMIC BRACING | 0926 | The water heater is not properly seismically anchored to the structure and is missing a drip pan. The 2018 IRC P2801.8 "...water heaters shall be anchored or strapped in the upper one-third and in the lower one-third of the appliance...". This project would provide funding for compliant seismic bracing and installation of a drip pan under the water heater. | GALLAGHER FISH HATCHERY RESIDENCE #1 | 9881 | Wildlife |  |  | Ruby Valley | 1956 | 1100 | 2020-06-05 | Immediate to Two Years | Currently Critical | 1 | 400
0926INT4 | KITCHEN REMODEL | 0926 | The kitchen is in fair to poor condition. The cabinets and equipment are showing signs of general wear and tear and are approaching the end of their expected life. This project recommends the replacement of the existing kitchen cabinets, countertops, fixtures, and equipment with mid range, high quality components. | GALLAGHER FISH HATCHERY RESIDENCE #1 | 9881 | Wildlife |  |  | Ruby Valley | 1956 | 1100 | 2020-06-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0927EXT4 | GARAGE DOOR REPLACEMENT | 0927 | The garage door is original to the building and has deteriorated from weather exposure. It has reached the end of its useful life. It is recommended that a new door be installed. | GALLAGHER HATCHERY RESIDENCE #1 GARAGE | 9881 | Wildlife |  |  | Ruby Valley | 1956 | 288 | 2020-06-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
0926SFT6 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0926 | This building is an R occupancy. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state regardless of occupancy having a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an "R" occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. | GALLAGHER FISH HATCHERY RESIDENCE #1 | 9881 | Wildlife |  |  | Ruby Valley | 1956 | 1100 | 2020-06-05 | Four to Ten Years | Long-Term Needs | 3 | 19800
0932ELE1 | GFCI OUTLET INSTALLATION | 0932 | The existing receptacles outside the residence, in the kitchen, and bathrooms appear to be standard duplex receptacles and may not be GFCI protected. The 2017 NEC 210.8 requires all locations within 6 feet of a water source, garages, accessory buildings, and outdoors shall have GFCI protection. This project would provide for removing the standard receptacles and installing GFCI receptacles. | GALLAGHER FISH HATCHERY RESIDENCE #4 | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 1100 | 2020-06-05 | Immediate to Two Years | Currently Critical | 1 | 150
0926SIT1 | SITE DRAINAGE IMPROVEMENTS | 0926 | The house has considerable soil accumulation at the foundation windows from improper drainage around the building. The grade does not slope away from the building in several areas, especially on the west side of the building. This is causing water to pool up next to the building, infiltrate the windows, and damage the concrete foundation walls. This project would create positive flow away from the building by regrading. | GALLAGHER FISH HATCHERY RESIDENCE #1 | 9881 | Wildlife |  |  | Ruby Valley | 1956 | 1100 | 2020-06-05 | Immediate to Two Years | Currently Critical | 1 | 3700
0926SFT3 | EXTERIOR STAIR HANDRAIL INSTALLATION | 0926 | The concrete exterior stairs at the entry are lacking a handrail as required in Section R311.7.8 of the 2018 International Residential Code. This project would provide for a tubular steel framed handrail to be installed in accordance with the code. This project should be implemented concurrently with the CONCRETE STAIR REPLACEMENT project. | GALLAGHER FISH HATCHERY RESIDENCE #1 | 9881 | Wildlife |  |  | Ruby Valley | 1956 | 1100 | 2020-06-05 | Immediate to Two Years | Currently Critical | 1 | 3500
0926SFT2 | CONCRETE STAIR REPLACEMENT | 0926 | The concrete stairs that access the front of the residence are not built to code, are a safety hazard, and should be replaced. 2018 IRC R311.7.5.1 allows no more than 3/8" difference in height between the tallest and shortest riser. It appears that removing, regrading, and replacing the concrete landing at the bottom of the existing stairs may meet this requirement; however, final scope of work shall be determined by the proper authorities. This project should be implemented concurrently with the EXTERIOR STAIR HANDRAIL INSTALLATION project. | GALLAGHER FISH HATCHERY RESIDENCE #1 | 9881 | Wildlife |  |  | Ruby Valley | 1956 | 1100 | 2020-06-05 | Immediate to Two Years | Currently Critical | 1 | 2500
0926EXT2 | EXTERIOR DOOR & JAM REPLACEMENT | 0926 | The existing exterior metal door and frame at the rear entrance appear to be showing signs of rot. They are damaged from age and general wear and tear. This project would provide for the replacement and installation of a new metal door, frame, and hardware. Removal and disposal of the existing door and painting of the new door is included in this estimate. | GALLAGHER FISH HATCHERY RESIDENCE #1 | 9881 | Wildlife |  |  | Ruby Valley | 1956 | 1100 | 2020-06-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
0926INT2 | VINYL FLOORING REPLACEMENT | 0926 | The vinyl flooring in the kitchen is damaged and reaching the end of its useful life. It is recommended that the vinyl flooring in the kitchen and bathroom be replaced. This project would provide for removal and disposal of the vinyl flooring and installation of the new vinyl flooring and base. This project should be implemented concurrently with the KITCHEN REMODEL and RESTROOM REMODEL project. | GALLAGHER FISH HATCHERY RESIDENCE #1 | 9881 | Wildlife |  |  | Ruby Valley | 1956 | 1100 | 2020-06-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
0926HVA1 | HVAC EQUIPMENT REPLACEMENT | 0926 | The existing ground set packaged HVAC system is reaching the end of its useful life. This project would provide for replacing the existing equipment with an exterior ground mounted packaged unit that provides propane gas-fired heating as well as air conditioning. The existing ducting and vents will need to be cleaned and repaired as well. This project includes removal and disposal of the existing HVAC unit and all required connections to utilities. | GALLAGHER FISH HATCHERY RESIDENCE #1 | 9881 | Wildlife |  |  | Ruby Valley | 1956 | 1100 | 2020-06-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
0926EXT1 | EXTERIOR FINISHES | 0926 | The exterior finishes of the vinyl siding are in good condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is cleaning the vinyl siding and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be cleaned and caulked in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | GALLAGHER FISH HATCHERY RESIDENCE #1 | 9881 | Wildlife |  |  | Ruby Valley | 1956 | 1100 | 2020-06-05 | Four to Ten Years | Long-Term Needs | 3 | 5500
0926INT3 | RESTROOM REMODEL | 0926 | The restroom in the residence is original to the building and in overall poor condition. The finishes, fixtures, cabinets, toilets, showers, and exhaust fans are showing signs of wear and deterioration. This project would provide for a complete remodel of the restroom. The removal and disposal of the existing fixtures and finishes are included in this estimate. | GALLAGHER FISH HATCHERY RESIDENCE #1 | 9881 | Wildlife |  |  | Ruby Valley | 1956 | 1100 | 2020-06-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0923ELE2 | EXTERIOR LIGHTING REPLACEMENT | 0923 | The building has 2 incandescent site lighting fixtures on the exterior of the building and is missing exterior lighting at the entry door. The light fixtures are old, failing, and not energy efficient. This project would provide for installing a new fixture at the front entry and the replacement of the exterior lighting fixtures with new LED light fixtures using existing wiring. | GALLAGHER FISH HATCHERY OFFICE & SHOP | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 3246 | 2020-06-05 | Four to Ten Years | Long-Term Needs | 3 | 1500
0933SFT2 | CARBON MONOXIDE DETECTOR INSTALLATION | 0933 | This building is lacking a carbon monoxide detection system. 2018 IRC R315, IFC 2018 Section 1109.3 (Carbon Monoxide Detection for Existing Buildings) and Section 915 carbon monoxide alarm requirements in Dwelling Units and Sleeping Units (Group I & R Occupancies) for buildings containing fuel-burning appliances. The carbon monoxide alarm(s) shall be listed as complying with UL 2034 and be installed and maintained in accordance with NFPA 720 and the manufacturer’s instructions. This project would provide funding for the purchase and installation of carbon monoxide alarms in accordance with this code. | GALLAGHER FISH HATCHERY RESIDENCE #5 | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 1100 | 2020-06-05 | Immediate to Two Years | Currently Critical | 1 | 900
0933SFT3 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0933 | This building is an R occupancy. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state regardless of occupancy having a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an "R" occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. | GALLAGHER FISH HATCHERY RESIDENCE #5 | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 1100 | 2020-06-05 | Four to Ten Years | Long-Term Needs | 3 | 19800
0933SIT1 | CONCRETE REPLACEMENT | 0933 | The existing concrete driveway is cracked, spalling, and presents a tripping hazard to pedestrians. Exposure to the weather has contributed to the damage and deterioration. It is believed the concrete is part of the original construction. This project would provide funding for the removal and disposal of the existing concrete and the installation of a new 4" thick concrete driveway. This project should coincide with other concrete work recommended for the site. This project or a portion thereof was previously recommended in the FCA report dated 06/27/2012. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2020. | GALLAGHER FISH HATCHERY RESIDENCE #5 | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 1100 | 2020-06-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
0933EXT1 | EXTERIOR FINISHES | 0933 | The exterior finishes are in fair condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is cleaning the vinyl siding and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be cleaned and caulked in the next 4 - 5 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | GALLAGHER FISH HATCHERY RESIDENCE #5 | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 1100 | 2020-06-05 | Four to Ten Years | Long-Term Needs | 3 | 5500
0936ELE2 | LIGHTING UPGRADE | 0936 | The existing lighting fixtures appear to be older incandescent type and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. LED are suggested using the existing wiring and conduit. | GALLAGHER HATCHERY SHADE SHELTER #1 | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 11000 | 2020-06-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
0936ELE1 | GFCI OUTLET INSTALLATION & PROTECTION | 0936 | The existing 220v receptacles mounted to the building column are not labeled as GFCI protected. In addition, 120v power is requested to be added at the same location. The new 120v circuit shall be GFCI protected. The 2017 NEC 210.8 requires all locations within 6 feet of a water source, garages, accessory buildings, and outdoors shall have GFCI protection. This project would provide for removing the standard receptacles and installing GFCI receptacles. | GALLAGHER HATCHERY SHADE SHELTER #1 | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 11000 | 2020-06-05 | Immediate to Two Years | Currently Critical | 1 | 500
0936EXT1 | EXTERIOR/ INTERIOR FINISHES | 0936 | The painted finishes are in poor condition with paint flaking off columns and potentially landing in the fish raceways. It is important to maintain the finish, weather resistance, and appearance of the structure. This project would provide for painting of the structure in 2 - 3 years and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | GALLAGHER HATCHERY SHADE SHELTER #1 | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 11000 | 2020-06-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 33000
0934EXT1 | EXTERIOR FINISHES | 0934 | The exterior finishes are in poor condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is cleaning the vinyl siding and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be cleaned and caulked in the next 2 - 3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | GALLAGHER FISH HATCHERY RESIDENCE #6 | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 1100 | 2020-06-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5500
0922EXT1 | EXTERIOR FINISHES | 0922 | The exterior finishes are in fair condition excluding the structural cracks associated with settling (addressed separately). It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete walls, and caulking of the windows, flashing, fixtures, cracks in the concrete and all other penetrations. It is recommended that the building be sealed and caulked in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | GALLAGHER FISH HATCHERY | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 5280 | 2020-06-05 | Four to Ten Years | Long-Term Needs | 3 | 26400
0922INT1 | INTERIOR FINISHES | 0922 | The interior finishes are in poor condition due to high humidity and spot corrosion on interior surfaces. It is recommended that the interior walls and ceilings be painted at least once in the next 2 - 3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | GALLAGHER FISH HATCHERY | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 5280 | 2020-06-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 52800
0923SFT7 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0923 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. | GALLAGHER FISH HATCHERY OFFICE & SHOP | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 3246 | 2020-06-05 | Immediate to Two Years | Currently Critical | 1 | 5000
0932SFT3 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0932 | This building is an R occupancy. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state regardless of occupancy having a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an "R" occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. | GALLAGHER FISH HATCHERY RESIDENCE #4 | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 1100 | 2020-06-05 | Four to Ten Years | Long-Term Needs | 3 | 19800
0932INT1 | INTERIOR FINISHES | 0932 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | GALLAGHER FISH HATCHERY RESIDENCE #4 | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 1100 | 2020-06-05 | Four to Ten Years | Long-Term Needs | 3 | 11000
0923HVA1 | HVAC EQUIPMENT REPLACEMENT | 0923 | The existing HVAC system in the office and boot area (below the office) consists of 2 electric baseboard heaters, 1 small evaporative cooler, and a propane wall heater. The shop area has 3 small gas fired infrared heaters. The electric heaters are inefficient and should be replaced with propane fired heaters. There is a need for cooling equipment to provide a comfortable work environment in the summer. This project would provide for replacing the equipment conditioning the office space and boot area with exterior ground mounted packaged units that provide propane fired heating as well as air conditioning. The shop area infrared heaters would be replaced with larger more efficient gas tube infrared heaters providing better comfort heating shop wide. | GALLAGHER FISH HATCHERY OFFICE & SHOP | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 3246 | 2020-06-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 61100
0932SIT1 | CONCRETE REPLACEMENT | 0932 | The existing concrete driveway is cracked, spalling, and presents a tripping hazard to pedestrians. Exposure to the weather has contributed to the damage and deterioration. It is believed the concrete is part of the original construction. This project would provide funding for the removal and disposal of the existing concrete and the installation of a new 4" thick concrete driveway. This project should coincide with other concrete work recommended for the site. This project or a portion thereof was previously recommended in the FCA report dated 06/27/2012. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2020. | GALLAGHER FISH HATCHERY RESIDENCE #4 | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 1100 | 2020-06-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
0923INT1 | INTERIOR FINISHES | 0923 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. The non-painted walls in the shop area are excluded from the estimate. | GALLAGHER FISH HATCHERY OFFICE & SHOP | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 3246 | 2020-06-05 | Four to Ten Years | Long-Term Needs | 3 | 11000
0923SFT5 | FIRE ALARM SYSTEM INSTALLATION | 0923 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1Section 7 and the 2018 International Fire Code. This project or a portion thereof was previously recommended in the FCA report dated 06/27/2012. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2020. | GALLAGHER FISH HATCHERY OFFICE & SHOP | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 3246 | 2020-06-05 | Immediate to Two Years | Currently Critical | 1 | 16300
0923ENV1 | BAT AND BIRD ABATEMENT | 0923 | There are numerous bat and bird droppings throughout the inside and outside of the building. Due to the potential risk of disease, this project provides for treatment and clean up of the pests by a licensed pest control business. This project or a portion thereof was previously recommended in the FCA report dated 06/27/2012. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2020. | GALLAGHER FISH HATCHERY OFFICE & SHOP | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 3246 | 2020-06-05 | Immediate to Two Years | Currently Critical | 1 | 2500
0923ENR1 | WINDOW REPLACEMENT | 0923 | The windows are original, dual pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 6 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 06/27/2012. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2020. | GALLAGHER FISH HATCHERY OFFICE & SHOP | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 3246 | 2020-06-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
0939EXT1 | EXTERIOR FINISHES | 0939 | The exterior finishes are in fair condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting, and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | DOMESTIC PUMP HOUSE | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 88 | 2020-06-05 | Four to Ten Years | Long-Term Needs | 3 | 900
0939INT1 | INTERIOR FINISHES | 0939 | The interior finishes are in poor condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2 - 3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | DOMESTIC PUMP HOUSE | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 88 | 2020-06-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1800
0934SIT1 | CONCRETE REPLACEMENT | 0934 | The existing concrete driveway is cracked, spalling, and presents a tripping hazard to pedestrians. Exposure to the weather has contributed to the damage and deterioration. It is believed the concrete is part of the original construction. This project would provide funding for the removal and disposal of the existing concrete and the installation of a new 4" thick concrete driveway. This project should coincide with other concrete work recommended for the site. This project or a portion thereof was previously recommended in the FCA report dated 06/27/2012. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2020. | GALLAGHER FISH HATCHERY RESIDENCE #6 | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 1100 | 2020-06-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
0934SFT3 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0934 | This building is an R occupancy. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state regardless of occupancy having a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an "R" occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. | GALLAGHER FISH HATCHERY RESIDENCE #6 | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 1100 | 2020-06-05 | Four to Ten Years | Long-Term Needs | 3 | 19800
0934SFT5 | EXTERIOR STAIR HANDRAIL INSTALLATION | 0934 | The concrete exterior stairs at the entry are lacking a compliant hand and handrail as required in Section R311.7.8 of the 2018 International Residential Code. This project would provide for a tubular steel framed handrail to be installed in accordance with the code. | GALLAGHER FISH HATCHERY RESIDENCE #6 | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 1100 | 2020-06-05 | Immediate to Two Years | Currently Critical | 1 | 3500
0934SFT2 | CARBON MONOXIDE DETECTOR INSTALLATION | 0934 | This building is lacking a carbon monoxide detection system. 2018 IRC R315, IFC 2018 Section 1109.3 (Carbon Monoxide Detection for Existing Buildings) and Section 915 carbon monoxide alarm requirements in Dwelling Units and Sleeping Units (Group I & R Occupancies) for buildings containing fuel-burning appliances. The carbon monoxide alarm(s) shall be listed as complying with UL 2034 and be installed and maintained in accordance with NFPA 720 and the manufacturer’s instructions. This project would provide funding for the purchase and installation of carbon monoxide alarms in accordance with this code. | GALLAGHER FISH HATCHERY RESIDENCE #6 | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 1100 | 2020-06-05 | Immediate to Two Years | Currently Critical | 1 | 900
0934SFT4 | WATER HEATER SEISMIC BRACING | 0934 | The water heater is not seismically anchored to the structure. This project would provide funding for seismic bracing of the water heater to the structure. | GALLAGHER FISH HATCHERY RESIDENCE #6 | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 1100 | 2020-06-05 | Immediate to Two Years | Currently Critical | 1 | 200
0934EXT2 | ROOF REPLACEMENT | 0934 | The asphalt composition shingle roof on this building was in fair condition at the time of the survey. It is recommended that this building be re-roofed in the next 3 - 4 years with a new 50 year asphalt composition shingle roof and new underlayment. This estimate includes removal and disposal of the old roofing system. | GALLAGHER FISH HATCHERY RESIDENCE #6 | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 1100 | 2020-06-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20700
0933INT1 | INTERIOR FINISHES | 0933 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4 - 5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | GALLAGHER FISH HATCHERY RESIDENCE #5 | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 1100 | 2020-06-05 | Four to Ten Years | Long-Term Needs | 3 | 11000
0923EXT3 | ROOF REPLACEMENT | 0923 | The asphalt composition shingle roof on the building entry was in fair condition at the time of the survey. It is recommended that this building be re-roofed in the next 4 - 5 years with a new 50 year asphalt composition shingle roof and new underlayment. This estimate includes removal and disposal of the old roofing system. | GALLAGHER FISH HATCHERY OFFICE & SHOP | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 3246 | 2020-06-05 | Four to Ten Years | Long-Term Needs | 3 | 5600
0932EXT1 | EXTERIOR FINISHES | 0932 | The exterior finishes are in fair condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is cleaning the vinyl siding and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be cleaned and caulked in the next 4 - 5 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | GALLAGHER FISH HATCHERY RESIDENCE #4 | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 1100 | 2020-06-05 | Four to Ten Years | Long-Term Needs | 3 | 5500
2447EXT2 | DEMOLISH STRUCTURE | 2447 | The structure is dilapidated and deteriorating and has reached the end of its useful life. The structure is over 50 years of age, has had continuous roof leaks. This project would provide funding for the demolition and disposal of the building. | QUONSET STORAGE | 9909 | Wildlife |  |  | Winnemucca | 1957 | 1120 | 2020-06-18 | Four to Ten Years | Long-Term Needs | 3 | 14000
2445EXT2 | EXTERIOR DOOR REPAIRS | 2445 | The two exterior metal man doors are damaged from age, general wear and tear, and are due for repairs. This project would provide for painting the doors and replacing the weather seals to maintain the doors in good working condition. This project or a portion thereof was previously recommended in the FCA report dated 05/11/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/18/2020. | NDOW SHOP | 9909 | Wildlife |  |  | Winnemucca | 1984 | 1260 | 2020-06-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
2445ENR1 | LIGHTING UPGRADE | 2445 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade the fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, closets, and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 05/11/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/18/2020. | NDOW SHOP | 9909 | Wildlife |  |  | Winnemucca | 1984 | 1260 | 2020-06-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3200
2445SFT2 | EXIT SIGN AND EGRESS LIGHTING INSTALLATION | 2445 | The building does not have any emergency lighting and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2006 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 05/11/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/18/2020. | NDOW SHOP | 9909 | Wildlife |  |  | Winnemucca | 1984 | 1260 | 2020-06-18 | Immediate to Two Years | Currently Critical | 1 | 3200
2445INT1 | RESTROOM REMODEL | 2445 | The restroom fixtures and finishes are in disrepair from general wear and tear, and should be scheduled for replacement. This project would provide for a complete remodel of the restroom including fixtures, hardware, floor, and wall finishes. This project or a portion thereof was previously recommended in the FCA report dated 05/11/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/18/2020. | NDOW SHOP | 9909 | Wildlife |  |  | Winnemucca | 1984 | 1260 | 2020-06-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
2445PLM1 | WATER HEATER REPLACEMENT | 2445 | There is a 10 gallon water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 4-5 years. It is recommended that a new natural gas fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 05/11/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/18/2020. | NDOW SHOP | 9909 | Wildlife |  |  | Winnemucca | 1984 | 1260 | 2020-06-18 | Four to Ten Years | Long-Term Needs | 3 | 1200
2446EXT2 | ROOF REPLACEMENT | 2446 | The corrugated metal roof on this building was in poor condition at the time of the survey and staff reported that there are active leaks. It is recommended that this building be re-roofed in the next 1-2 years with a standing seam metal roofing system. This estimate includes removal and disposal of the old roof. This project or a portion thereof was previously recommended in the FCA report dated 05/11/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/18/2020. | NDOW GAS STORAGE | 9909 | Wildlife |  |  | Winnemucca | 0 | 512 | 2020-06-18 | Immediate to Two Years | Currently Critical | 1 | 9600
2446ENV1 | PROVIDE HAZARDOUS MATERIALS CONTAINMENT | 2446 | At the time of the survey, there were oil drums stored on bare dirt next to the building as well as cans of pesticide and gas cans stored in the same area. This does not meet OSHA standards for proper storage containment. The oil drums should be stored on OSHA approved drum spill pallets and placed on a concrete slab in order to protect the environment from spills or leaks. This project will provide for purchasing four OSHA approved drum spill pallets capable of storing four drums each and purchasing an OSHA approved storage cabinet for miscellaneous items such as the gas cans. According to OSHA 1910.106 (d), a proper storage container shall be provided for flammable or combustible liquids in drums or other containers (including flammable aerosols) not exceeding 60 gallons individual capacity and those portable tanks not exceeding 660 gallons individual capacity. This project or a portion thereof was previously recommended in the FCA report dated 05/11/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/18/2020. | NDOW GAS STORAGE | 9909 | Wildlife |  |  | Winnemucca | 0 | 512 | 2020-06-18 | Immediate to Two Years | Currently Critical | 1 | 18000
2433ELE2 | ELECTRICAL PANEL UPGRADE | 2433 | The electrical panel on the second floor is recognized as a safety hazard. Federal Pacific Stab-Loc panels were part of a safety recall and should be replaced. Additionally, complaints by local staff indicate nuisance trips of the 30 amp breaker in this panel feeding the water heater. This project would provide funding for the installation of a replacement breaker panel, investigate and solve the cause of the nuisance trips, and removal and disposal of the existing panel. | WINNEMUCCA MAIN OFFICE BUILDING | 9909 | Wildlife |  |  | Winnemucca | 1964 | 7900 | 2020-06-18 | Immediate to Two Years | Currently Critical | 1 | 7500
2445EXT1 | EXTERIOR FINISHES | 2445 | The exterior finishes are in good condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 7 - 8 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NDOW SHOP | 9909 | Wildlife |  |  | Winnemucca | 1984 | 1260 | 2020-06-18 | Four to Ten Years | Long-Term Needs | 3 | 1400
2446EXT1 | EXTERIOR FINISHES | 2446 | The exterior finishes are in poor condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting, and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2 -3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NDOW GAS STORAGE | 9909 | Wildlife |  |  | Winnemucca | 0 | 512 | 2020-06-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2560
2433INT5 | INTERIOR FINISHES | 2433 | The interior finishes are in good condition. It is recommended to paint the interior walls and ceilings at least once in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | WINNEMUCCA MAIN OFFICE BUILDING | 9909 | Wildlife |  |  | Winnemucca | 1964 | 7900 | 2020-06-18 | Four to Ten Years | Long-Term Needs | 3 | 39500
2436EXT4 | WINDOW REPLACEMENT | 2436 | The windows are original, single pane construction in a wooden frame. These older windows are damaged and the wooden frames have deteriorated significantly. This project recommends replacing the windows with dual pane windows. This estimate is for the replacement of 2 small units and 2 larger units including wooden frames. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 05/11/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/18/2020. | NDOW LEAN-TO STORAGE | 9909 | Wildlife |  |  | Winnemucca | 1955 | 5596 | 2020-06-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
2436EXT1 | EXTERIOR DOOR REPLACEMENT | 2436 | The existing exterior wood door appears to be original to the building. It is damaged from age, general wear and tear, and the lock is not secure. This project would provide for the replacement of the wood door with a new metal door, frame, and hardware. Removal and disposal of the existing door and painting of the new door is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 05/11/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/18/2020. | NDOW LEAN-TO STORAGE | 9909 | Wildlife |  |  | Winnemucca | 1955 | 5596 | 2020-06-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
2436EXT3 | ROOF REPLACEMENT | 2436 | The corrugated metal on this building was in poor condition at the time of the survey and is showing signs of leaking. It is recommended that this building be re-roofed in the next 2 - 3 years with a standing seam metal roofing system. This estimate includes removal and disposal of the old roofing system. This project or a portion thereof was previously recommended in the FCA report dated 05/11/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/18/2020. | NDOW LEAN-TO STORAGE | 9909 | Wildlife |  |  | Winnemucca | 1955 | 5596 | 2020-06-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 105300
2436EXT2 | EXTERIOR FINISHES | 2436 | The exterior finishes are in poor condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting, and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2 - 3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project should be implemented concurrently with the EXTERIOR SIDING REPLACEMENT project. | NDOW LEAN-TO STORAGE | 9909 | Wildlife |  |  | Winnemucca | 1955 | 5596 | 2020-06-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 28000
2436EXT5 | EXTERIOR SIDING REPLACEMENT | 2436 | The lean-to has painted lap siding that is due for replacement. The existing siding is in poor condition and will no longer hold paint. This project recommends removing the existing siding and to replace it with new T1-11 siding finished with an oil-based paint. | NDOW LEAN-TO STORAGE | 9909 | Wildlife |  |  | Winnemucca | 1955 | 5596 | 2020-06-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 27980
2433ADA4 | ADA SIGNAGE | 2433 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The parking signage outside this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2018 IBC, ICC/ANSI A117.1, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/01/2015. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/18/2020. | WINNEMUCCA MAIN OFFICE BUILDING | 9909 | Wildlife |  |  | Winnemucca | 1964 | 7900 | 2020-06-18 | Immediate to Two Years | Currently Critical | 1 | 600
2433INT6 | KITCHENETTE REPLACEMENT | 2433 | The kitchenette and associated cabinets in the first floor of the two level portion of the building are over 20 years old. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and countertop are delaminating and failing. This project recommends the replacement of the existing kitchen counter, cabinets, sink and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. This estimate includes disposal of the existing materials. This project or a portion thereof was previously recommended in the FCA report dated 09/01/2015. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/18/2020. | WINNEMUCCA MAIN OFFICE BUILDING | 9909 | Wildlife |  |  | Winnemucca | 1964 | 7900 | 2020-06-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
2439ELE1 | LIGHTING UPGRADE | 2439 | The existing lighting fixtures are the older incandescent type and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. LED are suggested with occupancy sensors for additional savings. Any electrical wiring upgrades are not included in this estimate. | NDOW DRY STORAGE QUONSET | 9909 | Wildlife |  |  | Winnemucca | 1961 | 1640 | 2020-06-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
2433EXT6 | EXTERIOR FINISHES | 2433 | The exterior finishes are in good condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting, and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 8 - 9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | WINNEMUCCA MAIN OFFICE BUILDING | 9909 | Wildlife |  |  | Winnemucca | 1964 | 7900 | 2020-06-18 | Four to Ten Years | Long-Term Needs | 3 | 39500
2433SFT11 | GUARDRAIL REPLACEMENT | 2433 | The guard railing around the rear stairwell is older, non-code compliant in configuration, and due for replacement. A compliant railing is recommended because the elevation change from the walking surface at grade level to the bottom landing of the stairwell exceeds 30 inches. This project recommends the replacement of guard railing to form a protective barrier along the open side in accordance with the 2018 IBC Chapter 10, Section 1015. 20 linear feet was used to generate this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/01/2015. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/18/2020. | WINNEMUCCA MAIN OFFICE BUILDING | 9909 | Wildlife |  |  | Winnemucca | 1964 | 7900 | 2020-06-18 | Immediate to Two Years | Currently Critical | 1 | 2500
2433SFT4 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 2433 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building in 1 location (second location has been completed). This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 09/01/2015. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/18/2020. | WINNEMUCCA MAIN OFFICE BUILDING | 9909 | Wildlife |  |  | Winnemucca | 1964 | 7900 | 2020-06-18 | Immediate to Two Years | Currently Critical | 1 | 5000
2433ELE3 | GFCI OUTLET INSTALLATION | 2433 | The existing receptacles in the kitchen and bathrooms in the lower level appear to be standard duplex receptacles and may not be GFCI protected. The 2017 NEC 210.8 requires all locations within 6 feet of a water source and building exterior shall have GFCI protection. This project would provide for removing the standard receptacles and installing GFCI receptacles. | WINNEMUCCA MAIN OFFICE BUILDING | 9909 | Wildlife |  |  | Winnemucca | 1964 | 7900 | 2020-06-18 | Immediate to Two Years | Currently Critical | 1 | 100
2433SFT13 | FIRE EXTINGUISHER INSTALLATION | 2433 | The single story portion of the building did not have portable fire extinguishers installed at the time of the survey. International Fire Code Section 906 requires that portable fire extinguishers shall be installed in B occupancies. They shall be provided for employee use, selected, and distributed based on the classes of anticipated workplace fires and on the size and degree of hazard which would affect their use. This project would provide funding for the purchase and installation of 4 fire extinguishers, cabinets, and the hardware necessary to install them. | WINNEMUCCA MAIN OFFICE BUILDING | 9909 | Wildlife |  |  | Winnemucca | 1964 | 7900 | 2020-06-18 | Immediate to Two Years | Currently Critical | 1 | 1200
2433INT7 | CARPET INSTALLATION | 2433 | The single story portion of the building has been newly renovated; however, the floors were left as polished concrete. Acoustically, this is a difficult environment to work in due to hard surfaces on the floor, walls and hard-lid ceiling, and lack of sound absorbing materials. To address this issue, it is recommended that carpet or carpet tiles be installed with a high Noise Reduction Coefficient (NRC). | WINNEMUCCA MAIN OFFICE BUILDING | 9909 | Wildlife |  |  | Winnemucca | 1964 | 7900 | 2020-06-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 28100
2433EXT7 | WINDOW REPLACEMENT | 2433 | The windows on the second floor of the two level portion are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 11 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/01/2015. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/18/2020. | WINNEMUCCA MAIN OFFICE BUILDING | 9909 | Wildlife |  |  | Winnemucca | 1964 | 7900 | 2020-06-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8300
2444EXT2 | EXTERIOR FINISHES | 2444 | The exterior finishes are in poor condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting, and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2 - 3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NDOW OFFICE (VACANT) | 9909 | Wildlife |  |  | Winnemucca | 0 | 1440 | 2020-06-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7200
2444EXT3 | CONSERVE AND PROTECT VACANT BUILDING | 2444 | In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to removing water in the basement, providing drainage away from the building to prevent future water accumulation, pest control, and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. | NDOW OFFICE (VACANT) | 9909 | Wildlife |  |  | Winnemucca | 0 | 1440 | 2020-06-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7200
2436INT1 | INTERIOR FINISHES | 2436 | There is a small room in the building that is finished with painted gypsum board. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. This project should be implemented concurrently with the ROOF REPLACEMENT project. | NDOW LEAN-TO STORAGE | 9909 | Wildlife |  |  | Winnemucca | 1955 | 5596 | 2020-06-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
2439ELE2 | GFCI OUTLET INSTALLATION | 2439 | The existing receptacles in the storage building appear to be standard duplex receptacles and may not be GFCI protected. The 2017 NEC 210.8 requires all locations within 6 feet of a water source, garages and accessory buildings, and located outdoors shall have GFCI protection. This project would provide for removing the standard receptacles and installing GFCI receptacles or installing GFCI protected breakers. | NDOW DRY STORAGE QUONSET | 9909 | Wildlife |  |  | Winnemucca | 1961 | 1640 | 2020-06-18 | Immediate to Two Years | Currently Critical | 1 | 500
2439EXT1 | EXTERIOR FINISHES | 2439 | The exterior finishes on the ends of the building are in poor condition. It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the walls and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 2 - 3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NDOW DRY STORAGE QUONSET | 9909 | Wildlife |  |  | Winnemucca | 1961 | 1640 | 2020-06-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8200
2439EXT2 | ROOF REPLACEMENT | 2439 | The corrugated metal roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years, including the fiberglass skylights. This estimate includes removal and disposal of the old roofing system. | NDOW DRY STORAGE QUONSET | 9909 | Wildlife |  |  | Winnemucca | 1961 | 1640 | 2020-06-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 46300
2445ENV1 | OIL WATER SEPARATOR INSTALLATION | 2445 | The existing wash facility adjacent to the maintenance shop currently has a plugged drain and does not have an oil water separator. It is recommended that an oil water separator be installed and the drain restored to bring the wash rack back to full operational capability. Additionally, a backflow preventer should be installed on the wash rack supply line. The estimate is based on work and materials to unplug the drain, to install a 3/4" backflow preventer, and to install a 50 GPM steel oil interceptor. This project or a portion thereof was previously recommended in the FCA report dated 05/11/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/18/2020. | NDOW SHOP | 9909 | Wildlife |  |  | Winnemucca | 1984 | 1260 | 2020-06-18 | Immediate to Two Years | Currently Critical | 1 | 18000
9909ENR1 | EXTERIOR SITE LIGHTING REPLACEMENT | 9909 | The site lighting uses old style mercury lamps. It is recommended that these light fixtures be replaced with new, LED light fixtures to improve lighting and efficiency. This project would provide for the replacement of the existing light fixtures with new LED light fixtures and lamps, using existing wiring and poles. | WINNEMUCCA SITE | 9909 | Wildlife |  |  | Winnemucca | 0 |  | 2020-06-18 | Four to Ten Years | Long-Term Needs | 3 | 3000
9909SIT7 | CONCRETE APRON REPLACEMENT | 9909 | The concrete entrances to the parking lot of the Winnemucca Main Office Building has extensive cracking and spalling and is due for replacement. This project would provide for the installation of a new concrete slab-on-grade driveway at the entrances to the parking lot. Removal and disposal of the existing concrete is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 05/11/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/18/2020. | WINNEMUCCA SITE | 9909 | Wildlife |  |  | Winnemucca | 0 |  | 2020-06-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
9909SIT6 | CHAIN LINK FENCE REPLACEMENT | 9909 | Portions of the chain link fencing around the site have failed and some portions are in need of substantial repair. This project recommends the installation of a 6 foot high, 6 gauge wire perimeter chain link fence to replace the existing fence with two 14' wide gates with hardware. The cost estimate also includes demolition and disposal of the existing fence. This project or a portion thereof was previously recommended in the FCA report dated 05/11/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/18/2020. | WINNEMUCCA SITE | 9909 | Wildlife |  |  | Winnemucca | 0 |  | 2020-06-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 70000
9909SIT5 | SLURRY SEAL ASPHALT PAVING | 9909 | It is important to maintain the asphalt concrete paving for the site parking lots. This project would provide for minor crack filling and slurry sealing of the paving . Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 40,000 square feet of asphalt area was used to generate this estimate. This project or a portion thereof was previously recommended in the FCA report dated 05/11/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/18/2020. | WINNEMUCCA SITE | 9909 | Wildlife |  |  | Winnemucca | 0 |  | 2020-06-18 | Four to Ten Years | Long-Term Needs | 3 | 62800